## Sheet1
Base Standard Version | Standard Number | Requirement Number | Standard Title | Standard Purpose | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Enforcement (Current, Adopted by Board or FERC-approved, Regional, will retire, CIP) Note: current includes w/b in 2013 | Status of Standard | In Current Project | Suggestions for Improvements | In Para 81 Phase 1 | Para 81 List of candidates (Phase 1 remainders and Phase 2) | Why was this Para 81 candidate not included for deletion? | Supports a Reliability Objective (as defined by the Reliability Principles) (Yes/No/Maybe) | Para 81 Retire requirement? | Appropriate as a guide rather than a standard? | Why should this requirement be retired under Para 81 or is it better as a guide? | Technical Justification for N, O or Q | Is everything covered? | Are the correct Functional Entities Identified? | Does the content seem to be technically correct? (Including correct level of actions for accountability - Who, What, When) | Should it be kept as it is and not consolidated with other standards/requirements? | Is it RBS format? Drafted as one of these requirement types: Performance, Risk-based (preventative), Capability, & Format for subparts | Is it technology neutral? (Yes/No) | Applicability - are the expectations for each function clear? | Does the requirement align with the Purpose? | Is it a higher solution than the lowest common denominator (considering cost)? | Measurability? | Technical basis in engineering and operations? | Complete? Self-contained? | Clear language? Is RRO clarified? | Can it be practically implemented? | Consistent Terminology? | Passed the Reliability Principle test? | Passed the Para 81 or Guide test? | Content Score 0-3 | Quality Score 0-12 | RISC (urgency) High, Medium or Low | IE top 16 priority standards to improve? | Identified as one of the key impactful requirements (high is whatever top #) | Violation Risk Factor | BA | DP | GO | GOP | IA | LSE | NERC | PA | PC | PSE | RC | RE | RP | RRO | RSG | TO | TOP | TP | TSP | NERC_Net
BAL-001-0 | BAL-001-0.1a | R1. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit  is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. See Standard for Formula. | Current - will be replaced by Board adopted std | Board adoption 12/19/2012 Will be replaced with BAL-001 if FERC approves. |  |  |  | Yes |  | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes could be loosened which would make it lowest common denominator and reduce cost | Yes | Yes | No - dependent upon BAL-003 which defines bias | No - doesn't specify CPS1. Should sign convention on bias be addressed? | Yes | No bias (B) vs Frequency Response (Greek letter beta β). | Yes | Yes | 3 | 9 | Medium |  | Medium | Medium | BA
BAL-001-0 | BAL-001-0.1a | R2. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. See Standard for Formula. | Current - will be replaced by Board adopted std | Board adoption 12/19/2012 Will be replaced with BAL-001 if FERC approves. |  |  |  | Yes |  | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes could be loosened which would make it lowest common denominator and reduce cost | Yes | Yes | No - dependent upon BAL-003 which defines bias | No - doesn't specify CPS2. Should sign convention on bias be addressed? | Yes | No bias (B) vs Frequency Response (Greek letter beta β). | Yes | Yes | 3 | 9 | Medium |  | High | Medium | BA
BAL-001-0 | BAL-001-0.1a | R3. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | Current - will be replaced by Board adopted std | Board adoption 12/19/2012 Will be replaced with BAL-001 if FERC approves. |  |  |  | Yes |  | No - This is a defintion. Definition needs tweaking | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower | BA
BAL-001-0 | BAL-001-0.1a | R4. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | Current - will be replaced by Board adopted std | Board adoption 12/19/2012 Will be replaced with BAL-001 if FERC approves. |  |  |  | Yes |  | No - Overlap Regulation Service is a Definition | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower | BA
BAL-001-1 | BAL-001-1 | R1. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority shall operate such that, on a rolling 12-month basis, the average of the clock-minute averages of the Balancing Authority’s Area Control Error (ACE) divided by 10B (B is the clock-minute average of the Balancing Authority Area’s Frequency Bias) times the corresponding clock-minute averages of the Interconnection’s Frequency Error is less than a specific limit. This limit is a constant derived from a targeted frequency bound (separately calculated for each Interconnection) that is reviewed and set as necessary by the NERC Operating Committee. (See Standard for Formula). | Board Adopted | Board adopted 12/2012 but not approved by FERC or provinces | Yes - Project 2010-14.1 BARC Phase 1 |  |  |  |  | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - dependent upon BAL-003 which defines bias | No - doesn't specify CPS1. Should sign convention on bias be addressed? | Yes | No bias (B) vs Frequency Response (Greek letter beta β). | Yes | Yes | 3 | 9 | Medium |  | Medium | Medium | BA
BAL-001-1 | BAL-001-1 | R2. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority shall operate such that its average ACE for at least 90% of clock-ten-minute periods (6 non-overlapping periods per hour) during a calendar month is within a specific limit, referred to as L10. (See Standard for Formula) | Board Adopted | Board adopted 12/2012 but not approved by FERC or provinces | Yes - Project 2010-14.1 BARC Phase 1 |  |  |  |  | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes could be loosened which would make it lowest common denominator and reduce cost | Yes | Yes | No - dependent upon BAL-003 which defines bias | No - doesn't specify CPS2. Should sign convention on bias be addressed? | Yes | No bias (B) vs Frequency Response (Greek letter beta β). | Yes | Yes | 3 | 9 | Medium |  | High | Medium | BA
BAL-001-1 | BAL-001-1 | R3. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Each Balancing Authority providing Overlap Regulation Service shall evaluate Requirement R1 (i.e., Control Performance Standard 1 or CPS1) and Requirement R2 (i.e., Control Performance Standard 2 or CPS2) using the characteristics of the combined ACE and combined Frequency Bias Settings. | Board Adopted | Board adopted 12/2012 but not approved by FERC or provinces | Yes - Project 2010-14.1 BARC Phase 1 | Definition in Glossary of Overlap Regulation Service needs to be updated to cover R3 and R4 implementation |  |  |  | No - Overlap Regulation Service is a Definition | [19 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-001-1 | BAL-001-1 | R4. | Real Power Balancing Control Performance | To maintain Interconnection steady-state frequency within defined limits by balancing real power demand and supply in real-time. | Any Balancing Authority receiving Overlap Regulation Service shall not have its control performance evaluated (i.e. from a control performance perspective, the Balancing Authority has shifted all control requirements to the Balancing Authority providing Overlap Regulation Service). | Board Adopted | Board adopted 12/2012 but not approved by FERC or provinces | Yes - Project 2010-14.1 BARC Phase 1 | Definition in Glossary of Overlap Regulation Service needs to be updated to cover R3 and R4 implementation |  |  |  | No - Overlap Regulation Service is a Definition | [19 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-002-1 | BAL-002-1a | R1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | Each Balancing Authority shall have access to and/or operate Contingency Reserve to respond to Disturbances. Contingency Reserve may be supplied from generation, controllable load resources, or coordinated adjustments to Interchange Schedules. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | Yes - #2 | No | No |  |  | No - in order to understand requirement, you must read section 1.5, Additional Compliance Information, as well as the interpretation (R1.1) (which is pending FERC approval). Therefore, standard is not clear. | Yes | No - hard to tell. See gap comments. | No | No | Yes | No | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | 1 | 5 | Medium | Yes | High | High | BA
BAL-002-1 | BAL-002-1a | R1.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | No - not needed as RSG is in compliance registry | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | High | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R2. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | Each Regional Reliability Organization, sub-Regional Reliability Organization or Reserve Sharing Group shall specify its Contingency Reserve policies, including: | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | Yes - #2 | No | No |  |  | No - the policy needs to address the transmission availability to deliver reserves. Needs to address liability within a RSG (jointly, severally, proportionately) Procedure needs to be provided to all affected parties. | Yes | No - see "gap" comments | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Medium | Yes | HIgh | Medium | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The minimum reserve requirement for the group. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | HIgh | High | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.2. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | Its allocation among members. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | HIgh | Lower | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.3. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | HIgh | Lower | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.4. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The procedure for applying Contingency Reserve in practice. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - word "apply" is not clear - perhaps "activate" as in R3 of this std | Yes | Yes | Yes | Yes | 3 | 10 | Medium |  | HIgh | Lower | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.5. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The limitations, if any, upon the amount of interruptible load that may be included. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | HIgh | Lower | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R2.6. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | No | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | HIgh | Medium | [13 empty] | RRO | RSG
BAL-002-1 | BAL-002-1a | R3. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | Each Balancing Authority or Reserve Sharing Group shall activate sufficient Contingency Reserve to comply with the DCS. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium | Yes | High | High | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R3.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No - annually needs to be defined | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | Medium |  | High | High | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R4. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | A Balancing Authority or Reserve Sharing Group shall meet the Disturbance Recovery Criterion within the Disturbance Recovery Period for 100% of Reportable Disturbances. The Disturbance Recovery Criterion is: | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | Yes - #2 | No | No |  |  | No - too much pertinent information is in "additional Compliance Information" section | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 2 | 9 | Medium | Yes | High | Medium | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R4.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | No - too much pertinent information is in "additional Compliance Information" section | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 2 | 9 | Medium |  | High | Medium | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R4.2. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | No - this is a definition and is drafted as a statement; "default" is not clear. Needs to be drafted as a requirement - i.e."An entity shall recover within 15 min." and/or the definition needs to be included as a definition | Yes | Yes | Yes | No | Yes | No - default is not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | Medium |  | High | No Individual VRF Assigned | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R5. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | Each Reserve Sharing Group shall comply with the DCS. A Reserve Sharing Group shall be considered in a Reportable Disturbance condition whenever a group member has experienced a Reportable Disturbance and calls for the activation of Contingency Reserves from one or more other group members. (If a group member has experienced a Reportable Disturbance but does not call for reserve activation from other members of the Reserve Sharing Group, then that member shall report as a single Balancing Authority.) Compliance may be demonstrated by either of the following two methods: | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | No | No | [6 empty] | No | [11 empty] | No |  | 0 | 0 | Medium | Yes | N/A | Lower | [14 empty] | RSG
BAL-002-1 | BAL-002-1a | R5.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | No | No | Yes | [5 empty] | No | [11 empty] | No |  | 0 | 0 | Medium |  | N/A | No Individual VRF Assigned | [14 empty] | RSG
BAL-002-1 | BAL-002-1a | R5.2. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | No | No | Yes | [5 empty] | No | [11 empty] | No |  | 0 | 0 | Medium |  | N/A | No Individual VRF Assigned | [14 empty] | RSG
BAL-002-1 | BAL-002-1a | R6. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | A Balancing Authority or Reserve Sharing Group shall fully restore its Contingency Reserves within the Contingency Reserve Restoration Period for its Interconnection. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | Yes - Project 2010-14.1 BARC Phase 1 (BAL-002-2, BAL-013-1) |  |  |  |  | Yes - #2 | No | No |  |  | No - too much pertinent information is in "additional Compliance Information" section | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 2 | 9 | Medium | Yes | High | Medium | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R6.1. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | No - too much pertinent information is in "additional Compliance Information" section | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 2 | 9 | Medium |  | High | No Individual VRF Assigned | BA | [13 empty] | RSG
BAL-002-1 | BAL-002-1a | R6.2. | Disturbance Control Performance | The purpose of the Disturbance Control Standard (DCS) is to ensure the Balancing Authority is able to utilize its Contingency Reserve to balance resources and demand and return Interconnection frequency within defined limits following a Reportable Disturb | The default Contingency Reserve Restoration Period is 90 minutes. | Current | BAL-002-1 is the current standard. BAL-002-1a is an interpretation that the Board adopted 11/2012; Filed with FERC 2/2013. | [5 empty] | Yes - #2 | No | No |  |  | No - this is a definition and is drafted as a statement; "default" is not clear. Needs to be drafted as a requirement - i.e."An entity shall recover within 15 min." and/or the definition needs to be included as a definition | Yes | Yes | Yes | No | Yes | No - default is not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | Medium |  | High | No Individual VRF Assigned | BA | [13 empty] | RSG
BAL-003-0 | BAL-003-0.1b | R1. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Each Balancing Authority shall review its Frequency Bias Settings by January 1 of each year and recalculate its setting to reflect any change in the Frequency Response of the Balancing Authority Area. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. Should GO's and GOPs be covered under this std? Where in the NERC stds is the requirement for a generator to set its governor to provide frequency response? Should Frequency Response Sharing Groups be included? | No - Does not include GO's/GOP's. | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 11 | Medium |  | High | Lower | BA
BAL-003-0 | BAL-003-0.1b | R1.1. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. Should GO's and GOPs be covered under this std? Where in the NERC stds is the requirement for a generator to set its governor to provide frequency response? Should Frequency Response Sharing Groups be included? | No - Does not include GO's/GOP's. | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 11 | Medium |  | High | Lower | BA
BAL-003-0 | BAL-003-0.1b | R1.2. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. Should GO's and GOPs be covered under this std? Where in the NERC stds is the requirement for a generator to set its governor to provide frequency response? Should Frequency Response Sharing Groups be included? | No - Does not include GO's/GOP's. | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 11 | Medium |  | High | Lower | BA
BAL-003-0 | BAL-003-0.1b | R2. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Each Balancing Authority shall establish and maintain a Frequency Bias Setting that is as close as practical to, or greater than, the Balancing Authority’s Frequency Response. Frequency Bias may be calculated several ways: | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | Medium |  | Medium | Medium | BA
BAL-003-0 | BAL-003-0.1b | R2.1. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | Medium |  | Medium | Lower | BA
BAL-003-0 | BAL-003-0.1b | R2.2. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - no technical basis. | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | No - no technical basis. | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | Medium |  | Medium | Lower | BA
BAL-003-0 | BAL-003-0.1b | R3. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Frequency Bias, unless such operation is adverse to system or Interconnection reliability. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | Medium | Medium | BA
BAL-003-0 | BAL-003-0.1b | R4. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
BAL-003-0 | BAL-003-0.1b | R4.1. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. See Standard for Graphic. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
BAL-003-0 | BAL-003-0.1b | R4.2. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. See Standard for Graphic. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
BAL-003-0 | BAL-003-0.1b | R5. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Balancing Authorities that serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of the Balancing Authority’s estimated yearly peak demand per 0.1 Hz change. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - not a technical basis | Yes | No - not a technical basis | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Medium |  | Medium | Medium | BA
BAL-003-0 | BAL-003-0.1b | R5.1. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | No |  |  | No - not a technical basis | Yes | No - not a technical basis | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Medium |  | Medium | Medium | BA
BAL-003-0 | BAL-003-0.1b | R6. | Frequency Response and Bias | This standard provides a consistent method for calculating the Frequency Bias component of ACE. | A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority shall not change its Frequency Bias Setting when performing Supplemental Regulation Service. | Current - will be replaced by Board adopted std | will be replaced with BAL-003-1 | [5 empty] | Yes - #2 | No | Yes | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Medium | BA
BAL-003-1 | BAL-003-1 | R1. | Frequency Response and Frequency Bias Setting | To require sufficient Frequency Response from the Balancing Authority (BA) to maintain Interconnection Frequency within predefined bounds by arresting frequency deviations and supporting frequency until the frequency is restored to its scheduled value. T | Each Frequency Response Sharing Group (FRSG) or Balancing Authority that is not a member of a FRSG shall achieve an annual Frequency Response Measure (FRM) (as calculated and reported in accordance with Attachment A) that is equal to or more negative than its Frequency Response Obligation (FRO) to ensure that sufficient Frequency Response is provided by each FRSG or BA that is not a member of a FRSG to maintain Interconnection Frequency Response equal to or more negative than the Interconnection Frequency Response Obligation. | Board Adopted | Board adopted 2/2013 Not Filed with FERC | [5 empty] | Yes - #2 | No | No |  |  | No - should GO's and GOPs be covered under this std? Where in the NERC stds is the requirement for a generator to set its governor to provide frequency response? | No - Frequency Response Sharing Groups are included, but are not on the compliance registry | Yes | Yes | Yes | Yes | No - Frequency Response Sharing Groups are included, but are not on the compliance registry | No - There is no where in the stds that requires an GO to provide governor response. | Yes | Yes | Yes | Yes | No - language is hard to read | Yes | Yes | Yes | Yes | 1 | 9 | Medium |  | High |  | BA
BAL-003-1 | BAL-003-1 | R2. | Frequency Response and Frequency Bias Setting | To require sufficient Frequency Response from the Balancing Authority (BA) to maintain Interconnection Frequency within predefined bounds by arresting frequency deviations and supporting frequency until the frequency is restored to its scheduled value. T | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and uses a fixed Frequency Bias Setting shall implement the Frequency Bias Setting determined in accordance with Attachment A, as validated by the ERO, into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and shall use this Frequency Bias Setting until directed to change by the ERO. | Board Adopted | Board adopted 2/2013 Not Filed with FERC | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | Medium |  | BA
BAL-003-1 | BAL-003-1 | R3. | Frequency Response and Frequency Bias Setting | To require sufficient Frequency Response from the Balancing Authority (BA) to maintain Interconnection Frequency within predefined bounds by arresting frequency deviations and supporting frequency until the frequency is restored to its scheduled value. T | Each Balancing Authority that is a member of a multiple Balancing Authority Interconnection and is not receiving Overlap Regulation Service and is utilizing a variable Frequency Bias Setting shall maintain a Frequency Bias Setting that is: 1.1 Less than zero at all times, and 1.2 Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. | Board Adopted | Board adopted 2/2013 Not Filed with FERC | [5 empty] | Yes - #2 | No | No |  |  | Yes - note: AGC is covered in BAL-005-0.2b R6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | Medium |  | BA
BAL-003-1 | BAL-003-1 | R4. | Frequency Response and Frequency Bias Setting | To require sufficient Frequency Response from the Balancing Authority (BA) to maintain Interconnection Frequency within predefined bounds by arresting frequency deviations and supporting frequency until the frequency is restored to its scheduled value. T | Each Balancing Authority that is performing Overlap Regulation Service shall modify its Frequency Bias Setting in its ACE calculation, in order to represent the Frequency Bias Setting for the combined Balancing Authority Area, to be equivalent to either: • The sum of the Frequency Bias Settings as shown on FRS Form 1 and FRS Form 2 for the participating Balancing Authorities as validated by the ERO, or • The Frequency Bias Setting shown on FRS Form 1 and FRS Form 2 for the entirety of the participating Balancing Authorities’ Areas. | Board Adopted | Board adopted 2/2013 Not Filed with FERC | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes, but there is a numbering issue with points | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - unclear on difference between 2 sub-bullets | No - unclear on difference between 2 sub-bullets | Yes | Yes | Yes | 3 | 10 | Medium |  | Medium |  | BA
BAL-004-0 | BAL-004-0 | R1. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | Only a Reliability Coordinator shall be eligible to act as Interconnection Time Monitor. A single Reliability Coordinator in each Interconnection shall be designated by the NERC Operating Committee to serve as Interconnection Time Monitor. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | [10 empty] | RC
BAL-004-0 | BAL-004-0 | R2. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | The Interconnection Time Monitor shall monitor Time Error and shall initiate or terminate corrective action orders in accordance with the NAESB Time Error Correction Procedure. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | [10 empty] | RC
BAL-004-0 | BAL-004-0 | R3. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods: | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Medium | BA
BAL-004-0 | BAL-004-0 | R3.1. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-004-0 | BAL-004-0 | R3.2. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-004-0 | BAL-004-0 | R4. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | Any Reliability Coordinator in an Interconnection shall have the authority to request the Interconnection Time Monitor to terminate a Time Error Correction in progress, or a scheduled Time Error Correction that has not begun, for reliability considerations. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | [10 empty] | RC
BAL-004-0 | BAL-004-0 | R4.1. | Time Error Correction | The purpose of this standard is to ensure that Time Error Corrections are conducted in a manner that does not adversely affect the reliability of the Interconnection. | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R1. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Each BA that operates synchronously to the Western Interconnection shall continuously operate utilizing Automatic Time Error Correction (ATEC) in its Automatic Generation Control (AGC) system. See Standard for Formula | Regional |  |  | This is an equity issue, but there is not another vehicle for WECC to impose the requirement. |  |  |  | No - Continent wide said "no". This appears to be larger than WECC, but was not adopted in other regions. Version 2 | [23 empty] | Not ranked |  | Low | Lower | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R1.2. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Large accumulations of primary inadvertent point to an invalid implementation of ATEC, loose control, metering or accounting errors. A BA in such a situation should identify the source of the error(s) and make the corrections, recalculate the primary inadvertent from the time of the error, adjust the accumulated primary inadvertent caused by the error(s), validate the implementation of ATEC, set Lmax equal to L10 and continue to operate with ATEC reducing the accumulation as system parameters allow. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R2. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Each BA that is synchronously connected to the Western Interconnection and operates in any AGC operating mode other than ATEC shall notify all other BAs of its operating mode through the designated Interconnection communication system. Each BA while synchronously connected to the Western Interconnection will be allowed to have ATEC out of service for a maximum of 24 hours per calendar quarter, for reasons including maintenance and testing. | Regional | [30 empty] | Not ranked |  |  | Lower | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R3. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | BAs in the Western Interconnection shall be able to change their AGC operating mode between Flat Frequency (for blackout restoration); Flat Tie Line (for loss of frequency telemetry); Tie Line Bias; Tie Line Bias plus Time Error control (used in ATEC mode). The ACE used for NERC reports shall be the same ACE as the AGC operating mode in use. | Regional | [30 empty] | Not ranked |  |  | Lower | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R4. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Regardless of the AGC operating mode each BA in the Western Interconnection shall compute its hourly Primary Inadvertent Interchange when hourly checkout is complete. If hourly checkout is not complete by 50 minutes after the hour, compute Primary Inadvertent Interchange with best available data. This hourly value shall be added to the appropriate accumulated Primary Inadvertent Interchange balance for either On-Peak or Off-Peak periods. | Regional | [30 empty] | Not ranked |  |  | Lower | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R4.1. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Each BA in the Western Interconnection shall use the change in Time Error distributed by the Interconnection Time Monitor. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R4.2. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | All corrections to any previous hour Primary Inadvertent Interchange shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R4.3. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Month end Inadvertent Adjustments are 100% Primary Inadvertent Interchange and shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange, unless such adjustments can be pinpointed to specific hours in which case R4.2 applies. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | BA
BAL-004-WECC-01 | BAL-004-WECC-01 | R4.4. | Automatic Time Error Correction | To maintain Interconnection frequency within a predefined frequency profile under all conditions (i.e. normal and abnormal), and to ensure that Time Error Corrections are effectively conducted in a manner that does not adversely affect the reliability of | Each BA in the Western Interconnection shall synchronize its Time Error to the nearest 0.001 seconds of the system Time Error by comparing its reading at the designated time each day to the reading broadcast by the Interconnection Time Monitor. Any difference shall be applied as an adjustment to its current Time Error. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | BA
BAL-005-0 | BAL-005-0.2b | R1. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | Current | Current standard; no changes pending |  |  |  | Yes BAL-005-0.1b | Team determined entities need a plan | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned |  |  |  | GOP |  | LSE | [10 empty] | TOP
BAL-005-0 | BAL-005-0.2b | R1.1. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. | Current | Current standard; no changes pending | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium |  |  |  | GOP
BAL-005-0 | BAL-005-0.2b | R1.2. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. | Current | Current standard; no changes pending | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | [16 empty] | TOP
BAL-005-0 | BAL-005-0.2b | R1.3. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. | Current | Current standard; no changes pending | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | [5 empty] | LSE
BAL-005-0 | BAL-005-0.2b | R2. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Balancing Authority shall maintain Regulating Reserve that can be controlled by AGC to meet the Control Performance Standard. | Current | Current standard; no changes pending |  |  | Yes |  |  | Yes | Yes - Para 81 Phase 1 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | BA
BAL-005-0 | BAL-005-0.2b | R3. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | A Balancing Authority providing Regulation Service shall ensure that adequate metering, communications, and control equipment are employed to prevent such service from becoming a Burden on the Interconnection or other Balancing Authority Areas. | Current | Current standard; no changes pending | [5 empty] | Yes - #2, 5 | Yes - duplicative of R1 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R4. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | A Balancing Authority providing Regulation Service shall notify the Host Balancing Authority for whom it is controlling if it is unable to provide the service, as well as any Intermediate Balancing Authorities. | Current | Current standard; no changes pending | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes - but is very limited in scope (number of times that it would be used) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium | BA
BAL-005-0 | BAL-005-0.2b | R5. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | A Balancing Authority receiving Regulation Service shall ensure that backup plans are in place to provide replacement Regulation Service should the supplying Balancing Authority no longer be able to provide this service. | Current | Current standard; no changes pending | [5 empty] | Yes - #3 | No | No |  |  | No - does not specify what should be included in the back-up plan | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Medium | BA
BAL-005-0 | BAL-005-0.2b | R6. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority’s AGC shall compare total Net Actual Interchange to total Net Scheduled Interchange plus Frequency Bias obligation to determine the Balancing Authority’s ACE. Single Balancing Authorities operating asynchronously may employ alternative ACE calculations such as (but not limited to) flat frequency control. If a Balancing Authority is unable to calculate ACE for more than 30 minutes it shall notify its Reliability Coordinator. | Current | Current standard; no changes pending | [5 empty] | Yes - #2, 3 | No | No |  |  | Yes | Yes | No - check 30 min; seems too long (5-10 may be more appropriate) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | Medium | Medium | BA
BAL-005-0 | BAL-005-0.2b | R7. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall operate AGC continuously unless such operation adversely impacts the reliability of the Interconnection. If AGC has become inoperative, the Balancing Authority shall use manual control to adjust generation to maintain the Net Scheduled Interchange. | Current | Current standard; no changes pending | [5 empty] | Yes - #2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No - legacy language ("adversely impacts the reliability"…suggest replacing it with Adverse Reliability Impact) | No | Yes | Yes | Yes | 3 | 9 | High |  | Medium | Medium | BA
BAL-005-0 | BAL-005-0.2b | R8. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall ensure that data acquisition for and calculation of ACE occur at least every six seconds. | Current | Current standard; no changes pending | [5 empty] | Yes - #2, 5 | Yes - outdated due to technology | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R8.1. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. | Current | Current standard; no changes pending | [5 empty] | Yes - #2, 5 | Yes - outdated due to technology | [6 empty] | No - Six seconds is questionable | [11 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R9. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall include all Interchange Schedules with Adjacent Balancing Authorities in the calculation of Net Scheduled Interchange for the ACE equation. | Current | Current standard; no changes pending | [5 empty] | Yes | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | BA
BAL-005-0 | BAL-005-0.2b | R9.1. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. | Current | Current standard; no changes pending | [5 empty] | Yes | Yes | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | BA
BAL-005-0 | BAL-005-0.2b | R10. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall include all Dynamic Schedules in the calculation of Net Scheduled Interchange for the ACE equation. | Current | Current standard; no changes pending | [5 empty] | Yes | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | BA
BAL-005-0 | BAL-005-0.2b | R11. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Balancing Authorities shall include the effect of ramp rates, which shall be identical and agreed to between affected Balancing Authorities, in the Scheduled Interchange values to calculate ACE. | Current | Current standard; no changes pending |  |  |  | Yes BAL-005-0.1b |  | Yes | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R12. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Balancing Authority shall include all Tie Line flows with Adjacent Balancing Authority Areas in the ACE calculation. | Current | Current standard; no changes pending |  | Guide, or combine with BAL-001 |  |  |  | Yes | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R12.1. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to Boardh control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. | Current | Current standard; no changes pending |  | Guide, or combo with BAL-001 |  |  |  | Yes | Yes | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | BA
BAL-005-0 | BAL-005-0.2b | R12.2. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. | Current | Current standard; no changes pending |  | Guide, or combo with BAL-001 |  |  |  | Yes | Yes | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R12.3. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. | Current | Current standard; no changes pending |  | Guide, or combo with BAL-001 |  |  |  | Yes | Yes | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R13. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Balancing Authority shall perform hourly error checks using Tie Line megawatt-hour meters with common time synchronization to determine the accuracy of its control equipment. The Balancing Authority shall adjust the component (e.g., Tie Line meter) of ACE that is in error (if known) or use the interchange meter error (IME) term of the ACE equation to compensate for any equipment error until repairs can be made. | Current | Current standard; no changes pending | [5 empty] | Yes | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | BA
BAL-005-0 | BAL-005-0.2b | R14. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall provide its operating personnel with sufficient instrumentation and data recording equipment to facilitate monitoring of control performance, generation response, and after-the-fact analysis of area performance. As a minimum, the Balancing Authority shall provide its operating personnel with real-time values for ACE, Interconnection frequency and Net Actual Interchange with each Adjacent Balancing Authority Area. | Current | Current standard; no changes pending | [5 empty] | Yes - #5 | No | No |  |  | No - operating personnel are not defined | Yes | Yes | Yes | Yes | Yes | No - words are vague "sufficient", "at a minimum" | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Lower | BA
BAL-005-0 | BAL-005-0.2b | R15. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall provide adequate and reliable backup power supplies and shall periodically test these supplies at the Balancing Authority’s control center and other critical locations to ensure continuous operation of AGC and vital data recording equipment during loss of the normal power supply. | Current | Current standard; no changes pending | [5 empty] | Yes - #5 | No | No |  |  | Yes - but legacy language is not clear | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | High |  | Medium | Lower | BA
BAL-005-0 | BAL-005-0.2b | R16. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | The Balancing Authority shall sample data at least at the same periodicity with which ACE is calculated. The Balancing Authority shall flag missing or bad data for operator display and archival purposes. The Balancing Authority shall collect coincident data to the greatest practical extent, i.e., ACE, Interconnection frequency, Net Actual Interchange, and other data shall all be sampled at the same time. | Current | Current standard; no changes pending | [5 empty] | No | [19 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | BA
BAL-005-0 | BAL-005-0.2b | R17. | Automatic Generation Control | This standard establishes requirements for Balancing Authority Automatic Generation Control (AGC) necessary to calculate Area Control Error (ACE) and to routinely deploy the Regulating Reserve. The standard also ensures that all facilities and load electr | Each Balancing Authority shall at least annually check and calibrate its time error and frequency devices against a common reference. The Balancing Authority shall adhere to the minimum values for measuring devices as listed below: See Standard for Values | Current | Current standard; no changes pending | [5 empty] | Yes - #5 | No | No |  |  | No - legacy language. Today's technology is advanced beyond this need. | Yes | No - out of date | Yes | Yes | Yes | No - "annually" is in the std | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 7 | High |  | Low | Medium | BA
BAL-006-2 | BAL-006-2 | R1. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Each Balancing Authority shall calculate and record hourly Inadvertent Interchange. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R2. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Each Balancing Authority shall include all AC tie lines that connect to its Adjacent Balancing Authority Areas in its Inadvertent Interchange account. The Balancing Authority shall take into account interchange served by jointly owned generators. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R3. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Each Balancing Authority shall ensure all of its Balancing Authority Area interconnection points are equipped with common megawatt-hour meters, with readings provided hourly to the control centers of Adjacent Balancing Authorities. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Adjacent Balancing Authority Areas shall operate to a common Net Interchange Schedule and Actual Net Interchange value and shall record these hourly quantities, with like values but opposite sign. Each Balancing Authority shall compute its Inadvertent Interchange based on the following: | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4.1. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4.1.1. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | The hourly values of Net Interchange Schedule. | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4.1.2. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | The hourly integrated megawatt-hour values of Net Actual Interchange. | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4.2. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R4.3. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). | Current | Current standard; no changes pending | [5 empty] | No |  | Yes | [17 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-006-2 | BAL-006-2 | R5. | Inadvertent Interchange | This standard defines a process for monitoring Balancing Authorities to ensure that, over the long term, Balancing Authority Areas do not excessively depend on other Balancing Authority Areas in the Interconnection for meeting their demand or Interchange | Adjacent Balancing Authorities that cannot mutually agree upon their respective Net Actual Interchange or Net Scheduled Interchange quantities by the 15th calendar day of the following month shall, for the purposes of dispute resolution, submit a report to their respective Regional Reliability Organization Survey Contact. The report shall describe the nature and the cause of the dispute as well as a process for correcting the discrepancy. | Current | Current standard; no changes pending |  |  |  | Yes |  | No | [19 empty] | No | Yes | 0 | 0 | Not ranked |  | N/A | Lower | BA
BAL-502-RFC-02 | BAL-502-RFC-02 | R1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | The Planning Coordinator shall perform and document a Resource Adequacy analysis annually. The Resource Adequacy analysis shall: | Regional |  |  | Similar to WECC Bal-004 |  |  |  | Yes | No | yes | [21 empty] | Not ranked |  |  | Medium | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.1.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.1.2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median forecast peak Net Internal Demand (planning reserve margin). | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Be performed or verified separately for each of the following planning years: | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.2.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Perform an analysis for Year One. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.2.2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.2.2.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Include the following subject matter and documentation of its use: | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Load forecast characteristics: - Median (50:50) forecast peak Load. - Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). - Load diversity. - Seasonal Load variations. - Daily demand modeling assumptions (firm, interruptible). - Contractual arrangements concerning curtailable/Interruptible Demand. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3.2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Resource characteristics: - Historic resource performance and any projected changes - Seasonal resource ratings - Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. - Resource planned outage schedules, deratings, and retirements. - Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration - Criteria for including planned resource additions in the analysis | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3.3. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Transmission limitations that prevent the delivery of generation reserves | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3.3.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Criteria for including planned Transmission Facility additions in the analysis | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.3.4. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.4. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: - Availability and deliverability of fuel. - Common mode outages that affect resource availability - Environmental or regulatory restrictions of resource availability. - Any other demand (Load) response programs not included in R1.3.1. - Sensitivity to resource outage rates. - Impacts of extreme weather/drought conditions that affect unit availability. - Modeling assumptions for emergency operation procedures used to make reserves available. - Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.5. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.6. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R1.7. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | The Planning Coordinator shall annually document the projected Load and resource capability, for each area or Transmission constrained sub-area identified in the Resource Adequacy analysis | Regional | [30 empty] | Not ranked |  |  | Lower | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R2.1. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | This documentation shall cover each of the years in Year One through ten. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R2.2. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | This documentation shall include the planning reserve margin calculated per requirement R1.1 for each of the three years in the analysis. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-502-RFC-02 | BAL-502-RFC-02 | R2.3. | Planning Resource Adequacy Analysis, Assessment and Documentation | To establish common criteria, based on “one day in ten year” loss of Load expectation principles, for the analysis, assessment and documentation of Resource Adequacy for Load in the ReliabilityFirst Corporation (RFC) region | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned | [7 empty] | PA | PC
BAL-STD-002-0 | BAL-STD-002-0 | WR1. | Operating Reserves (WECC) | Regional Reliability Standard to address the Operating Reserve requirements of the Western Interconnection. | The reliable operation of the interconnected power system requires that adequate generating capacity be available at all times to maintain scheduled frequency and avoid loss of firm load following transmission or generation contingencies. This generating capacity is necessary to: supply requirements for load variations. replace generating capacity and energy lost due to forced outages of generation or transmission equipment. meet on-demand obligations. replace energy lost due to curtailment of interruptible imports. a. Minimum Operating Reserve. Each Balancing Authority shall maintain minimum Operating Reserve which is the sum of the following: (i) Regulating reserve. Sufficient Spinning Reserve, immediately responsive to Automatic Generation Control (AGC) to provide sufficient regulating margin to allow the Balancing Authority to meet NERC’s Control Performance Criteria (see BAL-001-0). (ii) Contingency reserve. An amount of Spinning Reserve and Nonspinning Reserve (at least half of which must be Spinning Reserve), sufficient to meet the NERC Disturbance Control Standard BAL-002-0, equal to the greater of: (a) The loss of generating capacity due to forced outages of generation or transmission equipment that would result from the most severe single contingency; or (b) The sum of five percent of the load responsibility served by hydro generation and seven percent of the load responsibility served by thermal generation. generating capacity must be capable of responding to the Spinning Reserve requirement of that Balancing Authority within ten minutes (iii) Additional reserve for interruptible imports. An amount of reserve, which can be made effective within ten minutes, equal to interruptible imports. (iv) Additional reserve for on-demand obligations. An amount of reserve, which can be made effective within ten minutes, equal to on-demand obligations to other entities or Balancing Authorities. b. Acceptable types of Nonspinning Reserve. The Nonspinning Reserve obligations identified in subsections a(ii), a(iii), and a(iv), if any, can be met by use of the following: (i) interruptible load; (ii) interruptible exports; (iii) on-demand rights from other entities or Balancing Authorities; (iv) Spinning Reserve in excess of requirements in subsections a(i) and a(ii); or (v) off-line generation which qualifies as Nonspinning Reserve. c. Knowledge of Operating Reserve. Operating Reserves shall be calculated such that the amount available which can be fully activated in the next ten minutes will be known at all times. d. Restoration of Operating Reserve. After the occurrence of any event necessitating the use of Operating Reserve, that reserve shall be restored as promptly as practicable. The time taken to restore reserves shall not exceed 60 minutes (Source: WECC Criterion) | Regional | [6 empty] | Yes | No | No |  |  | Yes - creates a higher expectation in the west than the continent wide standard. It is appropriate to have the regional variance. | [18 empty] | Not ranked |  | High |  | BA | [13 empty] | RSG
CIP-001-1 | CIP-001-2a | R1. | SaBoardage Reporting | Disturbances or unusual occurrences, suspected or determined to be caused by saBoardage, shall be reported to the appropriate systems, governmental agencies, and regulatory bodies. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the recognition of and for making their operating personnel aware of saBoardage events on its facilities and multi site saBoardage affecting larger portions of the Interconnection. | CIP - will be replaced by Board adopted standard (EOP) | May be replaced by EOP-004-2, which was Board adopted 11/7/2012 Filed with FERC 12/31/2012 | [5 empty] | Yes - #1 | No | No |  |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 8 | High |  |  | Medium | [6 empty] | BA |  |  | GOP |  | LSE |  |  |  |  | RC
CIP-001-1 | CIP-001-2a | R2. | SaBoardage Reporting | Disturbances or unusual occurrences, suspected or determined to be caused by saBoardage, shall be reported to the appropriate systems, governmental agencies, and regulatory bodies. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall have procedures for the communication of information concerning saBoardage events to appropriate parties in the Interconnection. | CIP - will be replaced by Board adopted standard (EOP) | May be replaced by EOP-004-2, which was Board adopted 11/7/2012 Filed with FERC 12/31/2012 | [5 empty] | Yes - #1 | No | No |  |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 8 | High |  |  | Medium | [6 empty] | BA |  |  | GOP |  | LSE |  |  |  |  | RC
CIP-001-1 | CIP-001-2a | R3. | SaBoardage Reporting | Disturbances or unusual occurrences, suspected or determined to be caused by saBoardage, shall be reported to the appropriate systems, governmental agencies, and regulatory bodies. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall provide its operating personnel with saBoardage response guidelines, including personnel to contact, for reporting disturbances due to saBoardage events. | CIP - will be replaced by Board adopted standard (EOP) | May be replaced by EOP-004-2, which was Board adopted 11/7/2012 Filed with FERC 12/31/2012 |  |  |  | Yes |  | Yes - #1 | No | No |  |  |  |  | No |  | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 8 | High |  |  | Medium | [6 empty] | BA |  |  | GOP |  | LSE |  |  |  |  | RC
CIP-001-1 | CIP-001-2a | R4. | SaBoardage Reporting | Disturbances or unusual occurrences, suspected or determined to be caused by saBoardage, shall be reported to the appropriate systems, governmental agencies, and regulatory bodies. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, and Load-Serving Entity shall establish communications contacts, as applicable, with local Federal Bureau of Investigation (FBI) or Royal Canadian Mounted Police (RCMP) officials and develop reporting procedures as appropriate to their circumstances. | CIP - will be replaced by Board adopted standard (EOP) | May be replaced by EOP-004-2, which was Board adopted 11/7/2012 Filed with FERC 12/31/2012 | [5 empty] | No | Yes | [18 empty] | No | No |  |  | High |  |  | Medium | [6 empty] | BA |  |  | GOP |  | LSE |  |  |  |  | RC
CIP-002-3 | CIP-002-3 | R1. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.1. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | The risk-based assessment shall consider the following assets: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.1. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.2. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Transmission substations that support the reliable operation of the Bulk Electric System. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.3. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Generation resources that support the reliable operation of the Bulk Electric System. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.4. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.5. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.6. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Special Protection Systems that support the reliable operation of the Bulk Electric System. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R1.2.7. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R2. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | High | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R3. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No | [25 empty] | High |  |  | High | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R3.1. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R3.2. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | The Cyber Asset uses a routable protocol within a control center; or, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R3.3. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | The Cyber Asset is dial-up accessible. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-3 | CIP-002-3 | R4. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-3 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-4 | CIP-002-4 | R1. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-4 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | High | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-4 | CIP-002-4 | R2. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-4 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: •The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | High | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-002-4 | CIP-002-4 | R3. | Cyber Security — Critical Cyber Asset Identification | Standard CIP-002-4 requires the identification and documentation of the Critical Cyber Assets associated with the Critical Assets that support the reliable operation of the Bulk Electric System. These Critical Assets are to be identified through the appl | Annual Approval —The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R1.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R1.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R1.3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R2.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The senior manager shall be identified by name, title, and date of designation. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R2.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R2.3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R2.4. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R3.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R3.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R3.3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R4. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R4.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R4.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R4.3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5.1.1. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5.1.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5.2. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R5.3. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-3 | CIP-003-3 | R6. | Cyber Security — Security Management Controls | Standard CIP-003-3 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Cyber Security Policy —The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R1.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R1.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R1.3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Leadership —The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R2.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The senior manager shall be identified by name, title, and date of designation. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R2.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R2.3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R2.4. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R3.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R3.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R3.3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R4. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Information Protection —The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R4.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R4.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R4.3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Access Control —The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5.1.1. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5.1.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5.2. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R5.3. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-003-4 | CIP-003-4 | R6. | Cyber Security — Security Management Controls | Standard CIP-003-4 requires that Responsible Entities have minimum security management controls in place to protect Critical Cyber Assets. Standard CIP-003-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R1. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Awareness — The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Training — The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.1. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.2. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.2.1. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The proper use of Critical Cyber Assets; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.2.2. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Physical and electronic access controls to Critical Cyber Assets; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.2.3. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The proper handling of Critical Cyber Asset information; and, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.2.4. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R2.3. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R3. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R3.1. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R3.2. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R3.3. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R4. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Access — The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R4.1. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-3 | CIP-004-3a | R4.2. | Cyber Security — Personnel & Training | Standard CIP-004-3 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R1. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.1. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.2. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.2.1. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The proper use of Critical Cyber Assets; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.2.2. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Physical and electronic access controls to Critical Cyber Assets; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.2.3. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The proper handling of Critical Cyber Asset information; and, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.2.4. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R2.3. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R3. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R3.1. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R3.2. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R3.3. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R4. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R4.1. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-004-4 | CIP-004-4a | R4.2. | Cyber Security — Personnel & Training | Standard CIP-004-4 requires that personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an appropriate level of personnel risk assessment, training, and security | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Electronic Security Perimeter — The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R1.6. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The required documentation shall, at least, identify and describe: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.5.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The processes for access request and authorization. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.5.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The authentication methods. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.5.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.5.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The controls used to secure dial-up accessible connections. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R2.6. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Monitoring Electronic Access — The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R3.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R3.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | A document identifying the vulnerability assessment process; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | A review to verify that only ports and services required for operations at these access points are enabled; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The discovery of all access points to the Electronic Security Perimeter; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | A review of controls for default accounts, passwords, and network management community strings; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R4.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | Documentation Review and Maintenance — The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R5.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R5.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-3 | CIP-005-3a | R5.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-3 requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-3 should be read as part of a group of sta | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Electronic Security Perimeter —The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4a. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R1.6. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The required documentation shall, at least, identify and describe: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.5.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The processes for access request and authorization. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.5.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The authentication methods. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.5.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.5.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The controls used to secure dial-up accessible connections. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R2.6. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Appropriate Use Banner —Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Monitoring Electronic Access —The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R3.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R3.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | A document identifying the vulnerability assessment process; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | A review to verify that only ports and services required for operations at these access points are enabled; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The discovery of all access points to the Electronic Security Perimeter; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4.4. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | A review of controls for default accounts, passwords, and network management community strings; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R4.5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R5. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | Documentation Review and Maintenance —The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4a. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R5.1. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4a reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4a at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R5.2. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-005-4 | CIP-005-4a | R5.3. | Cyber Security — Electronic Security Perimeter(s) | Standard CIP-005-4a requires the identification and protection of the Electronic Security Perimeter(s) inside which all Critical Cyber Assets reside, as well as all access points on the perimeter. Standard CIP-005-4a should be read as part of a group of s | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.4. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.5. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.6. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.6.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.6.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Continuous escorted access of visitors within the Physical Security Perimeter. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.7. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R1.8. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Annual review of the physical security plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R2.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Be protected from unauthorized physical access. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R2.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R4. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R5. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R6. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R7. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R8. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R8.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R8.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-3 | CIP-006-3c | R8.3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-3 is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-3 should be read as part of a group of standards numbered Standards CIP-002-3 through CIP-009-3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.4. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.5. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.6. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.6.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.6.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Continuous escorted access of visitors within the Physical Security Perimeter. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.7. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R1.8. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Annual review of the physical security plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R2.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Be protected from unauthorized physical access. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R2.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R4. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R5. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R6. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R7. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R8. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R8.1. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R8.2. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-006-4 | CIP-006-4c | R8.3. | Cyber Security — Physical Security of Critical Cyber Assets | Standard CIP-006-4c is intended to ensure the implementation of a physical security program for the protection of Critical Cyber Assets. Standard CIP-006-4c should be read as part of a group of standards numbered Standards CIP-002-4 through CIP-009-4. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R1.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R1.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R1.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document test results. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R2.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R2.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R2.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R3.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R3.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R4. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R4.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R4.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.1.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.1.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.1.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.2.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.2.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall identify those individuals with access to shared accounts. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.2.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.3.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall be a minimum of six characters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.3.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall consist of a combination of alpha, numeric, and “special” characters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R5.3.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall be changed at least annually, or more frequently based on risk. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6.4. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R6.5. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R7. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R7.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R7.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R7.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R8. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R8.1. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A document identifying the vulnerability assessment process; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R8.2. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R8.3. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A review of controls for default accounts; and, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R8.4. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-3 | CIP-007-3 | R9. | Cyber Security — Systems Security Management | Standard CIP-007-3 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Test Procedures —The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R1.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R1.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R1.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document test results. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Ports and Services —The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R2.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R2.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R2.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Security Patch Management —The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R3.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R3.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R4. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Malicious Software Prevention —The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R4.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R4.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.1.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.1.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.1.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.2.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.2.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall identify those individuals with access to shared accounts. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.2.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.3.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall be a minimum of six characters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.3.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall consist of a combination of alpha, numeric, and “special” characters. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R5.3.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Each password shall be changed at least annually, or more frequently based on risk. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6.4. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R6.5. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R7. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R7.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R7.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R7.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R8. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R8.1. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A document identifying the vulnerability assessment process; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R8.2. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R8.3. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | A review of controls for default accounts; and, | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R8.4. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-007-4 | CIP-007-4 | R9. | Cyber Security — Systems Security Management | Standard CIP-007-4 requires Responsible Entities to define methods, processes, and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the Electronic Security Perimeter(s). | Documentation Review and Maintenance —The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.1. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Procedures to characterize and classify events as reportable Cyber Security Incidents. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.2. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.3. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.4. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.5. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R1.6. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-3 | CIP-008-3 | R2. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-3 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-23 should be read as part of a group of standards numbered Standards CIP-002-3 through C | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Cyber Security Incident Response Plan —The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.1. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Procedures to characterize and classify events as reportable Cyber Security Incidents. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.2. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.3. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.4. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.5. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R1.6. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-008-4 | CIP-008-4 | R2. | Cyber Security — Incident Reporting and Response Planning | Standard CIP-008-4 ensures the identification, classification, response, and reporting of Cyber Security Incidents related to Critical Cyber Assets. Standard CIP-008-4 should be read as part of a group of standards numbered Standards CIP-002-4 through CI | Cyber Security Incident Documentation —The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R1. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | No - CIP | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R1.1. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R1.2. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Define the roles and responsibilities of responders. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R2. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R3. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R4. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-3 | CIP-009-3 | R5. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-3 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-3 should be read as part of a group o | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | CIP V3 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R1. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Recovery Plans —The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted |  |  |  | Yes | [25 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R1.1. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R1.2. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Define the roles and responsibilities of responders. | CIP | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Medium | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R2. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Exercises —The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R3. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R4. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Backup and Restore —The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
CIP-009-4 | CIP-009-4 | R5. | Cyber Security — Recovery Plans for Critical Cyber Assets | Standard CIP-009-4 ensures that recovery plan(s) are put in place for Critical Cyber Assets and that these plans follow established business continuity and disaster recovery techniques and practices. Standard CIP-009-4 should be read as part of a group o | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | CIP V4 | CIP V3: 10/1/10 CIP V4: 4/1/14 FERC approved CIP V5: 7/1/2015 Board Adopted | [29 empty] | High |  |  | Lower | BA |  | GO | GOP | IA | LSE | NERC |  |  |  | RC | RE |  |  |  | TO | TOP |  | TSP
COM-001-1 | COM-001-1.1 | R1. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | Yes | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - adequate and reliable is not clear | Yes | Yes | No - vague terms (adequate, reliable, internally, etc) | No | Yes | Yes | Yes | 2 | 8 | High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R1.1. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Internally. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | No - consolidate into R1 | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - adequate and reliable is not clear | Yes | Yes | No - vague terms (adequate, reliable, internally, etc) | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R1.2. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | No - consolidate into R1 | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - adequate and reliable is not clear | Yes | Yes | No - vague terms (adequate, reliable, internally, etc) | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R1.3. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | No - consolidate into R1 | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - adequate and reliable is not clear | Yes | Yes | No - vague terms (adequate, reliable, internally, etc) | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R1.4. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Where applicable, these facilities shall be redundant and diversely routed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | No - consolidate into R1 | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - adequate and reliable is not clear | Yes | Yes | No - vague terms (adequate, reliable, internally, etc) | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R2. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall manage, alarm, test and/or actively monitor vital telecommunications facilities. Special attention shall be given to emergency telecommunications facilities and equipment not used for routine communications. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - vague terms; standard is aged | Yes | No | Yes | Yes - all functions are individually responsible for compliance but this could be stated clearer | Yes | Yes | No - terms such as actively monitored, special attention, etc. | Yes | Yes | No - vague terms (actively monitored, special attention, etc) | No | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Medium | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R3. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall provide a means to coordinate telecommunications among their respective areas. This coordination shall include the ability to investigate and recommend solutions to telecommunications problems within the area and with other areas. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | Yes - duplicative of R1 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R4. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Unless agreed to otherwise, each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use English as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System. Transmission Operators and Balancing Authorities may use an alternate language for internal operations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces |  |  |  | Yes |  | Yes - #3 | No | No |  |  | No - need to provide for requirements of law (Canada, french) | Yes | Yes | Yes | Yes | Yes | Yes | No - the purpose is to have facilities; this is a protocol | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | Medium | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R5. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces | [5 empty] | Yes - #5 | No | No |  |  | No - need to test and periodically use alternative communication means | Yes | Yes | No - move into an EOP standard | Yes | Yes | Yes | Yes | No - no quality specs, no test/validate or implement requirement | Yes | Yes | Yes | Yes | yes | Yes | Yes | Yes | 2 | 10 | High |  | HIgh | Lower | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-1 | COM-001-1.1 | R6. | Telecommunications | Each Reliability Coordinator, Transmission Operator and Balancing Authority needs adequate and reliable telecommunications facilities internally and with others for the exchange of Interconnection and operating information necessary to maintain reliabilit | Each NERCNet User Organization shall adhere to the requirements in Attachment 1-COM-001-0, “NERCNet Security Policy.” | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by COM-001-2 if approved by FERC and provinces |  |  |  | No |  | No - there is no longer a need for the attachment | [19 empty] | No |  | 0 | 0 | High |  | N/A | Lower | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-2 | COM-001-2 | R1. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Reliability Coordinator shall have Interpersonal Communication capability with the following entities (unless the Reliability Coordinator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered. | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High | [11 empty] | RC
COM-001-2 | COM-001-2 | R2. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Reliability Coordinator shall designate an Alternative Interpersonal Communication capability with the following entities: | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High | [11 empty] | RC
COM-001-2 | COM-001-2 | R3. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Transmission Operator shall have Interpersonal Communication capability with the following entities (unless the Transmission Operator detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High | [17 empty] | TOP
COM-001-2 | COM-001-2 | R4. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Transmission Operator shall designate an Alternative Interpersonal Communication capability with the following entities: | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - consider inclusion of DP and GOP per R5.3 and 5.4; and internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High | [17 empty] | TOP
COM-001-2 | COM-001-2 | R5. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Balancing Authority shall have Interpersonal Communication capability with the following entities (unless the Balancing Authority detects a failure of its Interpersonal Communication capability in which case Requirement R10 shall apply): | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High |  | BA
COM-001-2 | COM-001-2 | R6. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Balancing Authority shall designate an Alternative Interpersonal Communication capability with the following entities: | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - consider inclusion of DP and GOP per R5.3 and 5.4; and internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R1-R6 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High |  | BA
COM-001-2 | COM-001-2 | R7. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Distribution Provider shall have Interpersonal Communication capability with the following entities (unless the Distribution Provider detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered. | Yes | No - there should not be a single point of failure | No - consolidate R7 and R8 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | Medium |  |  | DP
COM-001-2 | COM-001-2 | R8. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - internal communication and redundancy is Not covered | Yes | No - there should not be a single point of failure | No - consolidate R7 and R8 | Yes | Yes | Yes | Yes | No - does not specify requirement for no single point of failure | Yes | No - see single point of failure comment | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High |  |  |  |  | GOP
COM-001-2 | COM-001-2 | R9. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall test its Alternative Interpersonal Communication capability at least once each calendar month. If the test is unsuccessful, the responsible entity shall initiate action to repair or designate a replacement Alternative Interpersonal Communication capability within 2 hours. | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - the testing interval does not align with current industry practices | Yes | Yes | Yes | Yes | Yes | No - does not align with industry practice | Yes | No - does not align with industry practice; no basis for time interval | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High | Yes | Medium |  | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-2 | COM-001-2 | R10. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall notify entities as identified in Requirements R1, R3, and R5, respectively within 60 minutes of the detection of a failure of its Interpersonal Communication capability that lasts 30 minutes or longer. | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - No provision to initiate repair of primary if it fails in real time or to complete repair. Consider whether the Standard needs to provide for a reasonable timeframe to conduct repair and how compliance would be assessed for "reasonable". | Yes | No - 60 minutes is too long | Yes | Yes | Yes | Yes | Yes | No - time is too long | Yes | No - time is too long | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | High | Yes | High |  | BA | [9 empty] | RC | [5 empty] | TOP
COM-001-2 | COM-001-2 | R11. | Communications | To establish Interpersonal Communication capabilities necessary to maintain reliability. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | Board Adopted | Board adopted 11/7/2012 not approved by FERC | [5 empty] | Yes - #5 | No | No |  |  | No - there is No timeframe to consult each entity | Yes | No - there are two different requirements here - one for DP and one for GOP. Need to break out into 2 requirements. | Yes | Yes | Yes | No - see comments in "gap" | Yes | No - see comments in "gap" | No | Yes | Yes | No - see comments in "gap" | No - see comments in "gap" | Yes | Yes | Yes | 1 | 7 | High | Yes | Medium |  |  | DP |  | GOP
COM-002-2 | COM-002-2 | R1. | Communications and Coordination | To ensure Balancing Authorities, Transmission Operators, and Generator Operators have adequate communications and that these communications capabilities are staffed and available for addressing a real-time emergency condition. To ensure communications by | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | Current - will be replaced by Board adopted std | Currently enforceable standard. Board adopted COM-002-2a 2/9/2012 and COM-002-3 11/7/2012. Neither have been filed with FERC. COM-002-2a is not included on this spreadsheet. | [5 empty] | Yes | Yes - duplicative of COM-001-1.1 and COM-001-2 | [18 empty] | Yes | no | 0 | 0 | High |  | N/A | High | BA |  |  | GOP | [12 empty] | TOP
COM-002-2 | COM-002-2 | R1.1. | Communications and Coordination | To ensure Balancing Authorities, Transmission Operators, and Generator Operators have adequate communications and that these communications capabilities are staffed and available for addressing a real-time emergency condition. To ensure communications by | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. | Current - will be replaced by Board adopted std | Currently enforceable standard. Board adopted COM-002-2a 2/9/2012 and COM-002-3 11/7/2012. Neither have been filed with FERC. COM-002-2a is not included on this spreadsheet. | [5 empty] | Yes | Yes - duplicative of TOP, IRO and EOP stds (this speaks to operating the system) | [18 empty] | Yes | no | 0 | 0 | High |  | N/A | High | BA | [15 empty] | TOP
COM-002-2 | COM-002-2 | R2. | Communications and Coordination | To ensure Balancing Authorities, Transmission Operators, and Generator Operators have adequate communications and that these communications capabilities are staffed and available for addressing a real-time emergency condition. To ensure communications by | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner; shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. | Current - will be replaced by Board adopted std | Currently enforceable standard. Board adopted COM-002-2a 2/9/2012 and COM-002-3 11/7/2012. Neither have been filed with FERC. COM-002-2a is not included on this spreadsheet. | [5 empty] | Yes - #1 | No | No |  |  | No - this should cover Board emergency and Normal communications. | Yes | No - requirement is not clear on the following two items: the word "directive" is not clear; it is not clear that the recipient of the directive is expected to participate in 3-part communication protocol. | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 8 | High |  | High | Medium | BA | [9 empty] | RC | [5 empty] | TOP
COM-002-3 | COM-002-3 | R1. | Communication and Coordination | To ensure Emergency communications between operating personnel are effective. |  | Board Adopted | Board adopted on 11/2012 | Yes - COM-003 Project 2007-02 |  |  |  |  | Yes - #1, 4 | No | No |  |  | No - this should cover Board emergency and Normal communications. 3-part communication should be used whenever an RC, TO or BA requests action to be taken on the system (BPS), regardless of whether it is identified as a Reliability Directive. | Yes | No - see "gap" comments | Yes, but consider consolidating into one requirement | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High | BA | [9 empty] | RC | [5 empty] | TOP
COM-002-3 | COM-002-3 | R2. | Communication and Coordination | To ensure Emergency communications between operating personnel are effective. |  | Board Adopted | Board adopted on 11/2012 | Yes - COM-003 Project 2007-02 |  |  |  |  | Yes - #1, 4 | No | No |  |  | No - this should cover Board emergency and Normal communications. 3-part communication should be used whenever an RC, TO or BA requests action to be taken on the system (BPS), regardless of whether it is identified as a Reliability Directive. | Yes | No - see "gap" comments | Yes, but consider consolidating into one requirement | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High | BA | DP | [8 empty] | RC | [5 empty] | TOP
COM-002-3 | COM-002-3 | R3. | Communication and Coordination | To ensure Emergency communications between operating personnel are effective. |  | Board Adopted | Board adopted on 11/2012 | Yes - COM-003 Project 2007-02 |  |  |  |  | Yes - #1, 4 | No | No |  |  | No - this should cover Board emergency and Normal communications. 3-part communication should be used whenever an RC, TO or BA requests action to be taken on the system (BPS), regardless of whether it is identified as a Reliability Directive. | Yes | No - see "gap" comments | Yes, but consider consolidating into one requirement | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High | BA | [9 empty] | RC | [5 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | High | BA
EOP-001-0 | EOP-001-0.1b | R2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator shall have an emergency load reduction plan for all identified IROLs. The plan shall include the details on how the Transmission Operator will implement load reduction in sufficient amount and time to mitigate the IROL violation before system separation or collapse would occur. The load reduction plan must be capable of being implemented within 30 minutes. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Each Transmission Operator and Balancing Authority shall: | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R3.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R3.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R3.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Develop, maintain, and implement a set of plans for load shedding. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R3.4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Develop, maintain, and implement a set of plans for system restoration. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R4.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Communications protocols to be used during emergencies. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R4.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R4.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R4.4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Staffing levels for the emergency. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R5. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R6. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R7. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 |  | No | [25 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R7.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R7.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R7.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-0 | EOP-001-0.1b | R7.4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabil | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. | Retired | EOP-001-0.1b will be retired on 6/30/2013 when EOP-001-2.1b becomes effective. EOP-001-1 was not approved by FERC in lieu of EOP-001-2.1b. |  | Combine EOP-001, -002, -003 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Balancing Authorities shall have operating agreements with adjacent Balancing Authorities that shall, at a minimum, contain provisions for emergency assistance, including provisions to obtain emergency assistance from remote Balancing Authorities. | Current | Becomes enforceable 7/1 2013 |  |  |  | Yes EOP-001-2b | Team determined entities need a plan | Yes - #1, 4 | No | No |  |  | Yes | Yes | yes | Yes | Yes for content; No for format | Yes | No - strike "at a minimum"; contract should define how much assistance | Yes | Yes | No - see comment under applicability. | Yes | Yes | No - see comment under applicability. | No | Yes | Yes | Yes | 3 | 8 | High |  | Medium | High - Pending | BA
EOP-001-2 | EOP-001-2.1b | R2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Each Transmission Operator and Balancing Authority shall: | Current | Becomes enforceable 7/1 2013 |  |  |  | Yes EOP-001-2b | Team determined entities need a plan | Yes - #1, 4 | No | No |  |  | Yes | Yes | No - std has legacy-style language that is not precise | No - consider consolidating R2 and R4: One for BA (capacity emergency) and one for TOP (transmission emergency) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - see content comments | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R2.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | Yes | No - this R is about developing a plan; implement does not belong here. although std has legacy-style language | No - consider consolidating R2 and R4: One for BA (capacity emergency) and one for TOP (transmission emergency) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - see content comments | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R2.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | Yes | No - this R is about developing a plan; implement does not belong here. although std has legacy-style language | No - consider consolidating R2 and R4: One for BA (capacity emergency) and one for TOP (transmission emergency) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - see content comments | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R2.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Develop, maintain, and implement a set of plans for load shedding. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | Yes | No - this R is about developing a plan; implement does not belong here. although std has legacy-style language | No - consider consolidating R2 and R4: One for BA (capacity emergency) and one for TOP (transmission emergency) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - see content comments | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Each Transmission Operator and Balancing Authority shall have emergency plans that will enable it to mitigate operating emergencies. At a minimum, Transmission Operator and Balancing Authority emergency plans shall include: | Current | Becomes enforceable 7/1 2013 |  |  |  | Yes EOP-001-2b | Team determined entities need a plan | Yes - #1, 4 | No | No |  |  | Yes | No - need to add RC Note: there is a possible gap for RC in IRO-005-4 regarding RC handling emergencies as this has been dropped from IRO-005-3.1 | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R3.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Communications protocols to be used during emergencies. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | Yes - duplicative of other stds COM-002-2 R2 | [20 empty] | 2 | 12 | High |  | High | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R3.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | No - need to add RC | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R3.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | No - need to add RC | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R3.4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Staffing levels for the emergency. | Current | Becomes enforceable 7/1 2013 | [5 empty] | Yes - #1, 4 | No | No |  |  | No - there should be a requirement to get the entity's own center ready to deal with the emergency (staffing, lodging, fortifying facility, meals, etc) | No - need to add RC | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High |  | High | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | Each Transmission Operator and Balancing Authority shall include the applicable elements in Attachment 1-EOP-001 when developing an emergency plan. | Current | Becomes enforceable 7/1 2013 |  |  |  | Yes EOP-001-2b | Team determined entities need a plan | Yes - #1, 4 | No | No |  |  | No - EEA protocols are missing (move here from EOP-002) | Yes | No - Attachment 1 needs to be updated to reflect business environment (i.e. include EEA protocol as described in EOP-002 attachment 1) Move EEA Attachment from EOP-002 to EOP-001 | No - consider consolidating R2 and R4: One for BA (capacity emergency) and one for TOP (transmission emergency) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R5. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall annually review and update each emergency plan. The Transmission Operator and Balancing Authority shall provide a copy of its updated emergency plans to its Reliability Coordinator and to neighboring Transmission Operators and Balancing Authorities. | Current | Becomes enforceable 7/1 2013 |  | Combine EOP-001, -002, -003 |  | Yes EOP-001-2b | Team determined entities need a plan | Yes - #4 | No | No |  |  | No - The plan needs to be provided to any impacted functional entity. | Yes | Yes | Yes | Yes | Yes | No - "annually" and "neighboring" are not clear | Yes | Yes | No - "annually" and "neighboring" are not clear | Yes | Yes | No - "annually" and "neighboring" are not clear | No - "annually" and "neighboring" are not clear | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R6. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall coordinate its emergency plans with other Transmission Operators and Balancing Authorities as appropriate. This coordination includes the following steps, as applicable: | Current | Becomes enforceable 7/1 2013 |  | Combine EOP-001, -002, -003 |  | Yes EOP-001-2b |  | Yes - #1, 4 | Yes - duplicative of other Rs in this std (R4 and attachment) and other stds | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R6.1. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. | Current | Becomes enforceable 7/1 2013 |  | EOP-001, -002, -003, COM-002, COM-003 |  |  |  | Yes - #1, 4 | Yes - duplicative of other Rs in this std (R4 and attachment) and other stds | [18 empty] | Yes | No |  |  | High |  | N/A | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R6.2. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. | Current | Becomes enforceable 7/1 2013 |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1, 4 | Yes - duplicative of other Rs in this std (R4 and attachment) and other stds | [18 empty] | Yes | No |  |  | High |  | N/A | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R6.3. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) | Current | Becomes enforceable 7/1 2013 |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1, 4 | Yes - duplicative of other Rs in this std (R4 and attachment) and other stds | [18 empty] | Yes | No |  |  | High |  | N/A | Medium - Pending | BA | [15 empty] | TOP
EOP-001-2 | EOP-001-2.1b | R6.4. | Emergency Operations Planning | Each Transmission Operator and Balancing Authority needs to develop, maintain, and implement a set of plans to mitigate operating emergencies. These plans need to be coordinated with other Transmission Operators and Balancing Authorities, and the Reliabi | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. | Current | Becomes enforceable 7/1 2013 |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1, 4 | Yes - duplicative of other Rs in this std (R4 and attachment) and other stds | [18 empty] | Yes | No |  |  | High |  | N/A | Medium - Pending | BA | [15 empty] | TOP
EOP-002-3 | EOP-002-3.1 | R1. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Each Balancing Authority and Reliability Coordinator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its respective area and shall exercise specific authority to alleviate capacity and energy emergencies. | Current | Currently enforceable standard. |  |  |  | Yes EOP-002-3 | Team is recommending consolidating into an authority std; when approved, this requirement should be retired | Yes - #1, 6 | No | No |  |  | Yes | Yes | Yes | No - consider consolidating R1 and R2, and consider consolidating R1 into an overall authority std | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - "specific" authority is not clear | No | Yes | Yes | Yes | 3 | 9 | Low |  | High | High | BA | [9 empty] | RC
EOP-002-3 | EOP-002-3.1 | R2. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Each Balancing Authority shall, when required and as appropriate, take one or more actions as described in its capacity and energy emergency plan to reduce risks to the interconnected system. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1, 6 | Yes - the requirement to take action is in R1. | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R3. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | A Balancing Authority that is experiencing an operating capacity or energy emergency shall communicate its current and future system conditions to its Reliability Coordinator and neighboring Balancing Authorities. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of what is required to be in the plan under attachment 1 of EOP-001 | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R4. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | A Balancing Authority anticipating an operating capacity or energy emergency shall perform all actions necessary including bringing on all available generation, postponing equipment maintenance, scheduling interchange purchases in advance, and being prepared to reduce firm load. | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes - too much. Make concise to say "the BA will act to implement its plan in emergency conditions as provided in the plan". | Yes | No - it is not on target. See comments under gap. | No - consolidate with an overall Authority standard | Yes | Yes | No - too much language; not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | Low |  | High | High | BA
EOP-002-3 | EOP-002-3.1 | R5. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | A deficient Balancing Authority shall only use the assistance provided by the Interconnection’s frequency bias for the time needed to implement corrective actions. The Balancing Authority shall not unilaterally adjust generation in an attempt to return Interconnection frequency to normal beyond that supplied through frequency bias action and Interchange Schedule changes. Such unilateral adjustment may overload transmission facilities. | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - there needs to be a time element; it does not acknowledge the communication plan (RC giving oversight to the BA) or the responsibility the BA has to manage his ACE at all times. | Yes | No - see "gap" comments | Yes | No | Yes | No - see comments | No | No | No | No | Yes | No - see comments | No - see comments | Yes | Yes | Yes | 1 | 4 | Low |  | Low | High | BA
EOP-002-3 | EOP-002-3.1 | R6. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  | Yes EOP-002-3 |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.1. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Loading all available generating capacity. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.2. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Deploying all available operating reserve. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.3. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Interrupting interruptible load and exports. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.4. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Requesting emergency assistance from other Balancing Authorities. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.5. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Declaring an Energy Emergency through its Reliability Coordinator; and | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R6.6. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | Yes | Yes - duplicative of BAL stds to meet CPS and DPS | [18 empty] | Yes | No |  |  | Low |  | N/A | High | BA
EOP-002-3 | EOP-002-3.1 | R7. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Once the Balancing Authority has exhausted the steps listed in Requirement 6, or if these steps cannot be completed in sufficient time to resolve the emergency condition, the Balancing Authority shall: | Current | Currently enforceable standard. |  |  |  | Yes EOP-002-3 |  | Yes | No | No |  |  | Yes | Yes | No - the steps described here are out of sequence for what actually happens | No - consolidate with EOP-001 R4 (write plan) and EOP-002 R4 (implement) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Low |  | High | High | BA
EOP-002-3 | EOP-002-3.1 | R7.1. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Manually shed firm load without delay to return its ACE to zero; and | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes | Yes | No - the steps described here are out of sequence for what actually happens | No - consolidate with EOP-001 R4 (write plan) and EOP-002 R4 (implement) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Low |  | High | High | BA
EOP-002-3 | EOP-002-3.1 | R7.2. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes - See EOP-001 for moving plan (R4) (Move EEA protocols into here) | Yes | No - the steps described here are out of sequence for what actually happens | No - consolidate with EOP-001 R4 (write plan) and EOP-002 R4 (implement) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Low |  | High | High | BA
EOP-002-3 | EOP-002-3.1 | R8. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | A Reliability Coordinator that has any Balancing Authority within its Reliability Coordinator area experiencing a potential or actual Energy Emergency shall initiate an Energy Emergency Alert as detailed in Attachment 1-EOP-002 “Energy Emergency Alerts.” The Reliability Coordinator shall act to mitigate the emergency condition, including a request for emergency assistance if required. | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Low |  | High | High | [10 empty] | RC
EOP-002-3 | EOP-002-3.1 | R9. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | When a Transmission Service Provider expects to elevate the transmission service priority of an Interchange Transaction from Priority 6 (Network Integration Transmission Service from Non-designated Resources) to Priority 7 (Network Integration Transmission Service from designated Network Resources) as permitted in its transmission tariff: | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  | Yes EOP-002-3 |  | No | Yes - this is a tariff issue (market) | [18 empty] | No | No | 0 | 0 | Low |  | N/A | High | [5 empty] | LSE |  |  |  |  | RC
EOP-002-3 | EOP-002-3.1 | R9.1. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | No | Yes - this is a tariff issue (market) | [18 empty] | No | No |  |  | Low |  | N/A | High | [5 empty] | LSE
EOP-002-3 | EOP-002-3.1 | R9.2. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | No | Yes - this is a tariff issue (market) | [18 empty] | No | No |  |  | Low |  | N/A | High | [10 empty] | RC
EOP-002-3 | EOP-002-3.1 | R9.3. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | No | Yes - this is a tariff issue (market) | [18 empty] | No | No |  |  | Low |  | N/A | Lower | [10 empty] | RC
EOP-002-3 | EOP-002-3.1 | R9.4. | Capacity and Energy Emergencies | To ensure Reliability Coordinators and Balancing Authorities are prepared for capacity and energy emergencies. | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. | Current | Currently enforceable standard. |  | Combine EOP-001, -002, -003 |  |  |  | No | Yes - this is a tariff issue (market) | [18 empty] | No | No |  |  | Low |  | N/A | Lower | [10 empty] | RC
EOP-003-1 | EOP-003-1 | R1. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R2. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator and Balancing Authority shall establish plans for automatic load shedding for underfrequency or undervoltage conditions. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R3. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans among other interconnected Transmission Operators and Balancing Authorities. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R4. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | A Transmission Operator or Balancing Authority shall consider one or more of these factors in designing an automatic load shedding scheme: frequency, rate of frequency decay, voltage level, rate of voltage decay, or power flow levels. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R5. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | A Transmission Operator or Balancing Authority shall implement load shedding in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R6. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R7. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | The Transmission Operator and Balancing Authority shall coordinate automatic load shedding throughout their areas with underfrequency isolation of generating units, tripping of shunt capacitors, and other automatic actions that will occur under abnormal frequency, voltage, or power flow conditions. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-1 | EOP-003-1 | R8. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator or Balancing Authority shall have plans for operator-controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. | Retired | Currently enforceable standard; will be retired on 9/30/2013 and EOP-003-2 will become enforceable. |  | Combine EOP-001, -002, -003 | [27 empty] | Low |  |  | High | BA | [15 empty] | TOP
EOP-003-2 | EOP-003-2 | R1. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | After taking all other remedial steps, a Transmission Operator or Balancing Authority operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the Interconnection. | Current | Becomes enforceable 10/1/2013. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No - not clear which role is to shed load; is not clear whether the term "cascading" is meant to be the defined term | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | Low |  | High | High | BA | [15 empty] | TOP
EOP-003-2 | EOP-003-2 | R2. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator shall establish plans for automatic load shedding for undervoltage conditions if the Transmission Operator or its associated Transmission Planner(s) or Planning Coordinator(s) determine that an under-voltage load shedding scheme is required. | Current | Becomes enforceable 10/1/2013. |  | Combine EOP-001, -002, -003 |  | Yes |  | Yes - #1 | Yes - duplicative of PRC-010 and TPL stds | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | [16 empty] | TOP
EOP-003-2 | EOP-003-2 | R3. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator and Balancing Authority shall coordinate load shedding plans, excluding automatic under-frequency load shedding plans, among other interconnected Transmission Operators and Balancing Authorities. | Current | Becomes enforceable 10/1/2013. |  |  |  | Yes |  | Yes - #1 | No | No |  |  | No - clarity. It is not clear what load shedding plan is being referred to. | No - Not clear what is to be done | No - who and what is not clear | No - consolidate R3 and R8 | No | Yes | No | Yes | Yes - although not sure | No | Yes - coordination is good | Yes | No | No | Yes | Yes | Yes | 0 | 6 | Low |  | Medium | High | BA | [15 empty] | TOP
EOP-003-2 | EOP-003-2 | R4. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | A Transmission Operator shall consider one or more of these factors in designing an automatic under voltage load shedding scheme: voltage level, rate of voltage decay, or power flow levels. | Current | Becomes enforceable 10/1/2013. |  | Combine EOP-001, -002, -003 |  | Yes |  | Yes - #1 | Yes - duplicative of PRC-010 and TPL stds | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | [16 empty] | TOP
EOP-003-2 | EOP-003-2 | R5. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | A Transmission Operator or Balancing Authority shall implement load shedding, excluding automatic under-frequency load shedding, in steps established to minimize the risk of further uncontrolled separation, loss of generation, or system shutdown. | Current | Becomes enforceable 10/1/2013. |  | Combine EOP-001, -002, -003 |  | Yes |  | Yes - #1 | Yes - Duplicative of R1 and also covered under stds for TOP (TOP-002-3) | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | BA | [15 empty] | TOP
EOP-003-2 | EOP-003-2 | R6. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | After a Transmission Operator or Balancing Authority Area separates from the Interconnection, if there is insufficient generating capacity to restore system frequency following automatic underfrequency load shedding, the Transmission Operator or Balancing Authority shall shed additional load. | Current | Becomes enforceable 10/1/2013. |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1 | Yes - duplicative; an entity does the same actions as when not islanded. | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | BA | [15 empty] | TOP
EOP-003-2 | EOP-003-2 | R7. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | The Transmission Operator shall coordinate automatic undervoltage load shedding throughout their areas with tripping of shunt capacitors, and other automatic actions that will occur under abnormal voltage, or power flow conditions | Current | Becomes enforceable 10/1/2013. |  | Combine EOP-001, -002, -003 |  |  |  | Yes - #1 | Yes - duplicative of PRC-010 R1 | [18 empty] | Yes | No | 0 | 0 | Low |  | N/A | High | [16 empty] | TOP
EOP-003-2 | EOP-003-2 | R8. | Load Shedding Plans | A Balancing Authority and Transmission Operator operating with insufficient generation or transmission capacity must have the capability and authority to shed load rather than risk an uncontrolled failure of the Interconnection. | Each Transmission Operator or Balancing Authority shall have plans for operator controlled manual load shedding to respond to real-time emergencies. The Transmission Operator or Balancing Authority shall be capable of implementing the load shedding in a timeframe adequate for responding to the emergency. | Current | Becomes enforceable 10/1/2013. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R8 | Yes | Yes | No - does "plan" mean "capability"? | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 7 | Low |  | High | High | BA | [15 empty] | TOP
EOP-004-1 | EOP-004-1 | R1. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | Each Regional Reliability Organization shall establish and maintain a Regional reporting procedure to facilitate preparation of preliminary and final disturbance reports. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. |  |  |  | Yes |  | No - need new #10 | Yes - overcome by events; the creation of the voluntary EA procedure | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [19 empty] | RRO
EOP-004-1 | EOP-004-1 | R2. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall promptly analyze Bulk Electric System disturbances on its system or facilities. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. |  |  |  | Yes |  | No - need new #10 | Yes - overcome by events; the creation of the voluntary EA procedure | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R3. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | A Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity experiencing a reportable incident shall provide a preliminary written report to its Regional Reliability Organization and NERC. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. |  |  |  | Yes |  | No - need new #10 | No | No |  |  | Yes | No - DP needs to be added; RRO needs to be defined | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 9 | High |  | Low | Lower | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R3.1. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. | [5 empty] | No - need new #10 | No | No |  |  | Yes | No - DP needs to be added; RRO needs to be defined | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 9 | High |  | Low | Lower | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R3.2. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | Applicable reporting forms are provided in Attachments 022-1 and 022-2. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. | [5 empty] | No - need new #10 | Yes - statement; not requirement | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | No Individual VRF Assigned | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R3.3. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. | [5 empty] | No - need new #10 | No | No |  |  | Yes | No - DP needs to be added; RRO needs to be defined | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 9 | High |  | Low | Lower | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R3.4. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. | [5 empty] | No - need new #10 | No | No |  |  | Yes | No - DP needs to be added; RRO needs to be defined | No - RRO has a role and is not defined | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 9 | High |  | Low | Lower | [6 empty] | BA |  |  | GOP | RC | LSE |  |  |  |  | TOP
EOP-004-1 | EOP-004-1 | R4. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | When a Bulk Electric System disturbance occurs, the Regional Reliability Organization shall make its representatives on the NERC Operating Committee and Disturbance Analysis Working Group available to the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity immediately affected by the disturbance for the purpose of providing any needed assistance in the investigation and to assist in the preparation of a final report. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. |  |  |  | Yes |  | No - need new #10 | Yes - not enforceable | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [19 empty] | RRO
EOP-004-1 | EOP-004-1 | R5. | Disturbance Reporting | Disturbances or unusual occurrences that jeopardize the operation of the Bulk Electric System, or result in system equipment damage or customer interruptions, need to be studied and understood to minimize the likelihood of similar events in the future. | The Regional Reliability Organization shall track and review the status of all final report recommendations at least twice each year to ensure they are being acted upon in a timely manner. If any recommendation has not been acted on within two years, or if Regional Reliability Organization tracking and review indicates at any time that any recommendation is not being acted on with sufficient diligence, the Regional Reliability Organization shall notify the NERC Planning Committee and Operating Committee of the status of the recommendation(s) and the steps the Regional Reliability Organization has taken to accelerate implementation. | Current - will be replaced by Board adopted std | Will be replaced by EOP-004-2 if approved by FERC and provinces. -2 was filed with FERC on 12/31/2012. |  |  |  | Yes |  | No - need new #10 | Yes - not enforceable; administrative | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [19 empty] | RRO
EOP-004-2 | EOP-004-2 | R1. | Event Reporting | To improve the reliability of the Bulk Electric System by requiring the reporting of events by Responsible Entities. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Board Adopted | Board adopted on 11/7/2012; Filed with FERC 12/31/2012 | [5 empty] | Yes - #10 | No | No |  |  | Yes - Note: Analysis was removed from the new standard and became voluntary under the ERO Event Analysis process | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes b/c added #10 | Yes | 3 | 12 | High |  | Low | [11 empty] | RC |  |  |  |  | TO | TOP
EOP-004-2 | EOP-004-2 | R2. | Event Reporting | To improve the reliability of the Bulk Electric System by requiring the reporting of events by Responsible Entities. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | Board Adopted | Board adopted on 11/7/2012; Filed with FERC 12/31/2012 | [5 empty] | Yes - #10 | No | No |  |  | Yes - Note: Analysis was removed from the new standard and became voluntary under the ERO Event Analysis process | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes b/c added #10 | Yes | 3 | 12 | High |  | Medium | [11 empty] | RC |  |  |  |  | TO | TOP
EOP-004-2 | EOP-004-2 | R3. | Event Reporting | To improve the reliability of the Bulk Electric System by requiring the reporting of events by Responsible Entities. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | Board Adopted | Board adopted on 11/7/2012; Filed with FERC 12/31/2012 | [5 empty] | Yes - #10 | Yes - administrative. Could also combine into R1 | [18 empty] | Yes b/c added #10 | No | 0 | 0 | High |  | N/A | [11 empty] | RC |  |  |  |  | TO | TOP
EOP-005-1 | EOP-005-1 | R1. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 |  | Yes | [25 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R2. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator shall review and update its restoration plan at least annually and whenever it makes changes in the power system network, and shall correct deficiencies found during the simulated restoration exercises. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R3. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator shall develop restoration plans with a priority of restoring the integrity of the Interconnection. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R4. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator shall coordinate its restoration plans with the Generator Owners and Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R5. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator and Balancing Authority shall periodically test its telecommunication facilities needed to implement the restoration plan. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R6. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator and Balancing Authority shall train its operating personnel in the implementation of the restoration plan. Such training shall include simulated exercises, if practicable. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R7. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator and Balancing Authority shall verify the restoration procedure by actual testing or by simulation. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R8. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Each Transmission Operator shall verify that the number, size, availability, and location of system blackstart generating units are sufficient to meet Regional Reliability Organization restoration plan requirements for the Transmission Operator’s area. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R9. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The Transmission Operator shall document the Cranking Paths, including initial switching requirements, between each blackstart generating unit and the unit(s) to be started and shall provide this documentation for review by the Regional Reliability Organization upon request. Such documentation may include Cranking Path diagrams. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R10. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The Transmission Operator shall demonstrate, through simulation or testing, that the blackstart generating units in its restoration plan can perform their intended functions as required in the regional restoration plan. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R10.1. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The Transmission Operator shall perform this simulation or testing at least once every five years. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Following a disturbance in which one or more areas of the Bulk Electric System become isolated or blacked out, the affected Transmission Operators and Balancing Authorities shall begin immediately to return the Bulk Electric System to normal. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.1. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.2. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators on line, or load shedding. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | BA | [15 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.3. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | BA
EOP-005-1 | EOP-005-1 | R11.4. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.5. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.5.1. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Voltage, frequency, and phase angle permit. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.5.2. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.5.3. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [16 empty] | TOP
EOP-005-1 | EOP-005-1 | R11.5.4. | System Restoration Plans | To ensure plans, procedures, and resources are available to restore the electric system to a normal condition in the event of a partial or total shut down of the system. | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. | Retired | Will be replaced when EOP-005-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall have a restoration plan approved by its Reliability Coordinator. The restoration plan shall allow for restoring the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shut down area to service, to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: [Violation Risk Factor = High] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. |  |  |  | Yes |  | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.3. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.4. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.5. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.6. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Identification of acceptable operating voltage and frequency limits during restoration. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.7. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.8. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R1.9. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - the restoration plan needs to be broader than just blackstart for these functional entities OR make EOP-006 apply to the additional entities; it should include, at a minimum, a title change, a purpose change, and include the three topics from EOP-006-2 R1 | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the implementation date of the plan. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R3. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually agreed predetermined schedule. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - There is no requirement for the TOP to revise its plan if the RC does not approve it (also a time period for review) | Yes | No - There is no requirement for the TOP to revise its plan if the RC does not approve it (also a time period for review) | Yes | No | Yes | No - "annually", "mutually agreed predetermined schedule" is not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 7 | High |  | Medium | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R3.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | If there are no changes to the previously submitted restoration plan, the Transmission Operator shall confirm annually on a predetermined schedule to its Reliability Coordinator that it has reviewed its restoration plan and no changes were necessary. | Current | Becomes enforceable on 7/1/2013. |  |  | Yes |  |  | Yes | Yes - Para 81 Phase 1 | [18 empty] | Yes | No |  |  | High |  | N/A | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R4. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall update its restoration plan within 90 calendar days after identifying any unplanned permanent System modifications, or prior to implementing a planned BES modification, that would change the implementation of its restoration plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - need to include all system changes that impact an entities plan for an extended period of time Clarify what part of the system this applies to (cranking paths, etc) BES should be BPS | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 8 | High |  | Medium | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R4.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval within the same 90 calendar day period. | Current | Becomes enforceable on 7/1/2013. | [10 empty] | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R5. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its implementation date. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes | Yes - consider combining with EOP-006-2 R6 and EOP-008-1 R2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Low | Lower - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R6. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall verify through analysis of actual events, steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed every five years at a minimum. Such analysis, simulations or testing shall verify: [Violation Risk Factor = Medium] [Time Horizon = Long-term Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes - don't know how or why five years was determined | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R6.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes - don't know how or why five years was determined | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R6.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes - don't know how or why five years was determined | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R6.3. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes - don't know how or why five years was determined | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R7. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, each affected Transmission Operator shall implement its restoration plan. If the restoration plan cannot be executed as expected the Transmission Operator shall utilize its restoration strategies to facilitate restoration. [Violation Risk Factor = High] [Time Horizon = Real-time Operations] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | Yes - minutiae. This is a logical action that does not require a std. This is not measurable. | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R8. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Following a Disturbance in which one or more areas of the BES shuts down and the use of Blackstart Resources is required to restore the shut down area to service, the Transmission Operator shall resynchronize area(s) with neighboring Transmission Operator area(s) only with the authorization of the Reliability Coordinator or in accordance with the established procedures of the Reliability Coordinator. [Violation Risk Factor = High] [Time Horizon = Real-time Operations] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #1 | Yes - duplicative with EOP-005-2 R1.3 (have a plan) and RC authority in IRO-001-1.1b R3 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | A list of required tests including: | Current | Becomes enforceable on 7/1/2013. |  | Redraft all of R9.2 to state: the ability to start the unit and energize equipment under the conditions anticipated during an actual blackstart situation |  |  |  | Yes | No | No |  |  | Yes - but simplify - see comments in suggestions column | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9.2.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | Yes - but simplify - see comments in suggestions column | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9.2.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | Yes - but simplify - see comments in suggestions column | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R9.3. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The minimum duration of each of the required tests. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | Yes - does little to protect the reliability of the BPS | Yes | [6 empty] | Yes for content; No for format | [10 empty] | Yes | No |  |  | High |  | N/A | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R10. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall include training on the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. |  | Emphasis for training should be less on blackstart (although that is still necessary - especially validating cranking paths) and more on putting islands back together and synchronizing |  |  |  | Yes - #6 | No | No |  |  | Yes - but see note under suggestions for improvement | Yes | Yes | No - consolidate with PER-005 but keep the detail - don’t have strategic approach to training cover it | Yes for content; No for format | Yes | No - "annual" not clear | Yes | Yes | No - "annual" not clear | Yes | Yes | No - "annual" not clear | No - "annual" not clear | Yes | Yes | Yes | 3 | 7 | High |  | High | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R10.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | No - consolidate with PER-005 but keep the detail - don’t have strategic approach to training cover it | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R10.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Restoration priorities. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | No - consolidate with PER-005 but keep the detail - don’t have strategic approach to training cover it | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R10.3. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Building of cranking paths. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | No - consolidate with PER-005 but keep the detail - don’t have strategic approach to training cover it | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R10.4. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Synchronizing (re-energized sections of the System). | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | No - consolidate with PER-005 but keep the detail - don’t have strategic approach to training cover it | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | No Individual VRF Assigned | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R11. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium - Pending |  | DP | [13 empty] | TO | TOP
EOP-005-2 | EOP-005-2 | R12. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | Yes - duplicative with PER-005 R3 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium - Pending | [16 empty] | TOP
EOP-005-2 | EOP-005-2 | R13. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium - Pending |  |  |  | GOP | [12 empty] | TOP
EOP-005-2 | EOP-005-2 | R14. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 8 | High |  | Medium | Medium - Pending |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R15. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 8 | High |  | Medium | Medium - Pending |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R16. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | No - consolidate with R9 | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 7 | High |  | Medium | Medium - Pending |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R16.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | No | [19 empty] | No |  |  |  | High |  | N/A | No Individual VRF Assigned |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R16.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | No | [19 empty] | No |  |  |  | High |  | N/A | No Individual VRF Assigned |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R17. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | Yes | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | No - ambiguous term "operating personnel" | Yes | Yes | Yes | 1 | 8 | High |  | Medium | Medium - Pending |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R17.1. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | System restoration plan including coordination with the Transmission Operator. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | Yes | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | No - ambiguous term "operating personnel" | Yes | Yes | Yes | 1 | 8 | High |  | Medium | No Individual VRF Assigned |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R17.2. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The procedures documented in Requirement R14. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | No - this R should apply to a GOP that is identified in the TOPs plan (and has an executed agreement) | Yes | No - see "gap" comments | Yes | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | Yes | Yes | No - ambiguous term "operating personnel" | No - ambiguous term "operating personnel" | Yes | Yes | Yes | 1 | 8 | High |  | Medium | No Individual VRF Assigned |  |  |  | GOP
EOP-005-2 | EOP-005-2 | R18. | System Restoration from Blackstart Resources | Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes | Yes - but consider moving to PER-005 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium - Pending |  |  |  | GOP
EOP-006-1 | EOP-006-1 | R1. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall be aware of the restoration plan of each Transmission Operator in its Reliability Coordinator Area in accordance with NERC and regional requirements. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [10 empty] | RC
EOP-006-1 | EOP-006-1 | R2. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall monitor restoration progress and coordinate any needed assistance. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [10 empty] | RC
EOP-006-1 | EOP-006-1 | R3. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall have a Reliability Coordinator Area restoration plan that provides coordination between individual Transmission Operator restoration plans and that ensures reliability is maintained during system restoration events. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [10 empty] | RC
EOP-006-1 | EOP-006-1 | R4. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall serve as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators and Transmission Operators or Balancing Authorities not immediately involved in restoration. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [10 empty] | RC
EOP-006-1 | EOP-006-1 | R5. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Reliability Coordinators shall approve, communicate, and coordinate the re-synchronizing of major system islands or synchronizing points so as not to cause a Burden on adjacent Transmission Operator, Balancing Authority, or Reliability Coordinator Areas. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | High | [10 empty] | RC
EOP-006-1 | EOP-006-1 | R6. | Reliability Coordination – System Restoration | The Reliability Coordinator must have a coordinating role in system restoration to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall take actions to restore normal operations once an operating emergency has been mitigated in accordance with its restoration plan. | Retired | Will be replaced when EOP-006-2 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall have a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shut down area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and it its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: [Violation Risk Factor = High] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High | Yes | High | High - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.2. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Operating Processes for restoring the Interconnection. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.3. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.4. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.5. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - needs to specifically include RC approval to resyncing islands | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.6. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.7. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.8. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R1.9. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Criteria for transferring operations and authority back to the Balancing Authority. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - the GOs, DPs, TOPs and GOPs need to have a restoration plan | Yes | No - consider merging with EOP-005-2 to be comprehensive | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R2. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - all impacted functional entities should receive the plan, BAs need to be included; relevant DPs and GOPs | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High | Yes | Medium | Lower - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R3. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - all entities required to have a plan need to review it | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High | Yes | Medium | Medium - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R4. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall review their neighboring Reliability Coordinator’s restoration plans. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - all applicable entities should be included | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High | Yes | Medium | Medium - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R4.1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | No - all applicable entities should be included | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | Medium | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R5. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - no provision for what happens if the RC does not approve the TOP plan. If the RC does not approve, no requirement for Top to fix within a specific time | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High | Yes | Medium | Medium - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R5.1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - no provision for what happens if the RC does not approve the TOP plan. If the RC does not approve, no requirement for Top to fix within a specific time | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | Medium | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R6. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the implementation date. [Violation Risk Factor = Lower] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | Yes | Yes | Yes | Yes - consider combining with EOP-005-2 R6 and EOP-008-1 R2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | Low | Lower - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R7. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall work with its affected Generator Operators, and Transmission Operators as well as neighboring Reliability Coordinators to monitor restoration progress, coordinate restoration, and take actions to restore the BES frequency within acceptable operating limits. If the restoration plan cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate System restoration. [Violation Risk Factor = High] [Time Horizon = Real-time Operations] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | Yes - minutiae. This should be embedded in the plan (which should allow for coordination and flexibility). This is a logical action that does not require a std. This is not measurable. | [18 empty] | Yes | No | 0 | 0 | High | Yes | N/A | High - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R8. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The Reliability Coordinator shall coordinate or authorize resynchronizing islanded areas that bridge boundaries between Transmission Operators or Reliability Coordinators. If the resynchronization cannot be completed as expected the Reliability Coordinator shall utilize its restoration plan strategies to facilitate resynchronization. [Violation Risk Factor = High] [Time Horizon = Real-time Operations] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #4 | Yes - minutiae. This should be embedded in the plan | No |  |  | Yes - but does not need to be a separate R. This needs to be in the plan. The RC has te wide area view to make sure that re-syncing will not cause cascading. |  |  | No - Merge with EOP-006-2 R1.5. This is included, but needs to be more specific and beefed up | [11 empty] | Yes | No | 0 | 0 | High | Yes | N/A | High - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R9. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators to assure the proper execution of its restoration plan. This training program shall address the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | Yes - duplicative of PER-005 R3 | [18 empty] | Yes | No | 0 | 0 | High | Yes | N/A | Medium - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R9.1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | The coordination role of the Reliability Coordinator. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | Yes - duplicative of PER-005 R3 | [18 empty] | Yes | No |  |  | High |  | N/A | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R9.2. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Reestablishing the Interconnection. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | Yes - duplicative of PER-005 R3 | [18 empty] | Yes | No |  |  | High |  | N/A | No Individual VRF Assigned | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R10. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | Yes - duplicative of PER-005 R3 | [18 empty] | Yes | No | 0 | 0 | High | Yes | N/A | Medium - Pending | [10 empty] | RC
EOP-006-2 | EOP-006-2 | R10.1. | System Restoration Coordination | Ensure plans are established and personnel are prepared to enable effective coordination of the System restoration process to ensure reliability is maintained during restoration and priority is placed on restoring the Interconnection. | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #6 | Yes - duplicative of PER-005 R3 | [18 empty] | Yes | No |  |  | High |  | N/A | No Individual VRF Assigned | [10 empty] | RC
EOP-008-0 | EOP-008-0 | R1. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | Each Reliability Coordinator, Transmission Operator and Balancing Authority shall have a plan to continue reliability operations in the event its control center becomes inoperable. The contingency plan must meet the following requirements: | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 |  | no | [25 empty] | High |  |  | High | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.1. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.2. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The plan shall include procedures and responsibilities for providing basic tie line control and procedures and for maintaining the status of all inter-area schedules, such that there is an hourly accounting of all schedules. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | Combine EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.3. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.4. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other areas. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | High | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.5. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.6. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The plan shall include procedures and responsibilities for providing annual training to ensure that operating personnel are able to implement the contingency plans. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.7. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | The plan shall be reviewed and updated annually. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-0 | EOP-008-0 | R1.8. | Plans for Loss of Control Center Functionality | Each reliability entity must have a plan to continue reliability operations in the event its control center becomes inoperable. | Interim provisions must be included if it is expected to take more than one hour to implement the contingency plan for loss of primary control facility. | Retired | Will be replaced when EOP-008-1 becomes enforceable on 7/1/2013. |  | EOP-008 stands alone | [27 empty] | High |  |  | Medium | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R1. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include the following, at a minimum: [See standard for what the Operating Plan shall include] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R2. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes - consider combining with EOP-005-2 R6 and EOP-008-1 R2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Low | Lower - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R3. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards that depend on primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: [See standard for situations where a backup facility is not required] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High - Pending | [10 empty] | RC
EOP-008-1 | EOP-008-1 | R4. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that depend on a Balancing Authority and Transmission Operator’s primary control center functionality respectively. To avoid requiring tertiary functionality, backup functionality is not required during: [See standard for situations where a backup facility is not required] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High - Pending | BA | [15 empty] | TOP
EOP-008-1 | EOP-008-1 | R5. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. [See standard for update and approval requirements] | Current | Becomes enforceable on 7/1/2013. |  |  |  | Yes | Team determined entities should have a plan and update it | Yes - #5 | No | No |  |  | Yes | Yes | No - uses the word "annual" | Yes | Yes | Yes | No - 5.1 is not clear as to what an entity is to do | Yes | Yes | No - 5.1 is not clear as to what an entity is to do | Yes | Yes | No - 5.1 is not clear as to what an entity is to do | No - 5.1 is not clear as to what an entity is to do | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R6. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes - a little confusion on the language for "independent" - is it for control centers or functions | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R7. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: [See standard for what the annual test shall demonstrate] | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | Yes | Yes | No - uses the word "annual" | Yes | Yes | Yes | No - uses the word "annual" | Yes | Yes | No - uses the word "annual" | Yes | Yes | No - uses the word "annual" | No - uses the word "annual" | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-008-1 | EOP-008-1 | R8. | Loss of Control Center Functionality | Ensure continued reliable operations of the Bulk Electric System (BES) in the event that a control center becomes inoperable. | Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Current | Becomes enforceable on 7/1/2013. | [5 empty] | Yes - #5 | No | No |  |  | No - Six months is too long to go without a backup control center plan. Suggest two-four weeks to have a plan. The std should be to accomplish the plan not to provide it. The big missing piece is what the entity is going to use as a backup facility in the interim and a time to get this functioning. | Yes | No - The big missing piece is what the entity is going to use as a backup facility in the interim and a time to get this functioning. | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | High |  | Medium | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
EOP-009-0 | EOP-009-0 | R1. | Documentation of Blackstart Generating Unit Test Results | A system Blackstart Capability Plan (BCP) is necessary to ensure that the quantity and location of system blackstart generators are sufficient and that they can perform their expected functions as specified in overall coordinated Regional System Restorati | The Generator Operator of each blackstart generating unit shall test the startup and operation of each system blackstart generating unit identified in the BCP as required in the Regional BCP (Reliability Standard EOP-007-0_R1). Testing records shall include the dates of the tests, the duration of the tests, and an indication of whether the tests met Regional BCP requirements. | Retired | Will be replaced when EOP-006-2 and EOP-005-2 becomes enforceable on 7/1/2013. |  | EOP-005, -006 and -009 | [27 empty] | High |  |  | Medium |  |  |  | GOP
EOP-009-0 | EOP-009-0 | R2. | Documentation of Blackstart Generating Unit Test Results | A system Blackstart Capability Plan (BCP) is necessary to ensure that the quantity and location of system blackstart generators are sufficient and that they can perform their expected functions as specified in overall coordinated Regional System Restorati | The Generator Owner or Generator Operator shall provide documentation of the test results of the startup and operation of each blackstart generating unit to the Regional Reliability Organizations and upon request to NERC. | Retired | Will be replaced when EOP-006-2 and EOP-005-2 becomes enforceable on 7/1/2013. |  | EOP-005, -006 and -009 |  | No | [25 empty] | High |  |  | Lower |  |  | GO | GOP
FAC-001-0 | FAC-001-0 | R1. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | The Transmission Owner shall document, maintain, and publish facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Reliability Organization, subregional, Power Pool, and individual Transmission Owner planning criteria and facility connection requirements. The Transmission Owner’s facility connection requirements shall address connection requirements for: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  |  |  | Yes |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes for content; No for format | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R1.1. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Generation facilities, | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. | [5 empty] | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes for content; No for format | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R1.2. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Transmission facilities, and | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. | [5 empty] | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes for content; No for format | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R1.3. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | End-user facilities | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. | [5 empty] | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes for content; No for format | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | The Transmission Owner’s facility connection requirements shall address, but are not limited to, the following items: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  | Yes |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.1. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Procedures for coordinated joint studies of new facilities and their impacts on the interconnected transmission systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.10. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Power quality impacts. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.11. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Equipment Ratings. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.12. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Synchronizing of facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.13. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Maintenance coordination. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.14. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Operational issues (abnormal frequency and voltages). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.15. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Inspection requirements for existing or new facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.16. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Communications and procedures during normal and emergency operating conditions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.2. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Procedures for notification of new or modified facilities to others (those responsible for the reliability of the interconnected transmission systems) as soon as feasible. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.3. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Voltage level and MW and MVAR capacity or demand at point of connection. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.4. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Breaker duty and surge protection. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.5. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | System protection and coordination. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.6. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Metering and telecommunications. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.7. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Grounding and safety issues. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.8. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Insulation and insulation coordination. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R2.1.9. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | Voltage, Reactive Power, and power factor control. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  | Streamline the items in R2 by removing some…see comments in FAC-001-1 R3 |  |  |  | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-0 | FAC-001-0 | R3. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners must establish facility connection and performance requirements. | The Transmission Owner shall maintain and update its facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and NERC on request (five business days). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-001-1 if approved by FERC. |  |  |  | Yes |  | No | Yes - administrative. | No | [17 empty] | No |  | 0 | 0 | High |  | N/A | Medium | [15 empty] | TO
FAC-001-1 | FAC-001-1 | R1. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners and Generator Owners must establish Facility connection and performance requirements. | The Transmission Owner shall document, maintain, and publish Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. The Transmission Owner’s Facility connection requirements shall address connection requirements for: 1.1. Generation Facilities, 1.2. Transmission Facilities, and 1.3. End-user Facilities | Board Adopted | Board adopted 2/9/2012; Filed with FERC 7/30/2012 |  | Team had long discussion on the fact that FAC001 requires the TO to publish the FCR, but it does not put a requirement on anyone wanting to interconnect to meet the requirements in the FCR. NERC should work with industry to see if an enforcement on entities wanting to interconnect should be added to the NERC stds |  | Yes | Team determined to keep this as it is the only requirement that provides a technical basis for interconnection | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Medium | Medium | [15 empty] | TO
FAC-001-1 | FAC-001-1 | R2. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners and Generator Owners must establish Facility connection and performance requirements. | Each applicable Generator Owner shall, within 45 days of having an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems (under FAC-002-1), document and publish its Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. | Board Adopted | Board adopted 2/9/2012; Filed with FERC 7/30/2012 |  |  |  | Yes | Team determined to keep as this is the only requirement for GOs that provides a technical basis for interconnection | Yes - #1, 3, 5 | No | No |  |  | No - "suggestions for improvements " under R1 | No - the language "applicable Regional…" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | Yes | Yes | No - the word "published" is not clear | No - the language "applicable Regional …" is not clear | Yes | Yes | Yes | 0 | 9 | High |  | Low | Medium |  |  | GO
FAC-001-1 | FAC-001-1 | R3. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners and Generator Owners must establish Facility connection and performance requirements. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall address the following items in its Facility connection requirements: [See standard pdf for requirements] | Board Adopted | Board adopted 2/9/2012; Filed with FERC 7/30/2012 |  | Streamline the items in 3.1 by removing- 3.1.1, 3.1.2,3.1.3,3.1.9,3.1.11,3.1.13,3.1.15, 3.1.16 |  | Yes | Team determined that this requirement was necessary for support of the interconnection processes for new facilities. However, the team is recommending for the requirement to be streamlined and to remove some of the sub-requirements | Yes - #1, 3, 5 | No | No |  |  | No - see "suggestions for improvements" for items that can be removed | Yes | No - see "suggestions for improvements" for items that can be removed | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 12 | High |  | Medium | Medium |  |  | GO | [12 empty] | TO
FAC-001-1 | FAC-001-1 | R4. | Facility Connection Requirements | To avoid adverse impacts on reliability, Transmission Owners and Generator Owners must establish Facility connection and performance requirements. | The Transmission Owner shall maintain and update its Facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Entity, and ERO on request (five business days). | Board Adopted | Board adopted 2/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No |  | 0 | 0 | High |  | N/A | Medium | [15 empty] | TO
FAC-002-1 | FAC-002-1 | R1. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | Current | Currently enforceable standard. |  |  |  | Yes |  | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - has reference to TPL… also the reference is to an old version | No - the phrase " seeking to integrate" should be re-written to say "seeking to interconnect" | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R1.1. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - has reference to TPL… also the reference is to an old version | No - the phrase " seeking to integrate" should be re-written to say "seeking to interconnect" | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R1.2. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | Current | Currently enforceable standard. | [5 empty] | No - language is general and does not add specifics - the substance is in 1.4 | [7 empty] | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | [11 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R1.3. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | Current | Currently enforceable standard. | [5 empty] | No - language is general and does not add specifics - the substance is in 1.4 | [7 empty] | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | [11 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R1.4. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under Boardh normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - has reference to TPL… also the reference is to an old version | No - the phrase " seeking to integrate" should be re-written to say "seeking to interconnect" | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R1.5. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | Current | Currently enforceable standard. | [5 empty] | No - language is general and does not add specifics - the substance is in 1.4 |  | No | [5 empty] | No - merge 1.1 and 1.4; retire 1.2, 1.3 and 1.5. the new 1.1 and 1.4 should say 'the assessment shall address requirements as identified in the FCR and ther performance requirments as identified in the TPL stds." | [11 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Medium |  | DP | GO |  |  | LSE | [9 empty] | TO
FAC-002-1 | FAC-002-1 | R2. | Coordination of Plans For New Generation, Transmission, and End-User Facilities | To avoid adverse impacts on reliability, Generator Owners and Transmission Owners and electricity end-users must meet facility connection and performance requirements. | The Planning Authority, Transmission Planner, Generator Owner, Transmission Owner, Load-Serving Entity, and Distribution Provider shall each retain its documentation (of its evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems) for three years and shall provide the documentation to the Regional Reliability Organization(s) and NERC on request (within 30 calendar days). | Current | Currently enforceable standard. |  |  | Yes |  |  | No | Yes - Para 81 Phase 1 | No | [17 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | GO |  |  | LSE |  | PA | PC | [6 empty] | TO |  | TP
FAC-003-1 | FAC-003-1 | R1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The Transmission owner shall prepare, and keep current, a formal transmission vegetation management (TVM). The TVMP shall include the Transmission Owner's objectives, practices, approved procedures, and work Specifications. 1. ANSI A300, Tree Care Operations – Tree, Shrub, and Other Woody Plant Maintenance – Standard Practices, while not a requirement of this standard, is considered to be an industry best practice. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | No - IEEE std 516 that is included in this FAC003-1 was not designed for a vegetation mgt application. | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No - the language in R1 is not clear and defined; no-format | Yes | Yes | Yes | Yes | No - sustained outage not used left unclear | No; use of technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 0 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The TVMP shall define a schedule for and the type (aerial, ground) of ROW vegetation inspections. This schedule should be flexible enough to adjust for changing conditions. The inspection schedule shall be based on the anticipated growth of vegetation and any other environmental or operational factors that could impact the relationship of vegetation to the Transmission Owner’s transmission lines. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No - however after the first sentence, the rest is a guide. |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No - the language in R1 is not clear and defined; no-format | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | Medium | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The Transmission Owner, in the TVMP, shall identify and document clearances between vegetation and any overhead, ungrounded supply conductors, taking into consideration transmission line voltage, the effects of ambient temperature on conductor sag under maximum design loading, and the effects of wind velocities on conductor sway. Specifically, the Transmission Owner shall establish clearances to be achieved at the time of vegetation management work identified herein as Clearance 1, and shall also establish and maintain a set of clearances identified herein as Clearance 2 to prevent flashover between vegetation and overhead ungrounded supply conductors. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No - the language in R1 is not clear and defined; no-format | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.2.1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Clearance 1 — The Transmission Owner shall determine and document appropriate clearance distances to be achieved at the time of transmission vegetation management work based upon local conditions and the expected time frame in which the Transmission Owner plans to return for future vegetation management work. Local conditions may include, but are not limited to: operating voltage, appropriate vegetation management techniques, fire risk, reasonably anticipated tree and conductor movement, species types and growth rates, species failure characteristics, local climate and rainfall patterns, line terrain and elevation, location of the vegetation within the span, and worker approach distance requirements. Clearance 1 distances shall be greater than those defined by Clearance 2 below. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No - Clearance 2 is the minimum clearance for reliability; clearance 1 is merely the entity's plan |  | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.2.2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Clearance 2 — The Transmission Owner shall determine and document specific radial clearances to be maintained between vegetation and conductors under all rated electrical operating conditions. These minimum clearance distances are necessary to prevent flashover between vegetation and conductors and will vary due to such factors as altitude and operating voltage. These Transmission Owner-specific minimum clearance distances shall be no less than those set forth in the Institute of Electrical and Electronics Engineers (IEEE) Standard 516-2003 (Guide for Maintenance Methods on Energized Power Lines) and as specified in its Section 4.2.2.3, Minimum Air Insulation Distances without Tools in the Air Gap. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.2.2.1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Where transmission system transient overvoltage factors are not known, clearances shall be derived from Table 5, IEEE 516-2003, phase-to-ground distances, with appropriate altitude correction factors applied. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.2.2.2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Where transmission system transient overvoltage factors are known, clearances shall be derived from Table 7, IEEE 516-2003, phase-to-phase voltages, with appropriate altitude correction factors applied. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.3. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | All personnel directly involved in the design and implementation of the TVMP shall hold appropriate qualifications and training, as defined by the Transmission Owner, to perform their duties. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | Medium | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.4. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Each Transmission Owner shall develop mitigation measures to achieve sufficient clearances for the protection of the transmission facilities when it identifies locations on the ROW where the Transmission Owner is restricted from attaining the clearances specified in Requirement 1.2.1. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R1.5. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Each Transmission Owner shall establish and document a process for the immediate communication of vegetation conditions that present an imminent threat of a transmission line outage. This is so that action (temporary reduction in line rating, switching line out of service, etc.) may be taken until the threat is relieved. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | Yes | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | No | Yes | Yes | Yes | Yes | No; sustained outage not used left unclear | No; technical basis of IEEE 516 was incorrect | Yes; (FAC-003-1 does not refer to IROL) | No; unclear what TO objectives should state | No | Yes | Yes | Yes | 1 | 6 | Low |  | High | High | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The Transmission Owner shall create and implement an annual plan for vegetation management work to ensure the reliability of the system. The plan shall describe the methods used, such as manual clearing, mechanical clearing, herbicide treatment, or other actions. The plan should be flexible enough to adjust to changing conditions, taking into consideration anticipated growth of vegetation and all other environmental factors that may have an impact on the reliability of the transmission systems. Adjustments to the plan shall be documented as they occur. The plan should take into consideration the time required to obtain permissions or permits from landowners or regulatory authorities. Each Transmission Owner shall have systems and procedures for documenting and tracking the planned vegetation management work and ensuring that the vegetation management work was completed according to work specifications. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES | No - leaves out GO owned lines to the BES | No - the language in R2 should be more definitive & lay out the specific items the annual plan should include | No - merge R1 and R2- R1 says you must have a program and R2 says must then have an annual plan | Yes | Yes | No - the language gives examples but does not lay out the specific requirements | Yes | Yes | No | Yes | Yes | No; unclear what TO objectives should state | No | No; undefined terms | Yes | Yes | 0 | 6 | Low |  | High | High | [15 empty] | TO
Low
FAC-003-1 | FAC-003-1 | R3. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The Transmission Owner shall report quarterly to its RRO, or the RRO’s designee, sustained transmission line outages determined by the Transmission Owner to have been caused by vegetation. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 |  |  |  | Yes |  | No | Yes - adminstrative amd data reporting | [18 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Multiple sustained outages on an individual line, if caused by the same vegetation, shall be reported as one outage regardless of the actual number of outages within a 24-hour period. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The Transmission Owner is not required to report to the RRO, or the RRO’s designee, certain sustained transmission line outages caused by vegetation: (1) Vegetation-related outages that result from vegetation falling into lines from outside the ROW that result from natural disasters shall not be considered reportable (examples of disasters that could create non-reportable outages include, but are not limited to, earthquakes, fires, tornados, hurricanes, landslides, wind shear, major storms as defined either by the Transmission Owner or an applicable regulatory body, ice storms, and floods), and (2) Vegetation-related outages due to human or animal activity shall not be considered reportable (examples of human or animal activity that could cause a non-reportable outage include, but are not limited to, logging, animal severing tree, vehicle contact with tree, arboricultural activities or horticultural or agricultural activities, or removal or digging of vegetation). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.3. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The outage information provided by the Transmission Owner to the RRO, or the RRO’s designee, shall include at a minimum: the name of the circuit(s) outaged, the date, time and duration of the outage; a description of the cause of the outage; other pertinent comments; and any countermeasures taken by the Transmission Owner. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.4. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | An outage shall be categorized as one of the following: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.4.1. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Category 1 — Grow-ins: Outages caused by vegetation growing into lines from vegetation inside and/or outside of the ROW; | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.4.2. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Category 2 — Fall-ins: Outages caused by vegetation falling into lines from inside the ROW; | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R3.4.3. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | Category 3 — Fall-ins: Outages caused by vegetation falling into lines from outside the ROW. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [15 empty] | TO
FAC-003-1 | FAC-003-1 | R4. | Transmission Vegetation Management Program | To improve the reliability of the electric transmission systems by preventing outages from vegetation located on transmission rights-of-way (ROW) and minimizing outages from vegetation located adjacent to ROW, maintaining clearances between transmission l | The RRO shall report the outage information provided to it by Transmission Owner’s, as required by Requirement 3, quarterly to NERC, as well as any actions taken by the RRO as a result of any of the reported outages. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by FAC-003-2 OR FAC-003-3 if approved by FERC. FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 |  |  |  | Yes |  | No | Yes - adminstrative amd data reporting | Yes | [17 empty] | No |  |  |  | Low |  | N/A | Lower | [13 empty] | RRO
FAC-003-2 | FAC-003-2 | R1. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | High | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R2. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | Medium | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R3. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | Lower | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R4. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | Medium | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R5. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | Medium | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R6. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No |  |  | No - leaves out GO owned lines to the BES |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 11 | Low |  |  | Medium | [15 empty] | TO
FAC-003-2 | FAC-003-2 | R7. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t |  | Board adopted, but overtaken by future version | FAC-003-2: Board adoption 11/3/2011; Filed with FERC 12/21/2011 | [5 empty] | Yes - #1, 9 | No | No - but after the first sentence, the rest is a guide. |  |  | No - leaves out GO owned lines to the BES |  | Yes | No, (mostly compliance discussion; could state 100% in R1 and R2) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes |  | 10 | Low |  |  | Medium | [15 empty] | TO
FAC-003-3 | FAC-003-3 | R1. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below: [See Standard pdf for further information] | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | High |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R2. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below: [See Standard pdf for further information] | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R3. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: [See Standard pdf for further information] | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Lower |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R4. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment. | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - "intentional time delay" is difficult to measure | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R5. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | When a applicable Transmission Owner and applicable Generator Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments. | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | No - the language "shall take corrective actions" is not clear; meaning of term "annual" in R5 and R7 is not clear. | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R6. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW. | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No, requires FAC-014 to define IROL | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-003-3 | FAC-003-3 | R7. | Transmission Vegetation Management | To maintain a reliable electric transmission system by using a defense-in-depth strategy to manage vegetation located on transmission rights of way (ROW) and minimize encroachments from vegetation located adjacent to the ROW, thus preventing the risk of t | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include: [See Standard pdf for further information] | Board Adopted | FAC-003-3: Board adoption 5/9/2012; Filed with FERC 7/30/2012 | [5 empty] | Yes - #1, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - R7 requires the TO to complete 100% of its annual veg mgt work plan, but there are no requirements in the std to develop an annual veg mgt work plan-- language in R3 could be read to imply an annual veg mgt plan but wording is not clear. | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-008-3 | FAC-008-3 | R1. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | No - R2 language of 'shall have documented methodology' is better than language of 'documentation for determining' in R1 | Yes | No - R2 language of 'shall have documented methodology' is better than language of 'documentation for determining' in R1 | Yes | Yes | 3 | 9 | Low |  | High | Lower | [8 empty] | GO
FAC-008-3 | FAC-008-3 | R1.1. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | Yes - but must have basis |  |  | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Low |  | High | Lower | [8 empty] | GO
FAC-008-3 | FAC-008-3 | R1.2. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [See standard for documentation requirements] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | Yes - statement about most limiting facility is used a lot |  |  | No | Yes | Yes | Yes | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | No - R1.2 is not clear | Yes | No | Yes | No | 2 | 9 | Low |  | High | Lower | [8 empty] | GO
FAC-008-3 | FAC-008-3 | R2. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [See standard for methodology requirements] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | No - the subparts could be listed as guide |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 11 | Low |  | High | Medium | [8 empty] | GO
FAC-008-3 | FAC-008-3 | R3. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: [See standard for methodology requirements] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Medium | [15 empty] | TO
FAC-008-3 | FAC-008-3 | R4. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. | Current | Currently enforceable standard. It became enforceale on 1/1/2013. |  |  | Yes | Yes |  | No | Yes - Para 81 Phase 1 | No | [8 empty] | No - the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | [8 empty] | No |  | 0 | 0 | Low |  | N/A | Lower |  |  | GO | [12 empty] | TO
FAC-008-3 | FAC-008-3 | R5. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. | Current | Currently enforceable standard. It became enforceale on 1/1/2013. |  |  |  | Yes |  | No | Yes - Para 81 Phase 1 | No | [8 empty] | No - the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | [8 empty] | No |  | 0 | 0 | Low |  | N/A | Lower |  |  | GO | [12 empty] | TO
FAC-008-3 | FAC-008-3 | R6. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | High | Medium |  |  | GO | [12 empty] | TO
FAC-008-3 | FAC-008-3 | R7. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes - #3, 10 | No - from R8: retire R8 and rewrite R7 to read "Each TO and GO…", | No |  |  | Yes | No - need to add BA as he needs to kNow Generator ratings | Yes | No - R7 should read "Each TO and GO…", and then retire R8 | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Low |  | Medium | Medium |  |  | GO
FAC-008-3 | FAC-008-3 | R8. | Facility Ratings | To ensure that Facility Ratings used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on technically sound principles. A Facility Rating is essential for the determination of System Operating Limits. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [See standard for requirements of providing requested information] | Current | Currently enforceable standard. It became enforceale on 1/1/2013. | [5 empty] | Yes | No - however, should retire R8 and rewrite R7 to read "Each TO and GO…", | No |  |  | Yes | No - need to add BA as he needs to kNow Generator ratings | Yes | No - Should retire R8 and rewrite R7 to read "Each TO and GO…", | Yes | Yes | No; the requirement should clearly state that when a trasmission facility or generator facility is jointly owned facility, that the joint owners must reach agreement on the selected methodology | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Low |  | Medium | Medium |  |  | GO | [12 empty] | TO
FAC-010-2 | FAC-010-2.1 | R1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall have a documented SOL Methodology for use in developing SOLs within its Planning Authority Area. This SOL Methodology shall: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | yes - but PA should be PC | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - R1.1 refers to 'planning horizon' -- this is not clear; ie, not a defined term | Yes | No - would suggest that language say that shall develop a SOL methodology and use that methodology to determine SOLs-- get rid of develop, establish, determine construct | Yes | Yes | 3 | 8 | Low |  | Medium | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R1.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Be applicable for developing SOLs used in the planning horizon. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes - but PA should be PC | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No; planning horizon not defined; Long-term PH is in Glossary | Yes | Yes | 3 | 9 | Low |  | Medium | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R1.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | State that SOLs shall not exceed associated Facility Ratings. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes - but PA should be PC | Yes - but PA should be PC | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R1.3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes - but PA should be PC | Yes - but PA should be PC | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes | No on content; No on format | Yes | Yes | Yes | Yes | No - no definition of acceptable performance | Yes | No - sub-requirements point to TPL stds | Yes | Yes | No - would suggest that language say that shall develop a SOL methodology and use that methodology to determine SOLs-- get rid of develop, establish, determine construct | Yes | Yes | 1 | 8 | Low |  | Medium | No Individual VRF Assigned | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | High | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | High | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.2.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.2.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Loss of any generator, line, transformer, or shunt device without a Fault. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.2.3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.3.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.3.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | System reconfiguration through manual or automatic control or protection actions. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.4. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.5. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.6. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R2.6.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table |  |  | No - team does Not understand the rationale for R2.2, which seems to be a subset of the full TPL requirements | Yes - but PA should be PC | Yes | No -This is a restate of TPL-003-2b Table 1. These req'ts use the Table to bound limits for development of SOLs. | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; needs description of study cases from TPL-003 | Yes | Yes | No; need to use consistent term for determining, deveoloping or establishing SOL's | Yes | Yes | 2 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes | More appropriate as a Guideline. This is a checklist. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Selection of applicable Contingencies. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Level of detail of system models used to determine SOLs. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.4. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Allowed uses of Special Protection Systems or Remedial Action Plans. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.5. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Anticipated transmission system configuration, generation dispatch and Load level. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R3.6. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes | No - move to R1 of this std and make it R1.4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R4. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall issue its SOL Methodology, and any change to that methodology, to all of the following prior to the effectiveness of the change: | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | Yes | More appropriate as a Guideline. Description of appropriate coordination does not rise to a Standard. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R4.1. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R4.2. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R4.3. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-010-2 | FAC-010-2.1 | R5. | System Operating Limits Methodology for the Planning Horizon | To ensure that System Operating Limits (SOLs) used in the reliable planning of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Planning Authority shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | Current | Currently enforceable standard. |  |  | Yes | Yes |  | No | Yes - Para 81 Phase 1 | No | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-011-2 | FAC-011-2 | R1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator shall have a documented methodology for use in developing SOLs (SOL Methodology) within its Reliability Coordinator Area. This SOL Methodology shall: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R1.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Be applicable for developing SOLs used in the operations horizon. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R1.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | State that SOLs shall not exceed associated Facility Ratings. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R1.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Include a description of how to identify the subset of SOLs that qualify as IROLs. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Low |  | Medium | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator’s SOL Methodology shall include a requirement that SOLs provide BES performance consistent with the following: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | No Individual VRF Assigned | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | High | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | High | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.2.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.2.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Loss of any generator, line, transformer, or shunt device without a Fault. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.2.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | In determining the system’s response to a single Contingency, the following shall be acceptable: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes - the detailed conditions from the TPL table | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.3.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes - the detailed conditions from the TPL table | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.3.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies | Current | Currently enforceable standard. | [5 empty] | No | No | Yes - the detailed conditions from the TPL table | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.3.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | System reconfiguration through manual or automatic control or protection actions. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes - the detailed conditions from the TPL table | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R2.4. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes - the detailed conditions from the TPL table | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator’s methodology for determining SOLs, shall include, as a minimum, a description of the following, along with any reliability margins applied for each: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | Yes | More appropriate as a Guideline. This is a checklist. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Selection of applicable Contingencies | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.3.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | [17 empty] | No |  | 0 | 0 | Low |  | N/A | No Individual VRF Assigned | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.4. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Level of detail of system models used to determine SOLs. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.5. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Allowed uses of Special Protection Systems or Remedial Action Plans. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.6. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Anticipated transmission system configuration, generation dispatch and Load level | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The way that R3 is currently drafted (as a checklist of items to consider), there is no loss to reliability to retire the requirement and have this be a guide. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R3.7. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes |  |  | Yes | Yes | Yes | No - move to R1 of this std and make it R1.4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R4. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator shall issue its SOL Methodology and any changes to that methodology, prior to the effectiveness of the Methodology or of a change to the Methodology, to all of the following: | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | Yes | More appropriate as a Guideline. Description of appropriate coordination does not rise to a Standard. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R4.1. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R4.2. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R4.3. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Each Transmission Operator that operates in the Reliability Coordinator Area. | Current | Currently enforceable standard. | [5 empty] | No | No | Yes | The team recommended removing this requirement because they felt that it did not raise to the level of a std, however are recommending a guide as they felt that the coordination effort is important. | [16 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-011-2 | FAC-011-2 | R5. | System Operating Limits Methodology for the Operations Horizon | To ensure that System Operating Limits (SOLs) used in the reliable operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | If a recipient of the SOL Methodology provides documented technical comments on the methodology, the Reliability Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the SOL Methodology and, if no change will be made to that SOL Methodology, the reason why. | Current | Currently enforceable standard. |  |  | Yes | Yes |  | No | Yes - Para 81 Phase 1 | No | [17 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [10 empty] | RC
FAC-012 | FAC-012 | all |  |  |  | Not approved in Order 693 | Filed with FERC but not approved in Order 693. Replaced with FAC-010-1, FAC-011-1, and FAC-014-1. | [29 empty] | Low
FAC-013-1 | FAC-013-1 | R1. | Establish and Communicate Transfer Capabilities | To ensure that Transfer Capabilities used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator and Planning Authority shall each establish a set of inter-regional and intra-regional Transfer Capabilities that is consistent with its current Transfer Capability Methodology. | Not approved in Order 693 | Currently enforceable standard. Will be replaced when FAC-013-2 becomes enforceable on 4/1/2013. |  |  |  | Yes | [25 empty] | Low |  |  | Medium | [7 empty] | PA | PC |  | RC
FAC-013-1 | FAC-013-1 | R2. | Establish and Communicate Transfer Capabilities | To ensure that Transfer Capabilities used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator and Planning Authority shall each provide its inter-regional and intra-regional Transfer Capabilities to those entities that have a reliability-related need for such Transfer Capabilities and make a written request that includes a schedule for delivery of such Transfer Capabilities as follows: | Not approved in Order 693 | Currently enforceable standard. Will be replaced when FAC-013-2 becomes enforceable on 4/1/2013. |  |  |  | Yes | [25 empty] | Low |  |  | Medium | [7 empty] | PA | PC |  | RC
FAC-013-1 | FAC-013-1 | R2.1. | Establish and Communicate Transfer Capabilities | To ensure that Transfer Capabilities used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator shall provide its Transfer Capabilities to its associated Regional Reliability Organization(s), to its adjacent Reliability Coordinators, and to the Transmission Operators, Transmission Service Providers and Planning Authorities that work in its Reliability Coordinator Area. | Not approved in Order 693 | Currently enforceable standard. Will be replaced when FAC-013-2 becomes enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium | [10 empty] | RC
FAC-013-1 | FAC-013-1 | R2.2. | Establish and Communicate Transfer Capabilities | To ensure that Transfer Capabilities used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall provide its Transfer Capabilities to its associated Reliability Coordinator(s) and Regional Reliability Organization(s), and to the Transmission Planners and Transmission Service Provider(s) that work in its Planning Authority Area. | Not approved in Order 693 | Currently enforceable standard. Will be replaced when FAC-013-2 becomes enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R1. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | Each Planning Coordinator shall have a documented methodology it uses to perform an annual assessment of Transfer Capability in the Near-Term Transmission Planning Horizon (Transfer Capability methodology). The Transfer Capability methodology shall include, at a minimum, the following information: | Current | Becomes enforceable on 4/1/2013. |  | This Standard could be combined with MOD-001 (TOP and TSP in operations horizon). If MOD -001, -028, -029 and -030 are retired, there is a gap for the near term operating horizon. Review MODs for proper language to pull into a revised FAC-013-3 that addresses Boardh the near term planning horizon and the operational planning horizon. Review "transfer capability" and "total transfer capability" - these seem to be redundant or difference is not clear. Use of the term "transfer capability" should be revised to TTC. |  |  |  | Yes - #1, 7 | No | No |  |  | Yes - TC should be TTC; if MODs stay, there is no gap; if MODs are retired there is a gap | Yes | Yes | No - incorporate MOD-001, -028, -029 and -030 per comments in suggestions for improvement column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No; annual basis is vague | Yes | Yes | Yes | Yes | 3 | 10 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R2. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | Each Planning Coordinator shall issue its Transfer Capability methodology, and any revisions to the Transfer Capability methodology, to the following entities subject to the following: | Current | Becomes enforceable on 4/1/2013. | [5 empty] | No | Yes - administrative | No | [5 empty] | No - consolidate necessary parts into R5 and R6 (see below) | [11 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R3. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | If a recipient of the Transfer Capability methodology provides documented concerns with the methodology, the Planning Coordinator shall provide a documented response to that recipient within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Transfer Capability methodology and, if no change will be made to that Transfer Capability methodology, the reason why. | Current | Becomes enforceable on 4/1/2013. |  |  | Yes | Yes |  | No | Yes - Para 81 Phase 1 | [18 empty] | No |  | 0 | 0 | Low |  | N/A | Lower | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R4. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | During each calendar year, each Planning Coordinator shall conduct simulations and document an assessment based on those simulations in accordance with its Transfer Capability methodology for at least one year in the Near-Term Transmission Planning Horizon. | Current | Becomes enforceable on 4/1/2013. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes - clarify PA/PC | Yes | Yes | Yes | Yes | Yes | No; calendar year and annual are not the same | Yes | Yes | Yes | Yes | No; "year" is vague - needs word "calendar" | No | No - uses calendar year and annual | Yes | Yes | 3 | 8 | Low |  | Medium | Medium | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R5. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | Each Planning Coordinator shall make the documented Transfer Capability assessment results available within 45 calendar days of the completion of the assessment to the recipients of its Transfer Capability methodology pursuant to Requirement R2, Parts 2.1 and Part 2.2. However, if a functional entity that has a reliability related need for the results of the annual assessment of the Transfer Capabilities makes a written request for such an assessment after the completion of the assessment, the Planning Coordinator shall make the documented Transfer Capability assessment results available to that entity within 45 calendar days of receipt of the request | Current | Becomes enforceable on 4/1/2013. |  |  |  | Yes | Team determined that sharing of transfer capability results with other PCs within its interconnection provides a reliability benefit | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R2, R5, and R6; R2.2 is too vague and wide open | Yes | Yes | No - tighten up "entities that have a reliability need" - R6 is better | Yes | Yes | Yes | Yes | Yes | No - tighten up "entities that have a reliability need" - R6 is better | Yes | Yes | Yes | Yes | 3 | 9 | Low |  | Low | Lower | [7 empty] | PA | PC
FAC-013-2 | FAC-013-2 | R6. | Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon | To ensure that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting Facilities that could impact the Bulk Electric System’s (BES) ability to reliably transf | If a recipient of a documented Transfer Capability assessment requests data to support the assessment results, the Planning Coordinator shall provide such data to that entity within 45 calendar days of receipt of the request. The provision of such data shall be subject to the legal and regulatory obligations of the Planning Coordinator’s area regarding the disclosure of confidential and/or sensitive information. | Current | Becomes enforceable on 4/1/2013. |  |  |  | Yes | Team determined that sharing of transfer capability results with other PCs within its interconnection provides a reliability benefit | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R2, R5, and R6; R2.2 is too vague and wide open | Yes | Yes | No - tighten up "entities that have a reliability need" - R6 is better | Yes | Yes | Yes | Yes | Yes | No - tighten up "entities that have a reliability need" - R6 is better | Yes | Yes | Yes | Yes | 3 | 9 | Low |  | Low | Lower | [7 empty] | PA | PC
FAC-014-2 | FAC-014-2 | R1. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator shall ensure that SOLs, including Interconnection Reliability Operating Limits (IROLs), for its Reliability Coordinator Area are established and that the SOLs (including Interconnection Reliability Operating Limits) are consistent with its SOL Methodology. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | No - but consider a combined fac11/14 std being placed into the iro and/or top family stds | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - R1 speaks to "SOL Methodology" but it does not explicitly reference FAC 011 | No - use the framework that you DEVELOP a methodolgy and then you use the methdology to DETERMINE the value | Yes | Yes | Yes | Yes | 3 | 9 | Medium |  | High | Medium | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R2. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Transmission Operator shall establish SOLs (as directed by its Reliability Coordinator) for its portion of the Reliability Coordinator Area that are consistent with its Reliability Coordinator’s SOL Methodology. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - needs a new requirement that reads "the RC shall ensure that the determinatin of sols and irols are coordinated among its TOPs and directly interconnected (ie, have AC ties ) RCs" Bill - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | No - see r1 comment | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Medium |  | High | Medium | [16 empty] | TOP
FAC-014-2 | FAC-014-2 | R3. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall establish SOLs, including IROLs, for its Planning Authority Area that are consistent with its SOL Methodology. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | Yes | Yes | Yes | Yes; but verify with TPL series | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No; this establishes the limits, but what happens next? | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | High | Medium | [7 empty] | PA | PC
FAC-014-2 | FAC-014-2 | R4. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Transmission Planner shall establish SOLs, including IROLs, for its Transmission Planning Area that are consistent with its Planning Authority’s SOL Methodology. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - needs a new requirement that reads "the RC shall ensure that the determinatin of SOLs and IROLs are coordinated among its TOPs and directly interconnected (ie, have AC ties ) RCs" Incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | Yes; but verify with TPL series | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No; this establishes the limits, but what happens next? | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Medium |  | High | Medium | [17 empty] | TP
FAC-014-2 | FAC-014-2 | R5. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator, Planning Authority and Transmission Planner shall each provide its SOLs and IROLs to those entities that have a reliability-related need for those limits and provide a written request that includes a schedule for delivery of those limits as follows: | Current | Currently enforceable standard. |  | Team thinks that R5 should be streamlined to stop after the phrase "reliability-related needs", and . Do not need all of the sub-requirements R5.1-R5.4. |  |  |  | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | Yes | Yes | Yes on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - all the subrequirements not needed- see 'suggestions for improvement' | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | Medium | High | [7 empty] | PA | PC |  | RC | [6 empty] | TP
FAC-014-2 | FAC-014-2 | R5.1. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | High | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R5.1.1. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R5.1.2. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The value of the IROL and its associated Tv. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R5.1.3. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The associated Contingency(ies). | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R5.1.4. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [10 empty] | RC
FAC-014-2 | FAC-014-2 | R5.2. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [16 empty] | TOP
FAC-014-2 | FAC-014-2 | R5.3. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [7 empty] | PA | PC
FAC-014-2 | FAC-014-2 | R5.4. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes - streamline-- see "suggestions for improvements" | Yes | No - PA should be PC | Yes; (verify with IRO series) | No | Yes | No | Yes | Yes | No | Yes | No; this establishes the limits but IRO-008-1 R1, 2, 3 requires operation to the limit | No | No | No | Yes | Yes | 2 | 5 | Medium |  | Medium | Medium | [17 empty] | TP
FAC-014-2 | FAC-014-2 | R6. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall identify the subset of multiple contingencies (if any), from Reliability Standard TPL-003 which result in stability limits. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes | Yes | Yes | No - need to address how it fits with TPL-003 it references as well as FAC-011 R3.3 that references it | No on content; No on format | Yes | Yes | Yes | Yes | Yes | Yes | No; this refers back to TPL-003 for contingencies; also FAC 11 R3 points to Fac 14 R6 | No; this refers back to TPL-003 for contingencies; also FAC 11 R3 points to Fac 14 R6 | Yes | Yes | Yes | Yes | 2 | 8 | Medium |  | Medium | Medium | [7 empty] | PA | PC
FAC-014-2 | FAC-014-2 | R6.1. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes | Yes | No - PA should be PC | Yes; (verify with TPL series) | No | Yes | No | Yes | Yes | Yes | Yes | No; this refers back to TPL-003 for contingencies | Yes | Yes | Yes | Yes | Yes | 2 | 9 | Medium |  | Medium | Medium | [7 empty] | PA | PC
FAC-014-2 | FAC-014-2 | R6.2. | Establish and Communicate System Operating Limits | To ensure that System Operating Limits (SOLs) used in the reliable planning and operation of the Bulk Electric System (BES) are determined based on an established methodology or methodologies. | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 10 | No | No |  |  | Yes | Yes | No - PA should be PC | Yes; (verify with TPL series) | No | Yes | No | Yes | Yes | Yes | Yes | No; this refers back to TPL-003 for contingencies | Yes | Yes | Yes | Yes | Yes | 2 | 9 | Medium |  | Medium | Medium | [7 empty] | PA | PC
FAC-501-WECC-1 | FAC-501-WECC-1 | R2. | Transmission Maintenance | To ensure the Transmission Owner of a transmission path identified in the table titled “Major WECC Transfer Paths in the Bulk Electric System” including associated facilities has a Transmission Maintenance and Inspection Plan (TMIP); and performs and docu | Transmission Owners shall include the maintenance categories in Attachment 1-FAC-501-WECC-1 when developing their TMIP. [Time Horizon: Operations Assessment] | Regional | [30 empty] | Medium |  |  | Medium | [15 empty] | TO
FAC-501-WECC-1 | FAC-501-WECC-1 | R1. | Transmission Maintenance | To ensure the Transmission Owner of a transmission path identified in the table titled “Major WECC Transfer Paths in the Bulk Electric System” including associated facilities has a Transmission Maintenance and Inspection Plan (TMIP); and performs and docu | Transmission Owners shall have a TMIP detailing their inspection and maintenance requirements that apply to all transmission facilities necessary for System Operating Limits associated with each of the transmission paths identified in table titled “Major WECC Transfer Paths in the Bulk Electric System.” [Time Horizon: Long-term Planning] | Regional |  |  | Discussion whether this would be necessary for a continent wide std, however the team determined that WECC has the right to create a standard, but the team did not believe that there was a need for a continent-wide standard. |  |  |  | Yes | [23 empty] | Medium |  |  | Medium | [15 empty] | TO
FAC-501-WECC-1 | FAC-501-WECC-1 | R1.1. | Transmission Maintenance | To ensure the Transmission Owner of a transmission path identified in the table titled “Major WECC Transfer Paths in the Bulk Electric System” including associated facilities has a Transmission Maintenance and Inspection Plan (TMIP); and performs and docu | Transmission Owners shall annually review their TMIP and update as required. [Time Horizon: Long-term Planning] | Regional | [30 empty] | Medium |  |  | Medium | [15 empty] | TO
FAC-501-WECC-1 | FAC-501-WECC-1 | R3. | Transmission Maintenance | To ensure the Transmission Owner of a transmission path identified in the table titled “Major WECC Transfer Paths in the Bulk Electric System” including associated facilities has a Transmission Maintenance and Inspection Plan (TMIP); and performs and docu | Transmission Owners shall implement and follow their TMIP. [Time Horizon: Operations Assessment] | Regional | [30 empty] | Medium |  |  | Medium | [15 empty] | TO
INT-001-3 | INT-001-3 | R1. | Interchange Information | To ensure that Interchange information is submitted to the NERC-identified reliability analysis service. | The Load-Serving, Purchasing-Selling Entity shall ensure that Arranged Interchange is submitted to the Interchange Authority for: | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard |  |  | Yes | Team determined that there are situations within the various Interconnections where the PSE does perform this role | Yes - #1, 3 | No | No |  | Yes | Yes | Yes - there are places were the PSE does conduct the function | Yes | Yes, OK on its own but consider consolidating INT-001 and -003 with BAL standards | No | Yes | Yes | Yes | Yes | Yes | Yes | No - incorporates functional spec (that's OK here) | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Medium |  | High | Lower | [5 empty] | LSE |  |  |  | PSE
INT-001-3 | INT-001-3 | R1.1. | Interchange Information | To ensure that Interchange information is submitted to the NERC-identified reliability analysis service. | All Dynamic Schedules at the expected average MW profile for each hour. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE |  |  |  | PSE
INT-001-3 | INT-001-3 | R2. | Interchange Information | To ensure that Interchange information is submitted to the NERC-identified reliability analysis service. | The Sink Balancing Authority shall ensure that Arranged Interchange is submitted to the Interchange Authority: | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-001-3 | INT-001-3 | R2.1. | Interchange Information | To ensure that Interchange information is submitted to the NERC-identified reliability analysis service. | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-001-3 | INT-001-3 | R2.2. | Interchange Information | To ensure that Interchange information is submitted to the NERC-identified reliability analysis service. | For each bilateral Inadvertent Interchange payback. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-003-3 | INT-003-3 | R1. | Interchange Transaction Implementation | To ensure Balancing Authorities confirm Interchange Schedules with Adjacent Balancing Authorities prior to implementing the schedules in their Area Control Error (ACE) equations. | Each Receiving Balancing Authority shall confirm Interchange Schedules with the Sending Balancing Authority prior to implementation in the Balancing Authority’s ACE equation. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard |  |  | Yes | This requirement has not been overcome by the electronic process | Yes - #1, 3 | No | No |  | Yes | Yes | Yes | Yes | No - possible consolidate with 001-3; look at in conjunction with BAL standards | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - incorporates functional spec (that's OK here) | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Medium |  | High | Medium | BA
INT-003-3 | INT-003-3 | R1.1. | Interchange Transaction Implementation | To ensure Balancing Authorities confirm Interchange Schedules with Adjacent Balancing Authorities prior to implementing the schedules in their Area Control Error (ACE) equations. | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-003-3 | INT-003-3 | R1.1.1. | Interchange Transaction Implementation | To ensure Balancing Authorities confirm Interchange Schedules with Adjacent Balancing Authorities prior to implementing the schedules in their Area Control Error (ACE) equations. | Interchange Schedule start and end time. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-003-3 | INT-003-3 | R1.1.2. | Interchange Transaction Implementation | To ensure Balancing Authorities confirm Interchange Schedules with Adjacent Balancing Authorities prior to implementing the schedules in their Area Control Error (ACE) equations. | Energy profile. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-003-3 | INT-003-3 | R1.2. | Interchange Transaction Implementation | To ensure Balancing Authorities confirm Interchange Schedules with Adjacent Balancing Authorities prior to implementing the schedules in their Area Control Error (ACE) equations. | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Medium | BA
INT-004-2 | INT-004-2 | R1. | Dynamic Interchange Transaction Modifications | To ensure Dynamic Transfers are adequately tagged to be able to determine their reliability impacts. | At such time as the reliability event allows for the reloading of the transaction, the entity that initiated the curtailment shall release the limit on the Interchange Transaction tag to allow reloading the transaction and shall communicate the release of the limit to the Sink Balancing Authority. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-004-2 | INT-004-2 | R2. | Dynamic Interchange Transaction Modifications | To ensure Dynamic Transfers are adequately tagged to be able to determine their reliability impacts. | The Purchasing-Selling Entity responsible for tagging a Dynamic Interchange Schedule shall ensure the tag is updated for the next available scheduling hour and future hours when any one of the following occurs: | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [9 empty] | PSE
INT-004-2 | INT-004-2 | R2.1. | Dynamic Interchange Transaction Modifications | To ensure Dynamic Transfers are adequately tagged to be able to determine their reliability impacts. | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [9 empty] | PSE
INT-004-2 | INT-004-2 | R2.2. | Dynamic Interchange Transaction Modifications | To ensure Dynamic Transfers are adequately tagged to be able to determine their reliability impacts. | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [9 empty] | PSE
INT-004-2 | INT-004-2 | R2.3. | Dynamic Interchange Transaction Modifications | To ensure Dynamic Transfers are adequately tagged to be able to determine their reliability impacts. | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [9 empty] | PSE
INT-005-3 | INT-005-3 | R1. | Interchange Authority Distributes Arranged Interchange | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is distributed by an Interchange Authority such that Interchange information is available for reliability assessments. | Prior to the expiration of the time period defined in the timing requirements tables in this standard, Column A, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment to all reliability entities involved in the Interchange. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Medium |  |  |  |  | IA
INT-005-3 | INT-005-3 | R1.1. | Interchange Authority Distributes Arranged Interchange | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is distributed by an Interchange Authority such that Interchange information is available for reliability assessments. | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Medium |  |  |  |  | IA
INT-006-3 | INT-006-3 | R1. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Prior to the expiration of the reliability assessment period defined in the timing requirements tables in this standard, Column B, the Balancing Authority and Transmission Service Provider shall respond to each On-time Request for Interchange (RFI), and to each Emergency RFI and Reliability Adjustment RFI from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA | [17 empty] | TSP
INT-006-3 | INT-006-3 | R1.1. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-006-3 | INT-006-3 | R1.1.1. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Energy profile (ability to support the magnitude of the Interchange). | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-006-3 | INT-006-3 | R1.1.2. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Ramp (ability of generation maneuverability to accommodate). | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-006-3 | INT-006-3 | R1.1.3. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Scheduling path (proper connectivity of Adjacent Balancing Authorities). | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-006-3 | INT-006-3 | R1.2. | Response to Interchange Authority | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-007-1 | INT-007-1 | R1. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | The Interchange Authority shall verify that Arranged Interchange is balanced and valid prior to transitioning Arranged Interchange to Confirmed Interchange by verifying the following: | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.1. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Source Balancing Authority megawatts equal sink Balancing Authority megawatts (adjusted for losses, if appropriate). | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.2. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | All reliability entities involved in the Arranged Interchange are currently in the NERC registry. | Current | Currently enforceable standard. |  | Consider combining with BAL's | Yes |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.3. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | The following are defined: | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.3.1. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Generation source and load sink. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.3.2. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Megawatt profile. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.3.3. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Ramp start and stop times. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.3.4. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Interchange duration. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-007-1 | INT-007-1 | R1.4. | Interchange Confirmation | To ensure that each Arranged Interchange is checked for reliability before it is implemented. | Each Balancing Authority and Transmission Service Provider that received the Arranged Interchange information from the Interchange Authority for reliability assessment has provided approval. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-008-3 | INT-008-3 | R1. | Interchange Authority Distributes Status | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is coordinated by an Interchange Authority. | Prior to the expiration of the time period defined in the Timing Table, Column C, the Interchange Authority shall distribute to all Balancing Authorities (including Balancing Authorities on Boardh sides of a direct current tie), Transmission Service Providers and Purchasing-Selling Entities involved in the Arranged Interchange whether or not the Arranged Interchange has transitioned to a Confirmed Interchange. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-008-3 | INT-008-3 | R1.1. | Interchange Authority Distributes Status | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is coordinated by an Interchange Authority. | For Confirmed Interchange, the Interchange Authority shall also communicate: | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-008-3 | INT-008-3 | R1.1.1. | Interchange Authority Distributes Status | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is coordinated by an Interchange Authority. | Start and stop times, ramps, and megawatt profile to Balancing Authorities. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-008-3 | INT-008-3 | R1.1.2. | Interchange Authority Distributes Status | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is coordinated by an Interchange Authority. | Necessary Interchange information to NERC-identified reliability analysis services. | Current | Currently enforceable standard. |  | Consider combining with BAL's |  |  |  | Yes - #1, 3 | Yes | Exists - the functional spec for electronic tagging has it | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower |  |  |  |  | IA
INT-009-1 | INT-009-1 | R1. | Implementation of Interchange | To ensure that the implementation of Interchange between Source and Sink Balancing Authorities is coordinated by an Interchange Authority such that the Balancing Authorities implement the Interchange exactly as agreed upon in the Interchange confirmation | The Balancing Authority shall implement Confirmed Interchange as received from the Interchange Authority. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Medium | BA
INT-010-1 | INT-010-1 | R1. | Interchange Coordination Exemptions | Allow certain types of Interchange schedules to be initiated or modified by reliability entities, and to be exempt from compliance with other Interchange Standards under abnormal operating conditions. | The Balancing Authority that experiences a loss of resources covered by an energy sharing agreement shall ensure that a request for an Arranged Interchange is submitted with a start time no more than 60 minutes beyond the resource loss. If the use of the energy sharing agreement does not exceed 60 minutes from the time of the resource loss, no request for Arranged Interchange is required. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | BA
INT-010-1 | INT-010-1 | R2. | Interchange Coordination Exemptions | Allow certain types of Interchange schedules to be initiated or modified by reliability entities, and to be exempt from compliance with other Interchange Standards under abnormal operating conditions. | For a modification to an existing Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit the modified Arranged Interchange reflecting that modification within 60 minutes of the initiation of the event. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [10 empty] | RC
INT-010-1 | INT-010-1 | R3. | Interchange Coordination Exemptions | Allow certain types of Interchange schedules to be initiated or modified by reliability entities, and to be exempt from compliance with other Interchange Standards under abnormal operating conditions. | For a new Interchange schedule that is directed by a Reliability Coordinator for current or imminent reliability-related reasons, the Reliability Coordinator shall direct a Balancing Authority to submit an Arranged Interchange reflecting that Interchange schedule within 60 minutes of the initiation of the event. | Current | Currently enforceable standard. | Yes - Project 2008-12 Coordinate Interchange Standards - Adds a INT-011-1 as a new standard | Consider combining with BAL's |  | Yes |  | Yes - #1, 3 | Yes | A guideline exists in the the functional spec for electronic tagging. | [17 empty] | Yes | No | 0 | 0 | Medium |  | N/A | Lower | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R1. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | Each Regional Reliability Organization, subregion, or interregional coordinating group shall establish one or more Reliability Coordinators to continuously assess transmission reliability and coordinate emergency operations among the operating entities within the region and across the regional boundaries. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - overcome by events; legacy | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [13 empty] | RRO
IRO-001-1 | IRO-001-1.1 | R2. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall comply with a regional reliability plan approved by the NERC Operating Committee. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - overcome by events; legacy | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R3. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordinator Area to preserve the integrity and reliability of the Bulk Electric System. These actions shall be taken without delay, but no longer than 30 minutes. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes |  | Yes - #6 | No | No |  |  | Yes - but second sentence is not needed as it is duplicative of the 30 min requirement contained in the TOP and IRO standards. | Yes | Yes | Yes - consider combining with other authority stds | Yes | Yes | No - language is not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | High |  | High | High | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R4. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | Reliability Coordinators that delegate tasks to other entities shall have formal operating agreements with each entity to which tasks are delegated. The Reliability Coordinator shall verify that all delegated tasks are understood, communicated, and addressed within its Reliability Coordinator Area. All responsibilities for complying with NERC and regional standards applicable to Reliability Coordinators shall remain with the Reliability Coordinator. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - administrative | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R5. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall list within its reliability plan all entities to which the Reliability Coordinator has delegated required tasks. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - administrative | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R6. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall verify that all delegated tasks are carried out by NERC-certified Reliability Coordinator operating personnel. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - administrative. Gap clarifying that any System operator conducting RC tasks must be NERC RC certified in is PER-003 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R7. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall have clear, comprehensive coordination agreements with adjacent Reliability Coordinators to ensure that System Operating Limit or Interconnection Reliability Operating Limit violation mitigation requiring actions in adjacent Reliability Coordinator Areas are coordinated. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - a legacy requirement. It is administrative and duplicative of other IRO-014 R1 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [10 empty] | RC
IRO-001-1 | IRO-001-1.1 | R8. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes and IRO-001-1a |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes, but consider consolidating with other authority-related standards | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 3 | 12 | High |  | High | High | BA |  |  | GOP |  | LSE |  |  |  | PSE | [6 empty] | TOP |  | TSP
IRO-001-1 | IRO-001-1.1 | R9. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical | The Reliability Coordinator shall act in the interests of reliability for the overall Reliability Coordinator Area and the Interconnection before the interests of any other entity. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | No | [19 empty] | No |  | 0 | 0 | High |  | N/A | High | [10 empty] | RC
IRO-001-2 | IRO-001-2 | R1. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [16 empty] | RRO
IRO-001-2 | IRO-001-2 | R2. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-2 | IRO-001-2 | R3. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-2 | IRO-001-2 | R4. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-2 | IRO-001-2 | R5. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-2 | IRO-001-2 | R6. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-2 | IRO-001-2 | R7. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [12 empty] | PSE | [6 empty] | TOP |  | TSP
IRO-001-2 | IRO-001-2 | R8. | Reliability Coordination — Responsibilities and Authorities | Reliability Coordinators must have the authority, plans, and agreements in place to immediately direct reliability entities within their Reliability Coordinator Areas to re-dispatch generation, reconfigure transmission, or reduce load to mitigate critical |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011. Not filed with FERC |  | Combine IRO-001, IRO-002 and IRO-003 |  | Yes | [25 empty] | High | [13 empty] | RC
IRO-001-3 | IRO-001-3 | R1. | Reliability Coordination – Responsibilities and Authorities | To establish the authority of Reliability Coordinators to direct other entities to prevent an Emergency or Adverse Reliability Impacts to the Bulk Electric System. | Each Reliability Coordinator shall have the authority to act or direct others to act (which could include issuing Reliability Directives) to prevent identified events or mitigate the magnitude or duration of actual events that result in an Emergency or Adverse Reliability Impact. | Board Adopted | Board adopted 8/6/2012. Not filed with FERC pending approval of TOP standards. Board approved filing of TOP standards 2/7/2013. | [5 empty] | Yes - #6 | No | No |  |  | No - there are 3 concepts here and suggest the following: RC has the authority to direct others to act. RC has the obligation to direct others to act to prevent identified events or mitigate the magnitude or duration of actual events that result in an Emergency or Adverse Reliability Impact. When directing others to act in accordance with this requirement, a RC must identify its directive as a "Reliability Directive". | Yes | No - see redraft | Yes, but consider consolidating with other authority-related standards and COM-003 | No | Yes | No | Yes | Yes | No | Yes | No | No | No | Yes | Yes | Yes | 1 | 6 | High | Yes | High | High | [10 empty] | RC
IRO-001-3 | IRO-001-3 | R2. | Reliability Coordination – Responsibilities and Authorities | To establish the authority of Reliability Coordinators to direct other entities to prevent an Emergency or Adverse Reliability Impacts to the Bulk Electric System. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s direction unless compliance with the direction cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Board Adopted | Board adopted 8/6/2012. Not filed with FERC pending approval of TOP standards. Board approved filing of TOP standards 2/7/2013. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes - is equipment requirements a valid reason to Not comply? See comments in TOPs | Yes, but consider consolidating with other authority-related standards | Yes | Yes | Yes | Yes | Yes | No - what is "direction" | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 9 | High | Yes | High | High | [16 empty] | TOP
IRO-001-3 | IRO-001-3 | R3. | Reliability Coordination – Responsibilities and Authorities | To establish the authority of Reliability Coordinators to direct other entities to prevent an Emergency or Adverse Reliability Impacts to the Bulk Electric System. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator upon recognition of its inability to perform as directed in accordance with Requirement R2. | Board Adopted | Board adopted 8/6/2012. Not filed with FERC pending approval of TOP standards. Board approved filing of TOP standards 2/7/2013. | [5 empty] | Yes | No | No |  |  | No - doesn't require a reason to Not comply with the direction | Yes | Yes - is equipment requirements a valid reason to Not comply? See comments in TOPs | Yes, but consider consolidating with other authority-related standards | Yes | Yes | Yes | Yes | Yes | No - what is "direction" | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 9 | High | Yes | High | High | [16 empty] | TOP
IRO-002-2 | IRO-002-2 | R1. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall have adequate communications facilities (voice and data links) to appropriate entities within its Reliability Coordinator Area. These communications facilities shall be staffed and available to act in addressing a real-time emergency condition. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #6 however, the staffing requirement is no b/c it is overcome by events in technology | Yes - duplicative with COM-001-1.1 R1 with the exception of staffing | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R2. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator — or its Transmission Operators and Balancing Authorities — shall provide, or arrange provisions for, data exchange to other Reliability Coordinators or Transmission Operators and Balancing Authorities via a secure network. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | yes | Yes - duplicative with IRO-010 (currently enforceable) | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R3. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall have multi-directional communications capabilities with its Transmission Operators and Balancing Authorities, and with neighboring Reliability Coordinators, for Boardh voice and data exchange as required to meet reliability needs of the Interconnection. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative with COM-001-1.1 R1 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R4. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall have detailed real-time monitoring capability of its Reliability Coordinator Area and sufficient monitoring capability of its surrounding Reliability Coordinator Areas to ensure that potential or actual System Operating Limit or Interconnection Reliability Operating Limit violations are identified. Each Reliability Coordinator shall have monitoring systems that provide information that can be easily understood and interpreted by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant and highly reliable infrastructure. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes | Yes | No - the language is vague and legacy. | Yes - consider putting this into a certification requirement or consolidate into project 2009-02 | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R5. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall monitor Bulk Electric System elements (generators, transmission lines, buses, transformers, breakers, etc.) that could result in SOL or IROL violations within its Reliability Coordinator Area. Each Reliability Coordinator shall monitor Boardh real and reactive power system flows, and operating reserves, and the status of Bulk Electric System elements that are or could be critical to SOLs and IROLs and system restoration requirements within its Reliability Coordinator Area. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  | (Order 748) | Yes - concern: SOL issue. see IRO-008-1 R3 re: SOLS | Yes | Yes | Yes | Yes | Yes | No - what are the expectations for "monitor"? | Yes | Yes | No - what are the expectations for "monitor"? | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | High |  | High | High - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R6. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall have adequate analysis tools such as state estimation, pre- and post-contingency analysis capabilities (thermal, stability, and voltage), and wide-area overview displays. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes | Yes | No - the language is vague and legacy. | Yes - consider consolidating into project 2009-02 | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | High |  | High | High - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R7. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall continuously monitor its Reliability Coordinator Area. Each Reliability Coordinator shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable. Each Reliability Coordinator shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #5 | Yes - Covered under EOP-008 and R4 and R5 of this std | No | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | [10 empty] | RC
IRO-002-2 | IRO-002-2 | R8. | Reliability Coordination — Facilities | Reliability Coordinators need information, tools and other capabilities to perform their responsibilities. | Each Reliability Coordinator shall control its Reliability Coordinator analysis tools, including approvals for planned maintenance. Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - it needs to address the integrity of any hardware/software/telecom system etc that could affect the quality and the content of the data coming into the control center. | Yes | Yes - to the extent that it presently covers | Yes | Yes | Yes | No - the intent is inferred, but is not clear | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | High |  | High | High - Pending | [10 empty] | RC
IRO-002-3 | IRO-002-3 | R1. | Reliability Coordination — Analysis Tools | To ensure that Reliability Coordinators provide their System Operators with authority with respect to analysis tool outages and to have procedures to mitigate effects of analysis tool outages. | Each Reliability Coordinator shall provide its System Operators with the authority to approve, deny or cancel planned outages of its own analysis tools. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes | No | No |  |  | No - also needs to approve any other work being done on the tools, hardware/software/telecom systems within the RC that could affect the quality and the content of the data coming into the control center. | Yes | Yes - to the extent that it presently covers | Yes but consider consolidating with project 2009-02 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | Medium | [10 empty] | RC
IRO-002-3 | IRO-002-3 | R2. | Reliability Coordination — Analysis Tools | To ensure that Reliability Coordinators provide their System Operators with authority with respect to analysis tool outages and to have procedures to mitigate effects of analysis tool outages. | Each Reliability Coordinator shall have procedures in place to mitigate the effects of analysis tool outages. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes | No | No |  |  | No - the procedures need to address not only tools outages, but also tools maintenance or other inhibitors to quality performance of analysis tools. | Yes | Yes - to the extent that it presently covers | Yes, but consider consolidating with project 2009-02 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | HIgh | Medium | [10 empty] | RC
IRO-003-2 | IRO-003-2 | R1. | Reliability Coordination — Wide-Area View | The Reliability Coordinator must have a wide-area view of its own Reliability Coordinator Area and that of neighboring Reliability Coordinators. | Each Reliability Coordinator shall monitor all Bulk Electric System facilities, which may include sub-transmission information, within its Reliability Coordinator Area and adjacent Reliability Coordinator Areas, as necessary to ensure that, at any time, regardless of prior planned or unplanned events, the Reliability Coordinator is able to determine any potential System Operating Limit and Interconnection Reliability Operating Limit violations within its Reliability Coordinator Area. | Current | Currently enforceable standard. | [5 empty] | Yes - #7 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes - need to clarify "facilities" | Yes | Yes | No - the phrase "whch may include sub-tranmission" is not clear | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 9 | High |  | High | High | [10 empty] | RC
IRO-003-2 | IRO-003-2 | R2. | Reliability Coordination — Wide-Area View | The Reliability Coordinator must have a wide-area view of its own Reliability Coordinator Area and that of neighboring Reliability Coordinators. | Each Reliability Coordinator shall know the current status of all critical facilities whose failure, degradation or disconnection could result in an SOL or IROL violation. Reliability Coordinators shall also know the status of any facilities that may be required to assist area restoration objectives. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 7 | No | No |  |  | Yes | Yes | Yes | No. The first sentence is redundant with R1. The second sentence should be moved to EOP-006. | Yes | Yes | No - what does "know" mean? What critical facilities are meant; is it "Facilities"? | Yes | Yes | No - what does "know" mean? What critical facilities are meant; is it "Facilities"? | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 7 | High |  | High | High | [10 empty] | RC
IRO-004-2 | IRO-004-2 | R1. | Reliability Coordination — Operations Planning | Each Reliability Coordinator must conduct next-day reliability analyses for its Reliability Coordinator Area to ensure the Bulk Electric System can be operated reliably in anticipated normal and Contingency conditions. System studies must be conducted to | Each Transmission Operator, Balancing Authority, and Transmission Service Provider shall comply with the directives of its Reliability Coordinator based on the next day assessments in the same manner in which it would comply during real time operating events. | Current | Currently enforceable standard. |  |  |  | Yes |  | Yes | Yes - the intent is covered in IRO-008 R1 and is also duplicative of other IRO stds (IRO-001-1.1 R3) |  |  |  | No - the requirement does not fulfill the purpose of the standard. There is No requirment to do a next day study. |  |  | Consider consolidating with an authority standard | [11 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | BA | [15 empty] | TOP |  | TSP
IRO-005-3 | IRO-005-3.1a | R1. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Each Reliability Coordinator shall monitor its Reliability Coordinator Area parameters, including but not limited to the following: | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.1. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.2. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.3. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.4. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | System real and reactive reserves (actual versus required). | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.5. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Capacity and energy adequacy conditions. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.6. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Current ACE for all its Balancing Authorities. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.7. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Current local or Transmission Loading Relief procedures in effect. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.8. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Planned generation dispatches. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.9. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Planned transmission or generation outages. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R1.10 | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Contingency events. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-003-2 and IRO-010-1a | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R2. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. If necessary, the Reliability Coordinator shall direct the Balancing Authorities in the Reliability Coordinator Area to arrange for assistance from neighboring Balancing Authorities. The Reliability Coordinator shall issue Energy Emergency Alerts as needed and at the request of its Balancing Authorities and Load-Serving Entities. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | Yes - strike last two sentences; see reommendation in IRO-005-4 R1 | Yes | Yes - although after the first sentence, the language is commentary and is duplicative of EOP-002-3.1 R8 | Yes - keep until IRO-005-4 is enforceable | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R3. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Each Reliability Coordinator shall ensure its Transmission Operators and Balancing Authorities are aware of Geo-Magnetic Disturbance (GMD) forecast information and assist as needed in the development of any required response plans. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No | No | no - research being done on GMD. | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R4. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | The Reliability Coordinator shall disseminate information within its Reliability Coordinator Area, as required. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | No | Yes - This is a statement rather than a requirement | [18 empty] | No |  | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R5. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Each Reliability Coordinator shall monitor system frequency and its Balancing Authorities’ performance and direct any necessary rebalancing to return to CPS and DCS compliance. The Transmission Operators and Balancing Authorities shall utilize all resources, including firm load shedding, as directed by its Reliability Coordinator to relieve the emergent condition. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of the role the BA has under the BAL stds (1st sentence) the second sentence is duplicative of EOP and TOP stds requirements to shed load | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Pending | BA | [9 empty] | RC | [5 empty] | TOP
IRO-005-3 | IRO-005-3.1a | R6. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | The Reliability Coordinator shall coordinate with Transmission Operators, Balancing Authorities, and Generator Operators as needed to develop and implement action plans to mitigate potential or actual SOL, CPS, or DCS violations. The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in Boardh the real time and next-day reliability analysis timeframes. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #1, 9 (2nd sentence alone is much better (#3, 12)) | No - could retire sentence 1 and keep the second sentence- 1st sentence re: CPS/DCS - duplicative of requirements for BA under the BAL stds; same sentence re: SOLs - duplicative of TOP stds; | No |  |  | Yes | No | No - only keep the second sentence | Yes | No | Yes | Yes - but clarify "coordinate" and look at striking the word "pending" | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 8 | High |  | High | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R7. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | As necessary, the Reliability Coordinator shall assist the Balancing Authorities in its Reliability Coordinator Area in arranging for assistance from neighboring Reliability Coordinator Areas or Balancing Authorities. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of EOP-002 R8 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R8. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | The Reliability Coordinator shall identify sources of large Area Control Errors that may be contributing to Frequency Error, Time Error, or Inadvertent Interchange and shall discuss corrective actions with the appropriate Balancing Authority. The Reliability Coordinator shall direct its Balancing Authority to comply with CPS and DCS. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | No - eliminate second sentence as it is covered by the requirements under the BAL stds for the BA | Yes | No | Yes | No | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | High |  | Medium | Pending | [10 empty] | RC
IRO-005-3 | IRO-005-3.1a | R9. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. The Transmission Operator shall immediately inform the Reliability Coordinator of the status of the Special Protection System including any degradation or potential failure to operate as expected. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - poorly drafted. | Yes - but keep this pure to the responsibilities of the RC. To do this, look at dropping the second sentence | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 6 | High |  | High | Pending | [10 empty] | RC | [5 empty] | TOP
IRO-005-3 | IRO-005-3.1a | R10. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes IRO-005-3 and IRO-005-3a |  | Yes | No | No |  |  | No - the most limiting parameter is Not defined | No - need to add RCs; | No - need to strike TSP, LSE and PSE | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No - the word "parameter" | No | Yes | Yes | Yes | 0 | 8 | High |  | High | Pending | BA |  |  | GOP |  | LSE |  |  |  | PSE | [6 empty] | TOP |  | TSP
IRO-005-3 | IRO-005-3.1a | R11. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | The Transmission Service Provider shall respect SOLs and IROLs in accordance with filed tariffs and regional Total Transfer Calculation and Available Transfer Calculation processes. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | No | [19 empty] | No |  | 0 | 0 | High |  | N/A | Pending | [18 empty] | TSP
IRO-005-3 | IRO-005-3.1a | R12. | Reliability Coordination — Current Day Operations | The Reliability Coordinator must be continuously aware of conditions within its Reliability Coordinator Area and include this information in its reliability assessments. The Reliability Coordinator must monitor Bulk Electric System parameters that may hav | Each Reliability Coordinator who foresees a transmission problem (such as an SOL or IROL violation, loss of reactive reserves, etc.) within its Reliability Coordinator Area shall issue an alert to all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area without delay. The receiving Reliability Coordinator shall disseminate this information to its impacted Transmission Operators and Balancing Authorities. The Reliability Coordinator shall notify all impacted Transmission Operators, Balancing Authorities, when the transmission problem has been mitigated. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #3 | No | No |  |  | No - clarity is missing. Who shares what with who is Not clear. | No - the sending RC is Not identified | Yes | No - can consolidate with other Rs in this standard | No | Yes | No | Yes | Yes | No - 'without delay' and "foresees" | Yes | Yes | No - 'without delay' and "foresees" | No | Yes | Yes | Yes | 1 | 6 | High |  | High | Pending | [10 empty] | RC
IRO-005-4 | IRO-005-4 | R1. | Reliability Coordination — Current Day Operations | To ensure that entities are notified when an expected or actual event with Adverse Reliability Impacts is identified. | When the results of an Operational Planning Analysis or Real-time Assessment indicate an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area, each Reliability Coordinator shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #3 | No | No |  |  | No - need to include Emergency Also - there are gaps between the old std IRO-005-3 R2 to IRO-005-4: missing is: There is a possible gap for RC in IRO-005-4 regarding RC handling emergencies as this has been dropped from IRO-005-3.1 Each Reliability Coordinator shall monitor its Balancing Authorities’ parameters to ensure that the required amount of operating reserves is provided and available as required to meet the Control Performance Standard and Disturbance Control Standard requirements. (Minus strikethrough) from IRO-005-3 R6: The Reliability Coordinator shall coordinate pending generation and transmission maintenance outages with Transmission Operators, Balancing Authorities, and Generator Operators as needed in Boardh the real time and next-day reliability analysis timeframes. FROM IRO-005-3 R9: Whenever a Special Protection System that may have an inter-Balancing Authority, or inter-Transmission Operator impact (e.g., could potentially affect transmission flows resulting in a SOL or IROL violation) is armed, the Reliability Coordinators shall be aware of the impact of the operation of that Special Protection System on inter-area flows. From IRO-005-3 R10: In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | Yes | Yes | No - consolidate with IRO-008 R3. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High | Yes | High | [11 empty] | RC
IRO-005-4 | IRO-005-4 | R2. | Reliability Coordination — Current Day Operations | To ensure that entities are notified when an expected or actual event with Adverse Reliability Impacts is identified. | Each Reliability Coordinator that identifies an anticipated or actual condition with Adverse Reliability Impacts within its Reliability Coordinator Area shall notify all impacted Transmission Operators and Balancing Authorities in its Reliability Coordinator Area when the problem has been mitigated. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #3 | No | No |  |  | No - need to include Emergency Note: there is a possible gap for RC in IRO-005-4 regarding RC handling emergencies as this has been dropped from IRO-005-3.1 | Yes | Yes | No - move to IRO-008 and create an R4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High | Yes | Medium | High | [10 empty] | RC
IRO-006-5 | IRO-006-5 | R1. | Reliability Coordination — Transmission Loading Relief (TLR) | To ensure coordinated action between Interconnections when implementing Interconnection-wide transmission loading relief procedures to prevent or manage potential or actual SOL and IROL exceedances to maintain reliability of the bulk electric system. | Each Reliability Coordinator and Balancing Authority that receives a request pursuant to an Interconnection-wide transmission loading relief procedure (such as Eastern Interconnection TLR, WECC Unscheduled Flow Mitigation, or congestion management procedures from the ERCOT Protocols) from any Reliability Coordinator, Balancing Authority, or Transmission Operator in another Interconnection to curtail an Interchange Transaction that crosses an Interconnection boundary shall comply with the request, unless it provides a reliability reason to the requestor why it cannot comply with the request. | Current | [6 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes - considering consolidating with authority std | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | High | BA | [9 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R1. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | When acting or instructing others to act to mitigate the magnitude and duration of the instance of exceeding an IROL within that IROL’s TV, each Reliability Coordinator shall initiate, prior to or concurrently with the initiation of the Eastern Interconnection TLR procedure (or continuing management of this procedure if already initiated), one or more of the following actions: - Inter-area redispatch of generation - Intra-area redispatch of generation - Reconfiguration of the transmission system - Voluntary load reductions (e.g., Demad-side Management) - Controlled load reductions (e.g., load shedding) | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | High | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R2. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | To ensure operating entities are provided with information needed to maintain an awareness of changes to the Transmission System, when initiating the Eastern Interconnection TLR procedure to prevent or mitigate an SOL or IROL exceedance, and at least every clock hour (with the exception of TLR-1, where an hourly update is not required) after initiation up to and including the hour when the TLR level has been identified as TLR Level 0, the Reliability Coordinator shall identify: | Regional |  |  | Possible to combine in continent wide standard? | [8 empty] | Look at SOL language in here | [18 empty] | High |  |  | Medium | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R2.1. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | A list of congestion management actions to be implemented, and | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | No Individual VRF Assigned | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R2.2. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | No Individual VRF Assigned | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R3. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | Upon the identification of the TLR level and a list of congestion management actions to be implemented, the Reliability Coordinator initiating this TLR procedure shall: | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | Medium | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R3.1. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | No Individual VRF Assigned | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R3.2. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | No Individual VRF Assigned | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R3.3. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | No Individual VRF Assigned | [10 empty] | RC
IRO-006-EAST-1 | IRO-006-EAST-1 | R4. | Transmission Loading Relief Procedure for the Eastern Interconnection | To provide an Interconnection-wide transmission loading relief procedure (TLR) for the Eastern Interconnection that can be used to prevent and/or mitigate potential or actual System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IR | Each Reliability Coordinator that receives a request as described in Requirement R3, Part 3.3. shall, within 15 minutes of receiving the request, implement the congestion management actions requested by the issuing Reliability Coordinator as follows: - Instruct its Balancing Authorities to implement the Interchange Transaction schedule change requests. - Instruct its Balancing Authorities to implement the Network Integration Transmission Service and Native Load schedule changes for which the Balancing Authorities are responsible. - Instruct its Balancing Authorities to implement the Market Flow schedule changes for which the Balancing Authorities are responsible. - If as assessment determines shows that one or more of the congestion management actions communicated in Requirement R3, part 3.3 will result in a reliability concern or will be ineffective, the Reliability Coordinator may replace those specific actions with alternate congestion management actions, provided that: - The alternate congestion management actions have been agreed to by the initiating Reliability Coordinator, and - The assessment shows that the alternate congestion management actions will not adversely affect reliability. | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | High | [10 empty] | RC
IRO-006-TRE-1 | IRO-006-TRE-1 | R1. | IROL and SOL Mitigation in the ERCOT Region | To provide and execute transmission loading relief procedures that can be used to mitigate SOL or IROL exceedances for the purpose of maintaining reliable operation of the bulk electric system in the ERCOT Region. | The RC shall have procedures to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits (IROL) and System Operating Limits (SOL) that will not be resolved by the automatic actions of the ERCOT Nodal market operations system. The procedures shall address, but not be limited to, one or more of the following: redispatch of generation; reconfiguration of the Transmission system; controlled load reductions (including Boardh firm and non-firm load shedding). | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | Medium | [10 empty] | RC
IRO-006-TRE-1 | IRO-006-TRE-1 | R2. | IROL and SOL Mitigation in the ERCOT Region | To provide and execute transmission loading relief procedures that can be used to mitigate SOL or IROL exceedances for the purpose of maintaining reliable operation of the bulk electric system in the ERCOT Region. | The RC shall act to identify and mitigate exceedances of identified Interconnection Reliability Operating Limits and System Operating Limits that will not be resolved by the automatic actions of the ERCOT Nodal market operations system, in accordance with the procedures required by R1. | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | High | [10 empty] | RC
IRO-006-WECC-1 | IRO-006-WECC-1 | R1. | Qualified Transfer Path Unscheduled Flow (USF) Relief | Mitigation of transmission overloads due to unscheduled flow on Qualified Transfer Paths. | Upon receiving a request of Step 4 or greater (see Attachment 1-IRO-006-WECC-1) from the Transmission Operator of a Qualified Transfer Path, the Reliability Coordinator shall approve (actively or passively) or deny that request within five minutes. [Time Horizon: Real-time Operations] | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | High - Pending | [10 empty] | RC
IRO-006-WECC-1 | IRO-006-WECC-1 | R2. | Qualified Transfer Path Unscheduled Flow (USF) Relief | Mitigation of transmission overloads due to unscheduled flow on Qualified Transfer Paths. | The Balancing Authorities shall approve curtailment requests to the schedules as submitted, implement alternative actions, or a combination there of that collectively meets the Relief Requirement. [Time Horizon: Real-time Operations] | Regional |  |  | Possible to combine in continent wide standard? | [27 empty] | High |  |  | High - Pending | BA
IRO-008-1 | IRO-008-1 | R1. | Reliability Coordinator Operational Analyses and Real-time Assessments | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring that the Bulk Electric System is assessed during the operations horizon. | Each Reliability Coordinator shall perform an Operational Planning Analysis to assess whether the planned operations for the next day within its Wide Area, will exceed any of its Interconnection Reliability Operating Limits (IROLs) during anticipated normal and Contingency event conditions. (Time Horizon: Operations Planning) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - Need to add SOLs. Note from TOP-002-3: TOP-008-1 R4 needs to be incorporated. Also - the definition of "Operational Planning Analysis" provides too much latitude in time. Recommend removing the parenthesis in the definition; the entity will make the determination and document (documentation is evidence) the applicability of what it uses for their next day study incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High | Yes | High | High - Pending | [10 empty] | RC
IRO-008-1 | IRO-008-1 | R2. | Reliability Coordinator Operational Analyses and Real-time Assessments | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring that the Bulk Electric System is assessed during the operations horizon. | Each Reliability Coordinator shall perform a Real-Time Assessment at least once every 30 minutes to determine if its Wide Area is exceeding any IROLs or is expected to exceed any IROLs. (Time Horizon: Real-time Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - Real Time Assessment Glossary definition is not clear - what is "immediately available data"? SOLs need to be added Incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - need to verify whether 30 minutes is correct based on current technology and current common practice (could use state estimator data for five min slices?) | Yes | Yes | Yes | Yes | Yes | No - 30 min | No - amibiguity of glossary definition | Yes | Yes | No | Yes | Yes | Yes | Yes | 1 | 9 | High | Yes | High | High - Pending | [10 empty] | RC
IRO-008-1 | IRO-008-1 | R3. | Reliability Coordinator Operational Analyses and Real-time Assessments | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring that the Bulk Electric System is assessed during the operations horizon. | When a Reliability Coordinator determines that the results of an Operational Planning Analysis or Real-Time Assessment indicates the need for specific operational actions to prevent or mitigate an instance of exceeding an IROL, the Reliability Coordinator shall share its results with those entities that are expected to take those actions. (Time Horizon: Real-time Operations or Same Day Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - needs to add critical SOLs (need to define - ones that will move into an IROL). Need to define immediately available data (glossary definition for Real Time Assessment) and determine time in the definition of "Operational Planning Analysis" - see notes in R1 and R2. incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - see "gap" comments | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | Medium - Pending | [10 empty] | RC
IRO-009-1 | IRO-009-1 | R1. | Reliability Coordinator Actions to Operate Within IROLs | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring prompt action to prevent or mitigate instances of exceeding Interconnection Reliability Operating Limits (IROLs) | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) that can be implemented in time to prevent exceeding those IROLs. (Time Horizon: Operations Planning or Same Day Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footNote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | Medium - Pending | [10 empty] | RC
IRO-009-1 | IRO-009-1 | R2. | Reliability Coordinator Actions to Operate Within IROLs | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring prompt action to prevent or mitigate instances of exceeding Interconnection Reliability Operating Limits (IROLs) | For each IROL (in its Reliability Coordinator Area) that the Reliability Coordinator identifies one or more days prior to the current day, the Reliability Coordinator shall have one or more Operating Processes, Procedures, or Plans that identify actions it shall take or actions it shall direct others to take (up to and including load shedding) to mitigate the magnitude and duration of exceeding that IROL such that the IROL is relieved within the IROL’s Tv. (Time Horizon: Operations Planning or Same Day Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footNote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | Medium - Pending | [10 empty] | RC
IRO-009-1 | IRO-009-1 | R3. | Reliability Coordinator Actions to Operate Within IROLs | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring prompt action to prevent or mitigate instances of exceeding Interconnection Reliability Operating Limits (IROLs) | When an assessment of actual or expected system conditions predicts that an IROL in its Reliability Coordinator Area will be exceeded, the Reliability Coordinator shall implement one or more Operating Processes, Procedures or Plans (not limited to the Operating Processes, Procedures, or Plans developed for Requirements R1) to prevent exceeding that IROL. (Time Horizon: Real-time Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes - proving a negative | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High - Pending | [10 empty] | RC
IRO-009-1 | IRO-009-1 | R4. | Reliability Coordinator Actions to Operate Within IROLs | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring prompt action to prevent or mitigate instances of exceeding Interconnection Reliability Operating Limits (IROLs) | When actual system conditions show that there is an instance of exceeding an IROL in its Reliability Coordinator Area, the Reliability Coordinator shall, without delay, act or direct others to act to mitigate the magnitude and duration of the instance of exceeding that IROL within the IROL’s Tv. (Time Horizon: Real-time Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | No | No |  |  | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. GAP: Need to identify RC's authority to direct another RC to take action for any need - IROL, Adverse Reliability Impact and Emergencies, etc. - suggestion: create another Requirement i.e. R6 (reference IR0-014-1 R2) | Yes | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes - proving a negative | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High - Pending | [10 empty] | RC
IRO-009-1 | IRO-009-1 | R5. | Reliability Coordinator Actions to Operate Within IROLs | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring prompt action to prevent or mitigate instances of exceeding Interconnection Reliability Operating Limits (IROLs) | If unanimity cannot be reached on the value for an IROL or its Tv, each Reliability Coordinator that monitors that Facility (or group of Facilities) shall, without delay, use the most conservative of the values (the value with the least impact on reliability) under consideration. (Time Horizon: Real-time Operations) | Current | Currently enforceable standard. | [5 empty] | Yes | no | No |  |  | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | No - incorporate "grid impactful SOLs" into its methodology. These are SOLs that can become IROLs. Add a definition to the Glossary. (came up w/ discussion of IRO-008) Grid impactful SOLs is defined in footnote 31 of para 27 in order 748. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High |  | High | High - Pending | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R1. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | The Reliability Coordinator shall have a documented specification for data and information to build and maintain models to support Real-time monitoring, Operational Planning Analyses, and Real-time Assessments of its Reliability Coordinator Area to prevent instability, uncontrolled separation, and cascading outages. The specification shall include the following: (Time Horizon: Operations Planning) | Current | Currently enforceable standard. | [5 empty] | Yes - #3 (this is inserted from TOP-003-2 R1 and R2) | No | No |  |  | No - does not address level of accuracy required; this detail could come from project 2009-02 | Yes | Yes | No - consolidate R1 at minimum; consider consolidating with TOP-003-2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | Low | Medium- Pending | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R1.1. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 (this is inserted from TOP-003-2 R1 and R2) | No | No |  |  | No - does not address level of accuracy required; this detail could come from project 2009-02 | Yes | Yes | No - consider consolidating with TOP-003-2 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Low | No Individual VRF Assigned | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R1.2. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | Mutually agreeable format. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 (this is inserted from TOP-003-2 R1 and R2) | No | No |  |  | No - does not address level of accuracy required; this detail could come from project 2009-02 | Yes | Yes | No - consider consolidating with TOP-003-2 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Low | No Individual VRF Assigned | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R1.3. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). | Current | Currently enforceable standard. | [5 empty] | Yes - #3 (this is inserted from TOP-003-2 R1 and R2) | No | No |  |  | No - does not address level of accuracy required; this detail could come from project 2009-02 | Yes | Yes | No - consider consolidating with TOP-003-2 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Low | No Individual VRF Assigned | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R1.4. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | Process for data provision when automated Real-Time system operating data is unavailable. | Current | Currently enforceable standard. | [5 empty] | Yes - #3 (this is inserted from TOP-003-2 R1 and R2) | No | No |  |  | No - does not address level of accuracy required; this detail could come from project 2009-02 | Yes | Yes | No - consider consolidating with TOP-003-2 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | Low | No Individual VRF Assigned | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R2. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | The Reliability Coordinator shall distribute its data specification to entities that have Facilities monitored by the Reliability Coordinator and to entities that provide Facility status to the Reliability Coordinator. (Violation Risk Factor: Low) (Time Horizon: Operations Planning) | Current | Currently enforceable standard. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No - consider consolidating with TOP-003-2 R3 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | Low | Medium - Pending | [10 empty] | RC
IRO-010-1 | IRO-010-1a | R3. | Reliability Coordinator Data Specification and Collection | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the interconnection by ensuring the Reliability Coordinator has the data it needs to monitor and assess the operation of its Reliability Coordin | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. (Violation Risk Factor: Medium) (Time Horizon: Operations Planning; Same-day Operations; Real-time Operations) | Current | Currently enforceable standard. |  |  |  | Yes | This is the sole data sharing standard. Removal would create a gap | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No - consolidate with TOP-003-2 (R5) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | Medium - Pending | BA |  | GO | GOP | IA | LSE |  |  |  |  | RC |  |  |  |  | TO | TOP
IRO-014-1 | IRO-014-1 | R1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall have Operating Procedures, Processes, or Plans in place for activities that require notification, exchange of information or coordination of actions with one or more other Reliability Coordinators to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall address Scenarios that affect other Reliability Coordinator Areas as well as those developed in coordination with other Reliability Coordinators. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.2. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Energy and capacity shortages. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.3. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Planned or unplanned outage information. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.4. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Voltage control, including the coordination of reactive resources for voltage control. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.5. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Coordination of information exchange to support reliability assessments. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R1.1.6. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R2. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator’s Operating Procedure, Process, or Plan that requires one or more other Reliability Coordinators to take action (e.g., make notifications, exchange information, or coordinate actions) shall be: | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - administrative. | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R2.1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Agreed to by all the Reliability Coordinators required to take the indicated action(s). | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - administrative. | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R2.2. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Distributed to all Reliability Coordinators that are required to take the indicated action(s). | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - administrative. | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R3. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | A Reliability Coordinator’s Operating Procedures, Processes, or Plans developed to support a Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan shall include: | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - addressed in R1 | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R3.1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - addressed in R1 | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R3.2. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes - addressed in R1 | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R4. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each of the Operating Procedures, Processes, and Plans addressed in Reliability Standard IRO-014 Requirement 1 and Requirement 3 shall: | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes |  | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R4.1. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Include version control number or date | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R4.2. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Include a distribution list. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-1 | IRO-014-1 | R4.3. | Procedures, Processes, or Plans to Support Coordination Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Be reviewed, at least once every three years, and updated if needed. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | No | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R1. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator shall have Operating Procedures, Operating Processes, or Operating Plans for activities that require notification, exchange of information or coordination of actions that may impact other Reliability Coordinator Areas to support Interconnection reliability. These Operating Procedures, Processes, or Plans shall collectively address the following: [See standard for what needs to be addressed] | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | No | No - although subs and second sentence could be moved to a guide. Also check ability during certification; broaden to include coordination of BAs and TOPs |  |  | No - gap - Need to identify RC's authority to direct another RC to take action - suggestion: create another Requirement i.e. R6 (reference IR0-014-1 R2) This gap was put into IRO-009-1 R4 | Yes | No - see "gap" comments | Yes. The authority portion that needs to be created could be included in an authority standard. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High |  | Medium | Medium | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R2. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: [See standard for how to maintain procedures, processes, or plans] | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. |  |  |  | Yes |  | Yes - #1, 3 | Yes - administrative | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R3. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator shall make notifications and exchange reliability–related information with other Reliability Coordinators in accordance with the Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | No | No |  |  | No - this is to implement; R1 is to have the plan | Yes | Yes | No - combine with R1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | Medium | Medium | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R4. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator shall participate in agreed upon conference calls, at least weekly (per Requirement 1, Part 1.7) with other Reliability Coordinators within the same Interconnection. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | Yes - minutiae. | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R5. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | Each Reliability Coordinator, upon identification of an Adverse Reliability Impact, shall notify all other Reliability Coordinators. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | No | No |  |  | No - the std should include "notifying all IMPACTED RCs"; not "ALL" | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | 2 | 11 | High |  | High | Medium | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R6. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | During each instance where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact each impacted Reliability Coordinator shall operate as though the problem exists. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | No | No |  |  | Yes | Yes | Yes | No - consolidate with other stds that incorporate the concept of operating to the most conservative for reliability - IRO-009-1 R5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R7. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, the Reliability Coordinator that identified the Adverse Reliability Impact shall develop an action plan to resolve the Adverse Reliability Impact. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | Yes - this covered under R6. Also supported by IRO-009-1 R5 | No | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [10 empty] | RC
IRO-014-2 | IRO-014-2 | R8. | Coordination Among Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | During those instances where Reliability Coordinators disagree on the existence of an Adverse Reliability Impact, each Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identified the Adverse Reliability Impact unless such actions would violate safety, equipment, regulatory or statutory requirements. | Board Adopted | Board adopted 8/4/2011. Not filed with FERC - pending TOP standards filing. | [5 empty] | Yes - #1, 3 | Yes - this covered under R6. Look at IRO-009-1 R5 | No | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [10 empty] | RC
IRO-015-1 | IRO-015-1 | R1. | Notifications and Information Exchange Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall follow its Operating Procedures, Processes, or Plans for making notifications and exchanging reliability-related information with other Reliability Coordinators. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes |  | Yes | Yes - duplicative of IRO-014-1 R1 and -2 R2, even if R2 is removed. | Yes - communication/notifications. | [17 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-015-1 | IRO-015-1 | R1.1. | Notifications and Information Exchange Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. | Current | Currently enforceable standard. | [5 empty] | Yes | No | Yes - communication/notifications. | [17 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-015-1 | IRO-015-1 | R2. | Notifications and Information Exchange Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall participate in agreed upon conference calls and other communication forums with adjacent Reliability Coordinators. | Current - will be replaced by Board adopted std | Currently enforceable standard. |  |  |  | Yes |  | Yes | No | Yes - minutiae | [17 empty] | No | Yes | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-015-1 | IRO-015-1 | R2.1. | Notifications and Information Exchange Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. | Current | Currently enforceable standard. | [5 empty] | Yes | No | Yes - minutiae | [17 empty] | No | Yes | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
IRO-015-1 | IRO-015-1 | R3. | Notifications and Information Exchange Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall provide reliability-related information as requested by other Reliability Coordinators. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - administrative | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator that identifies a potential, expected, or actual problem that requires the actions of one or more other Reliability Coordinators shall contact the other Reliability Coordinator(s) to confirm that there is a problem and then discuss options and decide upon a solution to prevent or resolve the identified problem. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-014-1 R1 and IRO-014-2 R1 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1.1. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. | Current | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-005-4 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1.2. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). | Current | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-005-4 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1.2.1. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | If time permits, this re-evaluation shall be done before taking corrective actions. | Current | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-005-4 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1.2.2. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. | Current | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-005-4 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R1.3. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. | Current | Currently enforceable standard. | [5 empty] | Yes | Yes - duplicative of IRO-005-4 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Medium | [10 empty] | RC
IRO-016-1 | IRO-016-1 | R2. | Coordination of Real-time Activities Between Reliability Coordinators | To ensure that each Reliability Coordinator’s operations are coordinated such that they will not have an Adverse Reliability Impact on other Reliability Coordinator Areas and to preserve the reliability benefits of interconnected operations. | The Reliability Coordinator shall document (via operator logs or other data sources) its actions taken for either the event or for the disagreement on the problem(s) or for Boardh. | Current - will be replaced by Board adopted std | Currently enforceable standard but approved by Board for deletion under Para 81 Phase 1 |  |  | Yes |  |  |  | Yes - Para 81 Phase 1 | [18 empty] | No | Yes | 0 | 0 | High |  | N/A | Lower | [10 empty] | RC
MOD-001-1 | MOD-001-1a | R1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Operator shall select one of the methodologies listed below for calculating Available Transfer Capability (ATC) or Available Flowgate Capability (AFC) for each ATC Path per time period identified in R2 for those Facilities within its Transmission operating area: [Time Horizon: Operations Planning]  The Area Interchange Methodology, as described in MOD-028  The Rated System Path Methodology, as described in MOD-029  The Flowgate Methodology, as described in MOD-030 | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-001-1 | MOD-001-1a | R2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Service Provider shall calculate ATC or AFC values as listed below using the methodology or methodologies selected by its Transmission Operator(s): [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R2.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Hourly values for at least the next 48 hours. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R2.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Daily values for at least the next 31 calendar days. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R2.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Monthly values for at least the next 12 months (months 2-13). | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Service Provider shall prepare and keep current an Available Transfer Capability Implementation Document (ATCID) that includes, at a minimum, the following information: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | A description of the manner in which the Transmission Service Provider will account for counterflows including: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.2.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.2.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | A rationale for that accounting specified in R3.2. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.4. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.5. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.6. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.6.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.6.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R3.6.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. | Current |  |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The Transmission Service Provider shall notify the following entities before implementing a new or revised ATCID: [Time Horizon: Operations Planning] | Current |  | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Planning Coordinator associated with the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Reliability Coordinator associated with the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Operator associated with the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.4. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.5. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R4.6. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R5. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The Transmission Service Provider shall make available the current ATCID to all of the entities specified in R4. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Reitre MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R6. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | When calculating Total Transfer Capability (TTC) or Total Flowgate Capability (TFC) the Transmission Operator shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Reitre MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-001-1 | MOD-001-1a | R7. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | When calculating ATC or AFC the Transmission Service Provider shall use assumptions no more limiting than those used in the planning of operations for the corresponding time period studied, providing such planning of operations has been performed for that time period. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Reitre MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R8. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Each Transmission Service Provider that calculates ATC shall recalculate ATC at a minimum on the following frequency, unless none of the calculated values identified in the ATC equation have changed: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Reitre MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R8.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R8.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Daily values, once per day. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R8.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Monthly values, once per week. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | Within thirty calendar days of receiving a request by any Transmission Service Provider, Planning Coordinator, Reliability Coordinator, or Transmission Operator for data from the list below solely for use in the requestor’s ATC or AFC calculations, each Transmission Service Provider receiving said request shall begin to make the requested data available to the requestor, subject to the conditions specified in R9.1 and R9.2: [Time Horizon: Operations Planning] • Expected generation and Transmission outages, additions, and retirements. • Load forecasts. • Unit commitments and order of dispatch, to include all designated network resources and other resources that are committed or have the legal obligation to run, as they are expected to run, in one of the following formats chosen by the data provider:  Dispatch Order  Participation Factors  Block Dispatch • Aggregated firm capacity set-aside for Network Integration Transmission Service and aggregated non-firm capacity set aside for Network Integration Transmission Service (i.e. Secondary Service). • Firm and non-firm Transmission reservations. • Aggregated capacity set-aside for Grandfathered obligations • Firm roll-over rights. • Any firm and non-firm adjustments applied by the Transmission Service Provider to reflect parallel path impacts. • Power flow models and underlying assumptions. • Contingencies, provided in one or more of the following formats: A list of Elements  A list of Flowgates  A set of selection criteria that can be applied to the Transmission model used by the Transmission Operator and/or Transmission Service Provider • Facility Ratings. • Any other services that impact Existing Transmission Commitments (ETCs). • Values of Capacity Benefit Margin (CBM) and Transmission Reliability Margin (TRM) for all ATC Paths or Flowgates. • Values of Total Flowgate Capability (TFC) and AFC for any Flowgates considered by the Transmission Service Provider receiving the request when selling Transmission service. • Values of TTC and ATC for all ATC Paths for those Transmission Service Providers receiving the request that do not consider Flowgates when selling Transmission Service. • Source and sink identification and mapping to the model. | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9.1.1. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9.1.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9.1.3. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-001-1 | MOD-001-1a | R9.2. | Available Transmission System Capability | To ensure that calculations are performed by Transmission Service Providers to maintain awareness of available transmission system capability and future flows on their own systems as well as those of their neighbors | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - adminstrative amd data reporting | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Transmission Service Provider that maintains CBM shall prepare and keep current a “Capacity Benefit Margin Implementation Document” (CBMID) that includes, at a minimum, the following information: [Time Horizon: Operations Planning, Long-term Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1 certain areas of country use CBM for reliability purposes (e.g., PJM, Cal ISO) | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R1.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 certain areas of country use CBM for reliability purposes (e.g., PJM, Cal ISO) | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R1.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 certain areas of country use CBM for reliability purposes (e.g., PJM, Cal ISO) | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R1.3. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 certain areas of country use CBM for reliability purposes (e.g., PJM, Cal ISO) | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Transmission Service Provider that maintains CBM shall make available its current CBMID to the Transmission Operators, Transmission Service Providers, Reliability Coordinators, Transmission Planners, Resource Planners, and Planning Coordinators that are within or adjacent to the Transmission Service Provider’s area, and to the Load Serving Entities and Balancing Authorities within the Transmission Service Provider’s area, and notify those entities of any changes to the CBMID prior to the effective date of the change. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No - providing the CBMID document is a business practice | Yes - administrative | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R3. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Each Load-Serving Entity determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Medium - Pending | [5 empty] | LSE
MOD-004-1 | MOD-004-1 | R3.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Pending | [5 empty] | LSE
MOD-004-1 | MOD-004-1 | R3.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Identifying expected import path(s) or source region(s). | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Pending | [5 empty] | LSE
MOD-004-1 | MOD-004-1 | R4. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Each Resource Planner determining the need for Transmission capacity to be set aside as CBM for imports into a Balancing Authority Area shall determine that need by: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Medium - Pending | [12 empty] | RP
MOD-004-1 | MOD-004-1 | R4.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Pending | [12 empty] | RP
MOD-004-1 | MOD-004-1 | R4.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Identifying expected import path(s) or source region(s). | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | No - consolidate R3 and R4 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term "GCIR' is not clear- spell the term out | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Pending | [12 empty] | RP
MOD-004-1 | MOD-004-1 | R5. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | At least every 13 months, the Transmission Service Provider that maintains CBM shall establish a CBM value for each ATC Path or Flowgate to be used for ATC or Available Flowgate Capability (AFC) calculations during the 13 full calendar months (months 2-14) following the current month (the month in which the Transmission Service Provider is establishing the CBM values). This value shall: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R5.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R5.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R6. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | At least every 13 months, the Transmission Planner shall establish a CBM value for each ATC Path or Flowgate to be used in planning during each of the full calendar years two through ten following the current year (the year in which the Transmission Planner is establishing the CBM values). This value shall: [Time Horizon: Long-term Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - phrase "at least every 13 months" is not cleared" | Yes | Yes | Yes | Yes | 3 | 10 | Not ranked |  | Low | Pending | [17 empty] | TP
MOD-004-1 | MOD-004-1 | R6.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No-format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - phrase "at least every 13 months" is not cleared" | Yes | Yes | Yes | Yes | 3 | 10 | Not ranked |  | Low | Pending | [17 empty] | TP
MOD-004-1 | MOD-004-1 | R6.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No-format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - phrase "at least every 13 months" is not cleared" | Yes | Yes | Yes | Yes | 3 | 10 | Not ranked |  | Low | Pending | [17 empty] | TP
MOD-004-1 | MOD-004-1 | R7. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Less than 31 calendar days after the establishment of CBM, the Transmission Service Provider that maintains CBM shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the Transmission Service Provider’s system of the amount of CBM set aside. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No - business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R8. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Less than 31 calendar days after the establishment of CBM, the Transmission Planner shall notify all the Load-Serving Entities and Resource Planners that determined they had a need for CBM on the system being planned by the Transmission Planner of the amount of CBM set aside. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No - business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [17 empty] | TP
MOD-004-1 | MOD-004-1 | R9. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Transmission Service Provider that maintains CBM and the Transmission Planner shall each provide (subject to confidentiality and security requirements) copies of the applicable supporting data, including any models, used for determining CBM or allocating CBM over each ATC Path or Flowgate to the following: [Time Horizon: Operations Planning, Long-term Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No - business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [17 empty] | TP | TSP
MOD-004-1 | MOD-004-1 | R9.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | Each of its associated Transmission Operators within 30 calendar days of their making a request for the data. | Current | Currently enforceable standard. | [5 empty] | No - business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [17 empty] | TP | TSP
MOD-004-1 | MOD-004-1 | R9.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. | Current | Currently enforceable standard. | [5 empty] | No - business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [17 empty] | TP | TSP
MOD-004-1 | MOD-004-1 | R10. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Load-Serving Entity or Balancing Authority shall request to import energy over firm Transfer Capability set aside as CBM only when experiencing a declared NERC Energy Emergency Alert (EEA) 2 or higher. [Time Horizon: Same-day Operations] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes Consolidate into EOP-002-3.1, IRO-005-3.1a | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - EEA is not defined term and the levels of EEA are described in the EOP std | No - EEA is not defined term and the levels of EEA are described in the EOP std | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 10 | Not ranked |  | Medium | Pending | BA |  |  |  |  | LSE
MOD-004-1 | MOD-004-1 | R11. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | When reviewing an Arranged Interchange using CBM, all Balancing Authorities and Transmission Service Providers shall waive, within the bounds of reliable operation, any Real-time timing and ramping requirements. [Time Horizon: Same-day Operations] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - consolidate R11 and R12, with the R11 becoming the last sub-requirement of R12 | Yes | Yes | Yes | Yes | Yes | No - "reliable operations" is not a defined term | Yes | Yes | No - "reliable operations" is not a defined term | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 9 | Not ranked |  | Low | Pending | BA | [17 empty] | TSP
MOD-004-1 | MOD-004-1 | R12. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Transmission Service Provider that maintains CBM shall approve, within the bounds of reliable operation, any Arranged Interchange using CBM that is submitted by an “energy deficient entity ” under an EEA 2 if: [Time Horizon: Same-day Operations] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  |  | Team determined that, although CBM is not used in every interconnection, the continued use in some instances requires this requirement to be retained | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - consolidate R11 and R12, with the R11 becoming the last sub-requirement of R12 | No - format | Yes | Yes | Yes | Yes | No - "reliable operations" is not a defined term | Yes | No - footnote reference and use of "EEA" | No - "reliable operations" is not a defined term, use of term EEA and footnote | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 8 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R12.1. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The CBM is available | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No, duplicative- look at NERC stds related to callling an EEA (EOP-2-3.1 and IRO 5-3.1a and INT standards | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 10 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R12.2. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The EEA 2 is declared within the Balancing Authority Area of the “energy deficient entity,” and | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No, duplicative- look at NERC stds related to callling an EEA (EOP-2-3.1 and IRO 5-3.1a and INT standards | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 10 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-004-1 | MOD-004-1 | R12.3. | Capacity Benefit Margin | To promote the consistent and reliable calculation, verification, preservation, and use of Capacity Benefit Margin (CBM) to support analysis and system operations. | The Load of the “energy deficient entity” is located within the Transmission Service Provider’s area. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No, duplicative- look at NERC stds related to callling an EEA (EOP-2-3.1 and IRO 5-3.1a and INT standards | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Maybe- duplicative- look at NERC stds related to calling an EEA (EOP-2-3.1 and IRO 5-3.1a) | 3 | 10 | Not ranked |  | Low | Pending | [18 empty] | TSP
MOD-008-1 | MOD-008-1 | R1. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Each Transmission Operator shall prepare and keep current a TRM Implementation Document (TRMID) that includes, as a minimum, the following information: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although TRM is not used in every interconnection, the continued use in some instances requires this requirement to be retained. | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.1. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: - Aggregate Load forecast. - Load distribution uncertainty. - Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages). - Allowances for parallel path (loop flow) impacts. - Allowances for simultaneous path interactions. - Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation). - Short-term System Operator response (Operating Reserve actions ). - Reserve sharing requirements. - Inertial response and frequency bias. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | No - 'Aggregate load forecast' should be "load forecast error or uncertainty" | yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No -' Aggregate load forecast' should be "load forecast error or uncertainty" | Yes | Yes | Yes | Yes | 2 | 10 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.2. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | The description of the method used to allocate TRM across ATC Paths or Flowgates. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | No - not clear what is expected in "description" | Yes | Yes | No -not clear what is expected in "description" | Yes | No -not clear what is expected in "description" | Yes | No -not clear what is expected in "description" | Yes | Yes | Yes | 3 | 7 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.3. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | The identification of the TRM calculation used for the following time periods: | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.3.1. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Same day and real-time. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.3.2. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Day-ahead and pre-schedule. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | Yes |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R1.3.3. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Beyond day-ahead and pre-schedule, up to thirteen months ahead. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R2. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Each Transmission Operator shall only use the components of uncertainty from R1.1 to establish TRM, and shall not include any of the components of Capacity Benefit Margin (CBM). Transmission capacity set aside for reserve sharing agreements can be included in TRM. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes | Team determined that, although TRM is not used in every interconnection, the continued use in some instances requires this requirement to be retained. | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | No, but the second sentence is just a statement (redraft). | Yes | Yes | Yes | Yes | Yes | Yes | No - it requires you to consider CBM, which is spelled out in MOD-004 | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Not ranked |  | Medium | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R3. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Each Transmission Operator shall make available its TRMID, and if requested, underlying documentation (if any) used to determine TRM, in the format used by the Transmission Operator, to any of the following who make a written request no more than 30 calendar days after receiving the request. [Time Horizon: Operations Planning] • Transmission Service Providers • Reliability Coordinators • Planning Coordinators • Transmission Planner • Transmission Operators | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No - administrative | Yes - administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R4. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | Each Transmission Operator that maintains TRM shall establish TRM values in accordance with the TRMID at least once every 13 months. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | Unclear how R4 reconciles with the time periods defined in R1.3. |  | Yes | Team determined that, although TRM is not used in every interconnection, the continued use in some instances requires this requirement to be retained. | Yes - #1, 3, 4, 7 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - is "at least once every 13 months" clear enough? Same concern as confusion on "annual" | Yes | Yes | No - is "at least once every 13 months" clear enough? Same concern as confusion on "annual" | No - is "at least once every 13 months" clear enough? Same concern as confusion on "annual" | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Low | Pending | [16 empty] | TOP
MOD-008-1 | MOD-008-1 | R5. | Transmission Reliability Margin Calculation Methodology | To promote the consistent and reliable calculation, verification, preservation, and use of Transmission Reliability Margin (TRM) to support analysis and system operations. | The Transmission Operator that maintains TRM shall provide the TRM values to its Transmission Service Provider(s) and Transmission Planner(s) no more than seven calendar days after a TRM value is initially established or subsequently changed. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A |  |  | Yes |  | No | Yes - administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-010-0 | MOD-010-0 | R1. | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide appropriate equipment characteristics, system data, and existing and future Interchange Schedules in compliance with its respective Interconnection Regional steady-state modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-011-0_R 1. | Current | Currently enforceable standard. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. |  |  |  | Yes - #3 | No | No |  |  | No - see suggestions for improvements | Yes | Yes | No - consolidate 10,11,14 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - refers to MOD-011 for data to be provided; MOD-011 is not approved | No-capitlaized term of "Interconnection Regional", and refers to RRO | No not w/o MOD-011 | No RRO, ITS | Yes | Yes | 2 | 7 | Medium |  | Medium | Medium |  |  | GO | [9 empty] | RP |  |  | TO |  | TP
MOD-010-0 | MOD-010-0 | R2. | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide this steady-state modeling and simulation data to the Regional Reliability Organizations, NERC, and those entities specified within Reliability Standard MOD-011-0_R 1. If no schedule exists, then these entities shall provide the data on request (30 calendar days). | Current | Currently enforceable standard. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. |  | Yes | Team determined that this data collection supports reliability objectives, so the requirement should be retained. The team recommends that this requirement be improved as noted. | Yes - #3 | No | No |  |  | No - see suggestions for improvements | Yes | Yes | No - consolidate 10,11,14 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - refers to MOD-011 for data to be provided; MOD-011 is not approved | No-capitlaized term of "Interconnection Regional", and refers to RRO | No not w/o MOD 011 | No RRO, ITS | Yes | Yes | 2 | 7 | Medium |  | Medium | Medium |  |  | GO | [9 empty] | RP |  |  | TO |  | TP
MOD-011 | MOD-011 | R1. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling . MODs need proper language on validation. Delete "Eastern, Western and ERCOT on line 5 of R1. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.1. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.2. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.3. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.4. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.5. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.6. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R1.7. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-011 | MOD-011 | R2. |  |  |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No - but five day requirement is administrative/reporting | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 10,11,14 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - has RRO referenced | No - has RRO referenced | No - has RRO reference | Yes | Yes | 1 | 8 | Not ranked |  | Low | Pending | [13 empty] | RRO
MOD-012-0 | MOD-012-0 | R1. | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide appropriate equipment characteristics and system data in compliance with the respective Interconnection-wide Regional dynamics system modeling and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-013-0_R1. | Current | Currently enforceable standard. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. |  |  |  | Yes - #3 | No | No |  |  | No - see suggestions for improvements | Yes | Yes | No - consolidate 10,11,14 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - refers to MOD-013 for data to be provided; MOD-013 is not approved | No - capitlaized term of "Interconnection Regional", and refers to RRO | No not w/o MOD-013 | No RRO, ITS | Yes | Yes | 2 | 7 | Medium |  | Medium | Medium |  |  | GO | [9 empty] | RP |  |  | TO |  | TP
MOD-012-0 | MOD-012-0 | R2. | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R4) shall provide dynamics system modeling and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R 1. If no schedule exists, then these entities shall provide data on request (30 calendar days). | Current | Currently enforceable standard. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. |  | Yes | Team determined that this data collection supports reliability objectives, so the requirement should be retained. The team recommends that this requirement be improved as noted. | Yes - #3 | No | No |  |  | No - see suggestions for improvements | Yes | Yes | No - consolidate 12,13,15 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - refers to MOD-013 for data to be provided; MOD-013 is not approved | No - capitlaized term of "Interconnection Regional", and refers to RRO | No not w/o MOD-013 | No RRO, ITS | Yes | Yes | 2 | 7 | Medium |  | Medium | Medium |  |  | GO | [9 empty] | RP |  |  | TO |  | TP
MOD-013-1 | MOD-013-1 | R1. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.1. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.1.1. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.2. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.2.1. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.2.2. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.3. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.4. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R1.5. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | No - format | Yes | Yes | Yes | Yes | Yes | Yes | No | No - assigns requirment to the RRO | No -fill in blank std | No RRO, ITS | Yes | Yes | 1 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-013-1 | MOD-013-1 | R2. | Maintenance and Distribution of Dynamics Data Requirements and Reporting Procedures | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No - but five day requirement is administrative/reporting | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - has RRO referenced | No - has RRO referenced | No - has RRO reference | Yes | Yes | 1 | 8 | Not ranked |  | Low | Pending | [13 empty] | RRO
MOD-014-0 | MOD-014-0 | R1. | Development of Steady-State System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | No - the periodicity is not specified; lacks requirment for timely correction for modeling areas | No - consolidate 12,13,15 | No - the periodicity is not specified | Yes | No - role of RRO confuses things | Yes | No - periodicity not prescribed in the std. | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 0 | 5 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-014-0 | MOD-014-0 | R2. | Development of Steady-State System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | Yes | Yes | No - role of RRO confuses things | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO; has word 'annually' | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-015-0 | MOD-015-0 | R1. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | No - the periodicity is not specified; lacks requirment for timely correction for modeling areas | No - consolidate 12,13,15 | No - the periodicity is not specified | Yes | No - role of RRO confuses things | Yes | No - periodicity not prescribed in the std. | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 0 | 5 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-015-0 | MOD-015-0 | R1.1. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | No - the periodicity is not specified; lacks requirment for timely correction for modeling areas | No - consolidate 12,13,15 | No - periodicity not prescribed in the std. | Yes | No - role of RRO confuses things | Yes | No - periodicity not prescribed in the std. | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 0 | 6 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-015-0 | MOD-015-0 | R2. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | Yes | Yes | No - role off RRO confuses things | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO; has word 'annually' | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-015-0 | MOD-015-0.1 | R1. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 - not filed future version | Board adopted 10/29/2008; not filed with FERC because MOD-015-0 has not been approved. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | No - the periodicity is not specified; lacks requirment for timely correction for modeling areas | No - consolidate 12,13,15 | No - the periodicity is not specified | Yes | No - role of RRO confuses things | Yes | No - periodicity not prescribed in the std. | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 0 | 5 | Not ranked |  | Medium | Pending
MOD-015-0 | MOD-015-0.1 | R1.1. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 - not filed future version | Board adopted 10/29/2008; not filed with FERC because MOD-015-0 has not been approved. |  | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | No - the periodicity is not specified; lacks requirment for timely correction for modeling areas | No - consolidate 12,13,15 | No - periodicity not prescribed in the std. | Yes | No - role of RRO confuses things | Yes | No - periodicity not prescribed in the std. | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 0 | 6 | Not ranked |  | Medium | Pending
MOD-015-0 | MOD-015-0.1 | R2. | Development of Dynamics System Models | To establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the interconnected transmission systems. |  | Not approved in Order 693 - not filed future version | Board adopted 10/29/2008; not filed with FERC because MOD-015-0 has not been approved. | Yes - Project 2010-03 MOD B (Modeling Data) | Combine MODs 10-15-one std for steady state planning models, one std for stability models. Add two new NERC stds- one for fault duty(short ckt) modeling and one for EMS RTCA data modeling. MODs need proper language on validation. Also, consider combining MOD26-1 and 27-1 with MOD 10-15. Also, consider combining FAC 008 (Facility Ratings) with MOD 010-15. |  |  |  | Yes - #3 | No | No |  |  | No - see recommendations for improvements | No - refers to RRO and lacks reference to PC | Yes | No - consolidate 12,13,15 | Yes | Yes | No - role off RRO confuses things | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO; has word 'annually' | No - assigns requirment to the RRO | No RRO, ITS | Yes | Yes | 1 | 7 | Not ranked |  | Medium | Pending
MOD-016-1 | MOD-016-1.1 | R1. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The Planning Authority and Regional Reliability Organization shall have documentation identifying the scope and details of the actual and forecast (a) Demand data, (b) Net Energy for Load data, and (c) controllable DSM data to be reported for system modeling and reliability analyses. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes and MOD-016-1 |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [7 empty] | PA | PC |  |  |  |  | RRO
MOD-016-1 | MOD-016-1.1 | R1.1. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | Yes - #3 | No | No |  |  | No | No | No - R1.1 requires LSE to provide demand data-- it should be the DP | No - combine R1.1 into R1 and simplify to remove specific references to the specfic stds | No | Yes | No - the term 'dispersed' is not defined; | Yes | Yes | Yes | Yes | No - refers to other NERC stds | No - term 'dispersed' not defined | No - term 'dispersed' not defined | Yes | Yes | Yes | 0 | 6 | Medium |  | Medium | Lower | [7 empty] | PA | PC |  |  |  |  | RRO
MOD-016-1 | MOD-016-1.1 | R2. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The Regional Reliability Organization shall distribute its documentation required in Requirement 1 and any changes to that documentation, to all Planning Authorities that work within its Region. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes for MOD-016-1 |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [13 empty] | RRO
MOD-016-1 | MOD-016-1.1 | R2.1. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower | [13 empty] | RRO
MOD-016-1 | MOD-016-1.1 | R3. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The Planning Authority shall distribute its documentation required in R1 for reporting customer data and any changes to that documentation, to its Transmission Planners and Load-Serving Entities that work within its Planning Authority Area. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes and MOD-016-1 |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [7 empty] | PA | PC
MOD-016-1 | MOD-016-1.1 | R3.1. | Documentation of Data Reporting Requirements for Actual and Forecast Demands, Net Energy for Load, and Controllable Demand-Side Management | Ensure that accurate, actual Demand data is available to support assessments and validation of past events and databases. Forecast Demand data is needed to perform future system assessments to identify the need for system reinforcements for continued reli | The Planning Authority shall make this distribution within 30 calendar days of approval. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | Yes - #3 | No | No |  |  | Yes | No - it is not always TP and LSE who do this | Yes | No - merge R3 and R3.1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - term 'customer data' is not clear | Yes | Yes | Yes | Yes | 2 | 9 | Medium |  | Low | Lower | [7 empty] | PA | PC
MOD-017-0 | MOD-017-0.1 | R1. | Aggregated Actual and Forecast Demands and Net Energy for Load | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessment to identify the need for system reinforcement for contin | The Load-Serving Entity, Planning Authority and Resource Planner shall each provide the following information annually on an aggregated Regional, subregional, Power Pool, individual system, or Load-Serving Entity basis to NERC, the Regional Reliability Organizations, and any other entities specified by the documentation in Standard MOD-016-1_R1. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP
MOD-017-0 | MOD-017-0.1 | R1.1. | Aggregated Actual and Forecast Demands and Net Energy for Load | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessment to identify the need for system reinforcement for contin | Integrated hourly demands in megawatts (MW) for the prior year. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP
MOD-017-0 | MOD-017-0.1 | R1.2. | Aggregated Actual and Forecast Demands and Net Energy for Load | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessment to identify the need for system reinforcement for contin | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP
MOD-017-0 | MOD-017-0.1 | R1.3. | Aggregated Actual and Forecast Demands and Net Energy for Load | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessment to identify the need for system reinforcement for contin | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP
MOD-017-0 | MOD-017-0.1 | R1.4. | Aggregated Actual and Forecast Demands and Net Energy for Load | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessment to identify the need for system reinforcement for contin | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP
MOD-018-0 | MOD-018-0 | R1. | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | To ensure that Assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Planning Authority, Transmission Planner and Resource Planner’s report of actual and forecast demand data (reported on either an aggregated or dispersed basis) shall: | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-018-0 | MOD-018-0 | R1.1. | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | To ensure that Assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-018-0 | MOD-018-0 | R1.2. | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | To ensure that Assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-018-0 | MOD-018-0 | R1.3. | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | To ensure that Assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. | Current | Currently enforceable standard. |  | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  |  |  | No | [19 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-018-0 | MOD-018-0 | R2. | Treatment of Nonmember Demand Data and How Uncertainties are Addressed in the Forecasts of Demand and Net Energy for Load | To ensure that Assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each report data associated with Reliability Standard MOD-018-0_R1 to NERC, the Regional Reliability Organization, Load-Serving Entity, Planning Authority, and Resource Planner on request (within 30 calendar days). | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-019-0 | MOD-019-0.1 | R1. | Reporting of Interruptible Demands and Direct Control Load Management | To ensure that assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Planning Authority, Transmission Planner, and Resource Planner shall each provide annually its forecasts of interruptible demands and Direct Control Load Management (DCLM) data for at least five years and up to ten years into the future, as requested, for summer and winter peak system conditions to NERC, the Regional Reliability Organizations, and other entities (Load-Serving Entities, Planning Authorities, and Resource Planners) as specified by the documentation in Reliability Standard MOD-016-1_R 1. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Medium | [5 empty] | LSE |  | PA | PC |  |  |  | RP |  |  |  |  | TP
MOD-020-0 | MOD-020-0 | R1. | Providing Interruptible Demands and Direct Control Load Management Data to System Operators and Reliability Coordinators | To ensure that assessments and validation of past events and databases can be performed, reporting of actual demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Transmission Planner, and Resource Planner shall each make known its amount of interruptible demands and Direct Control Load Management (DCLM) to Transmission Operators, Balancing Authorities, and Reliability Coordinators on request within 30 calendar days. | Current | Currently enforceable standard. |  | MOD 020 does not provide any value for real time operations done by RC, BA, TOP, etc since it allows 30 days for data to be provided. MOD 020 is needed, but it needs to be re-written so that data is provided on Direct Load Control and Interruptible Demand in a time manner that will support reliable real-time operations. |  | Yes and MOD-020-1 | MOD 020 does not provide any value for real time operations done by RC, BA, TOP, etc since it allows 30 days for data to be provided. However, MOD 020 is needed but it needs to be re-written so that data is provided on Direct Load Control and Interruptible Demand in a time manner that will support reliable real-time operations. | Yes - #3 | No | No |  |  | No - allows for 30 days to give data to RC_ see 'suggestions for improvement' column | No - Resource Planner, BA and DP need to be addressed. In markets such as CalSO, the markets can provide this DSM resource | No - see comments under 'suggestions for improvement' | No - a modified MOD 020 that focusses more on real-time operations should be placed somewhere in the stds related to real time ops- BAL, IRO, TOP, EOP | Yes | Yes | Yes | No - Purpose is poorly written and 'all over the place' | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 0 | 9 | Medium |  | Medium | Lower | [5 empty] | LSE | [6 empty] | RP |  |  |  |  | TP
MOD-021-1 | MOD-021-1 | R1. | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Transmission Planner and Resource Planner’s forecasts shall each clearly document how the Demand and energy effects of DSM programs (such as conservation, time-of-use rates, interruptible Demands, and Direct Control Load Management) are addressed. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE | [6 empty] | RP |  |  |  |  | TP
MOD-021-1 | MOD-021-1 | R2. | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Transmission Planner and Resource Planner shall each include information detailing how Demand-Side Management measures are addressed in the forecasts of its Peak Demand and annual Net Energy for Load in the data reporting procedures of Standard MOD-016-0_R1. | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE | [6 empty] | RP |  |  |  |  | TP
MOD-021-1 | MOD-021-1 | R3. | Documentation of the Accounting Methodology for the Effects of Demand-Side Management in Demand and Energy Forecasts | To ensure that assessments and validation of past events and databases can be performed, reporting of actual Demand data is needed. Forecast demand data is needed to perform future system assessments to identify the need for system reinforcement for conti | The Load-Serving Entity, Transmission Planner and Resource Planner shall each make documentation on the treatment of its DSM programs available to NERC on request (within 30 calendar days). | Current | Currently enforceable standard. | Yes - Project 2010-04 MOD C (Demand Data Directives) | Retire MODs 16-19 and 21 and gather whatever data NERC needs for assessments and reports through Section 804 of NERC Rules of Procedure. |  | Yes |  | Yes - #3 | Yes - P 81 criteria: data collection/data retention | [20 empty] | 0 | 0 | Medium |  | N/A | Lower | [5 empty] | LSE | [6 empty] | RP |  |  |  |  | TP
MOD-024-1 | MOD-024-1 | R1. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  |  | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.1. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.2. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.3. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.4. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.5. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.5.1. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.5.2. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R1.5.3. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R2. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | Yes - administrative | No | [6 empty] | Yes | [10 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Pending | [13 empty] | RRO
MOD-024-1 | MOD-024-1 | R3. | Verification of Generator Gross and Net Real Power Capability | To ensure accurate information on generator gross and net Real Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693 |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | Yes | Yes | No - refererences RRO | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium | Pending |  |  | GO
MOD-025-1 | MOD-025-1 | R1. | Verification of Generator Gross and Net Reactive Power Capability | To ensure accurate information on generator gross and net Reactive Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693. Will be replaced when MOD-025-2 becomes enforceable |  | MOD-024-1 is an RRO 'fill in the blank std'. MOD 25-2 was approved at 2/13 NERC Board meeitng and it takes place of MOD-024-1 and MOD 025-1 |  |  |  | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | Yes | Yes | No - refererences RRO | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium
MOD-025-1 | MOD-025-1 | R2. | Verification of Generator Gross and Net Reactive Power Capability | To ensure accurate information on generator gross and net Reactive Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693. Will be replaced when MOD-025-2 becomes enforceable | [5 empty] | Yes - #3 | No | No | No |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Low
MOD-025-1 | MOD-025-1 | R3. | Verification of Generator Gross and Net Reactive Power Capability | To ensure accurate information on generator gross and net Reactive Power capability is available for steady-state models used to assess Bulk Electric System reliability. |  | Not approved in Order 693 | Not approved by FERC in Order 693. Will be replaced when MOD-025-2 becomes enforceable | [5 empty] | Yes - #3 | No | No |  |  | No | No - RRO is involved | No - RRO is involved | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - assigns requirment to the RRO | No - assigns requirment to the RRO | No RRO | Yes | Yes | 0 | 7 | Not ranked |  | Medium
MOD-025-2 | MOD-025-2 | R1. | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | To ensure that accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability is available for planning models used to assess Bulk Electric System (BES) reliability. |  | Board Adopted | Board adopted 2/7/2013- Team reviewed 25-2 because 24-1 and 25-1 were not approved in Order 693 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - paragraph at top of page 14 of 20 reads "… at least 90% …of at least 50%". This is hard to understand | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | High |  |  |  | GO
MOD-025-2 | MOD-025-2 | R2. | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | To ensure that accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability is available for planning models used to assess Bulk Electric System (BES) reliability. |  | Board Adopted | Board adopted 2/7/2013- Team reviewed 25-2 because 24-1 and 25-1 were not approved in Order 693 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - paragraph at top of page 14 of 20 reads "… at least 90% …of at least 50%". This is hard to understand | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | High |  |  |  | GO
MOD-025-2 | MOD-025-2 | R3. | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | To ensure that accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability is available for planning models used to assess Bulk Electric System (BES) reliability. |  | Board Adopted | Board adopted 2/7/2013- Team reviewed 25-2 because 24-1 and 25-1 were not approved in Order 693 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - paragraph at top of page 14 of 20 reads "… at least 90% …of at least 50%". This is hard to understand | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | High | [16 empty] | TO
MOD-026-1 | MOD-026-1 | R1. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Lower | [17 empty] | TP
MOD-026-1 | MOD-026-1 | R2. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No - Att. 1 that is integral part of this requirement is hard to interpret when you first read it. It takes several readings to get clear on what it is saying | Yes | Yes | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | Yes | No - Att. 1 contains reference to a definition of net capacity factor in NERC GADS document. | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | Yes | Yes | Yes | 3 | 6 | Not ranked |  | Medium | Medium |  |  | GO
MOD-026-1 | MOD-026-1 | R3. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No - R3 and R5 are about the same thing- a requirement for GO to reply to TP when TP, under R6, says there is model data problem, combine R3 and R5 | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | Yes | 3 | 8 | Not ranked |  | Medium | Lower |  |  | GO
MOD-026-1 | MOD-026-1 | R4. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | Yes | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 2. Difficult to follow and understand exactly what is required | Yes | Yes | Yes | 3 | 8 | Not ranked |  | Medium | Lower |  |  | GO
MOD-026-1 | MOD-026-1 | R5. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No - R3 and R5 are about the same thing- a requirement for GO to reply to TP when TP, under R6, says there is model data problem, combine R3 and R5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Lower |  |  | GO
MOD-026-1 | MOD-026-1 | R6. | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | To verify that the generator excitation control system or plant volt/var control function model (including the power system stabilizer model and the impedance compensator model) and the model parameters used in dynamic simulations accurately represent th |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Medium | [17 empty] | TP
MOD-027-1 | MOD-027-1 | R1. | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | To verify that the turbine/governor and load control or active power/frequency control model and the model parameters, used in dynamic simulations that assess Bulk Electric System (BES) reliability, accurately represent generator unit real power response |  | Board Adopted | Board adopted 2/7/2013 |  | MOD027-1 is about governor response model validation, and it is not about putting a requirement on generators having a certain amount of governor frequency response--should consider this need for governor response capability in the BAL stds. |  |  |  | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Lower | [17 empty] | TP
MOD-027-1 | MOD-027-1 | R2. | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | To verify that the turbine/governor and load control or active power/frequency control model and the model parameters, used in dynamic simulations that assess Bulk Electric System (BES) reliability, accurately represent generator unit real power response |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | Yes | No - Att. 1 contains reference to a definition of net capacity factor in NERC GADS document. | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | No - Att. 1 that is integral part of this requirement is very hard to interpret . This could make measurability difficult | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 8 | Not ranked |  | Medium | Medium |  |  | GO
MOD-027-1 | MOD-027-1 | R3. | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | To verify that the turbine/governor and load control or active power/frequency control model and the model parameters, used in dynamic simulations that assess Bulk Electric System (BES) reliability, accurately represent generator unit real power response |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 9 | Not ranked |  | Medium | Lower |  |  | GO
MOD-027-1 | MOD-027-1 | R4. | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | To verify that the turbine/governor and load control or active power/frequency control model and the model parameters, used in dynamic simulations that assess Bulk Electric System (BES) reliability, accurately represent generator unit real power response |  | Board Adopted | Board adopted 2/7/2013 | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | No - R3 and R4 must be read in conjunction with footnotes 3 and 4 and Row 5 of Attachment 1. Difficult to follow and understand exactly what is required | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 8 | Not ranked |  | Medium | Lower |  |  | GO
MOD-027-1 | MOD-027-1 | R5. | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | To verify that the turbine/governor and load control or active power/frequency control model and the model parameters, used in dynamic simulations that assess Bulk Electric System (BES) reliability, accurately represent generator unit real power response |  | Board Adopted | Board adopted 2/7/2013 |  | MOD 27-1 lacks the R5 that is found in 26-1-- . This appears to be a gap, unless there is documentation in std. drafting team record that explains why this was not included in MOD 27-1. |  |  |  | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | Not ranked |  | Medium | Medium | [17 empty] | TP
MOD-028-1 | MOD-028-1 | R1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Each Transmission Service Provider shall include in its Available Transfer Capability Implementation Document (ATCID), at a minimum, the following information relative to its methodology for determining Total Transfer Capability (TTC): [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation. However move R1 R1.1.1 - R1.1.4 to the FAC stds as these speak to TTC | No - however move R1 R1.1.1 - R1.1.4 to the FAC stds as these speak to TTC | [5 empty] | No - consider moving R1 R1.1.1 - R1.1.4 to the FAC stds as these speak to TTC | [11 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Any contractual obligations for allocation of TTC. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | A description of the manner in which Contingencies are identified for use in the TTC process. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.5. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | The following information on how source and sink for transmission service is accounted for in ATC calculations including: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.5.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.5.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.5.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | The source/sink or POR/POD identification and mapping to the model. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R1.5.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating TTC for ATC Paths, the Transmission Operator shall use a Transmission model that contains all of the following: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R2.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R2.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R2.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Facility Ratings specified by the Generator Owners and Transmission Owners. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating TTCs for ATC Paths, the Transmission Operator shall include the following data for the Transmission Service Provider’s area. The Transmission Operator shall also include the following data associated with Facilities that are explicitly represented in the Transmission model, as provided by adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | For on-peak and off-peak intra-day and next-day TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.1.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.1.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Load forecast for the applicable period being calculated. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.1.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | For days two through 31 TTCs and for months two through 13 TTCs, use the following (as well as any other values and internal parameters as specified in the ATCID): | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.2.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Expected generation and Transmission outages, additions, and Retirements, included as specified in the ATCID. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.2.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Daily load forecast for the days two through 31 TTCs being calculated and monthly forecast for months two through 13 months TTCs being calculated. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R3.2.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating TTCs for ATC Paths, the Transmission Operator shall meet all of the following conditions: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R4.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Use all Contingencies meeting the criteria described in the ATCID. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R4.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Respect any contractual allocations of TTC. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R4.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R5. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Each Transmission Operator shall establish TTC for each ATC Path as defined below: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R5.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R5.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | At least once per calendar month for TTCs used in monthly ATC calculations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R5.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R6. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Each Transmission Operator shall establish TTC for each ATC Path using the following process: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R6.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R6.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R6.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Use (as the TTC) the lesser of:  The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or  The sum of Facility Ratings of all ties comprising the ATC Path. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R6.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R7. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | The Transmission Operator shall provide the Transmission Service Provider of that ATC Path with the most current value for TTC for that ATC Path no more than: [Time Horizon: Operations Planning] | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R7.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R7.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | Seven calendar days after its determination for TTCs used in monthly ATC calculations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-028-1 | MOD-028-1 | R8. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating Existing Transmission Commitments (ETCs) for firm commitments (ETCF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R9. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating ETC for non-firm commitments (ETCNF) for all time periods for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R10. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall utilize the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-1 | MOD-028-1 | R11. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. | When calculating non-firm ATC for a ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced when MOD-028-2 is approved by FERC. The Board adopted MOD-028-2 2/9/2012 and it was filed with FERC 8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.5. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.5.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.5.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.5.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R1.5.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R2.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R2.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R2.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R3.1.5. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R4.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R4.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R4.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R5. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R5.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R5.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R5.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R6. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R6.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R6.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R6.3. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R6.4. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R7. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R7.1. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Reitre MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R7.2. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; administrative | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [16 empty] | TOP
MOD-028-2 | MOD-028-2 | R8. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R9. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R10. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-028-2 | MOD-028-2 | R11. | Area Interchange Methodology | To increase consistency and reliability in the development and documentation of Transfer Capability calculations for short-term use performed by entities using the Area Interchange Methodology to support analysis and system operations. |  | Board Adopted | Board adopted 8/24/2012; Filed with FERC8/24/2012 | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower | [18 empty] | TSP
MOD-029-1 | MOD-029-1a | R1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When calculating TTCs for ATC Paths, the Transmission Operator shall use a Transmission model which satisfies the following requirements: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Includes at least: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.1.1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.1.2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.1.3. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.10. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Includes any other modeling requirements or criteria specified in the ATCID. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Models all system Elements as in-service for the assumed initial conditions. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.3. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.4. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.5. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uses Load forecast by Balancing Authority. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.6. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uses Transmission Facility additions and retirements. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.7. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uses Generation Facility additions and retirements. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.8. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.1.9. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R1.2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | The Transmission Operator shall use the following process to determine TTC: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.1.1. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.1.2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.1.3. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Uncontrolled separation shall not occur. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.2. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.3. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.4. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.5. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.6. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.7. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R2.8. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Create a study report that describes the steps above that were undertaken (R2.1 – R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R3. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Each Transmission Operator shall establish the TTC at the lesser of the value calculated in R2 or any System Operating Limit (SOL) for that ATC Path. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R4. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | Within seven calendar days of the finalization of the study report, the Transmission Operator shall make available to the Transmission Service Provider of the ATC Path, the most current value for TTC and the TTC study report documenting the assumptions used and steps taken in determining the current value for TTC for that ATC Path. [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-029-1 | MOD-029-1a | R5. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When calculating ETC for firm Existing Transmission Commitments (ETCF) for a specified period for an ATC Path, the Transmission Service Provider shall use the algorithm below: [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-029-1 | MOD-029-1a | R6. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When calculating ETC for non-firm Existing Transmission Commitments (ETCNF) for all time horizons for an ATC Path the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-029-1 | MOD-029-1a | R7. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When calculating firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-029-1 | MOD-029-1a | R8. | Rated System Path Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Rated System Path Methodology to support analysis and system operations. | When calculating non-firm ATC for an ATC Path for a specified period, the Transmission Service Provider shall use the following algorithm:[Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The Transmission Service Provider shall include in its “Available Transfer Capability Implementation Document” (ATCID): [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The following information on how source and sink for transmission service is accounted for in AFC calculations including: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.2.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.2.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.2.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The source/sink or POR/POD identification and mapping to the model. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R1.2.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; documentation | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The Transmission Operator shall perform the following: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.1.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.1.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.1.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.2.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.2.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Only the most limiting element in a series configuration needs to be included as a Flowgate. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.2.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.4.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.1.4.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.5. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | At a minimum, establish the TFC once per calendar year. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.5.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R2.6. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The Transmission Operator shall make available to the Transmission Service Provider a Transmission model to determine Available Flowgate Capability (AFC) that meets the following criteria: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; reporting | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; reporting | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Updated at least once per month for AFC calculations for months two through 13. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; reporting | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; reporting | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R3.5. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice; reporting | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [16 empty] | TOP
MOD-030-2 | MOD-030-2 | R4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating AFCs, the Transmission Service Provider shall represent the impact of Transmission Service as follows: [Time Horizon: Operations Planning] - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate” representation in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point or an “equivalence” representation in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation use the immediately adjacent Balancing Authority associated with the Transmission Service Provider receiving the power as the sink. | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R5. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating AFCs, the Transmission Service Provider shall: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R5.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Use the models provided by the Transmission Operator. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R5.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R5.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating the impact of ETC for firm commitments (ETCFi) for all time periods for a Flowgate, the Transmission Service Provider shall sum the following: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.1.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Load forecast for the time period being calculated, including Native Load and Network Service load | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.1.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.2.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Load forecast for the time period being calculated, including Native Load and Network Service load | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.2.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.5. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.6. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R6.7. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of other firm services determined by the Transmission Service Provider. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating the impact of ETC for non-firm commitments (ETCNFi) for all time periods for a Flowgate the Transmission Service Provider shall sum: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.4. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.5. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.6. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R7.7. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | The impact of other non-firm services determined by the Transmission Service Provider. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R8. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R9. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When calculating non-firm AFC for a Flowgate for a specified period, the Transmission Service Provider shall use the following algorithm (subject to allocation processes described in the ATCID): [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R10. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | Each Transmission Service Provider shall recalculate AFC, utilizing the updated models described in R3.2, R3.3, and R5, at a minimum on the following frequency, unless none of the calculated values identified in the AFC equation have changed: [Time Horizon: Operations Planning] | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R10.1. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R10.2. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | For daily AFC, once per day. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R10.3. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | For monthly AFC, once per week. | Current | Currently enforceable standard. |  | Retire MODs -001, -028, -029, -030, as they are business practices. Need to review TTC related components in 028,029, 030 and consolidate those aspects related to reliability into FAC 12(no longer in force) and FAC 13. Determination of TTCs and providing that operationally is covered under FAC 12-1, 13-1 and 13-2. The FAC 12 and 13 stds that provide for the determination of TTCs, along with the TOP and IRO stds which direct operators to operate within limits, provide for reliable operations. |  |  |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
MOD-030-2 | MOD-030-2 | R11. | Flowgate Methodology | To increase consistency and reliability in the development and documentation of transfer capability calculations for short-term use performed by entities using the Flowgate Methodology to support analysis and system operations. | When converting Flowgate AFCs to ATCs for ATC Paths, the Transmission Service Provider shall convert those values based on the following algorithm: [Time Horizon: Operations Planning] See Standard for Formula | Current | Currently enforceable standard. | Yes - Project 2012-05 MOD A | P81. Calculation of ATC is a market (tariff) issue. Determination of TTCs for operational reliability is covered under FAC 12-1 (no longer enforced), 13-1 and 13-2. Other TOP and IRO Standards require operation within limits. NAESB or another organization will need to develop the business practices. |  | Yes |  | No - calculation of ATC for OASIS posting is a business practice | Yes - commercial or business practice | [7 empty] | Yes | [10 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Pending | [18 empty] | TSP
NUC-001-2 | NUC-001-2 | R1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Lower |  |  |  | GOP
NUC-001-2 | NUC-001-2 | R2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3, 4 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R4. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R4.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Incorporate the NPIRs into their operating analyses of the electric system. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R4.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Operate the electric system to meet the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R4.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1, 4 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R5. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  |  |  | GOP
NUC-001-2 | NUC-001-2 | R6. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #1, 3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R7. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  |  |  | GOP
NUC-001-2 | NUC-001-2 | R8. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, protection systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 3 | 12 | High |  | High | Medium | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Administrative elements: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | No - 9.1 is admin in nature-- necessary in an interface agreement but is not tied to reliability | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | 0 | 0 | High |  | N/A | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.1.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Definitions of key terms used in the agreement. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. |  |  | Yes |  |  | No - 9.1 is admin in nature-- necessary in an interface agreement but is not tied to reliability | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | 0 | 0 | High |  | N/A | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.1.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. |  |  | Yes |  |  | No - 9.1 is admin in nature-- necessary in an interface agreement but is not tied to reliability | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | 0 | 0 | High |  | N/A | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.1.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | A requirement to review the agreement(s) at least every three years. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. |  |  | Yes |  |  | No - 9.1 is admin in nature-- necessary in an interface agreement but is not tied to reliability | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | 0 | 0 | High |  | N/A | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.1.4. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | A dispute resolution mechanism. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. |  |  | Yes |  |  | No - 9.1 is admin in nature-- necessary in an interface agreement but is not tied to reliability | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No |  | 0 | 0 | High |  | N/A | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Technical requirements and analysis: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.2.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.2.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.2.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Operations and maintenance coordination: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.4. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.5. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.6. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.3.7. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Communications and training: | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4.1. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4.2. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4.3. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4.4. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
NUC-001-2 | NUC-001-2 | R9.4.5. | Nuclear Plant Interface Coordination | This standard requires coordination between Nuclear Plant Generator Operators and Transmission Entities for the purpose of ensuring nuclear plant safe operation and shutdown. | Provisions for personnel training, as related to NPIRs. | Current | NUC-001-2 is the currently enforceable standard. The errata has been approved by the SC and the Board on 4/11/2012. It has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | DP | GO | GOP |  | LSE |  | PA | PC |  | RC |  |  |  |  | TO | TOP | TP | TSP
PER-001-0 | PER-001-0.2 | R1. | Operating Personnel Responsibility and Authority | Transmission Operator and Balancing Authority operating personnel must have the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | Each Transmission Operator and Balancing Authority shall provide operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the Bulk Electric System. | Current | Currently enforceable standard. |  |  |  | Yes | Team is recommending a new Authority Standard be written and that this requirment be rolled into it. | Yes - #6 | No - TOP-001-1a R1 and R2 | No |  |  | No - need to add RC | No - need to add RC | Yes | Yes Include in an authority standard | Yes | Yes | No - consider changing operating personnel to System Operator | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R1. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | Each Transmission Operator and Balancing Authority shall be staffed with adequately trained operating personnel. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R2. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | Each Transmission Operator and Balancing Authority shall have a training program for all operating personnel that are in: | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R2.1. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R2.2. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | Positions directly responsible for complying with NERC standards. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R3. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | For personnel identified in Requirement R2, the Transmission Operator and Balancing Authority shall provide a training program meeting the following criteria: | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R3.1. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | A set of training program objectives must be defined, based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements. These objectives shall reference the knowledge and competencies needed to apply those standards, procedures, and requirements to normal, emergency, and restoration conditions for the Transmission Operator and Balancing Authority operating positions. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | Medium | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R3.2. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | The training program must include a plan for the initial and continuing training of Transmission Operator and Balancing Authority operating personnel. That plan shall address knowledge and competencies required for reliable system operations. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | Medium | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R3.3. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | The training program must include training time for all Transmission Operator and Balancing Authority operating personnel to ensure their operating proficiency. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | Lower | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R3.4. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | Training staff must be identified, and the staff must be competent in Boardh knowledge of system operations and instructional capabilities. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | Lower | BA | [15 empty] | TOP
PER-002-0 | PER-002-0 | R4. | Operating Personnel Training | Each Transmission Operator and Balancing Authority must provide their personnel with a coordinated training program that will ensure reliable system operation. | For personnel identified in Requirement R2, each Transmission Operator and Balancing Authority shall provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. | Retired | Retires 3/31/2013 | [29 empty] | High |  |  | High | BA | [15 empty] | TOP
PER-003-1 | PER-003-1 | R1. | Operating Personnel Credentials | To ensure that System Operators performing the reliability-related tasks of the Reliability Coordinator, Balancing Authority and Transmission Operator are certified through the NERC System Operator Certification Program when filling a Real-time operating | Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate: 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Current | Currently enforceable standard. | [5 empty] | Yes - #6 | No | No |  |  | No - ANY functional entity's System Operators performing RC tasks must be RC certified. Delegated "RC Tasks" must be defined | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - reliabiity related tasks/delegation issue | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | High | [10 empty] | RC
PER-003-1 | PER-003-1 | R2. | Operating Personnel Credentials | To ensure that System Operators performing the reliability-related tasks of the Reliability Coordinator, Balancing Authority and Transmission Operator are certified through the NERC System Operator Certification Program when filling a Real-time operating | Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Current | Currently enforceable standard. | [5 empty] | Yes - #6 | No | No |  |  | No - ANY functional entity's System Operators performing TOP tasks must be certified. Delegated "TOP Tasks" must be defined | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - reliabiity related tasks/delegation issue | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | High | [16 empty] | TOP
PER-003-1 | PER-003-1 | R3. | Operating Personnel Credentials | To ensure that System Operators performing the reliability-related tasks of the Reliability Coordinator, Balancing Authority and Transmission Operator are certified through the NERC System Operator Certification Program when filling a Real-time operating | Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates: 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Current | Currently enforceable standard. | [5 empty] | Yes - #6 | No | No |  |  | No - ANY functional entity's System Operators performing BA tasks must be certified. Delegated "BA Tasks" must be defined | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - reliabiity related tasks/delegation issue | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | High | BA
PER-004-1 | PER-004-1 | R3. | Reliability Coordination — Staffing | Reliability Coordinators must have sufficient, competent staff to perform the Reliability Coordinator functions. | Reliability Coordinator operating personnel shall have a comprehensive understanding of the Reliability Coordinator Area and interactions with neighboring Reliability Coordinator Areas. | Retired | Will be replaced by PER-005-1 on 4/1/2013. | [29 empty] | High |  |  | High | [10 empty] | RC
PER-004-1 | PER-004-1 | R4. | Reliability Coordination — Staffing | Reliability Coordinators must have sufficient, competent staff to perform the Reliability Coordinator functions. | Reliability Coordinator operating personnel shall have an extensive understanding of the Balancing Authorities, Transmission Operators, and Generation Operators within the Reliability Coordinator Area, including the operating staff, operating practices and procedures, restoration priorities and objectives, outage plans, equipment capabilities, and operational restrictions. | Retired | Will be replaced by PER-005-1 on 4/1/2013. | [29 empty] | High |  |  | High | [10 empty] | RC
PER-004-2 | PER-004-2 | R1. | Reliability Coordination — Staffing | Reliability Coordinators must have sufficient, competent staff to perform the Reliability Coordinator functions. | Each Reliability Coordinator shall be staffed with adequately trained and NERC-certified Reliability Coordinator operators, 24 hours per day, seven days per week. | Current | Currently enforceable standard. | [5 empty] | Yes - #6 | No | No |  |  | No - BA and TOP should be included | No - BA and TOP should be included | No - "adequately trained" is not technically correct; standard is vague | No - consolidate with PER-003 (which includes all functions) | Yes | Yes | No - vague terms - "adequately trained" | No - does not speak to sufficient | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | High - Pending | [10 empty] | RC
PER-004-2 | PER-004-2 | R2. | Reliability Coordination — Staffing | Reliability Coordinators must have sufficient, competent staff to perform the Reliability Coordinator functions. | Reliability Coordinator operating personnel shall place particular attention on SOLs and IROLs and inter-tie facility limits. The Reliability Coordinator shall ensure protocols are in place to allow Reliability Coordinator operating personnel to have the best available information at all times. | Current | Currently enforceable standard. | [5 empty] | Yes - #1, 7, 5 | yes - duplicative with currently enforceable IRO and TOPs related to managing SOLs and IROL's. | No | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | High - Pending | [10 empty] | RC
PER-005-1 | PER-005-1 | R1. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall use a systematic approach to training to establish a training program for the BES company-specific reliability-related tasks performed by its System Operators and shall implement the program. [Time Horizon: Long-term Planning] | Current | Will become enforceable 4/1/2013 | Yes - Project 2010-01 PER (Training Directives) |  |  |  |  | Yes - #6 | No | No |  |  | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | High | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R1.1. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R1.1.1. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | Yes | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R1.2. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | No - Include System Operators | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R1.3. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | No - define who training needs to be given to (all System Operators) | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - "deliver" is understood in the training world but may not be in this one; use "conduct"? | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R1.4. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | No - a guideline explaining how to do an annual evaluation is needed. How do you know if changes need to be made | Yes | No - a guideline explaining how to do an annual evaluation is needed. How do you know if changes need to be made | Yes | Yes for content; No for format | Yes | No | Yes | Yes | No | Yes | Yes | No - use of the word annual | No | Yes | Yes | Yes | 1 | 8 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R2. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform each assigned task identified in R1.1 at least one time. [Time Horizon: Long-term Planning] | Current | Will become enforceable 4/1/2013 | Yes - Project 2010-01 PER (Training Directives) |  |  |  |  | Yes - #6 | No | No |  |  | No - verification needs to happen prior to System Operating performing function | Yes | No - one time within what timeframe (need to specify time period). Also - is one time the appropriate number? | Yes | Yes for content; No for format | Yes | No - one time within what timeframe (need to specify time period). Also - is one time the appropriate number? | Yes | Yes | No -how do you measure "verify" | Yes | Yes | No - "verify" | No | Yes | Yes | Yes | 1 | 8 | High | Yes | High | High - Pending | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R2.1. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. | Current | Will become enforceable 4/1/2013 | [5 empty] | Yes - #6 | No | No |  |  | yes | Yes | No - need guidance to determine how to verify SO capabilities (what makes a SO capable?) | Yes | Yes for content; No for format | Yes | No - need guidance to determine how to verify SO capabilities (what makes a SO capable?) | Yes | Yes | No -how do you measure "verify" | Yes | Yes | No - "verify" | No | Yes | Yes | Yes | 2 | 8 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R3. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | At least every 12 months each Reliability Coordinator, Balancing Authority and Transmission Operator shall provide each of its System Operators with at least 32 hours of emergency operations training applicable to its organization that reflects emergency operations topics, which includes system restoration using drills, exercises or other training required to maintain qualified personnel. [Time Horizon: Long-term Planning] | Current | Currently enforceable standard. Became enforceable 4/1/2011. | Yes - Project 2010-01 PER (Training Directives) |  |  |  |  | Yes - #6 | No | No |  |  | No - the term emergency operations is not defined so expectation is not clear - does it refer to the list of identified tasks under R1? | Yes | Yes | No - consolidate all training standards into one (i.e., EOP stds on blackstart) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No -points to EOP standards (for 32 hours) | No -"every 12 months" and doesn't explicitly point to the EOP standard | Yes | Yes | Yes | Yes | 2 | 9 | High | Yes | High | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
PER-005-1 | PER-005-1 | R3.1. | System Personnel Training | To ensure that System Operators performing real-time, reliability-related tasks on the North American Bulk Electric System (BES) are competent to perform those reliability-related tasks. The competency of System Operators is critical to the reliability of | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. | Current | Will become enforceable 4/2014. | [5 empty] | Yes - #6 | No | No |  |  | No - need to specify how many hours of training need to be on a simulator | Yes | Yes | No - consolidate all training standards into one (i.e., EOP stds on blackstart) | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | No Individual VRF Assigned | BA | [9 empty] | RC | [5 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. | Current - will be replaced by Board adopted std | PRC-001-1 is the currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #6 | No - but at present it is duplicative of TOP-006-2 R3 and PER-005 R1 (although not as clearly). However, TOP-006-2 and -3 may be retired. If it is not retired, then consider retiring | No |  |  | No - oversight | No - RC for operating oversight | Yes - but ambiguous terms R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - consolidate into PER-005 (R3.1) standards | No - it fits as a 'Competency/Capability' RBS but the word 'familiar' is not clear-- need to sync up with PER 005 view of competency; also the term 'area' is not clear | Yes | No | No - needs to be in the PER std | Yes - but still have issue with the undefined word 'familiar' | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 5 | High |  | High | High | BA |  |  | GOP | [12 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #10 | No | No |  |  | No - oversight. This also needs to be clear that this requirement is for real time Note: if TOP-002-3 is approved, it may cover it (investigate) | No - RC for operating oversight | Yes - but ambiguous terms R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | Yes - it fits as a Performance and Risk based (preventative) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | High |  |  |  | GOP | [12 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R2.1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #10 | No | No |  |  | No - oversight | No - RC for operating oversight | Yes - but ambiguous terms R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - format bad | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | High |  |  |  | GOP
PRC-001-1 | PRC-001-1.1 | R2.2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #10 | No | No |  |  | No - oversight | No - RC for operating oversight | Yes - but ambiguous terms R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are 2 thoughts here - operation and coordination ; | No - format bad | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High |  | High | High | [16 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R3. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - oversight | No - RC for operating oversight | Yes - but ambiguous terms; protective systems as a glossary term should be capitalized like it is in R1 R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | No Individual VRF Assigned |  |  |  | GOP | [12 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R3.1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but ambiguous terms; protective systems as a glossary term should be capitalized like it is in R1 R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - format bad | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - protection system not capitalized | Yes | Yes | 1 | 11 | High |  | High | High |  |  |  | GOP
PRC-001-1 | PRC-001-1.1 | R3.2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | yes - but ambiguous terms; protective systems as a glossary term should be capitalized like it is in R1 R's 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - format bad | Yes | No | Yes | Yes | Yes | Yes | Yes | No - term 'neighboring' not clear | No - term 'neighboring' not clear | No - protection system not capitalized | Yes | Yes | 1 | 5 | High |  | High | High | [16 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R4. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect May be covered but may not be specific enough in regards to Protection Systems. Is Who is collecting the data specific enough? IRO-010-1a address obtaining Protection System data in regards to the RC role; TOP-003-2 addresses TOP's role and responsibility of other functions to provide; TPL-001-4 addresses the analysis of short circuit | No - TO and GO need to be included for design aspect Note: TO and GO are included in PRC-027 | Yes - but ambiguous terms; what is 'neighboring'-- using the term 'adjacent' would be clearer Note: Addressed in PRC-027 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - not clear on when this requirment applies. We think R4 is about the initial coordination when a facility goes in as well as when the scheme is changed See note from L&H in GAP column | Yes | No | Yes | Yes | Yes | Yes | Yes | No - term 'neighboring' not clear | No - term 'neighboring' not clear | Yes | Yes | Yes | 1 | 6 | High |  | High | High | [16 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R5. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others: | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but ambiguous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | High |  |  |  | GOP | [12 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R5.1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but amibigous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No-format bad | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High |  | High | High |  |  |  | GOP
PRC-001-1 | PRC-001-1.1 | R5.2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but amibigous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No-format bad | Yes | No - 'neighboring' is not clear | Yes | Yes | Yes | Yes | Yes | No - term 'neighboring' not clear | No - term 'neighboring' not clear | Yes | Yes | Yes | 1 | 5 | High |  | High | High | [16 empty] | TOP
PRC-001-1 | PRC-001-1.1 | R6. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status. | Current - will be replaced by Board adopted std | Currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | [5 empty] | Yes - #7 | No | No |  |  | No - oversight | No - RC for operating oversight | Yes - but amibigous terms; should say 'Special Protection Scheme/Remedial Action Scheme' . 1,2 and 6 are about operations; 3,4 and 5 are around design | No - consider combining with either IRO-010 R1 and R3; and TOP-003-2 R1 following FERC approval of TOP stds | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | High |  | High | High | BA | [15 empty] | TOP
PRC-001-1 | PRC-001-2 | R1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area. | Board Adopted | PRC-001-1 is the currently enforceable standard. PRC-001-1.1 errata to capitalize Protection System was approved by the SC (thus Board adopted) on 4/11/2012. | Yes - Project 2007-06 System Protection Coordination (PRC-001 and PRC-027) |  |  |  |  | Yes - #6 | No - but at present it is duplicative of TOP-006-2 R3 and PER-005 R1 (although not as clearly). However, TOP-006-2 and -3 may be retired. If it is not retired, then consider retiring | No |  |  | No - oversight | No - RC for operating oversight | Yes - but amibigous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - consolidate into PER-005 (R3.1) standards | No - it fits as a 'Competency/Capability' RBS but the word 'familiar' is not clear-- need to sync up with PER 005 view of competency; also the term 'area' is not clear | Yes | No | No - needs to be in the PER std | Yes - but still have issue with the undefined word 'familiar' | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 5 | High | Yes | High | High | BA |  |  | GOP | [12 empty] | TOP
PRC-001-2 | PRC-001-2 | R2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. |  | Board Adopted | Board adopted 5/9/2012. Filed with FERC on 4/16/2-13. | Yes - Project 2007-06 System Protection Coordination (PRC-001 and PRC-027) |  |  |  |  | Yes - #1 | No | No |  |  | No - oversight | No - RC for operating oversight | Yes - but amibigous terms; protective systems as a glossary term should be capitalized like it is in R1 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High | Yes | High | No Individual VRF Assigned
PRC-001-2 | PRC-001-2 | R2.1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. |  | Board Adopted | Board adopted 5/9/2012. Not filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but amibigous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - format bad | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - protection system not capitalized | Yes | Yes | 1 | 11 | High |  | High | High
PRC-001-2 | PRC-001-2 | R2.2. | System Protection Coordination | To ensure system protection is coordinated among operating entities. |  | Board Adopted | Board adopted 5/9/2012. Not filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - functions for design aspect | No - TO and GO need to be included for design aspect | Yes - but amibigous terms 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - format bad | Yes | No | Yes | Yes | Yes | Yes | Yes | No - term 'neighboring' not clear | No - term 'neighboring' not clear | No - protection system not capitalized | Yes | Yes | 1 | 5 | High |  | High | High
PRC-001-2 | PRC-001-2 | R3. | System Protection Coordination | To ensure system protection is coordinated among operating entities. |  | Board Adopted | Board adopted 5/9/2012. Not filed with FERC. | Yes - Project 2007-06 System Protection Coordination (PRC-001 and PRC-027) |  |  |  |  | Yes | No | No |  |  | No - functions for design aspect May be covered but may not be specific enough in regards to Protection Systems. Is Who is collecting the data specific enough? IRO-010-1a address obtaining Protection System data in regards to the RC role; TOP-003-2 addresses TOP's role and responsibility of other functions to provide; TPL-001-4 addresses the analysis of short circuit | No - TO and GO need to be included for design aspect | Yes - but amibigous terms; what is 'neighboring'-- using the term 'adjacent' would be clearer Note: Addressed in PRC-027 1,2 and 6 are about operations; 3,4 and 5 are around design | No - There are two thoughts here - operation and coordination ; | No - not clear on when this requirment applies. We think R4 is about the initial coordination when a facility goes in as well as when the scheme is changed See note from L&H in GAP column | Yes | No | Yes | Yes | No | Yes | Yes | No - term 'neighboring' not clear | No - term 'neighboring' not clear | Yes | Yes | Yes | 1 | 6 | High | Yes | High | High
PRC-001-2 | PRC-001-3 | R1. | System Protection Coordination | To ensure system protection is coordinated among operating entities. |  | In current project under development |  |  | Did not correct the issues spoted in -1. |  |  |  | Yes - #1 | No | No |  |  |  |  | Yes |  | Yes | Yes | No | Yes | Yes | No | No | Yes | No? | No | Yes | Yes | Yes | 3 | 6 | High |  | High | High
PRC-002-1 | PRC-002-1 | all | Define Regional Disturbance Monitoring and Reporting Requirements | Ensure that Regional Reliability Organizations establish requirements for installation of Disturbance Monitoring Equipment (DME) and reporting of Disturbance data to facilitate analyses of events and verify system models. |  | Not approved in Order 693 | Not approved by FERC in Order 693 | [29 empty] | Not ranked
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R1. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner and Generator Owner shall provide Sequence of Event (SOE) recording capability by installing Sequence of Event recorders or as part of another device, such as a Supervisory Control And Data Acquisition (SCADA) Remote Terminal Unit (RTU), a generator plant Digital (or Distributed) Control System (DCS) or part of Fault recording equipment. This capability shall: [See standard for requirements of SOE recording capability] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO | [12 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R2. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner shall provide Fault recording capability for the following Elements at facilities where Fault recording equipment is required to be installed as per R3: [See standard for list of elements] | Regional | [30 empty] | Not ranked |  |  | Medium | [15 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R3. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner shall have Fault recording capability that determines the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements. | Regional | [30 empty] | Not ranked |  |  | Medium | [15 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R4. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Generator Owner shall provide Fault recording capability for Generating Plants at and above 200 MVA Capacity and connected through a generator step up (GSU) transformer to a Bulk Electric System Element unless Fault recording capability is already provided by the Transmission Owner. | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R5. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner and Generator Owner shall record for Faults, sufficient electrical quantities for each monitored Element to determine the following: [See standard for list] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO | [12 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R6. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner and Generator Owner shall provide Fault recording with the following capabilities: [See standard for list of capabilities] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO | [12 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R7. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall establish its area’s requirements for Dynamic Disturbance Recording (DDR) capability that: [See standard for futher requirements] | Regional | [30 empty] | Not ranked |  |  | Medium | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R8. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall specify that DDRs installed, after the approval of this standard, function as continuous recorders. | Regional | [30 empty] | Not ranked |  |  | Medium | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R9. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall specify that DDRs are installed with the following capabilities: [See standard for list of capabilities] | Regional | [30 empty] | Not ranked |  |  | Medium | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R10. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall establish requirements such that the following quantities are monitored or derived where DDRs are installed: [See standard for quantities] | Regional | [30 empty] | Not ranked |  |  | Medium | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R11. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall document additional settings and deviations from the required trigger settings described in R9 and the required list of monitored quantities as described in R10, and report this to the Regional Entity (RE) upon request. | Regional | [30 empty] | Not ranked |  |  | Lower | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R12. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator shall specify its DDR requirements including the DDR setting triggers established in R9 to the Transmission Owners and Generator Owners. | Regional | [30 empty] | Not ranked |  |  | Medium | [10 empty] | RC
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R13. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner and Generator Owner that receives a request from the Reliability Coordinator to install a DDR shall acquire and install the DDR in accordance with R12. Reliability Coordinators, Transmission Owners, and Generator Owners shall mutually agree on an implementation schedule. | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO | [7 empty] | RC |  |  |  |  | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R14. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Transmission Owner and Generator Owner shall establish a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that includes: [See standard for list of inclusions] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  | GO | [12 empty] | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R15. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall share data within 30 days upon request. Each Reliability Coordinator, Transmission Owner, and Generator Owner shall provide recorded disturbance data from DMEs within 30 days of receipt of the request in each of the following cases: [See standard for the two cases] | Regional | [30 empty] | Not ranked |  |  | Lower |  |  | GO | [7 empty] | RC |  |  |  |  | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R16. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall submit the data files conforming to the following format requirements: [See standard for format requirements] | Regional | [30 empty] | Not ranked |  |  | Lower |  |  | GO | [7 empty] | RC |  |  |  |  | TO
PRC-002-NPCC-01 | PRC-002-NPCC-01 | R17. | Disturbance Monitoring | Ensure that adequate disturbance data is available to facilitate Bulk Electric System event analyses. All references to equipment and facilities herein unless otherwise noted wil be to Bulk Electric System (BES) elements. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall maintain, record and provide to the Regional Entity (RE), upon request, the following data on the DMEs installed to meet this standard: [See standard for types of data] | Regional | [30 empty] | Not ranked |  |  | Lower |  |  | GO | [7 empty] | RC |  |  |  |  | TO
PRC-003-1 | PRC-003-1 | all | Regional Procedure for Analysis of Misoperations of Transmission and Generation Protection Systems | To ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. |  | Not approved in Order 693 | [30 empty] | High
PRC-004-2 | PRC-004-2.1a | R1. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | Board Adopted | Errata change Edited R2 to add “…and generator interconnection Facility…” It was Board adopted/SC approved on 2/9/2012 and filed with FERC on 7/30/2012 | Yes - Project 2010-05.1 Protection System Phase 1 (Misoperations) |  |  |  |  | Yes - #1, 7 | No | No |  |  | No - needs timeframe ; verify that RE's have procedures | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High |  | DP | [13 empty] | TO
PRC-004-2 | PRC-004-2.1a | R2. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | Board Adopted | Errata change Edited R2 to add “…and generator interconnection Facility…” It was Board adopted/SC approved on 2/9/2012 and filed with FERC on 7/30/2012 | Yes - Project 2010-05.1 Protection System Phase 1 (Misoperations) |  |  |  |  | Yes - #1, 7 | No | No |  |  | No - needs timeframe ; verify that RE's have procedures | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High |  |  |  | GOP
PRC-004-2 | PRC-004-2.1a | R3. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | Board Adopted | Errata change Edited R2 to add “…and generator interconnection Facility…” It was Board adopted/SC approved on 2/9/2012 and filed with FERC on 7/30/2012 | Yes - Project 2010-05.1 Protection System Phase 1 (Misoperations) |  |  | Yes for PRC-004-1a and PRC-004-2a |  | Yes - #1, 7 | Yes - administrative | [19 empty] | No | 0 | 0 | High |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-004-2 | PRC-004-2a | R1. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #9, 10 | No | No |  |  | No - needs timeframe ; verify that RE's have procedures is dependent upon having all relay operations reviewed in order to be able to perform these | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - there is a value to industry in getting analysis done to share lessons learned with industry | Yes | Yes | No - points to RE procedure | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | High | High |  | DP | [13 empty] | TO
PRC-004-2 | PRC-004-2a | R2. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #9, 10 | No | No |  |  | No - needs timeframe ; verify that RE's have procedures | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - there is a value to industyry in getting analysis done to share lessons learned with industry | Yes | Yes | No - points to RE procedure | Yes | Yes | Yes | Yes | Yes | 2 | 10 | High |  | High | High |  |  | GO
PRC-004-2 | PRC-004-2a | R3. | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | Ensure all transmission and generation Protection System Misoperations affecting the reliability of the Bulk Electric System (BES) are analyzed and mitigated. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | Current - will be replaced by Board adopted std | Currently enforceable standard. | [5 empty] | Yes - #1, 7 | Yes - administrative | [18 empty] | No |  | 0 | 0 | High |  | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | System Operators and System Protection personnel of the Transmission Owners and Generator Owners shall analyze all Protection System and RAS operations. [Time Horizon: Operations Assessment] | Regional | [30 empty] | High |  |  | Lower |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R1.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R1.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Transmission Owners and Generator Owners shall perform the following actions for each Misoperation of the Protection System or RAS. It is not intended that Requirements R2.1 through R2.4 apply to Protection System and/or RAS actions that appear to be entirely reasonable and correct at the time of occurrence and associated system performance is fully compliant with NERC Reliability Standards. If the Transmission Owner or Generator Owner later finds the Protection System or RAS operation to be incorrect through System Protection personnel analysis, the requirements of R2.1 through R2.4 become applicable at the time the Transmission Owner or Generator Owner identifies the Misoperation: | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO | TOP
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. [Time Horizon: Same-day Operations] | Regional | [30 empty] | High |  |  | High |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. [Time Horizon: Same-day Operations] | Regional | [30 empty] | High |  |  | High |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.2.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.2.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.3. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. [Time Horizon: Same-day Operations] | Regional | [30 empty] | High |  |  | High |  |  | GO | [12 empty] | TO | TOP
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.3.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned | [15 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.3.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | When FERAS is not available, then | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [13 empty] | TOP
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.3.2.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | The Generator Owners shall adjust generation to a reliable operating level, or | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.3.2.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Transmission Operators shall adjust the SOL and operate the facilities within established limits. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned | [16 empty] | TOP
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.4. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS that failed, provided one of the following is performed. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.4.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Transmission Owners or Generator Owners shall repair or replace any Protection System or RAS that misoperated with FEPS and FERAS within 20 business days of the date of the Misoperation identification, or | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R2.4.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. [Time Horizon: Operations Assessment] | Regional | [30 empty] | High |  |  | Lower |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R3. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Transmission Owners and Generation Owners shall submit Misoperation incident reports to WECC within 10 business days for the following. [Time Horizon: Operations Assessment] | Regional |  |  |  |  | Yes and PRC-003-WECC-a | [25 empty] | High |  |  | Lower |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R3.1. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Identification of a Misoperation of a Protection System and/or RAS, | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-004-WECC-1 | PRC-004-WECC-1 | R3.2. | Protection System and Remedial Action Scheme Misoperation | Regional Reliability Standard to ensure all transmission and generation Protection System and Remedial Action Scheme (RAS) Misoperations on Transmission Paths and RAS defined in section 4 are analyzed and/or mitigated. | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. | Regional | [30 empty] | High |  |  | No Individual VRF Assigned |  |  | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 | [5 empty] | Yes - #5, 9 | No | No |  |  | No - need requirement to implement, does not have program specifics for equipment | Yes | Yes | Yes | No for format | Yes | No | Yes | No - because the requirement lacks specifics on what is needed in the protection program | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 9 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R1.1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 | [5 empty] | Yes - #5, 9 | No | No |  |  | No - need requirement to implement, does not have program specifics for equipment | Yes | Yes | Yes | No for format | Yes | No | Yes | No - because the requirement lacks specifics on what is needed in the protection program | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 9 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R1.2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 | [5 empty] | Yes - #5, 9 | No | No |  |  | No - need requirement to implement, does not have program specifics for equipment | Yes | Yes | Yes | No for format | Yes | No | Yes | No - because the requirement lacks specifics on what is needed in the protection program | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 9 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 |  |  |  | Yes |  | No - need to move implementation to R1 | Yes - adminnistrative - need to move implementation to R1 | [18 empty] | No |  | 0 | 0 | High |  | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R2.1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 | [5 empty] | No | Yes - administrative | [18 empty] | No |  | 0 | 0 | High |  | N/A | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1.1b | R2.2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. |  | Current - will be replaced by Board adopted std | Errata to PRC-005-1b; added "and generator iterconnection Facility…." to R2 | [5 empty] | No | Yes - administrative | [18 empty] | No |  | 0 | 0 | High |  | N/A | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | Retired | [30 empty] | High |  |  | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R1.1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Maintenance and testing intervals and their basis. | Retired | [30 empty] | High |  |  | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R1.2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Summary of maintenance and testing procedures. | Retired | [30 empty] | High |  |  | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: | Retired | [30 empty] | High |  |  | Lower |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R2.1. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Evidence Protection System devices were maintained and tested within the defined intervals. | Retired | [30 empty] | High |  |  | High |  | DP | GO | [12 empty] | TO
PRC-005-1 | PRC-005-1b | R2.2. | Transmission and Generation Protection System Maintenance and Testing | To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested. | Date each Protection System device was last tested/maintained. | Retired | [30 empty] | High |  |  | High |  | DP | GO | [12 empty] | TO
PRC-005-2 | PRC-005-2 | R1. | Protection System Maintenance | To document and implement programs for the maintenance of all Protection Systems affecting the reliability of the Bulk Electric System (BES) so that these Protection Systems are kept in working order. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. | Board Adopted | Board adopted 11/7/2012; it has not been filed with FERC. | Yes - Project 2007-17.2 Protection System Maintenance and Testing - Phase 2 (Reclosing Relays) | team discussed how prescriptive the std is but felt that this was one std where the level of prescription is necessary or desired |  |  |  | Yes - #5, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-005-2 | PRC-005-2 | R2. | Protection System Maintenance | To document and implement programs for the maintenance of all Protection Systems affecting the reliability of the Bulk Electric System (BES) so that these Protection Systems are kept in working order. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. | Board Adopted | Board adopted 11/7/2012; it has not been filed with FERC. | Yes - Project 2007-17.2 Protection System Maintenance and Testing - Phase 2 (Reclosing Relays) |  |  |  |  | Yes - #5, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-005-2 | PRC-005-2 | R3. | Protection System Maintenance | To document and implement programs for the maintenance of all Protection Systems affecting the reliability of the Bulk Electric System (BES) so that these Protection Systems are kept in working order. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. | Board Adopted | Board adopted 11/7/2012; it has not been filed with FERC. | Yes - Project 2007-17.2 Protection System Maintenance and Testing - Phase 2 (Reclosing Relays) |  |  |  |  | Yes - #5, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | high | High |  | DP | GO | [12 empty] | TO
PRC-005-2 | PRC-005-2 | R4. | Protection System Maintenance | To document and implement programs for the maintenance of all Protection Systems affecting the reliability of the Bulk Electric System (BES) so that these Protection Systems are kept in working order. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). | Board Adopted | Board adopted 11/7/2012; it has not been filed with FERC. | Yes - Project 2007-17.2 Protection System Maintenance and Testing - Phase 2 (Reclosing Relays) |  |  |  |  | Yes - #5, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-005-2 | PRC-005-2 | R5. | Protection System Maintenance | To document and implement programs for the maintenance of all Protection Systems affecting the reliability of the Bulk Electric System (BES) so that these Protection Systems are kept in working order. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. | Board Adopted | Board adopted 11/7/2012; it has not been filed with FERC. | Yes - Project 2007-17.2 Protection System Maintenance and Testing - Phase 2 (Reclosing Relays) |  |  |  |  | Yes - #5, 9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-006-0 | PRC-006-0 | R1. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #1, 2 | No | No |  |  |  |  | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 6 | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.1. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #1, 2 | No | No |  |  | No - oversight |  | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 6 | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.1. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.2. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.3. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.4. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.5. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.6. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.7. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.2.8. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #2 | No | [5 empty] | Yes |  | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes |  | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.3. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #10 | Yes | No |  |  |  |  | Yes |  | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 6 | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.4. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #7 | No | No |  |  | Yes - generator tripping due to uf |  | No |  | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 7 | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.4.1. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #7 | No | Yes | [21 empty] | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R1.4.2. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #7 | No | Yes | [21 empty] | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R2. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #1 | No | No |  |  |  |  | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 8 | Low |  |  | N/A
PRC-006-0 | PRC-006-0 | R3. | Development and Documentation of Regional Reliability Organizations’ Underfrequency Load Shedding Programs | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [5 empty] | Yes - #7 | No | No |  |  |  |  | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | 8 | Low |  |  | N/A
PRC-006-1 | PRC-006-1 | R1. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall develop and document criteria, including consideration of historical events and system studies, to select portions of the Bulk Electric System (BES), including interconnected portions of the BES in adjacent Planning Coordinator areas and Regional Entity areas that may form islands. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #1, 4 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | High | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R2. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall identify one or more islands to serve as a basis for designing its UFLS program including: 2.1. Those islands selected by applying the criteria in Requirement R1, and 2.2. Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and 2.3. A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | High | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R3. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall develop a UFLS program, including notification of and a schedule for implementation by UFLS entities within its area, that meets the following performance characteristics in simulations of underfrequency conditions resulting from an imbalance scenario, where an imbalance = [(load — actual generation output) / (load)], of up to 25 percent within the identified island(s). 3.1. Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.2. Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and 3.3. Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: 3.3.1. Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES 3.3.2. Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES 3.3.3. Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | High | Medium | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R4. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall conduct and document a UFLS design assessment at least once every five years that determines through dynamic simulation whether the UFLS program design meets the performance characteristics in Requirement R3 for each island identified in Requirement R2. The simulation shall model each of the following: 4.1. Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. 4.2. Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. 4.3. Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. 4.4. Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. 4.5. Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. 4.6. Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. 4.7. Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | High | High | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R5. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator, whose area or portions of whose area is part of an island identified by it or another Planning Coordinator which includes multiple Planning Coordinator areas or portions of those areas, shall coordinate its UFLS program design with all other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island through one of the following: • Develop a common UFLS program design and schedule for implementation per Requirement R3 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct a joint UFLS design assessment per Requirement R4 among the Planning Coordinators whose areas or portions of whose areas are part of the same identified island, or • Conduct an independent UFLS design assessment per Requirement R4 for the identified island, and in the event the UFLS design assessment fails to meet Requirement R3, identify modifications to the UFLS program(s) to meet Requirement R3 and report these modifications as recommendations to the other Planning Coordinators whose areas or portions of whose areas are also part of the same identified island and the ERO. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #4, 1 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | High | High | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R6. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall maintain a UFLS database containing data necessary to model its UFLS program for use in event analyses and assessments of the UFLS program at least once each calendar year, with no more than 15 months between maintenance activities. | Current | Will become enforceable on 10/1/2013. | [5 empty] | No - it is the actual study that is needed for reliability | [19 empty] | No |  | 0 | 0 | Low | Yes | N/A | Lower | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R7. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall provide its UFLS database containing data necessary to model its UFLS program to other Planning Coordinators within its Interconnection within 30 calendar days of a request. | Current | Will become enforceable on 10/1/2013. |  |  |  | Yes | There should be a clear expectation for PCs to share data necessary to determine their UFLS program parameters | Yes - #3 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 9 | Low | Yes | Low | Lower | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R8. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | Current | Will become enforceable on 10/1/2013. |  |  |  | Yes | There should be a clear expectation for PCs to share data necessary to determine their UFLS program parameters | Yes - #3 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | Lower |  | DP | [13 empty] | TO
PRC-006-1 | PRC-006-1 | R9. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #4 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | High | High |  | DP | [13 empty] | TO
PRC-006-1 | PRC-006-1 | R10. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #1, 4 | No | Yes - controlling voltage at all times regardless of circumstances (normal or during UFLS, etc) | Accountibility is met under the VAR and TPL stds. | [16 empty] | Yes | No | 0 | 0 | Low | Yes | N/A | High | [15 empty] | TO
PRC-006-1 | PRC-006-1 | R11. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator, in whose area a BES islanding event results in system frequency excursions below the initializing set points of the UFLS program, shall conduct and document an assessment of the event within one year of event actuation to evaluate: 11.1. The performance of the UFLS equipment, 11.2. The effectiveness of the UFLS program. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #7 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. (2) R11-13 are about a UFLS event analysis. Do we need a broader std on event analysis that speaks to not only UFLS events but also other types of BES events. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | Medium | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R12. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator, in whose islanding event assessment (per R11) UFLS program deficiencies are identified, shall conduct and document a UFLS design assessment to consider the identified deficiencies within two years of event actuation. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #7 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. (2) R11-13 are about a UFLS event analysis. Do we need a broader std on event analysis that speaks to not only UFLS events but also other types of BES events. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | Medium | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R13. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator, in whose area a BES islanding event occurred that also included the area(s) or portions of area(s) of other Planning Coordinator(s) in the same islanding event and that resulted in system frequency excursions below the initializing set points of the UFLS program, shall coordinate its event assessment (in accordance with Requirement R11) with all other Planning Coordinators whose areas or portions of whose areas were also included in the same islanding event through one of the following: • Conduct a joint event assessment per Requirement R11 among the Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 that reaches conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, or • Conduct an independent event assessment per Requirement R11 and where the assessment fails to reach conclusions and recommendations consistent with those of the event assessments of the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event, identify differences in the assessments that likely resulted in the differences in the conclusions and recommendations and report these differences to the other Planning Coordinators whose areas or portions of whose areas were included in the same islanding event and the ERO. | Current | Will become enforceable on 10/1/2013. | [5 empty] | Yes - #7 | No | No |  |  | No - (1) Generator Owners need to be required to provide appropriate machine trip points and other data for analysis and coordination done under this std. (2) R11-13 are about a UFLS event analysis. Do we need a broader std on event analysis that speaks to not only UFLS events but also other types of BES events. | No - Generator Owners need to be added -- see GAP column | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - because there are some regional UFLS stds that must be read in some regions | Yes | Yes | Yes | Yes | Yes | 1 | 11 | Low | Yes | Medium | Medium | [7 empty] | PA | PC
PRC-006-1 | PRC-006-1 | R14. | Automatic Underfrequency Load Shedding | To establish design and documentation requirements for automatic underfrequency load shedding (UFLS) programs to arrest declining frequency, assist recovery of frequency following underfrequency events and provide last resort system preservation measures. | Each Planning Coordinator shall respond to written comments submitted by UFLS entities and Transmission Owners within its Planning Coordinator area following a comment period and before finalizing its UFLS program, indicating in the written response to comments whether changes will be made or reasons why changes will not be made to the following: 14.1. UFLS program, including a schedule for implementation 14.2. UFLS design assessment 14.3. Format and schedule of UFLS data submittal | Current | Will become enforceable on 10/1/2013. | [5 empty] | No - administrative | [19 empty] | No |  | 0 | 0 | Low | Yes | N/A | Lower | [7 empty] | PA | PC
PRC-006-SERC-01 | PRC-006-SERC-01 | R1. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each Planning Coordinator shall include its SERC subregion as an identified island in the criteria (required by the NERC PRC standard on UFLS) for selecting portions of the BPS that may form islands. [See standard pdf for additional information] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium | [7 empty] | PA | PC
PRC-006-SERC-01 | PRC-006-SERC-01 | R2. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each Planning Coordinator shall select or develop an automatic UFLS scheme (percent of load to be shed, frequency set points, and time delays) for implementation by UFLS entities within its area that meets the following minimum requirements: [See standard pdf for minimum requirements] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium | [7 empty] | PA | PC
PRC-006-SERC-01 | PRC-006-SERC-01 | R3. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each Planning Coordinator, when performing design assessments specified in the NERC PRC standard on UFLS, shall conduct simulations of its UFLS scheme for an imbalance between load and generation of 13%, 22%, and 25% for all identified island(s) where such imbalance equals [(load minus actual generation output) / load]. | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | High | [7 empty] | PA | PC
PRC-006-SERC-01 | PRC-006-SERC-01 | R4. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each UFLS entity that has a total load of 100 MW or greater in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. [See standard pdf for requirements] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium |  | DP | [13 empty] | TO
PRC-006-SERC-01 | PRC-006-SERC-01 | R5. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each UFLS entity that has a total load less than 100 MW in a Planning Coordinator area in the SERC Region shall implement the UFLS scheme developed by their Planning Coordinator, but shall not be required to have more than one UFLS step. UFLS entities may implement the UFLS scheme developed by the Planning Coordinator by coordinating with other UFLS entities. The UFLS scheme shall meet the following requirements on May 1 of each calendar year. [See standard pdf for requirements] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium |  | DP | [13 empty] | TO
PRC-006-SERC-01 | PRC-006-SERC-01 | R6. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each UFLS entity shall implement changes to the UFLS scheme which involve frequency settings, relay time delays, or changes to the percentage of load in the scheme within 18 months of notification by the Planning Coordinator. | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Medium |  | DP | [13 empty] | TO
PRC-006-SERC-01 | PRC-006-SERC-01 | R7. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each Planning Coordinator shall provide the following information to SERC according to the schedule specified by SERC. [See standard pdf for information to be provided] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Lower | [7 empty] | PA | PC
PRC-006-SERC-01 | PRC-006-SERC-01 | R8. | Automatic Underfrequency Load Shedding Requirements | To establish consistent and coordinated requirements for the design, implementation, and analysis of automatic underfrequency load shedding (UFLS) programs among all SERC applicable entities. | Each Generator Owner shall provide the following information within 30 days of a request by SERC to facilitate post-event analysis of frequency disturbances. [See standard pdf for information to be provided] | Regional | Will become enforceable on 4/1/2013. | [29 empty] | Low |  |  | Lower |  |  | GO
PRC-007-0 | PRC-007-0 | R1. | Assuring Consistency of Entity Underfrequency Load Shedding Programs with Regional Reliability Organization’s Underfrequency Load Shedding Program Requirements | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall ensure that its UFLS program is consistent with its Regional Reliability Organization’s UFLS program requirements. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. | [13 empty] | PRC 007 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP | [13 empty] | TO
PRC-007-0 | PRC-007-0 | R2. | Assuring Consistency of Entity Underfrequency Load Shedding Programs with Regional Reliability Organization’s Underfrequency Load Shedding Program Requirements | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner, Transmission Operator, Distribution Provider, and Load-Serving Entity that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide, and annually update, its underfrequency data as necessary for its Regional Reliability Organization to maintain and update a UFLSprogram database. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. |  |  |  | Yes | [9 empty] | PRC 007 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Lower |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-007-0 | PRC-007-0 | R3. | Assuring Consistency of Entity Underfrequency Load Shedding Programs with Regional Reliability Organization’s Underfrequency Load Shedding Program Requirements | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner and Distribution Provider that owns a UFLS program (as required by its Regional Reliability Organization) shall provide its documentation of that UFLS program to its Regional Reliability Organization on request (30 calendar days). | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. |  |  |  | Yes | [9 empty] | PRC 007 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Lower |  | DP | [13 empty] | TO
PRC-008-0 | PRC-008-0 | R1. | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #9 | No | No |  |  | No - R1 lacks specificity on what are the good elements of a program | No - the RRO should be the PC as identified in PRC 006-1 | Yes - but R1 lacks specificity on what are the good elements of a program | No - consolidate R1 and R2 in single requirement | Yes | Yes | No - need clarity on "Distribution Provider with a UFLS program" | Yes | No - since the requirement lacks program specificity | Yes | No - since the requirement lacks program specificity | No -has reference to RRO | No -has reference to RRO | Yes | No -has reference to RRO | Yes | Yes | 1 | 5 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-008-0 | PRC-008-0 | R2. | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | Provide last resort system preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #9 however, requirement to implement the UFLS maintenance program is reliability; requirement to provide program results to RRO and NERC is not reliability, but administrative | No | No |  |  | Yes | No - the RRO should be the PC as identified in PRC 006-1 | Yes | No - consolidate R1 and R2 in single requirement; get rid of requirement to provide program results to RRO and NERC as it is not reliability, but administrative | No | Yes | No - need clarity on "Distribuiton Provider with a UFLS program" | Yes | No - since the requirement lacks program specificity | Yes | No - since the requirement lacks program specificity | No -has reference to RRO | No -has reference to RRO | Yes | No -has reference to RRO | Yes/No | Yes | 2 | 4 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-009-0 | PRC-009-0 | R1. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall analyze and document its UFLS program performance in accordance with its Regional Reliability Organization’s UFLS program. The analysis shall address the performance of UFLS equipment and program effectiveness following system events resulting in system frequency excursions below the initializing set points of the UFLS program. The analysis shall include, but not be limited to: | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. |  |  |  | Yes | [9 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-009-0 | PRC-009-0 | R1.1. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | A description of the event including initiating conditions. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. | [13 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-009-0 | PRC-009-0 | R1.2. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | A review of the UFLS set points and tripping times. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. | [13 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-009-0 | PRC-009-0 | R1.3. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | A simulation of the event. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. | [13 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-009-0 | PRC-009-0 | R1.4. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | A summary of the findings. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. | [13 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-009-0 | PRC-009-0 | R2. | Analysis and Documentation of Underfrequency Load Shedding Performance Following an Underfrequency Event | Provide last resort System preservation measures by implementing an Under Frequency Load Shedding (UFLS) program. | The Transmission Owner, Transmission Operator, Load-Serving Entity, and Distribution Provider that owns or operates a UFLS program (as required by its Regional Reliability Organization) shall provide documentation of the analysis of the UFLS program to its Regional Reliability Organization and NERC on request 90 calendar days after the system event. | Retired | Currently enforceable standard- will be retired 10-1-13 when PRC 006-1 takes effect. |  |  |  | Yes |  | Yes - #4 | Yes | Yes | [5 empty] | PRC 009 goes away when PRC 006-1 takes effect on 10-1-13 | [15 empty] | Low |  |  | Lower |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R1. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | Current | Currently enforceable standard. | Yes - Project 2008-02 Undervoltage Load Shedding (PRC-010 and PRC-022) | (1) get the applicable function cleared up- PC or the TP is responsible for doing the assessment, LSE, TO,TOP and DP are responsible for providing needed data. Is LSE an applicable function for this std? |  |  |  | Yes - #4, 7 | No | No |  |  | Yes | No - add PC. See 'suggestions for improvement' column. | Yes, but review the five-year time frame - annually or every two years may be more appropriate | No - consolidate R1.1.1,1.1.2 and 1.1.3 | Yes | Yes | No - see notes on proper Functions for this std to appply to | Yes | Yes | Yes | Yes | Yes - refers to TPLs | No - what does 'five years' mean | No | No | Yes | Yes | 2 | 7 | Low | Yes | High | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R1.1. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | This assessment shall include, but is not limited to: | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up- PC is responsible for doing the assessment, LSE, TO,TOP and DP are responsible for providing needed data. Is LSE an applicable function for this std? |  |  |  | Yes - #4, 7 | No | No |  |  | No - R1.1.1 says "Region' only-- should be modified to reach outside your Region as needed | No - add PC. See 'suggestions for improvement' column. | Yes | No - consolidate R1.1.1,1.1.2 and 1.1.3 | No - format | Yes | No - see notes on proper Functions for this std to appply to | Yes | Yes | Yes | Yes | Yes - refers to TPLs | No | No | No | Yes | Yes | 1 | 7 | Low |  | High | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R1.1.1. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up- PC is responsible for doing the assessment, LSE, TO,TOP and DP are responsible for providing needed data. Is LSE an applicable function for this std? |  |  |  | Yes - #4, 7 | No | No |  |  | No - R1.1.1 says "Region' only-- should be modified to reach outside your Region as needed | No - add PC. See 'suggestions for improvement' column. | Yes | No - consolidate R1.1.1,1.1.2 and 1.1.3 | No - format | Yes | No - see notes on proper Functions for this std to appply to | Yes | Yes | Yes | Yes | Yes - refers to TPLs | No - has RRO reference | No | No | Yes | Yes | 1 | 7 | Low |  | High | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R1.1.2. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up- PC is responsible for doing the assessment, LSE, TO,TOP and DP are responsible for providing needed data. Is LSE an applicable function for this std? |  |  |  | Yes - #4, 7 | No | No |  |  | Yes | No - add PC. See 'suggestions for improvement' column. | Yes | No - consolidate R1.1.1,1.1.2 and 1.1.3 | No - format | Yes | No - see notes on proper Functions for this std to appply to | Yes | Yes | Yes | Yes | Yes - refers to TPLs | No - has language to specific to a version reference of TPLs | No | No | Yes | Yes | 2 | 7 | Low |  | High | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R1.1.3. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | A review of the voltage set points and timing. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up- PC is responsible for doing the assessment, LSE, TO,TOP and DP are responsible for providing needed data. Is LSE an applicable function for this std? |  |  |  | Yes - #4, 7 | No | No |  |  | Yes | No - add PC. See 'suggestions for improvement' column. | Yes | No - consolidate R1.1.1,1.1.2 and 1.1.3 | No - format | Yes | No - see notes on proper Functions for this std to appply to | Yes | Yes | Yes | Yes | Yes - refers to TPLs | No | No | No | Yes | Yes | 2 | 7 | Low |  | High | Medium |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-010-0 | PRC-010-0 | R2. | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | Provide System preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall provide documentation of its current UVLS program assessment to its Regional Reliability Organization and NERC on request (30 calendar days). | Current | Currently enforceable standard. | Yes - Project 2008-02 Undervoltage Load Shedding (PRC-010 and PRC-022) |  | Yes |  |  | No - administrative. NERC Board has approved to retire under P81 | No - administrative. NERC Board has approved to retire under P81 | [18 empty] | No | No | 0 | 0 | Low | Yes | N/A | Lower |  | DP |  |  |  | LSE | [9 empty] | TO | TOP
PRC-011-0 | PRC-011-0 | R1. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.1. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | The UVLS system identification which shall include but is not limited to: | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.1.1. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Relays. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.1.2. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Instrument transformers. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.1.3. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Communications systems, where appropriate. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.1.4. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Batteries. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.2. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Documentation of maintenance and testing intervals and their basis. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.3. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Summary of testing procedure. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.4. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Schedule for system testing. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.5. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Schedule for system maintenance. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R1.6. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | Date last tested/maintained. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  | DP | [13 empty] | TO
PRC-011-0 | PRC-011-0 | R2. | Undervoltage Load Shedding System Maintenance and Testing | Provide system preservation measures in an attempt to prevent system voltage collapse or voltage instability by implementing an Undervoltage Load Shedding (UVLS) program. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. |  |  |  | Yes |  | No - administrative. The drafting does require implementation; only documentation. Not clear if that was intent. PRC-008 R2 language clearly requires implementation. | Yes - administrative/documentation | [18 empty] | No |  | 0 | 0 | Medium |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-012-0 | PRC-012-0 | all | Special Protection System Review Procedure | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c |  | Not approved in Order 693 | [30 empty] | High
PRC-013-0 | PRC-013-0 | all | Special Protection System Database | To ensure that all Special Protection Systems (SPSs) are properly designed, meet performance requirements, and are coordinated with other protection systems. |  | Not approved in Order 693 | [30 empty] | High
PRC-014-0 | PRC-014-0 | all | Special Protection System Assessment | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c |  | Not approved in Order 693 | [30 empty] | High
PRC-015-0 | PRC-015-0 | R1. | Special Protection System Data and Documentation | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R 1. | Current | Currently enforceable standard. |  | Team thinks that a complete rewrite of PRC-012, -013, -014, -015 into a single std is required |  |  |  | Yes - #1 | No | No |  |  | No - the std does not accomplish the purpose. The second sentence in the purpose is covered under PRC stds related to Maintenance and Testing of SPS schemes (PRC-005-2 and PRC-017-0). Std needs to address process (including RE process), data and required actions - see stds -012, -013, -014 that were not approved in order 693. | No - TP and PC need to be included. | No - only meets the first sentence of the purpose | No -needs to include content from PRC-012, PRC-013 and PRC-014 so SPS content is all approved and located in one std. | Yes | Yes | No - related stds are not approved | No | Yes | No | Yes | No | No - has reference to RRO | No | Yes | Yes | Yes | 0 | 5 | High | Yes | Low | Medium |  | DP | GO | [12 empty] | TO
PRC-015-0 | PRC-015-0 | R2. | Special Protection System Data and Documentation | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | Current | Currently enforceable standard. | [5 empty] | Yes - #6 | No | No |  |  | No - the std does not accomplish the purpose. The second sentence in the purpose is covered under PRC stds related to Maintenance and Testing of SPS schemes (PRC-005-2 and PRC-017-0). Std needs to address process (including RE process), data and required actions - see stds -012, -013, -014 that were not approved in order 693. | No - TP and PC need to be included. | No -only meets the first sentence of the purpose | No -needs to include content from PRC-012, PRC-013 and PRC-014 so SPS content is all approved and located in one std. | Yes | Yes | No - related stds are not approved | No | Yes | No | Yes | No | No - has reference to RRO | No | Yes | Yes | Yes | 0 | 5 | High | Yes | High | Medium |  | DP | GO | [12 empty] | TO
PRC-015-0 | PRC-015-0 | R3. | Special Protection System Data and Documentation | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | Current | Currently enforceable standard. |  |  |  | Yes |  | Yes | Yes - documentation | [19 empty] | No | 0 | 0 | High | Yes | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-016-0 | PRC-016-0.1 | R1. | Special Protection System Misoperations | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  |  |  | Yes | Yes - currently | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-016-0 | PRC-016-0.1 | R2. | Special Protection System Misoperations | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | No | No |  |  |  |  | Yes | Yes - currently | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-016-0 | PRC-016-0.1 | R3. | Special Protection System Misoperations | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | Current | Currently enforceable standard. |  |  |  | Yes |  | Yes | Yes - administrative/documentation | [19 empty] | No | 0 | 0 | High |  | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.1. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | SPS identification shall include but is not limited to: | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.1.1. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Relays. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.1.2. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Instrument transformers. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.1.3. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Communications systems, where appropriate. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.1.4. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Batteries. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #9 | No | No |  |  | Yes | Yes | Yes | Yes | No - format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.2. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Documentation of maintenance and testing intervals and their basis. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #7, 9 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.3. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Summary of testing procedure. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #7, 9 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.4. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Schedule for system testing. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #7, 9 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.5. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Schedule for system maintenance. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #7, 9 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R1.6. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | Date last tested/maintained. | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. | [5 empty] | Yes - #7, 9 | No | No |  |  | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-017-0 | PRC-017-0 | R2. | Special Protection System Maintenance and Testing | To ensure that all Special Protection Systems (SPS) are properly designed, meet performance requirements, and are coordinated with other protection systems. To ensure that maintenance and testing programs are developed and misoperations are analyzed and c | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | Current - will be replaced by Board adopted std | Currently enforceable standard; will be replaced by PRC-005-2 when FERC approved. Board adopted it on 11/7/2012; it has not been filed with FERC. |  |  |  | Yes and PRC-017-0.1 |  | No - administrative. The drafting does require implementation; only documentation. Not clear if that was intent. PRC-008 R2 language clearly requires implementation. | Yes - administrative/documentation | [18 empty] | No |  | 0 | 0 | High |  | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R1. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  |  |  | Yes - #5, 10 | No | No |  |  | Yes | No - RRO is referred to | No -the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No - combine R1 and R2. Consider combining this with the content of PRC-002 into one std | Yes for content; No for format | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | Yes | Yes | Yes | Yes | No - refers to PRC 002 | No - has RRO language | Yes | No | Yes | Yes | 1 | 6 | Not ranked | Yes | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R1.1. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) | Current | Currently enforceable standard. | [5 empty] | Yes - #5, 10 | No | No |  |  | Yes | No - RRO is referred to | No -the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No - combine R1 and R2 | Yes for content; No for format | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | Yes | Yes | Yes | Yes | No - refers to PRC 002 | No - has RRO language | Yes | No | Yes | Yes | 1 | 6 | Not ranked |  | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R1.2. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Recorded data from each Disturbance shall be retrievable for ten calendar days.. | Current | Currently enforceable standard. | [5 empty] | Yes - #5, 10 | No | No |  |  | Yes | No - RRO is referred to | No -the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No - combine R1 and R2 | Yes for content; No for format | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | Yes | Yes | Yes | Yes | No - refers to PRC 002 | No - has RRO language | Yes | No | Yes | Yes | 1 | 6 | Not ranked |  | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R2. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  |  |  | Yes - #5, 10 | No | No |  |  | No - requirements are not defined, relies on RRO | No - RRO is referred to | No -the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No - combine R1 and R2 | No - do not know what RRO requirements are | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No | Yes | Yes | Yes | Yes | No - refers to PRC 002 and RRO | No - RRO reference | No - PRC 002 and RRO refernce | No | Yes | Yes | 0 | 4 | Not ranked | Yes | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  | Yes |  | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked | Yes | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.1. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.2. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Make and model of equipment. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.3. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Installation location. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.4. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Operational status. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.5. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Date last tested. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.6. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Monitored elements, such as transmission circuit, bus section, etc. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | [18 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.7. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | Yes | [17 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R3.8. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Monitored electrical quantities, such as voltage, current, etc. | Current | Currently enforceable standard. | [5 empty] | No - administrative | Yes - administrative | Yes | [17 empty] | No | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R4. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  |  |  | Yes - #5, 10 | No | No |  |  | No - requirments are not defined, relies on RRO | No - RRO is referred to | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | No - do not know what RRO requirements are | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No | Yes | Yes | Yes | Yes | No - refers to prc 002 and rro | No - rro reference | No - prc 002 and rro refernce | No | Yes | Yes | 0 | 4 | Not ranked | Yes | Medium | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R5. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  | Yes | The data retained is considered necessary for event analysis, however the team agreed that the period for data retention needs to be evaluated (project 2007-11). | Yes - #10 | No | No |  |  | No - has RRO reference-- is 3 years appropriate ? | No - RRO is referred to | No - need to add specifics that clearly defines what a trigerring event is. | Yes | No - do not know what RRO requirements are | Yes | No - see comments under 'technical content column?' | Yes | Yes | Yes | Yes | No - do not know triggering event | No - rro reference, do not know triggering event | No - rro refernce | No | Yes | Yes | 0 | 6 | Not ranked | Yes | Low | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R6. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: | Current | Currently enforceable standard. | Yes - Project 2007-11 Disturbance Monitoring (PRC-002 and PRC-018) |  |  |  |  | Yes - #9 | No | No |  |  | No - requirments are not defined, relies on RRO | No - RRO is referred to | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | No - do not know what RRO requirements are | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No | Yes | Yes | Yes | Yes | No - refers to prc 002 and rro | No - rro reference | No - prc 002 and rro refernce | No | Yes | Yes | 0 | 5 | Not ranked | Yes | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R6.1. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Maintenance and testing intervals and their basis. | Current | Currently enforceable standard. | [5 empty] | Yes - #9 | No | No |  |  | No - requirments are not defined, relies on RRO | No - RRO is referred to | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | No - do not know what RRO requirements are | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No | Yes | Yes | Yes | Yes | No - refers to prc 002 and rro | No - rro reference | No - prc 002 and rro refernce | No | Yes | Yes | 0 | 5 | Not ranked |  | High | Lower |  |  | GO | [12 empty] | TO
PRC-018-1 | PRC-018-1 | R6.2. | Disturbance Monitoring Equipment Installation and Data Reporting | Ensure that Disturbance Monitoring Equipment (DME) is installed and that Disturbance data is reported in accordance with regional requirements to facilitate analyses of events. | Summary of maintenance and testing procedures. | Current | Currently enforceable standard. | [5 empty] | Yes - #9 | No | No |  |  | No - requirments are not defined, relies on RRO | No - RRO is referred to | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | Yes | No - do not know what RRO requirements are | No - the std is written assuming a 1950's technology and does not recognize emergence of PMU's | No | Yes | Yes | Yes | Yes | No - refers to prc 002 and rro | No - rro reference | No - prc 002 and rro refernce | No | Yes | Yes | 0 | 5 | Not ranked |  | High | Lower |  |  | GO | [12 empty] | TO
PRC-019-1 | PRC-019-1 | R1. | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | To verify coordination of generating unit Facility or synchronous condenser voltage regulating controls, limit functions, equipment capabilities and Protection System settings. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. 1.1. Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: 1.1.1. The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. 1.1.2. The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | Board Adopted | Board adopted 2/2013 with MOD-025-2, MOD-026-1, MOD-027-1, | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | High
PRC-019-1 | PRC-019-1 | R2. | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | To verify coordination of generating unit Facility or synchronous condenser voltage regulating controls, limit functions, equipment capabilities and Protection System settings. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Board Adopted | Board adopted 2/2013 with MOD-025-2, MOD-026-1, MOD-027-1, | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | High
PRC-021-1 | PRC-021-1 | R1. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | Current | Currently enforceable standard. | [5 empty] | Yes - #10 | Yes - adminstrative (it is a local issue; not a regional issue) | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R1.1. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Size and location of customer load, or percent of connected load, to be interrupted. | Current | Currently enforceable standard. | [5 empty] | Yes - #10 | Yes - adminstrative (it is a local issue; not a regional issue) | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R1.2. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Corresponding voltage set points and overall scheme clearing times. | Current | Currently enforceable standard. | [5 empty] | Yes - #10 | Yes - adminstrative (it is a local issue; not a regional issue) | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Medium |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R1.3. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Time delay from initiation to trip signal. | Current | Currently enforceable standard. | [5 empty] | Yes - #10 | Yes - adminstrative (it is a local issue; not a regional issue) | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R1.4. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Breaker operating times. | Current | Currently enforceable standard. | [5 empty] | Yes - #10 | Yes - adminstrative (it is a local issue; not a regional issue) | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R1.5. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | Current | Currently enforceable standard. | [5 empty] | Yes - #1 | Yes | No | [17 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-021-1 | PRC-021-1 | R2. | Under-Voltage Load Shedding Program Data | Ensure data is provided to support the Regional database maintained for Under-Voltage Load Shedding (UVLS) programs that were implemented to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | Current | Currently enforceable standard. |  |  |  | Yes and PRC-021-0.1 |  | No | Yes | [18 empty] | No |  | 0 | 0 | Not ranked |  | N/A | Lower |  | DP | [13 empty] | TO
PRC-022-1 | PRC-022-1 | R1. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall analyze and document all UVLS operations and Misoperations. The analysis shall include: | Current | Currently enforceable standard. | Yes - Project 2008-02 Undervoltage Load Shedding (PRC-010 and PRC-022) | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  | Yes |  | Yes - #7, 10 | No | No | Team believes there is value in doing an analysis of UVLS operations to determine if the UVLS scheme operated properly |  | No - there should be a requirement to review all UVLS operations and analyze misoperations consistent with the team's suggested wording for PRC-004 | No - this should apply to TOP, DP, TO. | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | Not ranked | Yes | High | Medium |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R1.1. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | A description of the event including initiating conditions. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  |  |  | Yes - #10 | Yes | Yes |  |  | Yes | No - this should apply to TOP, DP, TO | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Not ranked |  | High | Lower |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R1.2. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | A review of the UVLS set points and tripping times. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  |  |  | Yes - #10 | Yes | Yes |  |  | Yes | No - this should apply to TOP, DP, TO | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Not ranked |  | High | Medium |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R1.3. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  |  |  | Yes - #10 | Yes | Yes |  |  | Yes | No - this should apply to TOP, DP, TO. Refers to RRO | No - refers to RRO | Yes | Yes for content; No for format | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 9 | Not ranked |  | High | Lower |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R1.4. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | A summary of the findings. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  |  |  | Yes - #10 | Yes | Yes |  |  | Yes | No - this should apply to TOP, DP, TO | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Not ranked |  | High | Lower |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R1.5. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. | Current | Currently enforceable standard. |  | (1) get the applicable function cleared up to be the PC AND TRANSMISSION OWNER only; (2) Get rid of R1.1 and all the items under it.-- if you do keep them, keep them as a guide |  |  |  | Yes - #4 | Yes | Yes |  |  | Yes | No - this should apply to TOP, DP, TO | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 10 | Not ranked |  | High | Medium |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-022-1 | PRC-022-1 | R2. | Under-Voltage Load Shedding Program Performance | Ensure that Under Voltage Load Shedding (UVLS) programs perform as intended to mitigate the risk of voltage collapse or voltage instability in the Bulk Electric System (BES). | Each Transmission Operator, Load-Serving Entity, and Distribution Provider that operates a UVLS program shall provide documentation of its analysis of UVLS program performance to its Regional Reliability Organization within 90 calendar days of a request. | Current | Currently enforceable standard. | Yes - Project 2008-02 Undervoltage Load Shedding (PRC-010 and PRC-022) |  | Yes |  |  | No | Yes - Para 81 Phase 1 | [18 empty] | Yes | No | 0 | 0 | Not ranked | Yes | N/A | Lower |  | DP |  |  |  | LSE | [10 empty] | TOP
PRC-023-1 | PRC-023-1 | R1. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f |  | Retired | Retired | [5 empty] | Yes - #1 | No | No |  |  |  |  | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High
PRC-023-1 | PRC-023-1 | R2. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f |  | Retired | Retired |  |  |  | Yes |  | Yes - #1 | No | Yes |  |  |  |  | Yes | Yes | [11 empty] | Yes | No | 0 | 0 | High |  | N/A
PRC-023-1 | PRC-023-1 | R3. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | The Planning Coordinator shall determine which of the facilities (transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV) in its Planning Coordinator Area are critical to the reliability of the Bulk Electric System to identify the facilities from 100 kV to 200 kV that must meet Requirement 1 to prevent potential cascade tripping that may occur when protective relay settings limit transmission loadability. [Time Horizon: Long Term Planning] | Retired | Will become inactive on 12/31/2013. |  |  |  | Yes |  | Yes - #1, 7 | No | No |  |  | No - it does not look at sub 100kv | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | Medium | [7 empty] | PA | PC
PRC-023-1 | PRC-023-1 | R3.1. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | The Planning Coordinator shall have a process to determine the facilities that are critical to the reliability of the Bulk Electric System. | Retired | Will become inactive on 12/31/2013. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - it does not look at sub 100kv | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [7 empty] | PA | PC
PRC-023-1 | PRC-023-1 | R3.1.1. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | This process shall consider input from adjoining Planning Coordinators and affected Reliability Coordinators. | Retired | Will become inactive on 12/31/2013. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - it does not look at sub 100kv | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [7 empty] | PA | PC
PRC-023-1 | PRC-023-1 | R3.2. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | The Planning Coordinator shall maintain a current list of facilities determined according to the process described in R3.1. | Retired | Will become inactive on 12/31/2013. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - it does not look at sub 100kv | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [7 empty] | PA | PC
PRC-023-1 | PRC-023-1 | R3.3. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators’ ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | The Planning Coordinator shall provide a list of facilities to its Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within 30 days of the establishment of the initial list and within 30 days of any changes to the list. | Retired | Will become inactive on 12/31/2013. | [5 empty] | Yes - #1, 7 | No | No |  |  | No - it does not look at sub 100kv | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | No Individual VRF Assigned | [7 empty] | PA | PC
PRC-023-2 | PRC-023-2 | R1. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [See standard for criteria] | Current | Currently enforceable standard. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings |  |  |  |  | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-023-2 | PRC-023-2 | R2. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | Current | Currently enforceable standard. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings |  |  |  |  | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | High |  | DP | GO | [12 empty] | TO
PRC-023-2 | PRC-023-2 | R3. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | Current | Currently enforceable standard. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings |  |  | Yes |  | Yes - #1 | No | No | Team believes that there is a strong technical basis of support for this requirement given the work of the Std Drafting Team that very recently developed this std. |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | Medium |  | DP | GO | [12 empty] | TO
PRC-023-2 | PRC-023-2 | R4. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | Current | Currently enforceable standard. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings |  |  |  |  | Yes - #3 | No | No |  |  | Yes Needs to be examined. Why only criterion 2? Do other criterion need to be included? | Yes | No - the team is questioning whether 15 months is technically correct - consider within 30 days of change. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | Medium | Lower |  | DP | GO | [12 empty] | TO
PRC-023-2 | PRC-023-2 | R5. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | Current | Currently enforceable standard. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings |  |  |  |  | No - administrative | Yes - adminstrative amd data reporting | [18 empty] | No |  | 0 | 0 | High |  | N/A | Lower |  | DP | GO | [12 empty] | TO
PRC-023-2 | PRC-023-2 | R6. | Transmission Relay Loadability | Protective relay settings shall not limit transmission loadability; not interfere with system operators' ability to take remedial action to protect system reliability and; be set to reliably detect all fault conditions and protect the electrical network f | Each Planning Coordinator shall conduct an assessment at least once each calendar year, with no more than 15 months between assessments, by applying the criteria in Attachment B to determine the circuits in its Planning Coordinator area for which Transmission Owners, Generator Owners, and Distribution Providers must comply with Requirements R1 through R5. The Planning Coordinator shall: [See standard for what the Planning Coordinator shall do] | Current | Will become enforceable 1/1/2014. | Yes - Project 2010-13.2 Phase 2 Relay Loadability: Generation, and Phase 3: Stable Power Swings | Has reference to R1 to R5. If you eliminate R5, then need to change reference to R1 to R4 |  |  |  | Yes - #7 | No | No |  |  | No - needs to consider sub-100kV in attachment B | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High | [7 empty] | PA | PC
PRC-024-1 | PRC-024-1 | R1. |  |  | Each Generator Owner that has generator frequency protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: *Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. *Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). *Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Board Adopted |  |  | The Independent Review Team reviewed this on 3/9/12- Team believes this std is a good std to have as a mandatory std as it works to ensure generators remain on line during defined voltage and frequency excursions. |  |  |  | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | High | Medium
PRC-024-1 | PRC-024-1 | R2. |  |  | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection2) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: *Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). *Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). *Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. *Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | Board Adopted |  |  | The Independent Review Team reviewed this on 3/9/12- Team believes this std is a good std to have as a mandatory std as it works to ensure generators remain on line during defined voltage and frequency excursions. |  |  |  | Yes - #5 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | High | Medium
PRC-024-1 | PRC-024-1 | R3. |  |  | Each Generator Owner shall document each known regulatory or equipment limitation3 that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: *Identification of a regulatory or equipment limitation. *Repair of the equipment causing the limitation that removes the limitation. *Replacement of the equipment causing the limitation with equipment that removes the limitation. *Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | Board Adopted |  |  | The Independent Review Team reviewed this on 3/9/12- Team believes this std is a good std to have as a mandatory std as it works to ensure generators remain on line during defined voltage and frequency excursions. |  |  |  | Yes - #1 | No | No |  |  | No - std should include a requirement for PC and TPs to communicate information regarding these exceptions to the RC, BA, and other affected functions | No - add RC and BA | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | Not ranked |  | High | Lower
PRC-024-1 | PRC-024-1 | R4. |  |  | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. | Board Adopted |  |  | The Independent Review Team reviewed this on 3/9/12- Team believes this std is a good std to have as a mandatory std as it works to ensure generators remain on line during defined voltage and frequency excursions. |  |  |  | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | Medium | Lower
TOP-001-1 | TOP-001-1a | R1. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator shall have the responsibility and clear decision-making authority to take whatever actions are needed to ensure the reliability of its area and shall exercise specific authority to alleviate operating emergencies. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #6 but needs to apply to people employed by the functional entity | No | No |  |  | No - needs to apply to the personnel of the entity | Yes | Yes | No -R1 and R3 can be consolidate and made more concise | No - not who, what, when. | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 9 | High |  | High | High | [16 empty] | TOP
TOP-001-1 | TOP-001-1a | R2. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator shall take immediate actions to alleviate operating emergencies including curtailing transmission service or energy schedules, operating equipment (e.g., generators, phase shifters, breakers), shedding firm load, etc. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No | Yes | No -vague; legacy language | Yes | No | Yes | No - vague language | No | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 5 | High |  | High | High | [16 empty] | TOP
TOP-001-1 | TOP-001-1a | R3. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes | No | No |  |  | Yes | Yes | No -the phrase "unless it violates …..requirements" is too permissive or there may be a better way to phrase it | No -R1 and R3 can be consolidate and made more concise | No | Yes | No - "or" for noticication; use of "immediately" | Yes | Yes | No | Yes | Yes | No - "or" for noticication; use of "immediately" | No | Yes | Yes | Yes | 2 | 6 | High |  | High | High | BA |  |  | GOP | [12 empty] | TOP
TOP-001-1 | TOP-001-1a | R4. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Distribution Provider and Load-Serving Entity shall comply with all reliability directives issued by the Transmission Operator, including shedding firm load, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances, the Distribution Provider or Load-Serving Entity shall immediately inform the Transmission Operator of the inability to perform the directive so that the Transmission Operator can implement alternate remedial actions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes | No | No |  |  | Yes | Yes | No -the phrase "unless it violates …..requirements" is too permissive or there may be a better way to phrase it | No -R1 and R3 can be consolidated and made more concise | No | Yes | No - use of "immediately" | Yes | Yes | No | Yes | Yes | No - use of "immediately" | No | Yes | Yes | Yes | 2 | 6 | High |  | High | High |  | DP |  |  |  | LSE
TOP-001-1 | TOP-001-1a | R5. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator shall inform its Reliability Coordinator and any other potentially affected Transmission Operators of real-time or anticipated emergency conditions, and take actions to avoid, when possible, or mitigate the emergency. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No | Yes | No -vague; legacy language | No | No | No | Yes | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 5 | High |  | High | High | [16 empty] | TOP
TOP-001-1 | TOP-001-1a | R6. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No | Yes | No -vague; legacy language | No | No | No | Yes | Yes | No | No | Yes | Yes | no | no | Yes | Yes | Yes | 1 | 5 | High |  | High | High | BA |  |  | GOP | [12 empty] | TOP
TOP-001-1 | TOP-001-1a | R7. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes | No | No |  |  | No - there is a lot missing. The coordination process is poorly represented and does not facilitate management of outages | No - BA should be included | No -there is a lot of vague legacy language | Yes | No | Yes | No - see comments | Yes | Yes | No | Yes | No - missing language | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | High |  |  |  | GOP | [12 empty] | TOP
TOP-001-1 | TOP-001-1a | R7.1. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - there is a lot missing. The coordination process is poorly represented and does not facilitate management of outages | No - BA should be included | No -there is a lot of vague legacy language | Yes | No | Yes | No - see comments | Yes | Yes | No | Yes | No - missing language | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | High |  |  |  | GOP | [12 empty] | TOP
TOP-001-1 | TOP-001-1a | R7.2. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - there is a lot missing. The coordination process is poorly represented and does not facilitate management of outages | No - BA should be included | No -there is a lot of vague legacy language | Yes | No | Yes | No - see comments | Yes | Yes | No | Yes | No - missing language | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | High | [16 empty] | TOP
TOP-001-1 | TOP-001-1a | R7.3. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - there is a lot missing. The coordination process is poorly represented and does not facilitate management of outages | No - BA should be included | No -there is a lot of vague legacy language | Yes | No | Yes | No - see comments | Yes | Yes | No | Yes | No - missing language | No | No | Yes | Yes | Yes | 0 | 6 | High |  | High | High |  |  |  | GOP | [12 empty] | TOP
TOP-001-1 | TOP-001-1a | R8. | Reliability Responsibilities and Authorities | To ensure reliability entities have clear decision-making authority and capabilities to take appropriate actions or direct the actions of others to return the transmission system to normal conditions during an emergency. | During a system emergency, the Balancing Authority and Transmission Operator shall immediately take action to restore the Real and Reactive Power Balance. If the Balancing Authority or Transmission Operator is unable to restore Real and Reactive Power Balance it shall request emergency assistance from the Reliability Coordinator. If corrective action or emergency assistance is not adequate to mitigate the Real and Reactive Power Balance, then the Reliability Coordinator, Balancing Authority, and Transmission Operator shall implement firm load shedding. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | Yes - covered under other standards; see mapping doc for project 2007-03, real time operations | [19 empty] | No | 0 | 0 | High |  | N/A | High | BA | [15 empty] | TOP
TOP-001-2 | TOP-001-2 | R1. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall comply with each Reliability Directive issued and identified as such by its Transmission Operator(s), unless such action would violate safety, equipment, regulatory, or statutory requirements. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #6 (authority) | No | No |  |  | Yes | Yes | No -the phrase "unless it violates …..requirements" is too permissive or there may be a better way to phrase it | Yes | Yes | Yes | No - the expectation is not clear due to the "unles such action…" statement | Yes | Yes | Yes - valid reason may be debatable | Yes | Yes | No - see comments | Yes | Yes | Yes | Yes | 2 | 10 | High | Yes | High | High | BA | DP |  | GOP |  | LSE
TOP-001-2 | TOP-001-2 | R2. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | High | High | BA | DP |  | GOP |  | LSE
TOP-001-2 | TOP-001-2 | R3. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall inform its Reliability Coordinator and Transmission Operator(s) that are known or expected to be affected by each actual and anticipated Emergency based on its assessment of its Operational Planning Analysis. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | yes - #1, 4 | No | No |  |  | No - Adverse Reliability Impact not covered | No - BA should be included | Yes -This is day-ahead | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R4. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall render emergency assistance to other Transmission Operators, as requested and available, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | yes - #1, 4 | No | No |  |  | No - "emergency assistance" is not clear; when and how must assistance be rendered and what type of assistance? | No - BA should be included | Yes | No -consider moving to EOP standards (this is an "emergency" operating requirement) | Yes | Yes | No - "emergency assistance" is not clear; when and how must assistance be rendered and what type of assistance? | Yes | Yes | No - "emergency assistance" is not clear; when and how must assistance be rendered and what type of assistance? | Yes | No | No - it is not clear what "comparable emergency procedures" are | No | Yes | Yes | Yes | 1 | 6 | High | Yes | High | High | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R5. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall inform its Reliability Coordinator and other Transmission Operators of its operations known or expected to result in an Adverse Reliability Impact on those respective Transmission Operator Areas unless conditions do not permit such communications. Examples of such operations are relay or equipment failures, and changes in generation, Transmission, or Load. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1, 4 | No | No |  |  | No - Emergency not covered | No - BA should be included | Yes -This is real time or close | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 12 | High | Yes | High | High | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R6. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and negatively impacted interconnected NERC registered entities of planned outages of telemetering equipment, control equipment and associated communication channels between the affected entities. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #5 | No | No |  |  | No - needs to include real time outages of telecom as well as planned outages | Yes | Yes | No -consolidate with COM-001-1.1 R2 | Yes | Yes | No - "negatively" is unclear - what is the threshold/trigger (time, criticality or at all times there is an impact)? | Yes | Yes | Yes | Yes | Yes | No - see comments | No - see comments | Yes | Yes | Yes | 2 | 8 | High | Yes | Medium | Medium | BA | [15 empty] | TOP
TOP-001-2 | TOP-001-2 | R7. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes - IRO-009 covers RCs | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | High | High | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R8. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall inform its Reliability Coordinator of each SOL which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area based on its assessment of its Operational Planning Analysis. (See Standard for Rationale) | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - not clear. This clearly covers the first case but needs to cover 1) SOLs within a TOP's/RC's footprint, 2) SOLs that are within one TOP's/RC's footprint that could affect another entity and 3) an SOL that spans into 2 TOP's/RC's footprints | No - needs to also inform other impacted TOPs (The entity that could be impacted must tell the TOP that could impact them that it needs the info) | Yes | Yes | Yes | Yes | No - see comments | Yes | Yes | Yes | Yes | Yes | No - see comments | No | Yes | Yes | Yes | 1 | 9 | High | Yes | High | Medium | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R9. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall not operate outside any System Operating Limit (SOL) identified in Requirement R8 for a continuous duration that would cause a violation of the Facility Rating or Stability criteria upon which it is based. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | High | Medium | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R10. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall inform its Reliability Coordinator of its actions to return the system to within limits when an IROL, or an SOL identified in Requirement R8, has been exceeded. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1, 10 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High | Yes | High | Medium | [16 empty] | TOP
TOP-001-2 | TOP-001-2 | R11. | Transmission Operations | To prevent instability, uncontrolled separation, or cascading outages that adversely impact the reliability of the Interconnection by ensuring prompt action to prevent or mitigate such occurrences. | Each Transmission Operator shall act or direct others to act, to mitigate Boardh the magnitude and duration of exceeding an IROL within the IROL’s Tv, or of an SOL identified in Requirement R8. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1, 4 | No | No |  |  | No - some elements missing from new std TOP-001-2 R11 - identical SOLs for common facilities, coordination | Yes | Yes - This is getting at better/faster: look at language in IRO-009 for better language to get at this concept. | yes | Yes | Yes | Yes | Yes | Yes | No - would an entity demonstrate that they did it better, faster than the Tv? | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 9 | High | Yes | High | High | [16 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R1. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period. In addition, each Balancing Authority and Transmission Operator shall be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | Yes - this is legacy language (obvious) | [18 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R2. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes and TOP-002-2b |  | Yes | No | Yes - this is legacy language | [18 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R3. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Load-Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | Yes - this is legacy language | [18 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA |  |  | GOP |  | LSE | [12 empty] | TSP
TOP-002-2 | TOP-002-2.1b | R4. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | Yes - this is legacy language | [18 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R5. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - need to define the timeframe | Yes | Yes | Yes | Yes | Yes | No - see gap language | Yes | Yes | No - language is not clear | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | Medium |  | High | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R6. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - need to define the timeframe | Yes | Yes | Yes | Yes | Yes | No - see gap language | Yes | Yes | No - language is not clear | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | Medium |  | High | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R7. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority shall plan to meet capacity and energy reserve requirements, including the deliverability/capability for any single Contingency. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative of R5 and R6 of this std and covered under BAL and EOP-002 | [19 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA
TOP-002-2 | TOP-002-2.1b | R8. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority shall plan to meet voltage and/or reactive limits, including the deliverability/capability for any single contingency. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes and TOP-002-2b |  | Yes | Yes - duplicative of R6. This is also covered under VAR-001. This is the daily check that engineers do so that an N-1 is not violated | [19 empty] | No | 0 | 0 | Medium |  | N/A | Medium | BA
TOP-002-2 | TOP-002-2.1b | R9. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority shall plan to meet Interchange Schedules and ramps. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes and TOP-002-2b |  | Yes | Yes - This is covered by R5. | [19 empty] | No | 0 | 0 | Medium |  | N/A | Lower | BA
TOP-002-2 | TOP-002-2.1b | R10. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall plan to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | Yes | No - BA does not need to be included | Yes | No, consider combining with other standards that address IROL and SOLs | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Medium |  | HIgh | Medium | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R11. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | The Transmission Operator shall perform seasonal, next-day, and current-day Bulk Electric System studies to determine SOLs. Neighboring Transmission Operators shall utilize identical SOLs for common facilities. The Transmission Operator shall update these Bulk Electric System studies as necessary to reflect current system conditions; and shall make the results of Bulk Electric System studies available to the Transmission Operators, Balancing Authorities (subject to confidentiality requirements), and to its Reliability Coordinator. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | Yes | Yes | No - the third sentence is not measurable. Begins with "and shall"… | No -consolidate with other IROL/SOL stds (FAC-014-2 R2 and others) | Yes | Yes | Yes | Yes | Yes | No - unclear language | Yes | No - need to look to other stds to understand more about the requirements for studies | No - what is "as necessary"? | No - what is "as necessary"? | Yes | Yes | Yes | 2 | 8 | Medium |  | High | Medium | [16 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R12. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | The Transmission Service Provider shall include known SOLs or IROLs within its area and neighboring areas in the determination of transfer capabilities, in accordance with filed tariffs and/or regional Total Transfer Capability and Available Transfer Capability calculation processes. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | yes - addresses a market issue. FAC-013-2 R1 addresses the reliability concern; this is market. | [19 empty] | No | 0 | 0 | Medium |  | N/A | Medium | [18 empty] | TSP
TOP-002-2 | TOP-002-2.1b | R13. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | no | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Medium |  | High | Medium |  |  |  | GOP
TOP-002-2 | TOP-002-2.1b | R14. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  | MOD-024 and -025requires communication of original state; this requires changes | No - does not have requirement to report when you will return to the entity's normal capability | Yes - consider adding RC to provide for consolidation of R17 | Yes | Yes | Yes | Yes | No - intentional time delay is not clear | Yes | Yes | No - intentional time delay | Yes | Yes | No - intentional time delay | No - intentional time delay | Yes | Yes | Yes | 2 | 8 | Medium |  | High | Medium |  |  |  | GOP
TOP-002-2 | TOP-002-2.1b | R14.1. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Changes in real output capabilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  | MOD-024 and -025requires communication of original state; this requires changes | No - does not have requirement to report when you will return to the entity's normal capability | Yes | Yes | Yes | Yes | Yes | No - intentional time delay is not clear | Yes | Yes | No - intentional time delay | Yes | Yes | No - intentional time delay | No - intentional time delay | Yes | Yes | Yes | 2 | 8 | Medium |  | High | Medium |  |  |  | GOP
TOP-002-2 | TOP-002-2.1b | R15. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - reactive covered under VAR; | Yes - consider adding RC to provide for consolidation of R17 | Yes | Yes | Yes | Yes | No - does not explicity state hourly output data is required | Yes | Yes | Yes | Yes | Yes | No - hourly data not clear | No - hourly data not clear | Yes | Yes | Yes | 2 | 9 | Medium |  | Medium | Lower |  |  |  | GOP
TOP-002-2 | TOP-002-2.1b | R16. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Subject to standards of conduct and confidentiality agreements, Transmission Operators shall, without any intentional time delay, notify their Reliability Coordinator and Balancing Authority of changes in capabilities and characteristics including but not limited to: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  | FAC-008 requires ratings; this requires changes of ratings | No - does not have requirement to report when you will return to the entity's normal capability | Yes - consider adding RC to provide for consolidation of R17 | No - first phrase (subject to…) should be struck as should not be in a requirement | Yes | Yes | Yes | No - intentional time delay is not clear | Yes | Yes | No - intentional time delay | Yes | Yes | No - intentional time delay | No - intentional time delay | Yes | Yes | Yes | 1 | 8 | Medium |  | High | Medium | [16 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R16.1. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Changes in transmission facility status. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  | FAC-008 requires ratings; this requires changes of ratings | No - does not have requirement to report when you will return to the entity's normal capability | Yes | Yes | Yes | Yes | Yes | No - intentional time delay is not clear | Yes | Yes | No - intentional time delay | Yes | Yes | No - intentional time delay | No - intentional time delay | Yes | Yes | Yes | 2 | 8 | Medium |  | High | High | [16 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R16.2. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Changes in transmission facility rating. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  | FAC-008 requires ratings; this requires changes of ratings | No - does not have requirement to report when you will return to the entity's normal capability | Yes | Yes | Yes | Yes | Yes | No - intentional time delay is not clear | Yes | Yes | No - intentional time delay | Yes | Yes | No - intentional time delay | No - intentional time delay | Yes | Yes | Yes | 2 | 8 | Medium |  | High | High | [16 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R17. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Balancing Authorities and Transmission Operators shall, without any intentional time delay, communicate the information described in the requirements R1 to R16 above to their Reliability Coordinator. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No - consider consolidating with other Rs of this standard. Review to see where it is appropriate to add the RC. Consider adding to authority std. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | High | High | BA | [15 empty] | TOP
TOP-002-2 | TOP-002-2.1b | R18. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers, and Load-Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - it is broader than unified lines identifiers | No - TO needs to be included | Yes | Yes - move to COM-003 if and when COM-003 is approved | Yes | Yes | No - "transmission facilities of an interconnected network" is not clear and it needs to be updated for current glossary definitions | Yes | Yes | No - expectations are not clear | Yes | Yes | No - see comments | No - see comments | Yes | Yes | Yes | 1 | 8 | Medium |  | High | Medium | BA |  |  | GOP |  | LSE | [10 empty] | TOP |  | TSP
TOP-002-2 | TOP-002-2.1b | R19. | Normal Operations Planning | Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events. | Each Balancing Authority and Transmission Operator shall maintain accurate computer models utilized for analyzing and planning system operations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1, 3 | No | No |  |  | No - it doesn't specific which models are to be accurate (or what that means) | No - RC needs to be added | Yes - although it is not clear what accurate means | Yes - look at moving to project 2009-02 | Yes | Yes | No - "accurate" is not defined | Yes | Yes | No - what is "accurate"? | Yes | Yes | No - what is "accurate"? And not know what models are referred to | No | Yes | Yes | Yes | 1 | 8 | Medium |  | High | Medium | BA | [15 empty] | TOP
TOP-002-3 | TOP-002-3 | R1. | Operations Planning | To ensure that Transmission Operators have plans for operating within specified limits. | Each Transmission Operator shall have an Operational Planning Analysis that represents projected System conditions that will allow it to assess whether the planned operations for the next day within its Transmission Operator Area will exceed any of its Facility Ratings or Stability Limits during anticipated normal and Contingency event conditions. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - TOP-008-1 R4 needs to be incorporated. Also - the definition of "Operational Planning Analysis" provides too much latitude in time. Recommend removing the parenthesis in the definition; the entity will make the determination and document (documentation is evidence) the applicability of what it uses for their next day study | Yes | Yes | Yes | Yes | Yes | No - see comments | Yes | Yes | Yes | Yes | Yes | No - see comments | No | Yes | Yes | Yes | 2 | 9 | Medium |  | High | Medium
TOP-002-3 | TOP-002-3 | R2. | Operations Planning | To ensure that Transmission Operators have plans for operating within specified limits. | Each Transmission Operator shall develop a plan to operate within each Interconnection Reliability Operating Limit (IROL) and each System Operating Limit (SOL) which, while not an IROL, has been identified by the Transmission Operator as supporting reliability internal to its Transmission Operator Area, identified as a result of the Operational Planning Analysis performed in Requirement R1. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - "within" is not clear. This is a plan to not exceed an IROL. | Yes | Yes | Yes | Yes | 3 | 11 | Medium |  | High | Medium
TOP-002-3 | TOP-002-3 | R3. | Operations Planning | To ensure that Transmission Operators have plans for operating within specified limits. | Each Transmission Operator shall notify all NERC registered entities identified in the plan(s) cited in Requirement R2 as to their role in those plan(s). | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | No - see comments | Yes | Yes | Yes | Yes | Yes | No - see comments | Yes | Yes | Yes | Yes | 3 | 10 | Medium |  | High | Medium
TOP-003-1 | TOP-003-1 | R1. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Generator Operators and Transmission Operators shall provide planned outage information. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | No - doesn't cover all timeframes. Specificity of the requirement is not in sync with how industry operates. | Yes | No - b/c current standard has a list of prescriptive procedures associated with the data that is incomplete; it doesn't match the norm of industry operations. This std includes processes where the new version is data only; need to look at Boardh the process std as well (TOP-002 and TOP-003) It needs to be the what, not the how. The current std has too many hows. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | No Individual VRF Assigned -Pending |  |  |  | GOP | [12 empty] | TOP
TOP-003-1 | TOP-003-1 | R1.1. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - doesn't cover all timeframes. Specificity of the requirement is not in sync with how industry operates. | Yes | No - b/c current standard has a list of prescriptive procedures associated with the data that is incomplete; it doesn't match the norm of industry operations. This std includes processes where the new version is data only; need to look at Boardh the process std as well (TOP-002 and TOP-003) It needs to be the what, not the how. The current std has too many hows. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | Medium - Pending |  |  |  | GOP | [12 empty] | TOP
TOP-003-1 | TOP-003-1 | R1.2. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - doesn't cover all timeframes. Specificity of the requirement is not in sync with how industry operates. | Yes | No b/c current standard has a list of prescriptive procedures associated with the data that is incomplete; it doesn't match the norm of industry operations. This std includes processes where the new version is data only; need to look at Boardh the process std as well (TOP-002 and TOP-003) It needs to be the what, not the how. The current std has too many hows. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 11 | High |  | High | Medium - Pending | [16 empty] | TOP
TOP-003-1 | TOP-003-1 | R1.3. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - doesn't cover all timeframes. Specificity of the requirement is not in sync with how industry operates. | Yes | No - b/c current standard has a list of prescriptive procedures associated with the data that is incomplete; it doesn't match the norm of industry operations. This std includes processes where the new version is data only; need to look at Boardh the process std as well (TOP-002 and TOP-003) It needs to be the what, not the how. The current std has too many hows. | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 10 | High |  | Medium | Medium - Pending |  |  |  | GOP | [12 empty] | TOP
TOP-003-1 | TOP-003-1 | R2. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | Yes | Yes | Yes - but language is vague due to being legacy language (i.e., "etc") | Yes | Yes | Yes | No | Yes | No | No | Yes | No | No | No | No | Yes | Yes | 3 | 5 | High |  | High | Medium - Pending | BA |  |  | GOP | [12 empty] | TOP
TOP-003-1 | TOP-003-1 | R3. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | Yes | Yes | Yes - but language is vague due to being legacy language (i.e., "etc") | No -consider consolidating with COM-001 | Yes | Yes | No | Yes | No | No | Yes | No | No | No | No | Yes | Yes | 3 | 4 | High |  | High | Medium - Pending | BA |  |  | GOP | [12 empty] | TOP
TOP-003-1 | TOP-003-1 | R4. | Planned Outage Coordination | Scheduled generator and transmission outages that may affect the reliability of interconnected operations must be planned and coordinated among Balancing Authorities, Transmission Operators, and Reliability Coordinators. | Each Reliability Coordinator shall resolve any scheduling of potential reliability conflicts. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | Yes - duplicative with IRO-009 (or the proposed authority std) and is legacy language | [19 empty] | No | 0 | 0 | High |  | N/A | Medium - Pending | [10 empty] | RC
TOP-003-2 | TOP-003-2 | R1. | Operational Reliability Data | To ensure that the Transmission Operator and Balancing Authority have the data needed to fulfill their operational planning and Real-time monitoring responsibilities. | Each Transmission Operator shall create a documented specification for the data necessary for it to perform its Operational Planning Analyses and Real-time monitoring. The specification shall include: [See Standard pdf for further information] | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - does not address level of accuracy required; see if this is provided elsewhere (i.e. project 2009-02) | Yes | Yes | No -consolidate R1 and R2 at minimum; at max consolidate with RC (IRO-010-1a R1) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | Low | Lower
TOP-003-2 | TOP-003-2 | R2. | Operational Reliability Data | To ensure that the Transmission Operator and Balancing Authority have the data needed to fulfill their operational planning and Real-time monitoring responsibilities. | Each Balancing Authority shall create a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The specification shall include: [See Standard pdf for further information] | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | No - does not address level of accuracy required; see if this is provided elsewhere (i.e. project 2009-02) | Yes | Yes | No -consolidate R1 and R2 at minimum; at max consolidate with RC (IRO-010-1a R1) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | Low | Lower
TOP-003-2 | TOP-003-2 | R3. | Operational Reliability Data | To ensure that the Transmission Operator and Balancing Authority have the data needed to fulfill their operational planning and Real-time monitoring responsibilities. | Each Transmission Operator shall distribute its data specification, as developed in Requirement R1,to entities that have data required by the Transmission Operator’s Operational Planning Analysis and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No -consolidate R3 and R4 at minimum; at max consolidate with RC (IRO-010-1a R2) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | Low | Lower
TOP-003-2 | TOP-003-2 | R4. | Operational Reliability Data | To ensure that the Transmission Operator and Balancing Authority have the data needed to fulfill their operational planning and Real-time monitoring responsibilities. | Each Balancing Authority shall distribute its data specification, as developed in Requirement R2, to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring process used in meeting its NERC-mandated reliability requirements. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No -consolidate R3 and R4 at minimum; at max consolidate with RC (IRO-010-1a R2) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | Low | Lower
TOP-003-2 | TOP-003-2 | R5. | Operational Reliability Data | To ensure that the Transmission Operator and Balancing Authority have the data needed to fulfill their operational planning and Real-time monitoring responsibilities. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | Board Adopted | Board adopted 5/9/2012 and endorsed for filing with FERC 2/7/2013. This standard has not yet been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes | Yes | No -consolidate IRO-010-1a R3 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | High | Medium
TOP-004-2 | TOP-004-2 | R1. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Each Transmission Operator shall operate within the Interconnection Reliability Operating Limits (IROLs) and System Operating Limits (SOLs). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - does not include the concept of Tv | Yes | No - does not include the concept of Tv - however, the word "within" is not clear "will operate so as not to exceed" is better | No -consolidate with other stds that include the Tv concept | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | 1 | 9 | High |  | High | High | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R2. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - inadequate protection for reliability of the BPS | Yes | No - the bar is too low. It is also incomplete. No allowance for timeframe to recover from a contingency | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 7 | High |  | High | High | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R3. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Each Transmission Operator shall operate to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | No - the language is not clear as to the expectation, so can't tell | Yes | No - the language is not clear as to the expectation, so can't tell | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | 1 | 6 | High |  | High | High | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R4. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | If a Transmission Operator enters an unknown operating state (i.e. any state for which valid operating limits have not been determined), it will be considered to be in an emergency and shall restore operations to respect proven reliable power system limits within 30 minutes. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | Yes | No - RC should be included? | Yes | Yes | Yes | Yes | No - the language is not clear "proven reliable power system limits", "respect", etc for "unknown", suggest "unstudied" or "unanalyzed" | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | High |  | High | High | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R5. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Each Transmission Operator shall make every effort to remain connected to the Interconnection. If the Transmission Operator determines that by remaining interconnected, it is in imminent danger of violating an IROL or SOL, the Transmission Operator may take such actions, as it deems necessary, to protect its area. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  | This requirement does not consider the role of the RC in making the wide area view decisions related to one TOP separating from the interconnection. This requirement needs to be rewritten to meet the current functional model role and responsibilities of the RC and TOP. |  |  |  | Yes - #1 | No | No |  |  | No - requirement as written does not consider the role of the RC in making the wide area decision | No - RC must be included | No -RC's role must be included | No -consolidate into the IRO standards | No | Yes | No | No | Yes | No | No | Yes | No | No | Yes | Yes | Yes | 0 | 4 | High |  | High | High | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R6. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Transmission Operators, individually and jointly with other Transmission Operators, shall develop, maintain, and implement formal policies and procedures to provide for transmission reliability. These policies and procedures shall address the execution and coordination of activities that impact inter- and intra-Regional reliability, including: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R6.1. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Monitoring and controlling voltage levels and real and reactive power flows. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R6.2. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Switching transmission elements. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R6.3. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Planned outages of transmission elements. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
TOP-004-2 | TOP-004-2 | R6.4. | Transmission Operations | To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. | Responding to IROL and SOL violations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
TOP-005-2 | TOP-005-2a | R1. | Operational Reliability Information | To ensure reliability entities have the operating data needed to monitor system conditions within their areas. | As a condition of receiving data from the Interregional Security Network (ISN), each ISN data recipient shall sign the NERC Confidentiality Agreement for “Electric System Reliability Data.” | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | No | Yes - legacy language that is out of date. | [19 empty] | No | 0 | 0 | High |  | N/A | Pending | BA | [15 empty] | TOP
TOP-005-2 | TOP-005-2a | R2. | Operational Reliability Information | To ensure reliability entities have the operating data needed to monitor system conditions within their areas. | Upon request, each Balancing Authority and Transmission Operator shall provide to other Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability, the operating data that are necessary to allow these Balancing Authorities and Transmission Operators to perform operational reliability assessments and to coordinate reliable operations. Balancing Authorities and Transmission Operators shall provide the types of data as listed in Attachment 1-TOP-005 “Electric System Reliability Data,” unless otherwise agreed to by the Balancing Authorities and Transmission Operators with immediate responsibility for operational reliability. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #3 | No | No |  |  | Yes | Yes - RC is addressed in the IRO-010 std | Yes | Yes - considering combining with the RC role (see IRO-010) | Yes | Yes | No - language "immediate responsibility", etc. The language in IRO-010 is better | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 8 | High |  | Medium | Pending | BA | [15 empty] | TOP
TOP-005-2 | TOP-005-2a | R3. | Operational Reliability Information | To ensure reliability entities have the operating data needed to monitor system conditions within their areas. | Each Purchasing-Selling Entity shall provide information as requested by its Host Balancing Authorities and Transmission Operators to enable them to conduct operational reliability assessments and coordinate reliable operations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes and TOP-005-2 |  | Yes - #3 | No | No |  |  | Yes | Yes - RC is addressed in the IRO-010 std | Yes | Yes - considering combining with the RC role (see IRO-010) | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 9 | High |  | Medium | Pending | [9 empty] | PSE
TOP-006-2 | TOP-006-2 | R1. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Transmission Operator and Balancing Authority shall know the status of all generation and transmission resources available for use. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium - Pending | BA |  |  | GOP | [12 empty] | TOP
TOP-006-2 | TOP-006-2 | R1.1. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium - Pending |  |  |  | GOP
TOP-006-2 | TOP-006-2 | R1.2. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium - Pending | BA | [15 empty] | TOP
TOP-006-2 | TOP-006-2 | R2. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #1, 3 | No | No |  |  | Yes - probably too much, but the limiting word "applicable" is too vague | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 5 | Medium/High |  | High | High - Pending | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-2 | TOP-006-2 | R3. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall provide appropriate technical information concerning protective relays to their operating personnel. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative with PRC-001-2 | [19 empty] | No | 0 | 0 | Medium/High |  | N/A | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-2 | TOP-006-2 | R4. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Transmission Operator, and Balancing Authority shall have information, including weather forecasts and past load patterns, available to predict the system’s near-term load pattern. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | Yes | No - RC needs to be included | Yes | Yes | Yes | Yes | No - "near term" is not clear or measurable | Yes | Yes | No - "near term" is not clear or measurable | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | Medium/High |  | High | Medium - Pending | BA | [15 empty] | TOP
TOP-006-2 | TOP-006-2 | R5. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | Yes - out of date with today's control rooms and how entity's alarm | [19 empty] | No | 0 | 0 | Medium/High |  | N/A | Medium - Pending | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-2 | TOP-006-2 | R6. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Balancing Authority and Transmission Operator shall use sufficient metering of suitable range, accuracy and sampling rate (if applicable) to ensure accurate and timely monitoring of operating conditions under Boardh normal and emergency situations. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | Yes | [18 empty] | No | 0 | 0 | Medium/High |  | N/A | High - Pending | BA | [15 empty] | TOP
TOP-006-2 | TOP-006-2 | R7. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall monitor system frequency. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative of the BAL(-001, -003) stds | [19 empty] | No | 0 | 0 | Medium/High |  | N/A | High - Pending | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-3 | TOP-006-3 | R1. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium | BA | [15 empty] | TOP
TOP-006-3 | TOP-006-3 | R1.1. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium |  |  |  | GOP
TOP-006-3 | TOP-006-3 | R1.2. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium | [16 empty] | TOP
TOP-006-3 | TOP-006-3 | R1.3. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | No | No |  |  | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | No - phrase "available for use" is not clear as to whether some assets are excluded. The term "all" and "transmission resources" are not clear - there are specific assets that the TOP needs to know. | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | No | No | Yes | Yes | Yes | 1 | 8 | Medium/High |  | High | Medium | BA
TOP-006-3 | TOP-006-3 | R2. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes - #1, 3 | No | No |  |  | Yes - probably too much, but the limiting word "applicable" is too vague | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 3 | 7 | Medium/High |  | High | High | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-3 | TOP-006-3 | R3. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | No | No |  |  | Yes | Yes | Yes | Yes - consider combining with PRC-001-2 R1 | Yes | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | Medium/High |  | High | Medium | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-3 | TOP-006-3 | R4. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes - #3 | No | No |  |  | Yes | No - RC needs to be included | Yes | Yes | Yes | Yes | No - "near term" is not clear or measurable | Yes | Yes | No - "near term" is not clear or measurable | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 8 | Medium/High |  | High | Medium | BA | [15 empty] | TOP
TOP-006-3 | TOP-006-3 | R5. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes - #3 | Yes - out of date with today's control rooms and how entity's alarm | [19 empty] | No | 0 | 0 | Medium/High |  | N/A | Medium | BA | [9 empty] | RC | [5 empty] | TOP
TOP-006-3 | TOP-006-3 | R6. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes - #3 | No | Yes | [18 empty] | No | 0 | 0 | Medium/High |  | N/A | High | BA | [15 empty] | TOP
TOP-006-3 | TOP-006-3 | R7. | Monitoring System Conditions | To ensure critical reliability parameters are monitored in real-time. |  | Board adopted, but overtaken by future version | Pending interpretation that was conducted as a rapid revision project. This standard will be retired when TOP-001-2, TOP-002-3 and TOP-003-2 become enforceable. |  | Look at IRO standards (IRO-001-3 and IRO-005-4) and MOD-025-2. Possible authority standard |  |  |  | Yes | Yes - duplicative of the BAL stds | [18 empty] | Yes | No | 0 | 0 | Medium/High |  | N/A | High | BA | [9 empty] | RC | [5 empty] | TOP
TOP-007-0 | TOP-007-0 | R1. | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | This standard ensures SOL and IROL violations are being reported to the Reliability Coordinator so that the Reliability Coordinator may evaluate actions being taken and direct additional corrective actions as needed. | A Transmission Operator shall inform its Reliability Coordinator when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Not ranked |  | High | High | [16 empty] | TOP
TOP-007-0 | TOP-007-0 | R2. | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | This standard ensures SOL and IROL violations are being reported to the Reliability Coordinator so that the Reliability Coordinator may evaluate actions being taken and direct additional corrective actions as needed. | Following a Contingency or other event that results in an IROL violation, the Transmission Operator shall return its transmission system to within IROL as soon as possible, but not longer than 30 minutes. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | No | No |  |  | Yes | Yes | Yes - however, the word "within" is not clear "does not exceed" is better | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Not ranked |  | High | High | [16 empty] | TOP
TOP-007-0 | TOP-007-0 | R3. | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | This standard ensures SOL and IROL violations are being reported to the Reliability Coordinator so that the Reliability Coordinator may evaluate actions being taken and direct additional corrective actions as needed. | A Transmission Operator shall take all appropriate actions up to and including shedding firm load, or directing the shedding of firm load, in order to comply with Requirement R 2. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative with EOP stds | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | High | [16 empty] | TOP
TOP-007-0 | TOP-007-0 | R4. | Reporting System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) Violations | This standard ensures SOL and IROL violations are being reported to the Reliability Coordinator so that the Reliability Coordinator may evaluate actions being taken and direct additional corrective actions as needed. | The Reliability Coordinator shall evaluate actions taken to address an IROL or SOL violation and, if the actions taken are not appropriate or sufficient, direct actions required to return the system to within limits. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative of IRO-009 | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | High | [10 empty] | RC
TOP-007-WECC-1 | TOP-007-WECC-1 | R2. | System Operating Limits | When actual flows on Major WECC Transfer Paths exceed System Operating Limits (SOL), their associated schedules and actual flows are not exceeded for longer than a specified time. | The Transmission Operator shall not have the Net Scheduled Interchange for power flow over an interconnection or Transmission path above the path’s SOL when the Transmission Operator implements its real-time schedules for the next hour. For paths internal to a Transmission Operator Area that are not scheduled, this requirement does not apply. [Time Horizon: Real-time Operations] | Regional | [30 empty] | Not ranked |  |  | Lower - Pending | [16 empty] | TOP
TOP-007-WECC-1 | TOP-007-WECC-1 | R1. | System Operating Limits | When actual flows on Major WECC Transfer Paths exceed System Operating Limits (SOL), their associated schedules and actual flows are not exceeded for longer than a specified time. | When the actual power flow exceeds an SOL for a Transmission path, the Transmission Operators shall take immediate action to reduce the actual power flow across the path such that at no time shall the power flow for the Transmission path exceed the SOL for more than 30 minutes. [Time Horizon: Real-time Operations] | Regional | [30 empty] | Not ranked |  |  | Medium - Pending | [16 empty] | TOP
TOP-007-WECC-1 | TOP-007-WECC-1 | R2.1. | System Operating Limits | When actual flows on Major WECC Transfer Paths exceed System Operating Limits (SOL), their associated schedules and actual flows are not exceeded for longer than a specified time. | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. | Regional | [30 empty] | Not ranked |  |  | No Individual VRF Assigned -Pending | [16 empty] | TOP
TOP-008-1 | TOP-008-1 | R1. | Response to Transmission Limit Violations | To ensure Transmission Operators take actions to mitigate SOL and IROL violations. | The Transmission Operator experiencing or contributing to an IROL or SOL violation shall take immediate steps to relieve the condition, which may include shedding firm load. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - duplicative of EOP-003-1 and TOP-007-0 | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | High | [16 empty] | TOP
TOP-008-1 | TOP-008-1 | R2. | Response to Transmission Limit Violations | To ensure Transmission Operators take actions to mitigate SOL and IROL violations. | Each Transmission Operator shall operate to prevent the likelihood that a disturbance, action, or inaction will result in an IROL or SOL violation in its area or another area of the Interconnection. In instances where there is a difference in derived operating limits, the Transmission Operator shall always operate the Bulk Electric System to the most limiting parameter. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | No - "limiting parameter" is not clear. | No - wide area view is an RC role | No - the TOP is not generally going to be able to see more than 3 buses into the neighboring system (what is neighboring?) | Yes | No | Yes | No - ambiguous terms, see content and functional entity issues | Yes | Yes | No - not clear | Yes | Yes | No | No | Yes | Yes | Yes | 0 | 7 | Not ranked |  | High | Medium | [16 empty] | TOP
TOP-008-1 | TOP-008-1 | R3. | Response to Transmission Limit Violations | To ensure Transmission Operators take actions to mitigate SOL and IROL violations. | The Transmission Operator shall disconnect the affected facility if the overload on a transmission facility or abnormal voltage or reactive condition persists and equipment is endangered. In doing so, the Transmission Operator shall notify its Reliability Coordinator and all neighboring Transmission Operators impacted by the disconnection prior to switching, if time permits, otherwise, immediately thereafter. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. | [5 empty] | Yes | Yes - legacy language that adds little to the protection of the BPS. The language is not actionable. | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | High | [16 empty] | TOP
TOP-008-1 | TOP-008-1 | R4. | Response to Transmission Limit Violations | To ensure Transmission Operators take actions to mitigate SOL and IROL violations. | The Transmission Operator shall have sufficient information and analysis tools to determine the cause(s) of SOL violations. This analysis shall be conducted in all operating timeframes. The Transmission Operator shall use the results of these analyses to immediately mitigate the SOL violation. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TOP-001-2, TOP-002-3 and TOP-003-2 when FERC approves. TOP-001-2, TOP-002-3 and TOP-003-2 were Board adopted on 5/9/2012; it has not been filed with FERC. |  |  |  | Yes |  | Yes - #3 | No | No |  |  | No - "sufficient information and analysis tools" is vague; needs greater clarity | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | 2 | 7 | Not ranked |  | High | Medium | [16 empty] | TOP
TPL-001-0 | TPL-001-0.1 | R1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.4. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.5. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.6. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.7. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.8. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.3.9. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R1.4. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2.1.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2.1.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2.1.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R2.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-001-0 | TPL-001-0.1 | R3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-001-3 if FERC approves. Board adopted TPL-001-4 and TPL-001-3 on 2/7/2013. These standards were filed with FERC on 2/28/2013. |  |  |  | Yes for TPL-001-0 | [25 empty] | High |  | Not rated | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-2 | TPL-001-2 | R1. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R2. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R3. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R4. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R5. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R6. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R7. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-2 | TPL-001-2 | R8. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board adopted, but overtaken by future version | Board adopted 8/4/2011; Filed with FERC 10/19/2011 | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.4. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.5. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.6. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.7. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.3.8. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R1.4. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2.1.1. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2.1.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2.1.3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R2.2. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-3 | TPL-001-3 | R3. | System Performance Under Normal (No Contingency) Conditions (Category A) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted 2/7/2013; not yet filed with FERC | [29 empty] | High
TPL-001-4 | TPL-001-4 | R1. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 | [5 empty] | Yes - #3 |  | Yes | [17 empty] | Yes | No | 0 | 0 | High |  | N/A | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R2. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 |  | Consider making this requirement more concise and include performance levels (currently in the table). This requirement is very prescriptive and focuses on the "how" rather than the "what". Conduct transmission planning studies to determine performance levels for expected system conditions. |  |  |  | Yes - #3 | No | No |  |  | No, In addition creating models under MOD-010 and -012, TPs and RCs should perform sensitivity analyses to understand the effect of changes to the models as described R2.1 This is much too prescriptive and describes industry best practice. A lot of detail was added so there would be clarity for compliance assessment. | Yes | Yes | Yes | Yes | Yes | No - has the word "annually", but otherwise, yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R3. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 |  | Consider making this requirement more concise and include performance levels (currently in the table). This requirement is very prescriptive and focuses on the "how" rather than the "what". Conduct transmission planning studies to determine performance levels for expected system conditions. |  |  |  | Yes - #3 | No | No |  |  | No, In addition creating models under MOD-010 and -012, TPs and RCs should perform sensitivity analyses to understand the effect of changes to the models as described R2.1 This is much too prescriptive and describes industry best practice. A lot of detail was added so there would be clarity for compliance assessment. | Yes | Yes | Yes | Yes | Yes | No - has the word "annually", but otherwise, yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R4. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 |  | Consider making this requirement more concise and include performance levels (currently in the table). This requirement is very prescriptive and focuses on the "how" rather than the "what". Conduct transmission planning studies to determine performance levels for expected system conditions. |  |  |  | Yes - #3 | No | No |  |  | No, In addition creating models under MOD-010 and -012, TPs and RCs should perform sensitivity analyses to understand the effect of changes to the models as described R2.1 This is much too prescriptive and describes industry best practice. A lot of detail was added so there would be clarity for compliance assessment. | Yes | Yes | Yes | Yes | Yes | No - has the word "annually", but otherwise, yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 11 | High |  | High | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R5. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 | [5 empty] | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R6. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 | [5 empty] | Yes - #1, 2 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | Medium | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R7. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 | [5 empty] | Yes | Yes - administrative | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | [8 empty] | PA | PC | [8 empty] | TP
TPL-001-4 | TPL-001-4 | R8. | Transmission System Planning Performance Requirements | Establish Transmission system planning performance requirements within the planning horizon to develop a Bulk Electric System (BES) that will operate reliably over a broad spectrum of System conditions and following a wide range of probable Contingencies. |  | Board Adopted | Board adopted 2/7/2013; filed with FERC 2/28/2013 | [5 empty] | Yes | No - but see comment for what is thought to be the intent of the standard | No |  |  | No - the standard should focus on coordination of studies between adjacents and addressing discrepancies. As written, it is an administrative requirement. | Yes | No - see "gap" comments | Yes | Yes | Yes | Yes | No - see gap | No - see gap | Yes | No - see gap | Yes | Yes | Yes | Yes | Yes | Yes | 1 | 9 | High |  | Low | [8 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the Network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category B of Table I. To be valid, the Planning Authority and Transmission Planner assessments shall: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | High | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be made annually. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.10. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned protection systems, including any backup or redundant systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.11. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned control devices. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.12. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be conducted annually unless changes to system conditions do not warrant such analyses. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.4. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.5. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Have all projected firm transfers modeled. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.6. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Be performed and evaluated for selected demand levels over the range of forecast system Demands. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.7. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Demonstrate that system performance meets Category B contingencies. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.8. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Include existing and planned facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.3.9. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.4. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R1.5. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Consider all contingencies applicable to Category B. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-002-0_R1, the Planning Authority and Transmission Planner shall each: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2.1.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Including a schedule for implementation. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2.1.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Including a discussion of expected required in-service dates of facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2.1.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Consider lead times necessary to implement plans. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R2.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-0 | TPL-002-0b | R3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each document the results of its Reliability Assessments and corrective plans and shall annually provide the results to its respective Regional Reliability Organization(s), as required by the Regional Reliability Organization. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced with TPL-001-4 or TPL-002-2b if FERC approves. Board adopted TPL-002-2b and TPL-001-4 on 2/7/2013. These standards were filed with FERC on 2/28/2013. |  |  |  | Yes | [25 empty] | High |  | Not rated | Lower | [7 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.10. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.11. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.12. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.4. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.5. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.6. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.7. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.8. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.3.9. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.4. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R1.5. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2.1.1. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2.1.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2.1.3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R2.2. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-002-2 | TPL-002-2b | R3. | System Performance Following Loss of a Single Bulk Electric System Element (Category B) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements with sufficient lead time, and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013; filed with FERC 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission systems is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand Levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached). The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard. To be valid, the Planning Authority and Transmission Planner assessments shall: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | High | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be made annually. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.10. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned protection systems, including any backup or redundant systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.11. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned control devices. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.12. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be conducted annually unless changes to system conditions do not warrant such analyses. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.4. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.5. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Have all projected firm transfers modeled. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.6. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be performed and evaluated for selected demand levels over the range of forecast system demands. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.7. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Demonstrate that System performance meets Table 1 for Category C contingencies. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.8. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include existing and planned facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.3.9. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.4. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Address any planned upgrades needed to meet the performance requirements of Category C. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R1.5. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Consider all contingencies applicable to Category C. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | When system simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2.1.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Including a schedule for implementation. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2.1.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Including a discussion of expected required in-service dates of facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2.1.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Consider lead times necessary to implement plans. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R2.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0a | R3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replaced by TPL-003-2b or TPL-001-4 if FERC approves. TPL-003-2b and TPL-001-4 were adopted by the Board on 2/7/2013 and filed with FERC on 2/28/2013. |  |  |  | Yes | [25 empty] | High |  | Not rated | Lower | [7 empty] | PA | PC | [8 empty] | TP
TPL-003-0 | TPL-003-0b | all | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was filed with FERC on 4/12/2013. | [29 empty] | High
TPL-003-2 | TPL-003-2a | all | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Filed with FERC on 2/28/2013. | [29 empty] | High
TPL-003-2 | TPL-003-2b | R1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.10. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.11. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.12. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.4. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.5. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.6. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.7. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.8. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.3.9. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.4. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R1.5. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2.1.1. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2.1.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2.1.3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R2.2. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-003-2 | TPL-003-2b | R3. | System Performance Following Loss of Two or More Bulk Electric System Elements (Category C) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | This interpretation was Board adopted 2/7/2013; filed with FERC 4/12/2013 | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I. To be valid, the Planning Authority’s and Transmission Planner’s assessment shall: | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  | Not rated | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be made annually. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be conducted for near-term (years one through five). | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Cover critical system conditions and study years as deemed appropriate by the responsible entity. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.3. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Be conducted annually unless changes to system conditions do not warrant such analyses. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.4. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Have all projected firm transfers modeled. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.5. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include existing and planned facilities. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.6. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.7. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned protection systems, including any backup or redundant systems. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.8. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the effects of existing and planned control devices. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.3.9. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R1.4. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | Consider all contingencies applicable to Category D. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. | [29 empty] | High |  |  | Medium | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-0 | TPL-004-0 | R2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen | The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization. | Current - will be replaced by Board adopted std | Currently enforceable standard. It will be replaced with TPL-004-2a or TPL-001-4 if FERC approves. The Board adopted TPL-004-2a and TPL-001-4 on 2/7/2013; these standards were filed with FERC on 2/28/2013. |  |  |  | Yes | [25 empty] | High |  | Not rated | Lower | [7 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.1. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.3. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.4. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.5. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.6. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.7. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.8. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.3.9. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R1.4. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-004-2 | TPL-004-2a | R2. | System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Elements (Category D) | System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet presen |  | Board adopted, but overtaken by future version | Board adopted on 2/7/2013 and it was filed with FERC on 2/28/2013. | [29 empty] | High | [10 empty] | PA | PC | [8 empty] | TP
TPL-005-0 | TPL-005-0 | R1. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.1. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.1.1. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.1.2. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.1.3. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.2. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.3. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R1.4. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R2. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.1. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.2. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.3. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.4. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.5. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-005-0 | TPL-005-0 | R3.6. | Regional and Interregional Self-Assessment Reliability Reports | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.1. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.2. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.3. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.4. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.5. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.6. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-0 | TPL-006-0 | R1.7. | Data From the Regional Reliability Organization Needed to Assess Reliability | To ensure that each Regional Reliability Organization complies with planning criteria, for assessing the overall reliability (Adequacy and Security) of the interconnected Bulk Electric Systems, Boardh existing and as planned. |  | Not approved in Order 693 | This standard was not approved by FERC in Order 693. | [29 empty] | Not ranked | [16 empty] | RRO
TPL-006-1 | TPL-006-1 | all |  |  |  | Not approved in Order 693 - not filed future version | This standard has not been filed with FERC as the -0 standard has not been approved. | [29 empty] | Not ranked
VAR-001-2 | VAR-001-2 | R1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 | [5 empty] | Yes - #1 | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - what does "formal" mean? | Yes | Yes | No - what does "formal" mean? | Yes | Yes | No - what does "formal" mean? | No - what does "formal" mean? | Yes | Yes | Yes | 3 | 8 | High |  | High | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R2. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #2 | No - this is a "what" | No |  |  | No - too much and items are missing. Redraft to state: Each TOP shall acquire sufficient reactive resources to protect the voltage levels under normal and contingency conditions. | Yes | Yes - see gap comment | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R3. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | No | No |  |  | No - delete the phrase "and Requirement 6.1" | Yes | Yes | No - but combine 3 and 3.1 | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | Low | Lower | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R3.1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | Yes | No - but combine 3 and 3.1 | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | High |  | Low | Lower | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R3.2. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | No | [19 empty] | No |  | 0 | 0 | High |  | N/A | Lower | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R4. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1, 3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R5. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. |  |  | Yes | Yes |  | Yes - #1 | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [5 empty] | LSE |  |  |  | PSE
VAR-001-2 | VAR-001-2 | R6. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - TOP and other stds require you to have info to operate the system | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R6.1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R7. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - duplicative of R2 of this std and the TOP 001 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R8. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - duplicative in same senses as R7 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R9. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - duplicative with R2 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R9.1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - duplicative with R2 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R10. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. |  |  |  | Yes |  | Yes - #1 | Yes - duplicative of TOP-001-2 (newly filed) R7, R8, R9 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R11. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - covered under interconnection studies | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [16 empty] | TOP
VAR-001-2 | VAR-001-2 | R12. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | Current - will be replaced by Board adopted std | Currently enforceable standard. Will be replace by VAR-001-3 if FERC approves. VAR-001-3 was adopted by the Board 5/9/2012 and filed with FERC 2/25/2013. | [5 empty] | Yes - #1 | Yes - covered under EOP, PRC-006 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator, individually and jointly with other Transmission Operators, shall ensure that formal policies and procedures are developed, maintained, and implemented for monitoring and controlling voltage levels and Mvar flows within their individual areas and with the areas of neighboring Transmission Operators. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | No | No |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - what does "formal" mean? | Yes | Yes | No - what does "formal" mean? | Yes | Yes | No - what does "formal" mean? | No - what does "formal" mean? | Yes | Yes | Yes | 3 | 8 | High |  | High | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R2. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall acquire sufficient reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load – within its area to protect the voltage levels under normal and Contingency conditions. This includes the Transmission Operator’s share of the reactive requirements of interconnecting transmission circuits. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #2 | No - this is a "what" | No |  |  | No - too much and items are missing. Redraft to state: Each TOP shall acquire sufficient reactive resources to protect the voltage levels under normal and contingency conditions. | Yes | Yes - see gap comment | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 12 | High |  | High | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R3. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall specify criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | yes - #1 | No | No |  |  | No - delete the phrase "and Requirement 6.1" | Yes | Yes | No - but combine 3 and 3.1 | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | Low | Lower | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R3.1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | [5 empty] | yes - #1 | No | No |  |  | No - delete the phrase "and Requirement 6.1" | Yes | Yes | No - but combine 3 and 3.1 | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | Low | Lower | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R3.2. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | [5 empty] | Yes - #1 | No | No |  |  | No - delete the phrase "and Requirement 6.1" | Yes | Yes | No - but combine 3 and 3.1 | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 10 | High |  | Low | Lower | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R4. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. The Transmission Operator shall provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1, 3 | No | No |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | High |  | High | Medium | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R5. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Purchasing-Selling Entity and Load Serving Entity shall arrange for (self-provide or purchase) reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to satisfy its reactive requirements identified by its Transmission Service Provider. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  | Team determined that there are situations with the various Interconnections where the PSE does perform this role | Yes - #1 | Yes | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [5 empty] | LSE |  |  |  | PSE
VAR-001-3 | VAR-001-3 | R6. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - TOP and other stds requires an entity to have info to operate the system | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Medium | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R6.1 | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | [29 empty] | High
VAR-001-3 | VAR-001-3 | R7. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall be able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - duplicative of R2 of this std and the TOP 001 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R8. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall operate or direct the operation of capacitive and inductive reactive resources within its area – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching; controllable load; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - duplicative in same senses as R7 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R9. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall maintain reactive resources – which may include, but is not limited to, reactive generation scheduling; transmission line and reactive resource switching;, and controllable load– to support its voltage under first Contingency conditions. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - duplicative with R2 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R9.1. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | [5 empty] | Yes - #1 | Yes - duplicative with R2 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R10. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | Each Transmission Operator shall correct IROL or SOL violations resulting from reactive resource deficiencies (IROL violations must be corrected within 30 minutes) and complete the required IROL or SOL violation reporting. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - duplicative of TOP-001-2 (newly filed) R7, R8, R9 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R11. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - covered under interconnection studies | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | Lower | [16 empty] | TOP
VAR-001-3 | VAR-001-3 | R12. | Voltage and Reactive Control | To ensure that voltage levels, reactive flows, and reactive resources are monitored, controlled, and maintained within limits in real time to protect equipment and the reliable operation of the Interconnection. | The Transmission Operator shall direct corrective action, including load reduction, necessary to prevent voltage collapse when reactive resources are insufficient. | Board Adopted | Board adopted 5/9/2012 and filed with FERC on 2/25/2013. | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | Yes - covered under EOP, PRC-006 | [18 empty] | Yes | No | 0 | 0 | High |  | N/A | High | [16 empty] | TOP
VAR-002-1 | VAR-002-1.1b | R2.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Medium |  |  |  | GOP
VAR-002-1 | VAR-002-1.1b | R2.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Medium |  |  |  | GOP
VAR-002-1 | VAR-002-1.1b | R3.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Medium |  |  |  | GOP
VAR-002-1 | VAR-002-1.1b | R3.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Medium |  |  |  | GOP
VAR-002-1 | VAR-002-1.1b | R4.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  | GO
VAR-002-1 | VAR-002-1.1b | R4.1.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Tap settings. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  | GO
VAR-002-1 | VAR-002-1.1b | R4.1.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Available fixed tap ranges. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  | GO
VAR-002-1 | VAR-002-1.1b | R4.1.3. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Impedance data. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  | GO
VAR-002-1 | VAR-002-1.1b | R4.1.4. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | The +/- voltage range with step-change in % for load-tap changing transformers. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  | GO
VAR-002-1 | VAR-002-1.1b | R5.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. | Current - will be replaced by FERC approved std | Currently enforceable standard. Will be replaced by VAR-002-2; VAR-002-2 was Board adopted 8/16/2012; FERC approved on April 16, 2013 | [29 empty] | Not ranked |  |  | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage) unless the Generator Operator has notified the Transmission Operator of one of the following: -That the generator is being operated in start-up or shutdown mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or -That the generator is not being operated in the automatic voltage control mode for a reason other than start-up or shutdown. | Current | Board adopted 8/16/2012; filed with FERC 11/21/2012 | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | No | No |  |  | No - synchronous condensors should be included | Yes | No - exemption for certain generators as in R2 should also be included in R1 | Yes | Yes | Yes | No - time for notification not clear (one time blanket notification or each time/day?) Should be done each time there is a request to parallel. Second bullet tries to provide for exemptions | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | No - time for notification | No | Yes | Yes | Yes | 1 | 8 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings) as directed by the Transmission Operator. | Current | Board adopted 8/16/2012; filed with FERC 11/21/2012 | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1 | No | No |  |  | No - what should a GOP do if they can't maintain the reactive power schedule? 2.2 doesn't get at what a GOP should do if unable to "maintain" - it gets at if the GOP can't go above or below schedule when asked. | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R2.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #1 | No | No |  |  | No - what should a GOP do if they can't maintain the reactive power schedule? 2.2 doesn't get at what a GOP should do if unable to "maintain" - it gets at if the GOP can't go above or below schedule when asked. | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R2.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #1 | No | No |  |  | No - what should a GOP do if they can't maintain the reactive power schedule? 2.2 doesn't get at what a GOP should do if unable to "maintain" - it gets at if the GOP can't go above or below schedule when asked. | Yes | Yes | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R3. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Each Generator Operator shall notify its associated Transmission Operator as soon as practical, but within 30 minutes of any of the following: | Current | Board adopted 8/16/2012; filed with FERC 11/21/2012 | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  | Yes |  | Yes - #1 | No | No |  |  | Yes | Yes | No - exemption for certain generators being required to have an AVR applies here as it does in R1 | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R3.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | No - exemption for certain generators being required to have an AVR applies here as it does in R1 | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R3.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #1 | No | No |  |  | Yes | Yes | No - exemption for certain generators being required to have an AVR applies here as it does in R1 | Yes | Yes for content; No for format | Yes | Yes | Yes | Yes | Yes | Yes | No - needs to refer to VAR-001 for exceptions | Yes | Yes | Yes | Yes | Yes | 2 | 11 | Not ranked |  | Medium | Medium |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. | Current | Board adopted 8/16/2012; filed with FERC 11/21/2012 | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4.1.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Tap settings. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4.1.2. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Available fixed tap ranges. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4.1.3. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | Impedance data. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R4.1.4. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | The +/- voltage range with step-change in % for load-tap changing transformers. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #3 | Yes - covered in MODs | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Lower |  |  |  | GOP
VAR-002-2 | VAR-002-2b | R5. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. | Current | Board adopted 8/16/2012; filed with FERC 11/21/2012 | Yes - Project 2013-04 VAR (Voltage and Reactive Control Directives) |  |  |  |  | Yes - #1, 3 | Yes - covered under OATT | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Medium |  |  | GO
VAR-002-2 | VAR-002-2b | R5.1. | Generator Operation for Maintaining Network Voltage Schedules | To ensure generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the Interconnection. | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. | FERC Approved | Board adopted 8/16/2012; filed with FERC 11/21/2012 | [5 empty] | Yes - #1, 3 | Yes - covered under OATT | [18 empty] | Yes | No | 0 | 0 | Not ranked |  | N/A | Medium |  |  | GO
VAR-002-WECC-1 | VAR-002-WECC-1 | R1. | Automatic Voltage Regulators (AVR) | To ensure that Automatic Voltage Regulators on synchronous generators and condensers shall be kept in service and controlling voltage. | Generator Operators and Transmission Operators shall have AVR in service and in automatic voltage control mode 98% of all operating hours for synchronous generators or sychronous condensers. Generator Operators and Tranmission Operators may exclude hours for R1.1 through R1.10 to achieve the 98% requirement. [See standard pdf for R1.1 through R1.10] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  |  | GOP | [12 empty] | TOP
VAR-002-WECC-1 | VAR-002-WECC-1 | R2. | Automatic Voltage Regulators (AVR) | To ensure that Automatic Voltage Regulators on synchronous generators and condensers shall be kept in service and controlling voltage. | Generator Operators and Transmission Operators shall have documentation identifying the number of hours excluded for each requirement R1.1 through R1.10. | Regional |  |  |  |  | Yes | [25 empty] | Not ranked |  |  | Lower |  |  |  | GOP | [12 empty] | TOP
VAR-501-WECC-1 | VAR-501-WECC-1 | R1. | Power System Stabilizer (PSS) | To ensure that Power System Stabilizers (PSS) on synchronous generators shall be kept in service. | Generator Operators shall have PSS in service 98% of all operating hours for synchronous generators equipped with PSS. Generator Operators may exclude hours for R1.1 through R1.12 to achieve the 98% requirement. [See standard pdf for R1.1 through R1.12] | Regional | [30 empty] | Not ranked |  |  | Medium |  |  |  | GOP
VAR-501-WECC-1 | VAR-501-WECC-1 | R2. | Power System Stabilizer (PSS) | To ensure that Power System Stabilizers (PSS) on synchronous generators shall be kept in service. | Generator Operators shall have documentation identifying the number of hours excluded for each requirement in R1.1 through R1.12. | Regional |  |  |  |  | Yes | [25 empty] | Not ranked |  |  | Lower |  |  |  | GOP