## 2020 Summary
2020 Standard Grading Summary
|  | Content Questions | [5 empty] | Quality Questions
Standard | Req. | OC | PC | RE | NERC | Avg | Delta | OC | PC | RE | NERC | Avg | Delta
COM-001-3 | R12. | 4 | 4 | 4 | 3 | 3.75 | 1 | 11 | 13 | 13 | 12 | 12.25 | 2
COM-001-3 | R13. | 3 | 4 | 4 | 3 | 3.5 | 1 | 11 | 13 | 13 | 12 | 12.25 | 2
IRO-001-4 | R1. | 4 | 3 | 3 | 3 | 3.25 | 1 | 13 | 13 | 11 | 12 | 12.25 | 2
IRO-001-4 | R2. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
IRO-001-4 | R3. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
IRO-002-5 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
IRO-002-5 | R2. | 4 | 3 | 3 | 3 | 3.25 | 1 | 12 | 12 | 10 | 11 | 11.25 | 2
IRO-002-5 | R3. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
IRO-002-5 | R4. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
IRO-002-5 | R5. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 12 | 12.75 | 1
IRO-002-5 | R6. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
IRO-008-2 | R1. | 4 | 4 | 4 | 3 | 3.75 | 1 | 13 | 13 | 13 | 12 | 12.75 | 1
IRO-008-2 | R2. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 13 | 12.75 | 1
IRO-008-2 | R3. | 3 | 4 | 3 | 4 | 3.5 | 1 | 12 | 13 | 13 | 13 | 12.75 | 1
IRO-008-2 | R4. | 3 | 4 | 4 | 4 | 3.75 | 1 | 13 | 13 | 12 | 12 | 12.5 | 1
IRO-008-2 | R5. | 3 | 3 | 3 | 4 | 3.25 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
IRO-008-2 | R6. | 3 | 4 | 3 | 4 | 3.5 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
IRO-010-2 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 11 | 13 | 12.25 | 2
IRO-010-2 | R2. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
IRO-010-2 | R3. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
IRO-014-3 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12 | 12.5 | 1
IRO-014-3 | R2. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
IRO-014-3 | R3. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 13 | 12.75 | 1
IRO-014-3 | R4. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 11 | 13 | 12.5 | 2
IRO-014-3 | R5. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
IRO-014-3 | R6. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
IRO-014-3 | R7. | 3 | 4 | 3 | 4 | 3.5 | 1 | 9 | 10 | 10 | 10 | 9.75 | 1
IRO-017-1 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
IRO-017-1 | R2. | 4 | 3 | 4 | 4 | 3.75 | 1 | 13 | 13 | 12 | 12 | 12.5 | 1
IRO-017-1 | R3. | 4 | 4 | 3 | 3 | 3.5 | 1 | 13 | 13 | 12 | 12 | 12.5 | 1
IRO-017-1 | R4. | 4 | 3 | 3 | 4 | 3.5 | 1 | 13 | 12 | 13 | 11 | 12.25 | 2
IRO-018-1(i) | R1. | 4 | 4 | 4 | 3 | 3.75 | 1 | 13 | 13 | 11 | 13 | 12.5 | 2
IRO-018-1(i) | R2. | 4 | 4 | 4 | 3 | 3.75 | 1 | 13 | 13 | 13 | 12 | 12.75 | 1
IRO-018-1(i) | R3. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 11 | 13 | 12.5 | 2
TOP-001-4 | R1. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
TOP-001-4 | R2. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 12 | 12 | 13 | 12.5 | 1
TOP-001-4 | R3. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
TOP-001-4 | R4. | 3 | 3 | 3 | 4 | 3.25 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
TOP-001-4 | R5. | 3 | 4 | 3 | 4 | 3.5 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
TOP-001-4 | R6. | 3 | 4 | 3 | 4 | 3.5 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
TOP-001-4 | R7. | 3 | 4 | 3 | 4 | 3.5 | 1 | 10 | 10 | 9 | 10 | 9.75 | 1
TOP-001-4 | R8. | 3 | 4 | 3 | 4 | 3.5 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
TOP-001-4 | R9. | 3 | 4 | 3 | 3 | 3.25 | 1 | 11 | 13 | 13 | 11 | 12 | 2
TOP-001-4 | R10. | 4 | 4 | 4 | 4 | 4 | 0 | 11 | 13 | 13 | 13 | 12.5 | 2
TOP-001-4 | R11. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R12. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R13. | 3 | 4 | 4 | 4 | 3.75 | 1 | 13 | 13 | 13 | 12 | 12.75 | 1
TOP-001-4 | R14. | 4 | 4 | 3 | 4 | 3.75 | 1 | 11 | 13 | 11 | 13 | 12 | 2
TOP-001-4 | R15. | 4 | 4 | 3 | 4 | 3.75 | 1 | 11 | 13 | 11 | 13 | 12 | 2
TOP-001-4 | R16. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R17. | 4 | 3 | 4 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
TOP-001-4 | R18. | 3 | 4 | 4 | 4 | 3.75 | 1 | 12 | 13 | 12 | 13 | 12.5 | 1
TOP-001-4 | R19. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R20. | 4 | 4 | 3 | 4 | 3.75 | 1 | 11 | 13 | 11 | 13 | 12 | 2
TOP-001-4 | R21. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R22. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-001-4 | R23. | 4 | 4 | 3 | 4 | 3.75 | 1 | 12 | 13 | 11 | 13 | 12.25 | 2
TOP-001-4 | R24. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
TOP-002-4 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-002-4 | R2. | 4 | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 13 | 0
TOP-002-4 | R3. | 3 | 4 | 3 | 4 | 3.5 | 1 | 13 | 13 | 13 | 13 | 13 | 0
TOP-002-4 | R4. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 12 | 13 | 12.75 | 1
TOP-002-4 | R5. | 4 | 4 | 3 | 3 | 3.5 | 1 | 13 | 13 | 13 | 13 | 13 | 0
TOP-002-4 | R6. | 3 | 4 | 3 | 3 | 3.25 | 1 | 11 | 13 | 13 | 13 | 12.5 | 2
TOP-002-4 | R7. | 3 | 4 | 3 | 3 | 3.25 | 1 | 11 | 13 | 13 | 13 | 12.5 | 2
TOP-003-3 | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 9 | 11 | 11 | 11 | 10.5 | 2
TOP-003-3 | R2. | 4 | 4 | 4 | 4 | 4 | 0 | 9 | 11 | 11 | 11 | 10.5 | 2
TOP-003-3 | R3. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
TOP-003-3 | R4. | 4 | 4 | 3 | 4 | 3.75 | 1 | 13 | 13 | 13 | 13 | 13 | 0
TOP-003-3 | R5. | 4 | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 11 | 12.25 | 2
TOP-010-1(i) | R1. | 4 | 4 | 4 | 4 | 4 | 0 | 10 | 12 | 11 | 12 | 11.25 | 2
TOP-010-1(i) | R2. | 4 | 4 | 4 | 4 | 4 | 0 | 10 | 12 | 11 | 12 | 11.25 | 2
TOP-010-1(i) | R3. | 4 | 4 | 4 | 4 | 4 | 0 | 11 | 12 | 13 | 12 | 12 | 2
TOP-010-1(i) | R4. | 3 | 3 | 2 | 3 | 2.75 | 1 | 13 | 13 | 11 | 13 | 12.5 | 2
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## Summary Comments
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Content Score (0-4) | Quality Score (0-13) | Combined (OC/PC/RE/NERC) Comment/Rationale | Content Delta | Quality Delta | Comments from Review
COM-001-3 | R12. | R12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Delta:1 OC:4 PC:4 RE:4 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:12 | OC: Q1: This seems to be a redundant requirement to R1, R4, R5 & R8. Also, Does Generator Operator mean every plant or a common location? PC: No comment RE: No comment NERC: C1 (Tech correct): Scott-The requirement reads that internal Interpersonal Communication "capabilities" is required, but the Measure reads that the entity had a "capability" (singular). The Requirement implies that more than one capability is required since is uses the plural. Q13: Since having interpersonal communications are needed in order to issue/receive and comply with Operating Instructions, this requirement may be duplicative with with several TOP/IRO requirements. (industry comment) | 1 | 2
COM-001-3 | R13. | R13. Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Delta:1 OC:3 PC:4 RE:4 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:12 | OC: Q1, Q4: This seems to be a redundant requirement to R12. This could be combined with R12. C3: A small DP may not have a control center, voice recordings, etc. PC: No comment RE: No comment NERC: C1 (Tech correct): Scott-The requirement reads that internal Interpersonal Communication "capabilities" is required, but the Measure reads that the entity had a "capability" (singular). The Requirement implies that more than one capability is required since is uses the plural. Q13: Since having interpersonal communications are needed in order to issue/receive and comply with Operating Instructions, this requirement may be duplicative with with several TOP/IRO requirements. (industry comment) | 1 | 2
IRO-001-4 | R1. | R1. Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Delta:1 OC:4 PC:3 RE:3 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:12 | OC: OC echoes RE/NERC comments on "shall act" verbiage PC: C2: This is a mirror image of R3. In order to make this more clear the entities that the RC is addressing should be identified. RE: C4: It is unclear how quickly the RC must act. Q4, Q7, and Q11: "Shall act" is vague. All actions RC take support reliablity. What value is this requirement adding. What specific reliablity issues are being addressed? NERC: C4/Q11: "shall act"; (verb used without object); the actions and trigger for action are ubiquitous and all-encompassing; This language was drafted in response to "Authority" gaps identified by the Independent Experts in their 2013 report. No change recommended. | 1 | 2
IRO-001-4 | R2. | R2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for complying with Operating Instructions NERC: No comment | 1 | 0
IRO-001-4 | R3. | R3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C3: Would it improve the requirement to require a confirmation that the RC received and understood the inability to perform the instruction? NERC: No comment | 1 | 0
IRO-002-5 | R1. | R1. Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
IRO-002-5 | R2. | R2. Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Delta:1 OC:4 PC:3 RE:3 NERC:3 | Delta:2 OC:12 PC:12 RE:10 NERC:11 | OC: OC echoes RE/NERC comments on language with diversly routed. Implementation Guidance drafted for requirement PC: C2/Q4: Should also include data exchange with GOPs. RE: C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. Q7, Q9- The "diversely routed" language provided does not provide clarity on what an entity is being asked to do which causes issues in determining compliance. Routing invariably implies physical relationships which is covered in NIST 400-53 PE-9. Q11 - Real-time monitoring needs fuller definition to recognize what parameters are necessary. NERC: C4/Q4/Q11: The expectations are unclear as to whether data exchange "infrastructure" or "capability" is to be redundant. In response to a directive in FERC Order 817, NERC revised IRO-002-4 to clarify that Reliability Coordinators shall have redundant and diversely routed data exchange capabilities and explains in its rationale that redundant and diversely routed data exchange capabilities consist of data exchange infrastructure components that would provide continued functionality despite failure or malfunction of an individual component within the applicable entity’s primary Control Center. “Redundant infrastructure” is equivalent to redundant and diversely routed data exchange capabilities but "redundant and diversely routed data exchange capabilities" may not always require “Redundant infrastructure” of every part. | 1 | 2
IRO-002-5 | R3. | R3. Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: Required testing every 90 days implies quarterly, but in order to be compliant there could be an instance 5 tests per year are required, first test is done Jan. 1-5. (industry comment) NERC: No comment | 1 | 0
IRO-002-5 | R4. | R4. Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
IRO-002-5 | R5. | R5. Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: No comment NERC: Q10: The determiniation of SOL and IROL is dependent on each RC's methodology (developed in FAC-011), therefore monitoring for exceedance of the limit depends on the limit having first been determined (FAC-014). | 0 | 1
IRO-002-5 | R6. | R6. Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
IRO-008-2 | R1. | R1. Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Delta:1 OC:4 PC:4 RE:4 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: No comment NERC: C4: The requirement is unclear when the OPA should be performed and under what conditions the OPA should be re-performed/updated. (meaning an OPA performed on Friday for Saturday, Sunday, and Monday could be valid) Q10: The determiniation of SOL and IROL is dependent on each RC's methodology (developed in FAC-011), therefore monitoring for exceedance of the limit depends on the limit having first been determined (FAC-014). Requirement should be evaluated upon conclusion of Project 2015-09 Establish and Communicate System Operating Limits - FAC-010, FAC-011, FAC-014 (drafting estimated to be completed by May 2020) | 1 | 1
IRO-008-2 | R2. | R2. Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: Q10: Relies on OPA completion to develop plans NERC: No comment | 0 | 1
IRO-008-2 | R3. | R3. Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:13 NERC:13 | OC: C3/Q2: It is unclear what notification entails. Is this just posting the information (file share, website) for the entities to review or does it require a notification? This Requirement seems administrative in nature. PC: No comment RE: C4: No time frame for Notification NERC: No comment | 1 | 1
IRO-008-2 | R4. | R4. Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Delta:1 OC:3 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:12 | OC: C4: Ambiguity around what is required for a Real-time Assessment. PC: No comment RE: Q10: RTA relies on data quality from IRO-018 NERC: Q4: The expectation for "performance" of RTA is not clear in the standard requirement. TOP-001, R13 is corollary requirement for TOP. What is the difference between the RC's RTA and the TOP's RTA? Are they interchangeable? | 1 | 1
IRO-008-2 | R5. | R5. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | Delta:1 OC:3 PC:3 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C4: Unclear when the notification needs to take place. PC: C1: The language is confusing. Does this refer to an OPA or a real time assessment? The Operating Plan and Real Time Assessment will have different results. RE: C4: No time frame for Notification Q11: The phrase "or could result in" is unclear. It could be assumed that this phrase is addressing the post-contingency aspect of the Real-time Assessment. If this is the intent, then it should be reworded to improve clarity. It is our understanding that the FAC DT is taking steps that may address this concern NERC: No comment | 1 | 1
IRO-008-2 | R6. | R6. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C4: Unclear when the notification needs to take place. PC: No comment RE: C4: No time frame for notification Q11: SOL exceedances include both pre- and post-contingency states for thermal, voltage (low and high) and stability. There is little reliability benefit in requiring an RC to notify the TOP every time a high-voltage limit exceedance is prevented or mitigated. RCs should have flexibility in determining when it is appropriate to notify its TOPs and BAs of such preventions and mitigations. NERC: No comment | 1 | 1
IRO-010-2 | R1. | R1. The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: 1.1. A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:12 PC:13 RE:11 NERC:13 | OC: Q11: OC echoes comments regarding the ambiguity of RTM. PC: No comment RE: Q12: Special Protection System (SPS) should be Remedial Action Scheme (RAS) Q11: The term Real-time monitoring is unclear. Should this be a defined term. NERC: No comment | 0 | 2
IRO-010-2 | R2. | R2. The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: C4: When does RC have to distribute, including after modifications? Q10: This requires the entities to have the external document from R1. NERC: No comment | 1 | 1
IRO-010-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: 3.1. A mutually agreeable format 3.2. A mutually agreeable process for resolving data conflicts 3.3. A mutually agreeable security protocol | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C2: Include UFLS-only DP to list of applicable entities? NERC: No comment | 1 | 0
IRO-014-3 | R1. | R1. Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:12 | OC: No comment PC: No comment RE: Q10: In light of the requirements in IRO-017 related to the RC's outage coordination process, this requirement can be improved by adding "outage coordination responsibilities" to the list of items to subpart 1.4. Operational Planning Analyses per the definition are an assessment of the next day's operations. The RC needs data that is separate and unique from the OPA that is specific to the outage coordination process. NERC: Q5: Since IRO-014, IRO-015 and IRO-016 were consolidated into a revised IRO-014, the concept of "reliability directive" has changed with COM-002 and "Joint Operating Agreement" concepts for RC-to-RC coordination have been widely adopted. This requirement could be better aligned with its purpose statement to explicitly require Joint Operating Agreements among RC's to address coordination of actions that may impact adjacent Reliability Coordinator Areas in support of Interconnection reliability and should address the use of "Operating Instructions" as a tool when communicating with other RC's. | 0 | 1
IRO-014-3 | R2. | R2. Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
IRO-014-3 | R3. | R3. Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: Q11: Consider review of EOP-011 R5, to revising R5 to say "impacted" rather than neighboring RCs NERC: No comment | 0 | 1
IRO-014-3 | R4. | R4. Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: C4: when does revised operation have to begin? Q7: It may be hard to measure whether the impacted RC acts as if the Emergency existed. Q11 It is unclear as to what constitues "disagreement." NERC: No comment | 1 | 2
IRO-014-3 | R5. | R5. Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for development Q12: "I"dentifies should not be capitalized. NERC: No comment | 1 | 1
IRO-014-3 | R6. | R6. Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: How quickly must the RC implement? NERC: No comment | 1 | 0
IRO-014-3 | R7. | R7. Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:9 PC:10 RE:10 NERC:10 | OC: Q4, Q7, Q8, and Q11: (OC echoes comment from RE) It is unclear as to what "assist" means. It does not clearly state what action needs to be taken. C4: how quickly must the RC provide the assistance? PC: Echo comments from OC/RE RE: Q4, Q7, Q8,: It is unclear as to what "assist" means. C4: how quickly must the RC provide the assistance? NERC: NERC echoes concern about the term "assist" and when the RC is obligated to assist | 1 | 1
IRO-017-1 | R1. | R1. Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] 1.1. Identify applicable roles and reporting responsibilities including: 1.1.1. Development and communication of outage schedules. 1.1.2. Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). 1.2. Specify outage submission timing requirements. 1.3. Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. 1.4. Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
IRO-017-1 | R2. | R2. Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Delta:1 OC:4 PC:3 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:12 | OC: No comment PC: C2: Need to include GOP RE: Q10: TOP and BA must rely on the process developed in R1 but there is no requirement in R1 for the RC to distribute the process. NERC: Q10: the Reliability Coordinator’s outage coordination process specifies what performance is required; the requirement is digital with respect to level of perfomance | 1 | 1
IRO-017-1 | R3. | R3. Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Delta:1 OC:4 PC:4 RE:3 NERC:3 | Delta:1 OC:13 PC:13 RE:12 NERC:12 | OC: No comment PC: No comment RE: C4: No time frame for the PC and TP to provide their Planning Assessment. Q1:Consider moving this under TPL-001. The Technical Basis section of IRO-017-1 states that such coordination should take place in the TPL standards. In a draft SAR for TPL-001-4 that would revise Requirement R8 to make the Reliability Coordinator an explicit party in the review process described there. (industry comment) NERC: C4: the requirement is not clear when the action needs to be taken within the standard; TPL-001-5 provides for "within 90 calendar days of completing its Planning Assessment" it is unclear whether the two requirements have the same timing need. Q4: What is the Reliability Coordinator supposed to do with the Planning Assessment? Some Planning Assessments sent to RC's are not being used. | 1 | 1
IRO-017-1 | R4. | R4. Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Delta:1 OC:4 PC:3 RE:3 NERC:4 | Delta:2 OC:13 PC:12 RE:13 NERC:11 | OC: No comment PC: Q8: A deadline for a joint solution is not identified. RE: C4: No time frame for developing the solutions. NERC: Q1: R3 and R4 could be combined to focus on what the Reliability Coordinator's obligations are with respect to the Planning Analysis Q11: The clear, unambiguous language should state that the Reliability Coordinator should provide available system adjustments such as Transmission configuration changes and re-dispatch of generation if such adjustments are realistic mitigation for SOL or IROL exceedances and can be used as Corrective Actions to be studied in the planning horizon. | 1 | 2
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Delta:1 OC:4 PC:4 RE:4 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: C4: the requirement relies on an understood meaning of "implement" | 1 | 2
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Delta:1 OC:4 PC:4 RE:4 NERC:3 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: No comment PC: No comment RE: No comment NERC: C4: the requirement relies on an understood meaning of "implement" Q4: R2.3 is incomplete in the expectation for system operator awareness as it impacts RTA; the requirement does not align with the expectations stated in the rationale. | 1 | 1
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: No comment | 0 | 2
TOP-001-4 | R1. | R1. Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for TOP actions. Q11: shall act is vague. NERC: No comment | 1 | 1
TOP-001-4 | R2. | R2. Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:12 RE:12 NERC:13 | OC: No comment PC: Q1: This might be more appropriate to move to BAL-006 RE: C4: No time fram for the BA to act. Q11: shall act is vague. Should the language from other requirements "unless such actions would violate safety, equipment, regulatory, or statutory requirements" be added? NERC: No comment | 1 | 1
TOP-001-4 | R3. | R3. Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame that the BA, GOP, and DP must comply. Is that included in the Operating Instruction? Q4: Uncertain when they must be implemented NERC: No comment | 1 | 1
TOP-001-4 | R4. | R4. Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Delta:1 OC:3 PC:3 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C4, Q7: Difficult to prove the negative PC: C4: The requirement implies that a BA/GOP/DP has 1 TOP to report to. In cases today the RC and BA have the same footprint so there might be multiple TOPs to report to. RE: C4: No time frame that the BA, GOP, and DP must notify the RC. Q4: Uncertain when they must notify NERC: No comment | 1 | 1
TOP-001-4 | R5. | R5. Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C4, Q7: Difficult to prove the negative PC: No comment RE: C4: No time frame that the TOP, GOP, and DP must comply. Is that included in the Operating Instruction? Q4: Uncertain when they must be implemented NERC: No comment | 1 | 1
TOP-001-4 | R6. | R6. Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C4, Q7: Difficult to prove the negative PC: No comment RE: C4: No time frame that the TOP, GOP, and DP must notify the RC. Q4: Uncertain when they must notify NERC: No comment | 1 | 1
TOP-001-4 | R7. | R7. Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:10 PC:10 RE:9 NERC:10 | OC: Q4, Q7, Q8: (OC echoes comments from RE) It is unclear as to what "assist" means. C4: how quickly Must the TOP provide the assistance? PC: Echo comments from OC/RE RE: Q4, Q7, Q8: It is unclear as to what "assist" means. C4: how quickly Must the TOP provide the assistance? NERC: Q7/Q8: Echo comments from RE about the word "assist" | 1 | 1
TOP-001-4 | R8. | R8. Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: C3, C4, TOP can impact neighboring TOPs, but not know until after the fact. Agree with RE comments about whether this relates to post-contingency analysis. PC: No comment RE: C4: How quickly must the TOP inform its RC and impacted BAs? Q11: The phrase "or could result in" is unclear. It could be assumed that this phrase is addressing the post-contingency aspect of the Real-time Assessment. If this is the intent, then it should be reworded to improve clarity. NERC: No comment | 1 | 1
TOP-001-4 | R9. | R9. Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Delta:1 OC:3 PC:4 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:11 | OC: C3, C4, Q7, Q11: Confusing language on the distinction between a planned or unplanned outage. The timing requirement is difficult to objectively measure due to the "unplanned" nature. There is also a lack of defined terminology, such as "telemetering and control equipment". Example with RTU outage or data quality issue, when would this issue need to be flagged and communicated to RC. PC: No comment RE: C4: How quickly must the BA and TOP notify the RC NERC: Q8/Q11: Could be difficult to distinguish between planned and unplanned outage, and example being an intermittent RTU issue that occurs then has a planned fix for the next day. | 1 | 2
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Q4, Q7: Unclear on what "monitor" means, PC: No comment RE: No comment NERC: No comment | 0 | 2
TOP-001-4 | R11. | R11. Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R12. | R12. Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R13. | R13. Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Delta:1 OC:3 PC:4 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:13 NERC:12 | OC: C4: Ambiguity around what is required for a Real-time Assessment. PC: No comment RE: No comment NERC: Q8: Many entitites cannot perform RTA as specified with EMS down, which is occasionally inevitable. It is debatable whether an alternative RTA performed by the respective RC or an adjacent TOP meets the intent during an EMS outage. | 1 | 1
TOP-001-4 | R14. | R14. Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:2 OC:11 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: C4: How quickly must OP be initiated. Is this identified in the OP? Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: No comment | 1 | 2
TOP-001-4 | R15. | R15. Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:2 OC:11 PC:13 RE:11 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for the TOP notification to the RC Q4 &Q11: Ambiguous as to how quickly they must act and how quickly they must inform the RC. NERC: No comment | 1 | 2
TOP-001-4 | R16. | R16. Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R17. | R17. Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Delta:1 OC:4 PC:3 RE:4 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: C2: IRO-017 requires that the RC develop an outage methodology. RE: Q1: This could be combined with R16 "each TOP and BA" NERC: No comment | 1 | 1
TOP-001-4 | R18. | R18. Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Delta:1 OC:3 PC:4 RE:4 NERC:4 | Delta:1 OC:12 PC:13 RE:12 NERC:13 | OC: C2/Q11: Should also define most limiting parameter between any entity, not just TOP. Meaning TOP-RC or TOP-TOP? PC: No comment RE: Q11: Unclear as to who the difference is between. Two TOPs is assumed but not stated. NERC: No comment | 1 | 1
TOP-001-4 | R19. | R19. Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R20. | R20. Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:2 OC:11 PC:13 RE:11 NERC:13 | OC: Q7, Q11: Unclear on how redundant and diversely routed is achieved PC: No comment RE: C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. There has been much discussion/debate regarding where the edge of a Control Center is, which has led to confusion about how far the redundant/diverse routes need to extend (for example, communications equipment outside of the PSP datacenter, but still within the same building). Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: No comment | 1 | 2
TOP-001-4 | R21. | R21. Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R22. | R22. Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-001-4 | R23. | R23. Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:2 OC:12 PC:13 RE:11 NERC:13 | OC: Q11: Unclear on how redundant and diversely routed is achieved PC: No comment RE: C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. There has been much discussion/debate regarding where the edge of a Control Center is, which has led to confusion about how far the redundant/diverse routes need to extend (for example, communications equipment outside of the PSP datacenter, but still within the same building). Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: No comment | 1 | 2
TOP-001-4 | R24. | R24. Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C3: Should the BA have to notify the RC if the test is unsuccessful? NERC: No comment | 1 | 0
TOP-002-4 | R1. | R1. Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-002-4 | R2. | R2. Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: No comment NERC: No comment | 0 | 0
TOP-002-4 | R3. | R3. Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Delta:1 OC:3 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: C4: Unclear exactly what kind notification should be made. PC: No comment RE: C4: No time frame for the TOP to notify the entities. Is that included in the OP? NERC: No comment | 1 | 0
TOP-002-4 | R4. | R4. Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1. Expected generation resource commitment and dispatch 4.2. Interchange scheduling 4.3. Demand patterns 4.4. Capacity and energy reserve requirements, including deliverability capability | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:1 OC:13 PC:13 RE:12 NERC:13 | OC: No comment PC: No comment RE: C1 & Q11: Discussions with several individuals indicate that there is confusion with the meaning and intent of the phrase "including deliverability capability" (4.4). The ability to deliver energy to a load is a transmission system assessment, and accordingly cannot be performed by a BA, who may have no knowledge of the transmission system. The assessments to determine whether generation can be delivered to the load through the transmission system should be performed by a TOP. If this phrase isn't addressing the transmission system's ability to deliver the energy to the load, then what is it talking about? It needs to be addressed or clarified. NERC: No comment | 1 | 1
TOP-002-4 | R5. | R5. Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Delta:1 OC:4 PC:4 RE:3 NERC:3 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for the BA to notify the entities. Is that included in the OP NERC: C4: Not explicity stated when the action has to be taken. | 1 | 0
TOP-002-4 | R6. | R6. Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Delta:1 OC:3 PC:4 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Q4, Q6: Just providing this to the RC does not increase reliability unless the RC is actively reviewing plans - no actions around that. PC: No comment RE: C4: No time frame for the TOP to provide its OP to its RC. NERC: C4: Not explicity stated when the action has to be taken. | 1 | 2
TOP-002-4 | R7. | R7. Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Delta:1 OC:3 PC:4 RE:3 NERC:3 | Delta:2 OC:11 PC:13 RE:13 NERC:13 | OC: Q4, Q6: Just providing this to the RC does not increase reliability unless the RC is actively reviewing plans - no actions around that. PC: No comment RE: C4: No time frame for the BA to provide its OP to its RC. NERC: C4: Not explicity stated when the action has to be taken. | 1 | 2
TOP-003-3 | R1. | R1. Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: 1.1. A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:9 PC:11 RE:11 NERC:11 | OC: Q6, Q7, Q8, Q11 This is difficult to maintain at the TOP level. Many TOPs already provided this data on a schedule to their RC. The RC should be the one maintaining the data spec. This does not increase BPS reliability. PC: Q8/Q12: agree with discussion on if RTM needs to be a defined term RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Periodicity of data provided gives some clarity for RTM, but RTM is not a defined term. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: Q7/Q11: concerns around ambiguity of OPA/RTA/RTM and what can and cannot be requested in data specificiation is outline in SER Operational Data Simplification SAR. The Guidelines and Technical Basis (GTB) for TOP-010 does include a description for Real-time monitoring, but it is not in the Glossary of Terms. Real-time monitoring may include the following activities performed in Real-time: • Acquisition of operating data; • Display of operating data as needed for visualization of system conditions; • Audible or visual alerting when warranted by system conditions; and • Audible or visual alerting when monitoring and analysis capabilities degrade or become unavailable. | 0 | 2
TOP-003-3 | R2. | R2. Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. 2.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 2.3. A periodicity for providing data. 2.4. The deadline by which the respondent is to provide the indicated data. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:9 PC:11 RE:11 NERC:11 | OC: Q6, Q7, Q8, Q11 This does not increase BPS reliability. PC: Q8/Q12: agree with discussion on if RTM needs to be a defined term RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: Q7/Q11: concerns around ambiguity of OPA/RTA/RTM and what can and cannot be requested in data specificiation is outline in SER Operational Data Simplification SAR. The Guidelines and Technical Basis (GTB) for TOP-010 does include a description for Real-time monitoring, but it is not in the Glossary of Terms. | 0 | 2
TOP-003-3 | R3. | R3. Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for distribution to the entities or requirement for updating. NERC: No comment | 1 | 0
TOP-003-3 | R4. | R4. Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Delta:1 OC:4 PC:4 RE:3 NERC:4 | Delta:0 OC:13 PC:13 RE:13 NERC:13 | OC: No comment PC: No comment RE: C4: No time frame for distribution to the entities or requirement for updating. NERC: No comment | 1 | 0
TOP-003-3 | R5. | R5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:12 PC:13 RE:13 NERC:11 | OC: Q2: Burdensome, and seemingly administrative in nature, to entities to track when to send data request to other entities, because there is too much to keep track of especially if entities have differing data requirements than the RC. PC: No comment RE: No comment NERC: Q8/Q11: With Measure for R5, does an attestation from the requesting entity saying that the sender satisfied obligations meet the intent. | 0 | 2
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:10 PC:12 RE:11 NERC:12 | OC: Q7, Q11 What does the definition of quality mean? This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined. PC: See comments from OC RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: Q11 The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues. The criteria support identification of applicable data quality issues, which may include: • Data outside of a prescribed data range; • Analog data not updated within a predetermined time period; • Data entered manually to override telemetered information; or • Data otherwise identified as invalid or suspect. | 0 | 2
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:10 PC:12 RE:11 NERC:12 | OC: Q7, Q11 What does the definition of quality mean? This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined. PC: See comments from OC RE: Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included. NERC: Q11: The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues. | 0 | 2
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Delta:0 OC:4 PC:4 RE:4 NERC:4 | Delta:2 OC:11 PC:12 RE:13 NERC:12 | OC: Q7, Q11 What does the definition of quality mean? Example Implementation Guidance for TOP-010 R3 (approved in May 2019) was a 13 page document to address this ambiguity. This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined. PC: See comments from OC RE: No comment NERC: Q11: The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues. | 0 | 2
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Delta:1 OC:3 PC:3 RE:2 NERC:3 | Delta:2 OC:13 PC:13 RE:11 NERC:13 | OC: Action to address the failure (and notifying RC) of alarm process monitor is implied and not explicitely stated. PC: Echo comments from OC/RE/NERC RE: C3, C4, &Q10: There seems to be a gap. Nothing is required beyond notifying the System Operator of a failure of the alarm processor. Should some type of notification be given to the RC for a specific duration of the suspected failure before it is restored? should there be some action required to address the lack of alarm(s) in the Operating Plan to operate more conservatively? Q4: Should there be a requirement to adddress the failure rather than just be notified of it. NERC: Action to address the failure (and notifying RC) of alarm process monitor is implied and not explicitely stated. | 1 | 2
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## OC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
COM-001-3 | R12. | R12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 11 | Q1: This seems to be a redundant requirement to R1, R4, R5 & R8. Also, Does Generator Operator mean every plant or a common location?
COM-001-3 | R13. | R13. Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Yes | No | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Q1, Q4: This seems to be a redundant requirement to R12. This could be combined with R12. C3: A small DP may not have a control center, voice recordings, etc.
IRO-001-4 | R1. | R1. Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 | OC echoes RE/NERC comments on "shall act" verbiage
IRO-001-4 | R2. | R2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-001-4 | R3. | R3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R1. | R1. Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R2. | R2. Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | OC echoes RE/NERC comments on language with diversly routed. Implementation Guidance drafted for requirement
IRO-002-5 | R3. | R3. Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R4. | R4. Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R5. | R5. Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R6. | R6. Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R1. | R1. Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R2. | R2. Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R3. | R3. Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C3/Q2: It is unclear what notification entails. Is this just posting the information (file share, website) for the entities to review or does it require a notification? This Requirement seems administrative in nature.
IRO-008-2 | R4. | R4. Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Ambiguity around what is required for a Real-time Assessment.
IRO-008-2 | R5. | R5. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: Unclear when the notification needs to take place.
IRO-008-2 | R6. | R6. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: Unclear when the notification needs to take place.
IRO-010-2 | R1. | R1. The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: 1.1. A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: OC echoes comments regarding the ambiguity of RTM.
IRO-010-2 | R2. | R2. The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: 3.1. A mutually agreeable format 3.2. A mutually agreeable process for resolving data conflicts 3.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R1. | R1. Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R2. | R2. Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R3. | R3. Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R4. | R4. Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R5. | R5. Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R6. | R6. Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R7. | R7. Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | 3 | 9 | Q4, Q7, Q8, and Q11: (OC echoes comment from RE) It is unclear as to what "assist" means. It does not clearly state what action needs to be taken. C4: how quickly must the RC provide the assistance?
IRO-017-1 | R1. | R1. Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] 1.1. Identify applicable roles and reporting responsibilities including: 1.1.1. Development and communication of outage schedules. 1.1.2. Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). 1.2. Specify outage submission timing requirements. 1.3. Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. 1.4. Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R2. | R2. Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R3. | R3. Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R4. | R4. Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R1. | R1. Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R2. | R2. Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R3. | R3. Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R4. | R4. Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4, Q7: Difficult to prove the negative
TOP-001-4 | R5. | R5. Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4, Q7: Difficult to prove the negative
TOP-001-4 | R6. | R6. Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4, Q7: Difficult to prove the negative
TOP-001-4 | R7. | R7. Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Q4, Q7, Q8: (OC echoes comments from RE) It is unclear as to what "assist" means. C4: how quickly Must the TOP provide the assistance?
TOP-001-4 | R8. | R8. Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3, C4, TOP can impact neighboring TOPs, but not know until after the fact. Agree with RE comments about whether this relates to post-contingency analysis.
TOP-001-4 | R9. | R9. Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C3, C4, Q7, Q11: Confusing language on the distinction between a planned or unplanned outage. The timing requirement is difficult to objectively measure due to the "unplanned" nature. There is also a lack of defined terminology, such as "telemetering and control equipment". Example with RTU outage or data quality issue, when would this issue need to be flagged and communicated to RC.
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 11 | Q4, Q7: Unclear on what "monitor" means,
TOP-001-4 | R11. | R11. Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R12. | R12. Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R13. | R13. Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Ambiguity around what is required for a Real-time Assessment.
TOP-001-4 | R14. | R14. Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | 4 | 11
TOP-001-4 | R15. | R15. Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | 4 | 11
TOP-001-4 | R16. | R16. Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R17. | R17. Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R18. | R18. Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C2/Q11: Should also define most limiting parameter between any entity, not just TOP. Meaning TOP-RC or TOP-TOP?
TOP-001-4 | R19. | R19. Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R20. | R20. Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7, Q11: Unclear on how redundant and diversely routed is achieved
TOP-001-4 | R21. | R21. Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R22. | R22. Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R23. | R23. Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Unclear on how redundant and diversely routed is achieved
TOP-001-4 | R24. | R24. Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R1. | R1. Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R2. | R2. Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R3. | R3. Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Unclear exactly what kind notification should be made.
TOP-002-4 | R4. | R4. Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1. Expected generation resource commitment and dispatch 4.2. Interchange scheduling 4.3. Demand patterns 4.4. Capacity and energy reserve requirements, including deliverability capability | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R5. | R5. Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R6. | R6. Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Q4, Q6: Just providing this to the RC does not increase reliability unless the RC is actively reviewing plans - no actions around that.
TOP-002-4 | R7. | R7. Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | Q4, Q6: Just providing this to the RC does not increase reliability unless the RC is actively reviewing plans - no actions around that.
TOP-003-3 | R1. | R1. Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: 1.1. A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | 4 | 9 | Q6, Q7, Q8, Q11 This is difficult to maintain at the TOP level. Many TOPs already provided this data on a schedule to their RC. The RC should be the one maintaining the data spec. This does not increase BPS reliability.
TOP-003-3 | R2. | R2. Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. 2.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 2.3. A periodicity for providing data. 2.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | No | Yes | Yes | 4 | 9 | Q6, Q7, Q8, Q11 This does not increase BPS reliability.
TOP-003-3 | R3. | R3. Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R4. | R4. Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R5. | R5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q2: Burdensome, and seemingly administrative in nature, to entities to track when to send data request to other entities, because there is too much to keep track of especially if entities have differing data requirements than the RC.
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 10 | Q7, Q11 What does the definition of quality mean? This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined.
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 10 | Q7, Q11 What does the definition of quality mean? This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined.
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7, Q11 What does the definition of quality mean? Example Implementation Guidance for TOP-010 R3 (approved in May 2019) was a 13 page document to address this ambiguity. This could mean a wide range of things to different entities. Dependent on how a Real-time assessment is defined.
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Action to address the failure (and notifying RC) of alarm process monitor is implied and not explicitely stated.
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## PC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
COM-001-3 | R12. | R12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
COM-001-3 | R13. | R13. Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-001-4 | R1. | R1. Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: This is a mirror image of R3. In order to make this more clear the entities that the RC is addressing should be identified.
IRO-001-4 | R2. | R2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-001-4 | R3. | R3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R1. | R1. Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R2. | R2. Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C2/Q4: Should also include data exchange with GOPs.
IRO-002-5 | R3. | R3. Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R4. | R4. Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R5. | R5. Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R6. | R6. Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R1. | R1. Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R2. | R2. Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R3. | R3. Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R4. | R4. Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R5. | R5. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C1: The language is confusing. Does this refer to an OPA or a real time assessment? The Operating Plan and Real Time Assessment will have different results.
IRO-008-2 | R6. | R6. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R1. | R1. The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: 1.1. A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R2. | R2. The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: 3.1. A mutually agreeable format 3.2. A mutually agreeable process for resolving data conflicts 3.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R1. | R1. Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R2. | R2. Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R3. | R3. Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R4. | R4. Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R5. | R5. Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R6. | R6. Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R7. | R7. Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 4 | 10 | Echo comments from OC/RE
IRO-017-1 | R1. | R1. Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] 1.1. Identify applicable roles and reporting responsibilities including: 1.1.1. Development and communication of outage schedules. 1.1.2. Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). 1.2. Specify outage submission timing requirements. 1.3. Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. 1.4. Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R2. | R2. Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: Need to include GOP
IRO-017-1 | R3. | R3. Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R4. | R4. Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Q8: A deadline for a joint solution is not identified.
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R1. | R1. Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R2. | R2. Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: This might be more appropriate to move to BAL-006
TOP-001-4 | R3. | R3. Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R4. | R4. Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: The requirement implies that a BA/GOP/DP has 1 TOP to report to. In cases today the RC and BA have the same footprint so there might be multiple TOPs to report to.
TOP-001-4 | R5. | R5. Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R6. | R6. Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R7. | R7. Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 4 | 10 | Echo comments from OC/RE
TOP-001-4 | R8. | R8. Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R9. | R9. Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R11. | R11. Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R12. | R12. Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R13. | R13. Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R14. | R14. Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R15. | R15. Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R16. | R16. Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R17. | R17. Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: IRO-017 requires that the RC develop an outage methodology.
TOP-001-4 | R18. | R18. Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R19. | R19. Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R20. | R20. Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R21. | R21. Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R22. | R22. Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R23. | R23. Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R24. | R24. Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R1. | R1. Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R2. | R2. Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R3. | R3. Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R4. | R4. Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1. Expected generation resource commitment and dispatch 4.2. Interchange scheduling 4.3. Demand patterns 4.4. Capacity and energy reserve requirements, including deliverability capability | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R5. | R5. Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R6. | R6. Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R7. | R7. Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R1. | R1. Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: 1.1. A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | 4 | 11 | Q8/Q12: agree with discussion on if RTM needs to be a defined term
TOP-003-3 | R2. | R2. Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. 2.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 2.3. A periodicity for providing data. 2.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | 4 | 11 | Q8/Q12: agree with discussion on if RTM needs to be a defined term
TOP-003-3 | R3. | R3. Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R4. | R4. Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R5. | R5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | See comments from OC
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | See comments from OC
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | See comments from OC
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Echo comments from OC/RE/NERC
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on Q34: Will Tootle: The PC, TP, and RC are all focused on different time horizons and take into account different study assumptions. Realistically, the "jointly developed solution" has a small chance of being implemented in real time.
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## RE
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
COM-001-3 | R12. | R12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
COM-001-3 | R13. | R13. Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-001-4 | R1. | R1. Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C4: It is unclear how quickly the RC must act. Q4, Q7, and Q11: "Shall act" is vague. All actions RC take support reliablity. What value is this requirement adding. What specific reliablity issues are being addressed?
IRO-001-4 | R2. | R2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for complying with Operating Instructions
IRO-001-4 | R3. | R3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3: Would it improve the requirement to require a confirmation that the RC received and understood the inability to perform the instruction?
IRO-002-5 | R1. | R1. Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R2. | R2. Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | Yes | 3 | 10 | C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. Q7, Q9- The "diversely routed" language provided does not provide clarity on what an entity is being asked to do which causes issues in determining compliance. Routing invariably implies physical relationships which is covered in NIST 400-53 PE-9. Q11 - Real-time monitoring needs fuller definition to recognize what parameters are necessary.
IRO-002-5 | R3. | R3. Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Required testing every 90 days implies quarterly, but in order to be compliant there could be an instance 5 tests per year are required, first test is done Jan. 1-5. (industry comment)
IRO-002-5 | R4. | R4. Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R5. | R5. Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R6. | R6. Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R1. | R1. Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R2. | R2. Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: Relies on OPA completion to develop plans
IRO-008-2 | R3. | R3. Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for Notification
IRO-008-2 | R4. | R4. Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: RTA relies on data quality from IRO-018
IRO-008-2 | R5. | R5. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4: No time frame for Notification Q11: The phrase "or could result in" is unclear. It could be assumed that this phrase is addressing the post-contingency aspect of the Real-time Assessment. If this is the intent, then it should be reworded to improve clarity. It is our understanding that the FAC DT is taking steps that may address this concern
IRO-008-2 | R6. | R6. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4: No time frame for notification Q11: SOL exceedances include both pre- and post-contingency states for thermal, voltage (low and high) and stability. There is little reliability benefit in requiring an RC to notify the TOP every time a high-voltage limit exceedance is prevented or mitigated. RCs should have flexibility in determining when it is appropriate to notify its TOPs and BAs of such preventions and mitigations.
IRO-010-2 | R1. | R1. The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: 1.1. A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | 4 | 11 | Q12: Special Protection System (SPS) should be Remedial Action Scheme (RAS) Q11: The term Real-time monitoring is unclear. Should this be a defined term.
IRO-010-2 | R2. | R2. The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | C4: When does RC have to distribute, including after modifications? Q10: This requires the entities to have the external document from R1.
IRO-010-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: 3.1. A mutually agreeable format 3.2. A mutually agreeable process for resolving data conflicts 3.3. A mutually agreeable security protocol | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: Include UFLS-only DP to list of applicable entities?
IRO-014-3 | R1. | R1. Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: In light of the requirements in IRO-017 related to the RC's outage coordination process, this requirement can be improved by adding "outage coordination responsibilities" to the list of items to subpart 1.4. Operational Planning Analyses per the definition are an assessment of the next day's operations. The RC needs data that is separate and unique from the OPA that is specific to the outage coordination process.
IRO-014-3 | R2. | R2. Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R3. | R3. Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Consider review of EOP-011 R5, to revising R5 to say "impacted" rather than neighboring RCs
IRO-014-3 | R4. | R4. Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C4: when does revised operation have to begin? Q7: It may be hard to measure whether the impacted RC acts as if the Emergency existed. Q11 It is unclear as to what constitues "disagreement."
IRO-014-3 | R5. | R5. Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 3 | 12 | C4: No time frame for development Q12: "I"dentifies should not be capitalized.
IRO-014-3 | R6. | R6. Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: How quickly must the RC implement?
IRO-014-3 | R7. | R7. Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 3 | 10 | Q4, Q7, Q8,: It is unclear as to what "assist" means. C4: how quickly must the RC provide the assistance?
IRO-017-1 | R1. | R1. Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] 1.1. Identify applicable roles and reporting responsibilities including: 1.1.1. Development and communication of outage schedules. 1.1.2. Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). 1.2. Specify outage submission timing requirements. 1.3. Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. 1.4. Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R2. | R2. Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: TOP and BA must rely on the process developed in R1 but there is no requirement in R1 for the RC to distribute the process.
IRO-017-1 | R3. | R3. Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: No time frame for the PC and TP to provide their Planning Assessment. Q1:Consider moving this under TPL-001. The Technical Basis section of IRO-017-1 states that such coordination should take place in the TPL standards. In a draft SAR for TPL-001-4 that would revise Requirement R8 to make the Reliability Coordinator an explicit party in the review process described there. (industry comment)
IRO-017-1 | R4. | R4. Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for developing the solutions.
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-001-4 | R1. | R1. Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4: No time frame for TOP actions. Q11: shall act is vague.
TOP-001-4 | R2. | R2. Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4: No time fram for the BA to act. Q11: shall act is vague. Should the language from other requirements "unless such actions would violate safety, equipment, regulatory, or statutory requirements" be added?
TOP-001-4 | R3. | R3. Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: No time frame that the BA, GOP, and DP must comply. Is that included in the Operating Instruction? Q4: Uncertain when they must be implemented
TOP-001-4 | R4. | R4. Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: No time frame that the BA, GOP, and DP must notify the RC. Q4: Uncertain when they must notify
TOP-001-4 | R5. | R5. Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: No time frame that the TOP, GOP, and DP must comply. Is that included in the Operating Instruction? Q4: Uncertain when they must be implemented
TOP-001-4 | R6. | R6. Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: No time frame that the TOP, GOP, and DP must notify the RC. Q4: Uncertain when they must notify
TOP-001-4 | R7. | R7. Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | No | Yes | Yes | 3 | 9 | Q4, Q7, Q8: It is unclear as to what "assist" means. C4: how quickly Must the TOP provide the assistance?
TOP-001-4 | R8. | R8. Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4: How quickly must the TOP inform its RC and impacted BAs? Q11: The phrase "or could result in" is unclear. It could be assumed that this phrase is addressing the post-contingency aspect of the Real-time Assessment. If this is the intent, then it should be reworded to improve clarity.
TOP-001-4 | R9. | R9. Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: How quickly must the BA and TOP notify the RC
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R11. | R11. Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R12. | R12. Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R13. | R13. Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R14. | R14. Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C4: How quickly must OP be initiated. Is this identified in the OP? Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-001-4 | R15. | R15. Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C4: No time frame for the TOP notification to the RC Q4 &Q11: Ambiguous as to how quickly they must act and how quickly they must inform the RC.
TOP-001-4 | R16. | R16. Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R17. | R17. Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: This could be combined with R16 "each TOP and BA"
TOP-001-4 | R18. | R18. Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Unclear as to who the difference is between. Two TOPs is assumed but not stated.
TOP-001-4 | R19. | R19. Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R20. | R20. Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. There has been much discussion/debate regarding where the edge of a Control Center is, which has led to confusion about how far the redundant/diverse routes need to extend (for example, communications equipment outside of the PSP datacenter, but still within the same building). Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-001-4 | R21. | R21. Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R22. | R22. Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R23. | R23. Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C3: There is ambiguity with using the term Control Center to delineate the boundary for where redundant/diverse paths must exist. The glossary definition of Control Center refers to ‘facilities’, which is undefined. There has been much discussion/debate regarding where the edge of a Control Center is, which has led to confusion about how far the redundant/diverse routes need to extend (for example, communications equipment outside of the PSP datacenter, but still within the same building). Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-001-4 | R24. | R24. Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3: Should the BA have to notify the RC if the test is unsuccessful?
TOP-002-4 | R1. | R1. Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R2. | R2. Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R3. | R3. Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for the TOP to notify the entities. Is that included in the OP?
TOP-002-4 | R4. | R4. Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1. Expected generation resource commitment and dispatch 4.2. Interchange scheduling 4.3. Demand patterns 4.4. Capacity and energy reserve requirements, including deliverability capability | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C1 & Q11: Discussions with several individuals indicate that there is confusion with the meaning and intent of the phrase "including deliverability capability" (4.4). The ability to deliver energy to a load is a transmission system assessment, and accordingly cannot be performed by a BA, who may have no knowledge of the transmission system. The assessments to determine whether generation can be delivered to the load through the transmission system should be performed by a TOP. If this phrase isn't addressing the transmission system's ability to deliver the energy to the load, then what is it talking about? It needs to be addressed or clarified.
TOP-002-4 | R5. | R5. Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for the BA to notify the entities. Is that included in the OP
TOP-002-4 | R6. | R6. Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for the TOP to provide its OP to its RC.
TOP-002-4 | R7. | R7. Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for the BA to provide its OP to its RC.
TOP-003-3 | R1. | R1. Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: 1.1. A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Periodicity of data provided gives some clarity for RTM, but RTM is not a defined term. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-003-3 | R2. | R2. Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. 2.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 2.3. A periodicity for providing data. 2.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-003-3 | R3. | R3. Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for distribution to the entities or requirement for updating.
TOP-003-3 | R4. | R4. Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for distribution to the entities or requirement for updating.
TOP-003-3 | R5. | R5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7 & Q11: Real-time monitoring needs fuller definition to recognize what parameters are necessary. Care should be taken to recognize the need for reliable operations balancing compliance obligations. If a quantity, such as current (Amps), status (Trip, Open, etc.), temperature (ambient, oil, winding coil, etc.) is required for reliable operations the definition should include those items. If it comes before a System Operator for action, whether that action is immediate, next hour, or next day (etc.), that implies it should be included.
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 2 | 11 | C3, C4, &Q10: There seems to be a gap. Nothing is required beyond notifying the System Operator of a failure of the alarm processor. Should some type of notification be given to the RC for a specific duration of the suspected failure before it is restored? should there be some action required to address the lack of alarm(s) in the Operating Plan to operate more conservatively? Q4: Should there be a requirement to adddress the failure rather than just be notified of it.
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## NERC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
COM-001-3 | R12. | R12. Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | C1 (Tech correct): Scott-The requirement reads that internal Interpersonal Communication "capabilities" is required, but the Measure reads that the entity had a "capability" (singular). The Requirement implies that more than one capability is required since is uses the plural. Q13: Since having interpersonal communications are needed in order to issue/receive and comply with Operating Instructions, this requirement may be duplicative with with several TOP/IRO requirements. (industry comment)
COM-001-3 | R13. | R13. Each Distribution Provider shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between control centers within the same functional entity, and/or between a control center and field personnel. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | C1 (Tech correct): Scott-The requirement reads that internal Interpersonal Communication "capabilities" is required, but the Measure reads that the entity had a "capability" (singular). The Requirement implies that more than one capability is required since is uses the plural. Q13: Since having interpersonal communications are needed in order to issue/receive and comply with Operating Instructions, this requirement may be duplicative with with several TOP/IRO requirements. (industry comment)
IRO-001-4 | R1. | R1. Each Reliability Coordinator shall act to address the reliability of its Reliability Coordinator Area via direct actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4/Q11: "shall act"; (verb used without object); the actions and trigger for action are ubiquitous and all-encompassing; This language was drafted in response to "Authority" gaps identified by the Independent Experts in their 2013 report. No change recommended.
IRO-001-4 | R2. | R2. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-001-4 | R3. | R3. Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R1. | R1. Each Reliability Coordinator shall have data exchange capabilities with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for it to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R2. | R2. Each Reliability Coordinator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Reliability Coordinator's primary Control Center, for the exchange of Real-time data with its Balancing Authorities and Transmission Operators, and with other entities it deems necessary, for performing its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C4/Q4/Q11: The expectations are unclear as to whether data exchange "infrastructure" or "capability" is to be redundant. In response to a directive in FERC Order 817, NERC revised IRO-002-4 to clarify that Reliability Coordinators shall have redundant and diversely routed data exchange capabilities and explains in its rationale that redundant and diversely routed data exchange capabilities consist of data exchange infrastructure components that would provide continued functionality despite failure or malfunction of an individual component within the applicable entity’s primary Control Center. “Redundant infrastructure” is equivalent to redundant and diversely routed data exchange capabilities but "redundant and diversely routed data exchange capabilities" may not always require “Redundant infrastructure” of every part.
IRO-002-5 | R3. | R3. Each Reliability Coordinator shall test its primary Control Center data exchange capabilities specified in Requirement R2 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Reliability Coordinator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R4. | R4. Each Reliability Coordinator shall provide its System Operators with the authority to approve planned outages and maintenance of its telecommunication, monitoring and analysis capabilities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-002-5 | R5. | R5. Each Reliability Coordinator shall monitor Facilities, the status of Remedial Action Schemes, and non-BES facilities identified as necessary by the Reliability Coordinator, within its Reliability Coordinator Area and neighboring Reliability Coordinator Areas to identify any System Operating Limit exceedances and to determine any Interconnection Reliability Operating Limit exceedances within its Reliability Coordinator Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: The determiniation of SOL and IROL is dependent on each RC's methodology (developed in FAC-011), therefore monitoring for exceedance of the limit depends on the limit having first been determined (FAC-014).
IRO-002-5 | R6. | R6. Each Reliability Coordinator shall have monitoring systems that provide information utilized by the Reliability Coordinator’s operating personnel, giving particular emphasis to alarm management and awareness systems, automated data transfers, and synchronized information systems, over a redundant infrastructure. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R1. | R1. Each Reliability Coordinator shall perform an Operational Planning Analysis that will allow it to assess whether the planned operations for the next-day will exceed System Operating Limits (SOLs) and Interconnection Operating Reliability Limits (IROLs) within its Wide Area. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | C4: The requirement is unclear when the OPA should be performed and under what conditions the OPA should be re-performed/updated. (meaning an OPA performed on Friday for Saturday, Sunday, and Monday could be valid) Q10: The determiniation of SOL and IROL is dependent on each RC's methodology (developed in FAC-011), therefore monitoring for exceedance of the limit depends on the limit having first been determined (FAC-014). Requirement should be evaluated upon conclusion of Project 2015-09 Establish and Communicate System Operating Limits - FAC-010, FAC-011, FAC-014 (drafting estimated to be completed by May 2020)
IRO-008-2 | R2. | R2. Each Reliability Coordinator shall have a coordinated Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) and Interconnection Reliability Operating Limit (IROL) exceedances identified as a result of its Operational Planning Analysis as performed in Requirement R1 while considering the Operating Plans for the next-day provided by its Transmission Operators and Balancing Authorities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R3. | R3. Each Reliability Coordinator shall notify impacted entities identified in its Operating Plan(s) cited in Requirement R2 as to their role in such plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R4. | R4. Each Reliability Coordinator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q4: The expectation for "performance" of RTA is not clear in the standard requirement. TOP-001, R13 is corollary requirement for TOP. What is the difference between the RC's RTA and the TOP's RTA? Are they interchangeable?
IRO-008-2 | R5. | R5. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the results of a Real-time Assessment indicate an actual or expected condition that results in, or could result in, a System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance within its Wide Area | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-008-2 | R6. | R6. Each Reliability Coordinator shall notify impacted Transmission Operators and Balancing Authorities within its Reliability Coordinator Area, and other impacted Reliability Coordinators as indicated in its Operating Plan, when the System Operating Limit (SOL) or Interconnection Reliability Operating Limit (IROL) exceedance identified in Requirement R5 has been prevented or mitigated. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R1. | R1. The Reliability Coordinator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include but not be limited to: 1.1. A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R2. | R2. The Reliability Coordinator shall distribute its data specification to entities that have data required by the Reliability Coordinator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-010-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: 3.1. A mutually agreeable format 3.2. A mutually agreeable process for resolving data conflicts 3.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R1. | R1. Each Reliability Coordinator shall have and implement Operating Procedures, Operating Processes, or Operating Plans, for activities that require notification or coordination of actions that may impact adjacent Reliability Coordinator Areas, to support Interconnection reliability. These Operating Procedures, Operating Processes, or Operating Plans shall include, but are not limited to, the following: 1.1. Criteria and processes for notifications. 1.2. Energy and capacity shortages. 1.3. Control of voltage, including the coordination of reactive resources. 1.4. Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. 1.5. Provisions for periodic communications to support reliable operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q5: Since IRO-014, IRO-015 and IRO-016 were consolidated into a revised IRO-014, the concept of "reliability directive" has changed with COM-002 and "Joint Operating Agreement" concepts for RC-to-RC coordination have been widely adopted. This requirement could be better aligned with its purpose statement to explicitly require Joint Operating Agreements among RC's to address coordination of actions that may impact adjacent Reliability Coordinator Areas in support of Interconnection reliability and should address the use of "Operating Instructions" as a tool when communicating with other RC's.
IRO-014-3 | R2. | R2. Each Reliability Coordinator shall maintain its Operating Procedures, Operating Processes, or Operating Plans identified in Requirement R1 as follows: 2.1. Review and update annually with no more than 15 months between reviews. 2.2. Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. 2.3. Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R3. | R3. Each Reliability Coordinator, upon identification of an expected or actual Emergency in its Reliability Coordinator Area, shall notify other impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R4. | R4. Each impacted Reliability Coordinator shall operate as though the Emergency exists during each instance where Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R5. | R5. Each Reliability Coordinator that Identifies an Emergency in its Reliability Coordinator Area shall develop an action plan to resolve the Emergency during those instances where impacted Reliability Coordinators disagree on the existence of an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R6. | R6. Each impacted Reliability Coordinator shall implement the action plan developed by the Reliability Coordinator that identifies the Emergency during those instances where Reliability Coordinators disagree on the existence of an Emergency, unless such actions would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-014-3 | R7. | R7. Each Reliability Coordinator shall assist Reliability Coordinators, if requested and able, provided that the requesting Reliability Coordinator has implemented its emergency procedures, unless such actions cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 4 | 10 | NERC echoes concern about the term "assist" and when the RC is obligated to assist
IRO-017-1 | R1. | R1. Each Reliability Coordinator shall develop, implement, and maintain an outage coordination process for generation and Transmission outages within its Reliability Coordinator Area. The outage coordination process shall: [See standard for additional information.] 1.1. Identify applicable roles and reporting responsibilities including: 1.1.1. Development and communication of outage schedules. 1.1.2. Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). 1.2. Specify outage submission timing requirements. 1.3. Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. 1.4. Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
IRO-017-1 | R2. | R2. Each Transmission Operator and Balancing Authority shall perform the functions specified in its Reliability Coordinator’s outage coordination process. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10: the Reliability Coordinator’s outage coordination process specifies what performance is required; the requirement is digital with respect to level of perfomance
IRO-017-1 | R3. | R3. Each Planning Coordinator and Transmission Planner shall provide its Planning Assessment to impacted Reliability Coordinators. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: the requirement is not clear when the action needs to be taken within the standard; TPL-001-5 provides for "within 90 calendar days of completing its Planning Assessment" it is unclear whether the two requirements have the same timing need. Q4: What is the Reliability Coordinator supposed to do with the Planning Assessment? Some Planning Assessments sent to RC's are not being used.
IRO-017-1 | R4. | R4. Each Planning Coordinator and Transmission Planner shall jointly develop solutions with its respective Reliability Coordinator(s) for identified issues or conflicts with planned outages in its Planning Assessment for the Near-Term Transmission Planning Horizon. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q1: R3 and R4 could be combined to focus on what the Reliability Coordinator's obligations are with respect to the Planning Analysis Q11: The clear, unambiguous language should state that the Reliability Coordinator should provide available system adjustments such as Transmission configuration changes and re-dispatch of generation if such adjustments are realistic mitigation for SOL or IROL exceedances and can be used as Corrective Actions to be studied in the planning horizon.
IRO-018-1(i) | R1. | R1. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: the requirement relies on an understood meaning of "implement"
IRO-018-1(i) | R2. | R2. Each Reliability Coordinator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 2.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 2.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | C4: the requirement relies on an understood meaning of "implement" Q4: R2.3 is incomplete in the expectation for system operator awareness as it impacts RTA; the requirement does not align with the expectations stated in the rationale.
IRO-018-1(i) | R3. | R3. Each Reliability Coordinator shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R1. | R1. Each Transmission Operator shall act to maintain the reliability of its Transmission Operator Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R2. | R2. Each Balancing Authority shall act to maintain the reliability of its Balancing Authority Area via its own actions or by issuing Operating Instructions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R3. | R3. Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R4. | R4. Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R5. | R5. Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R6. | R6. Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R7. | R7. Each Transmission Operator shall assist other Transmission Operators within its Reliability Coordinator Area, if requested and able, provided that the requesting Transmission Operator has implemented its comparable Emergency procedures, unless such assistance cannot be physically implemented or would violate safety, equipment, regulatory, or statutory requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | 4 | 10 | Q7/Q8: Echo comments from RE about the word "assist"
TOP-001-4 | R8. | R8. Each Transmission Operator shall inform its Reliability Coordinator, known impacted Balancing Authorities, and known impacted Transmission Operators of its actual or expected operations that result in, or could result in, an Emergency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R9. | R9. Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator and known impacted interconnected entities of all planned outages, and unplanned outages of 30 minutes or more, for telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between the affected entities. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | 3 | 11 | Q8/Q11: Could be difficult to distinguish between planned and unplanned outage, and example being an intermittent RTU issue that occurs then has a planned fix for the next day.
TOP-001-4 | R10. | R10. Each Transmission Operator shall perform the following for determining System Operating Limit (SOL) exceedances within its Transmission Operator Area: 10.1. Monitor Facilities within its Transmission Operator Area; 10.2. Monitor the status of Remedial Action Schemes within its Transmission Operator Area; 10.3. Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; 10.4. Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; 10.5. Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and 10.6. Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R11. | R11. Each Balancing Authority shall monitor its Balancing Authority Area, including the status of Remedial Action Schemes that impact generation or Load, in order to maintain generation-Load-interchange balance within its Balancing Authority Area and support Interconnection frequency. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R12. | R12. Each Transmission Operator shall not operate outside any identified Interconnection Reliability Operating Limit (IROL) for a continuous duration exceeding its associated IROL Tv. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R13. | R13. Each Transmission Operator shall ensure that a Real-time Assessment is performed at least once every 30 minutes. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q8: Many entitites cannot perform RTA as specified with EMS down, which is occasionally inevitable. It is debatable whether an alternative RTA performed by the respective RC or an adjacent TOP meets the intent during an EMS outage.
TOP-001-4 | R14. | R14. Each Transmission Operator shall initiate its Operating Plan to mitigate a SOL exceedance identified as part of its Real-time monitoring or Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R15. | R15. Each Transmission Operator shall inform its Reliability Coordinator of actions taken to return the System to within limits when a SOL has been exceeded. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R16. | R16. Each Transmission Operator shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R17. | R17. Each Balancing Authority shall provide its System Operators with the authority to approve planned outages and maintenance of its telemetering and control equipment, monitoring and assessment capabilities, and associated communication channels between affected entities. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R18. | R18. Each Transmission Operator shall operate to the most limiting parameter in instances where there is a difference in SOLs. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R19. | R19. Each Transmission Operator shall have data exchange capabilities with the entities it has identified it needs data from in order to perform its Operational Planning Analyses. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R20. | R20. Each Transmission Operator shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Transmission Operator's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Balancing Authority, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R21. | R21. Each Transmission Operator shall test its primary Control Center data exchange capabilities specified in Requirement R20 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Transmission Operator shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R22. | R22. Each Balancing Authority shall have data exchange capabilities with the entities it has identified it needs data from in order to develop its Operating Plan for next-day operations. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R23. | R23. Each Balancing Authority shall have data exchange capabilities, with redundant and diversely routed data exchange infrastructure within the Balancing Authority's primary Control Center, for the exchange of Real-time data with its Reliability Coordinator, Transmission Operator, and the entities it has identified it needs data from in order for it to perform its Real-time monitoring and analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-001-4 | R24. | R24. Each Balancing Authority shall test its primary Control Center data exchange capabilities specified in Requirement R23 for redundant functionality at least once every 90 calendar days. If the test is unsuccessful, the Balancing Authority shall initiate action within two hours to restore redundant functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R1. | R1. Each Transmission Operator shall have an Operational Planning Analysis that will allow it to assess whether its planned operations for the next day within its Transmission Operator Area will exceed any of its System Operating Limits (SOLs). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R2. | R2. Each Transmission Operator shall have an Operating Plan(s) for next-day operations to address potential System Operating Limit (SOL) exceedances identified as a result of its Operational Planning Analysis as required in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R3. | R3. Each Transmission Operator shall notify entities identified in the Operating Plan(s) cited in Requirement R2 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R4. | R4. Each Balancing Authority shall have an Operating Plan(s) for the next-day that addresses: 4.1. Expected generation resource commitment and dispatch 4.2. Interchange scheduling 4.3. Demand patterns 4.4. Capacity and energy reserve requirements, including deliverability capability | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-002-4 | R5. | R5. Each Balancing Authority shall notify entities identified in the Operating Plan(s) cited in Requirement R4 as to their role in those plan(s). | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Not explicity stated when the action has to be taken.
TOP-002-4 | R6. | R6. Each Transmission Operator shall provide its Operating Plan(s) for next-day operations identified in Requirement R2 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Not explicity stated when the action has to be taken.
TOP-002-4 | R7. | R7. Each Balancing Authority shall provide its Operating Plan(s) for next-day operations identified in Requirement R4 to its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: Not explicity stated when the action has to be taken.
TOP-003-3 | R1. | R1. Each Transmission Operator shall maintain a documented specification for the data necessary for it to perform its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments. The data specification shall include, but not be limited to: 1.1. A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. 1.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 1.3. A periodicity for providing data. 1.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7/Q11: concerns around ambiguity of OPA/RTA/RTM and what can and cannot be requested in data specificiation is outline in SER Operational Data Simplification SAR. The Guidelines and Technical Basis (GTB) for TOP-010 does include a description for Real-time monitoring, but it is not in the Glossary of Terms. Real-time monitoring may include the following activities performed in Real-time: • Acquisition of operating data; • Display of operating data as needed for visualization of system conditions; • Audible or visual alerting when warranted by system conditions; and • Audible or visual alerting when monitoring and analysis capabilities degrade or become unavailable.
TOP-003-3 | R2. | R2. Each Balancing Authority shall maintain a documented specification for the data necessary for it to perform its analysis functions and Real-time monitoring. The data specification shall include, but not be limited to: 2.1. A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. 2.2. Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. 2.3. A periodicity for providing data. 2.4. The deadline by which the respondent is to provide the indicated data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | 4 | 11 | Q7/Q11: concerns around ambiguity of OPA/RTA/RTM and what can and cannot be requested in data specificiation is outline in SER Operational Data Simplification SAR. The Guidelines and Technical Basis (GTB) for TOP-010 does include a description for Real-time monitoring, but it is not in the Glossary of Terms.
TOP-003-3 | R3. | R3. Each Transmission Operator shall distribute its data specification to entities that have data required by the Transmission Operator’s Operational Planning Analyses, Real-time monitoring, and Real-time Assessment. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R4. | R4. Each Balancing Authority shall distribute its data specification to entities that have data required by the Balancing Authority’s analysis functions and Real-time monitoring. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TOP-003-3 | R5. | R5. Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [See standard for additional information.] 5.1. A mutually agreeable format 5.2. A mutually agreeable process for resolving data conflicts 5.3. A mutually agreeable security protocol | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | 4 | 11 | Q8/Q11: With Measure for R5, does an attestation from the requesting entity saying that the sender satisfied obligations meet the intent.
TOP-010-1(i) | R1. | R1. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its Real-time monitoring and Real-time Assessments. The Operating Process or Operating Procedure shall include: 1.1. Criteria for evaluating the quality of Real-time data; 1.2. Provisions to indicate the quality of Real-time data to the System Operator; and 1.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues. The criteria support identification of applicable data quality issues, which may include: • Data outside of a prescribed data range; • Analog data not updated within a predetermined time period; • Data entered manually to override telemetered information; or • Data otherwise identified as invalid or suspect.
TOP-010-1(i) | R2. | R2. Each Balancing Authority shall implement an Operating Process or Operating Procedure to address the quality of the Real-time data necessary to perform its analysis functions and Real-time monitoring. The Operating Process or Operating Procedure shall include: 2.1. Criteria for evaluating the quality of Real-time data; 2.2. Provisions to indicate the quality of Real-time data to the System Operator; and 2.3. Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues.
TOP-010-1(i) | R3. | R3. Each Transmission Operator shall implement an Operating Process or Operating Procedure to address the quality of analysis used in its Real-time Assessments. The Operating Process or Operating Procedure shall include: 3.1. Criteria for evaluating the quality of analysis used in its Real-time Assessments; 3.2. Provisions to indicate the quality of analysis used in its Real-time Assessments; and 3.3. Actions to address analysis quality issues affecting its Real-time Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: The meaning of 'quality' of data can have wide interpretation. The Requirement allows flexibility for entity to create quality criteria. See TOP-010 GTB for data quality issues.
TOP-010-1(i) | R4. | R4. Each Transmission Operator and Balancing Authority shall have an alarm process monitor that provides notification(s) to its System Operators when a failure of its Real-time monitoring alarm processor has occurred. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | Action to address the failure (and notifying RC) of alarm process monitor is implied and not explicitely stated.
Note on B9: Chris Larson: Do not grade; SER Retirement
Note on Y34: Carter Edge: requirements are intended to strengthen the collaboration and consultation between the Reliability Coordinator and the Transmission Planner or Planning Coordinator at the outset of determining the known outages that should be assessed in the Near-Term Transmission Planning Horizon. However, there is not a clear linkage to TPL-001-5, R2.1.4 or MOD-033, R2 in selecting known outages to assess that would result in issues or conflicts for which solutions should be jointly developed.
Note on Y35: Carter Edge: Standard is responsive to August 4, 2003 Blackout Report recommendation 22, SW Outage Report Recommendation 12, as well as Order 693 directives; Reliability Standards IRO-018-1 and TOP-010-1 were created to improve realtime situational awareness capabilities and enhance reliable operations by requiring reliability coordinators, transmission operators, and balancing authorities to provide operators with awareness of monitoring and analysis capabilities, including alarm availability, so that entities may take appropriate steps to ensure reliability.
Note on B56: Chris Larson: No not grade; SER retirement
Note on B59: Chris Larson: No not grade; SER retirement

## Resources
Questions: | Supporting Resource(s):
Supports a Reliability Objective (as defined by the Reliability Principles) | https://www.nerc.com/pa/Stand/Resources/Documents/Reliability_Principles.pdf
C2. Are the correct functional entities identified? | https://www.nerc.com/pa/Stand/Pages/FunctionalModel.aspx
Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or capability)? | https://www.nerc.com/pa/Stand/Resources/Documents/Results-Based_Reliability_Standard_Development_Guidance.pdf
Q4. Are the expectation(s) of each applicable functional entity clear? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q5. Does the requirement align with the standard's purpose statement? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q6. Does the requirement provide more than adequate protection of BPS? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q7. Can compliance be objectively measured? | https://www.nerc.com/pa/comp/Pages/ERO-Enterprise-Compliance-Auditor-Manual.aspx https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q8. Can it be practically implemented? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q9. Does it have a technical basis in engineering and operations? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q10. Does the requirement depend on external information to determine the required level of performance? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q11. Is the requirement language clear and unambiguous? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q12. Does it use consistent and current terminology? | https://www.nerc.com/files/glossary_of_terms.pdf https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | https://www.nerc.com/pa/Stand/Pages/Cost-Effective-Analysis-Process-CEAP-for-NERC-ERO-Standards.aspx