## 2021 Summary
2021 Standard Grading Summary
|  | Content Questions |  |  |  |  | Quality Questions
Standard | Req. | RSTC | RE | NERC | Avg | Delta | RSTC | RE | NERC | Avg | Delta
BAL-002-3 | R1. | 3 | 3 | 3 | 3 | 0 | 12 | 12 | 12 | 12 | 0
BAL-002-3 | R2. | 4 | 4 | 4 | 4 | 0 | 12 | 12 | 13 | 12.3333 | 1
BAL-002-3 | R3. | 4 | 3 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
BAL-005-1 | R1. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
BAL-005-1 | R2. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 11 | 12 | 2
BAL-005-1 | R3. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
BAL-005-1 | R4. | 4 | 4 | 4 | 4 | 0 | 12 | 12 | 12 | 12 | 0
BAL-005-1 | R5. | 4 | 4 | 4 | 4 | 0 | 12 | 11 | 13 | 12 | 2
BAL-005-1 | R6. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 12 | 12.3333 | 1
BAL-005-1 | R7. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 12.6667 | 1
EOP-004-4 | R1. | 4 | 2 | 4 | 3.3333 | 2 | 13 | 13 | 12 | 12.6667 | 1
EOP-004-4 | R2. | 4 | 3 | 3 | 3.3333 | 1 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R1. | 4 | 4 | 3 | 3.6667 | 1 | 13 | 13 | 11 | 12.3333 | 2
EOP-005-3 | R2. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 12 | 13 | 12.6667 | 1
EOP-005-3 | R3. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R4. | 4 | 4 | 4 | 4 | 0 | 12 | 12 | 12 | 12 | 0
EOP-005-3 | R5. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 12.6667 | 1
EOP-005-3 | R6. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 12.6667 | 1
EOP-005-3 | R7. | 4 | 4 | 3 | 3.6667 | 1 | 13 | 13 | 12 | 12.6667 | 1
EOP-005-3 | R8. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R9. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R10. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 12.6667 | 1
EOP-005-3 | R11. | 4 | 3 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
EOP-005-3 | R12. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R13. | 4 | 3 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
EOP-005-3 | R14. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 12 | 12.6667 | 1
EOP-005-3 | R15. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
EOP-005-3 | R16. | 4 | 3 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
EOP-006-3 | R1. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12.6667 | 1
EOP-006-3 | R2. | 3 | 4 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
EOP-006-3 | R3. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
EOP-006-3 | R4. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
EOP-006-3 | R5. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
EOP-006-3 | R6. | 4 | 4 | 4 | 4 | 0 | 13 | 12 | 13 | 12.6667 | 1
EOP-006-3 | R7. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12.6667 | 1
EOP-006-3 | R8. | 3 | 4 | 4 | 3.6667 | 1 | 12 | 13 | 13 | 12.6667 | 1
EOP-008-2 | R1. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 12 | 11 | 12 | 2
EOP-008-2 | R2. | 4 | 4 | 4 | 4 | 0 | 13 | 12 | 13 | 12.6667 | 1
EOP-008-2 | R3. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 12 | 13 | 12.6667 | 1
EOP-008-2 | R4. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 12 | 13 | 12.6667 | 1
EOP-008-2 | R5. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 13 | 12.6667 | 1
EOP-008-2 | R6. | 4 | 4 | 4 | 4 | 0 | 12 | 12 | 13 | 12.3333 | 1
EOP-008-2 | R7. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
EOP-008-2 | R8. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 11 | 13 | 12.3333 | 2

## Summary Comments
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Content Score (0-4) | Quality Score (0-13) | Combined (RSTC/Regions/NERC) Comment/Rationale | Content Delta | Quality Delta
BAL-002-3 | R1. | R1. The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: 1.1 within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. 1.2 document all Reportable Balancing Contingency Events using CR Form 1. 1.3 deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity 1.3.1 is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | Delta:0 RSTC:3 RE:3 NERC:3 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: C4/C10 - R1.3.1 might benefit from rewording so that there is a logical flow/decision tree without having to go out to EOP-002 Attachments for context and direction.; Also it's unclear why the statement of "within system constraints" is included RE: Q4: The BA owns no assets so although they can issues Operating Instructions, they should not be the only entity responsible for compliance and ACE recovery NERC: (C1, Q9) R1.3 This requirement directs the BA to deploy contingency reserves irrespective of system frequency or entity Balancing Authority ACE Limit (BAAL). If for example, the BA has recovered ACE through deployment of frequency responsive or regulating reserves there is no need for the BA to deploy contingency reserves which could have an adverse impact on system frequency and BPS reliability. The requirement could be linked to recovery of ACE to within BAAL limits. | 0 | 0
BAL-002-3 | R2. | R2. Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:12 NERC:13 | RSTC: Q11 - End the sentence after the last citation of Most Sever Single Contingency. RE: Q6: The concern with this requirement is it only requires a process to determine the MSSC and make preparations to have reserves. MSSC as the grid transforms will result in changes to how it is calculated, the amount of reserves needed etc. e.g. loss of all wind, AMI hacks disconnecting all customer load, etc. Additionally there is no data requirement or analysis to annually evaluate the process for continued validity. This standard needs to be updated in consideration of DER/VER and decarbonization. NERC: No comment | 0 | 1
BAL-002-3 | R3. | R3. Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 - What is a "design" scan rate. It is possible to have a scan rate of 6 seconds or less, but a report by exception deadbands that invalidates this. RE: C2: The BA owns no assets so although they can issues Operating Instructions, they should not be the only entity responsible for compliance and ACE recovery NERC: No comment | 1 | 1
BAL-005-1 | R1. | R1. The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
BAL-005-1 | R2. | R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:2 RSTC:12 RE:13 NERC:11 | RSTC: Q11 – Suggest rewording so that the BA has a full 45 minutes prior to reporting. Right now the time is <15 minutes grace before the reporting deadline (i.e., >30 but <45). Suggested rewording is: “R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 15 minutes after the 30-minute calculation window. RE: No comment NERC: (Q9) Is there a technical basis 45 minutes? Or simply a standoff of 15 minutes after the first 30 minutes of the inability to calculate. (Q7) The measure could be more clear. It seems more correct to ensure that the entity has dated records indicating their ability to calculate for the full evidence retention period as that is better quality evidence to validate as opposed to evidence that they weren't able to calculate ACE for some period. The compliance evidence in this example seems to prove a negative. | 0 | 2
BAL-005-1 | R3. | R3. Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. 3.1 that is available a minimum of 99.95% for each calendar year; and, 3.2 with a minimum accuracy of 0.001 Hz. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
BAL-005-1 | R4. | R4. The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: Q7 – Needs metric components outlined if needing to be measurable and comparable across time periods. RE: Q12: This requirement could be impoved by using the NERC defined term "System Operator" instead of the general word "operator", unless it was intentially generic. NERC: Q12: operator should be replaced with "System Operator" which is a defined term in the NERC Glossary. Also, this requirement should be rephrased, because it's circular - requiring the BA to provide data to it's own operators. How do you distinguish between the two? | 0 | 0
BAL-005-1 | R5. | R5. Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:2 RSTC:12 RE:11 NERC:13 | RSTC: Q1 - Could this be combined with BAL-005-1 R3 and settle on a consistent availability %? RE: Q6, Q9: The 99.5% availability is inconsistent with the availability rate in R3.1 (99.95%). Additionally there is no guidance pertaining to acceptable system conditions when the 0.5% unavailability doesn't impact reliable operation. At light and shoulder system loads, unavailability may not be an issue but if there is an EEA or capacity shortage during unavailbility it may be more impactful to reliability. NERC: No comment | 0 | 2
BAL-005-1 | R6. | R6. Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:12 | RSTC: Q1 - If you follow BAL-005-1 R1, how could you be in violation of this requirement. R6 seems duplicative with R1. RE: No comment NERC: Q11: the phrase "within a multiple Balancing Authority Interconnection" should be changed, because it combines two separate Glossary terms (Balancing Authority and Interconnection) in series, giving the impression that it's one term. There is a separate term called Balancing Authority Area. Suggested change: "within an Interconnection with multiple Balancing Authority Areas" | 0 | 1
BAL-005-1 | R7. | R7. Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: 7.1 a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, 7.2 a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q10 - It is not clear enough to determine which BA must provide this. RE: No comment NERC: No comment | 0 | 1
EOP-004-4 | R1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Delta:2 RSTC:4 RE:2 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: C3: Requirement R1 contains several required inclusions within a single requirement sentence. This requirement could be improved by splitting out the different required inclusions into different subparts. C2: As the industry reacts to Order 2222 DER aggregators will assume a more important role with respect to reliability. Contempraneously, as Distribution System Operators and Platforms are deployed there should be additonal categories of functional entities created to ensure sufficient reporting is done at the distribution level. NERC: (Q11) It is unclear whether or not "inverter based resources (IBR)" would be included in "Generation Loss" in Attachment 1. A definition for "monitoring or control" referenced in Attachment 1 would provide more clarity about which tools are used by RE's. | 2 | 1
EOP-004-4 | R2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Delta:1 RSTC:4 RE:3 NERC:3 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C2: As the industry reacts to Order 2222 DER aggregators will assume a more important role with respect to reliability. Contempraneously, as Distribution System Operators and Platforms are deployed there should be additonal categories of functional entities created to ensure sufficient reporting is done at the distribution level. NERC: C2: Attachment 1, Reportable Events, should be updated for certain "Entity with Reporting Responsibility", such as: Adding GOP to Physical Threats to its BES control center, Unplanned evacuation of its BES control center, and Complete loss of monitoring or control capability at its staffed BES control center. Also, need to review the Law Enforcement flow chart for accurancy and whether its needed. Under "No", it says "ERO conducts "Investigation"" but that may or may not actually happen. | 1 | 0
EOP-005-3 | R1. | R1. Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: 1.1. Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. 1.2. A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. 1.5. Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. 1.6. Identification of acceptable operating voltage and frequency limits during restoration. 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | Delta:1 RSTC:4 RE:4 NERC:3 | Delta:2 RSTC:13 RE:13 NERC:11 | RSTC: No comment RE: No comment NERC: C3, Q4: R1.4 Include dual fuel capability if the unit is capable of Blackstart on both fuel types. Q11: The following phrase could be worded more clearly "to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage.." | 1 | 2
EOP-005-3 | R2. | R2. Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: C4, Q11: Requirement R2 could be clearer. From the language, it is unclear if the intent is to provide the approved restoration plan to all entities identified in the plan, or only to those entities whose roles and specific tasks have changed. NERC: No comment | 1 | 1
EOP-005-3 | R3. | R3. Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C3: It could be argued that requirement R3 contains two requirements - to review the plan and to submit it to its RC. The requirement could be improved by splitting it into two requirements. NERC: No comment | 1 | 0
EOP-005-3 | R4. | R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: Q11 – Sub-requirements are confusing as it relates to context of the R4. Text. Suggest rewording to: “R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision changes its ability to implement its restoration plan. The revised restoration plan should be submitted, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. RE: Q11: Doesn't require the Plan to be provided to anyone but the RC (identified entities). May be addressed in R2 NERC: Q6: R4.1 - 90 days seems like too long have a revised restoration plan. 30-60 days seems more appropriate. | 0 | 0
EOP-005-3 | R5. | R5. Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q3 - I believe the word 'copy' implies hard copy. There are other methods and technology solutions to ensure Operators have access to the restoration plan. RE: No comment NERC: No comment | 0 | 1
EOP-005-3 | R6. | R6. Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: 6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. 6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. 6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 – Sub-requirements are confusing as it relates to context of the R6. text. Suggest rewording to: “R6. Each Transmission Operator shall verify that its restoration plan accomplishes its intended function through analysis of actual events, a combination of steady state and dynamic simulations, or testing. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify:…” RE: No comment NERC: No comment | 0 | 1
EOP-005-3 | R7. | R7. Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include:7.1. The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. 7.2. A list of required tests including: 7.2.1. The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. 7.2.2. The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. 7.3. The minimum duration of each of the required tests. | Delta:1 RSTC:4 RE:4 NERC:3 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: (C3, Q4): R7 If the unit is blackstart capable on more than one fuel type, the unit shall be tested with each fuel type once every three calendar years. | 1 | 1
EOP-005-3 | R8. | R8. Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: 8.1. System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. 8.2. Restoration priorities. 8.3. Building of cranking paths. 8.4. Synchronizing (re-energized sections of the System). 8.5. Transition of Demand and resource balance within its area to the Balancing Authority. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
EOP-005-3 | R9. | R9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
EOP-005-3 | R10. | R10. Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 - Simplify this by stating "participation in drills, exercises, or simulation as requested by Reliability Coordinator. RE: No comment NERC: No comment | 0 | 1
EOP-005-3 | R11. | R11. Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q12 – The use of “Blackstart Resource Agreements” is a proper noun that is not defined within the EOP-005-3 document nor in the NERC Glossary of Terms. Suggest changing to “Blackstart Resource agreements” and/or defining it within EOP-005-3 or in the NERC GoT. RE: C3: Requirement R11 contains two specific "shall" requirements within a single requirement. This requirement could be improved by splitting out the different parts or combining into a single statement with one "shall" NERC: No comment | 1 | 1
EOP-005-3 | R12. | R12. Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans. NERC: No comment | 1 | 0
EOP-005-3 | R13. | R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 – GO might not know or understand that the change has affected its ability to meet the TO resotoration plan until notified by the TO or through internal analysis or testing. Suggest rewording to: “…within 24 hours of identifying such change.” RE: C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans. NERC: No comment | 1 | 1
EOP-005-3 | R14. | R14.Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2 Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans. NERC: (Q4) R14.1 Include the type of unit and fuel type if dual fuel capable. | 1 | 1
EOP-005-3 | R15. | R15. Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: 15.1. System restoration plan including coordination with the Transmission Operator 15.2. The procedures documented in Requirement R12 | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans. NERC: No comment | 1 | 0
EOP-005-3 | R16. | R16. Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 - Simplify by stating "participation in drills, exercises, or simulation as requested by Reliability Coordinator. RE: C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans. NERC: No comment | 1 | 1
EOP-006-3 | R1. | R1. Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: 1.1. A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. 1.2. Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. 1.3. Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. 1.4. Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.5. Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. 1.6. Criteria for transferring operations and authority back to the Balancing Authority. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: Q11: R1 contains the following sentence which is not a requirement but a statement: " The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas." The statement reads more like a definition than a requirement. | 0 | 1
EOP-006-3 | R2. | R2. The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | Delta:1 RSTC:3 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: C3, Q11 – Current wording is ambiguous to what approved version of the restoration plan is required for distribution. Suggest rewording to: “…within 30 calendar days of revision approval. RE: No comment NERC: No comment | 1 | 1
EOP-006-3 | R3. | R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
EOP-006-3 | R4. | R4. Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. 4.1. If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
EOP-006-3 | R5. | R5. Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. 5.1. The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C3: Subpart 5.1 could be improved by splitting it into two subparts since it contains two separate requirements. NERC: No comment | 1 | 0
EOP-006-3 | R6. | R6. Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: Q11: Why is control rooms used instead of Control Center? Is it intended to be more generic? NERC: No comment | 0 | 1
EOP-006-3 | R7. | R7. Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: Q6: R7.1 and 7.2 seem incomplete in terms of what should be included in a training program. Perhaps there should be a reference to the components of R1, at a minimum. | 0 | 1
EOP-006-3 | R8. | R8. Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. 8.1. Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | Delta:1 RSTC:3 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: C1, Q13 - There are regional drills not conducted by a single RC that could satisfy this if the language was slightly modified using "participate in" instead of conduct. RE: No comment NERC: No comment | 1 | 1
EOP-008-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: 1.1. The location and method of implementation for providing backup functionality. 1.2. A summary description of the elements required to support the backup functionality. These elements shall include: 1.2.1. Tools and applications to ensure that System Operators have situational awareness of the BES. 1.2.2. Data exchange capabilities. 1.2.3. Interpersonal Communications. 1.2.4. Power source(s). 1.2.5. Physical and cyber security. 1.3. An Operating Process for keeping the backup functionality consistent with the primary control center. 1.4. Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. 1.5. A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. 1.6. An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: 1.6.1. A list of all entities to notify when there is a change in operating locations. 1.6.2. Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. 1.6.3. Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:2 RSTC:13 RE:12 NERC:11 | RSTC: No comment RE: Q11: Large distribution requiring distribution system operators with associated systems should be subject to similar requirements as TOPs. If there are large amounts of DER on the system providing essential reliablity services to the grid, the functionality of the DSO systems are important. Additionally there will visibility, situational awareness, and telemetry issues that may exist between the DSO and TOP. Why is control center not capitalized? NERC: Q4 and Q7. For entities with peer configurations (2+ fully staffed and operating CCs that are monitoring/operating a portion of the footprint but capable of absorbing the footprint of another peer CC in the event of it's loss of capability), it is not clear which is the "Primary" and which is "Backup". From a engineering perspective they are both primary and both backups. This makes it difficult to implement consistent compliance determinations. Perhaps a clarification of defined terms would be helpful. | 1 | 2
EOP-008-2 | R2. | R2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: Q11: Why is control center not capitalized? NERC: No comment | 0 | 1
EOP-008-2 | R3. | R3. Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: Q11: Needs the word "that" added . "Reliability Standards that are applicable" control center is not capitalized No time limit on length of unplanned outage NERC: No comment | 1 | 1
EOP-008-2 | R4. | R4. Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: Q11: control center is not capitalized No time limit on length of unplanned outage NERC: No comment | 1 | 1
EOP-008-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. 5.1. An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q11 – Is there a specific need to define differing time periods for Operting Plan review? • EOP-006-3 R3. states ”R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review.” • EOP-008-2 R2.5 states “R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality.”. RE: No comment NERC: No comment | 0 | 1
EOP-008-2 | R6. | R6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:12 NERC:13 | RSTC: Q12 - "control center" is a defined termin the NERC Got. Should be "Control Center" RE: Q11: control center is not capitalized NERC: No comment | 0 | 1
EOP-008-2 | R7. | R7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
EOP-008-2 | R8. | R8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:2 RSTC:13 RE:11 NERC:13 | RSTC: No comment RE: C4: There is not a specific time period in which the back-up or primary facility must be restored. Q1, Q6: This requirement does not support reliablity and should be a guideline or perhaps part of the certification program. It aligns with P-81 principles and is primarily a courtesy and administrative. NERC: No comment | 1 | 2

## RSTC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this requirement meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
BAL-002-3 | R1. | R1. The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: 1.1 within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. 1.2 document all Reportable Balancing Contingency Events using CR Form 1. 1.3 deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity 1.3.1 is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 3 | 12 | C4/C10 - R1.3.1 might benefit from rewording so that there is a logical flow/decision tree without having to go out to EOP-002 Attachments for context and direction.; Also it's unclear why the statement of "within system constraints" is included
BAL-002-3 | R2. | R2. Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 - End the sentence after the last citation of Most Sever Single Contingency.
BAL-002-3 | R3. | R3. Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 - What is a "design" scan rate. It is possible to have a scan rate of 6 seconds or less, but a report by exception deadbands that invalidates this.
BAL-005-1 | R1. | R1. The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R2. | R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 – Suggest rewording so that the BA has a full 45 minutes prior to reporting. Right now the time is <15 minutes grace before the reporting deadline (i.e., >30 but <45). Suggested rewording is: “R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 15 minutes after the 30-minute calculation window.
BAL-005-1 | R3. | R3. Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. 3.1 that is available a minimum of 99.95% for each calendar year; and, 3.2 with a minimum accuracy of 0.001 Hz. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R4. | R4. The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q7 – Needs metric components outlined if needing to be measurable and comparable across time periods.
BAL-005-1 | R5. | R5. Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1 - Could this be combined with BAL-005-1 R3 and settle on a consistent availability %?
BAL-005-1 | R6. | R6. Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1 - If you follow BAL-005-1 R1, how could you be in violation of this requirement. R6 seems duplicative with R1.
BAL-005-1 | R7. | R7. Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: 7.1 a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, 7.2 a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10 - It is not clear enough to determine which BA must provide this.
EOP-004-4 | R1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-004-4 | R2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R1. | R1. Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: 1.1. Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. 1.2. A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. 1.5. Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. 1.6. Identification of acceptable operating voltage and frequency limits during restoration. 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R2. | R2. Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R3. | R3. Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R4. | R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 – Sub-requirements are confusing as it relates to context of the R4. Text. Suggest rewording to: “R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision changes its ability to implement its restoration plan. The revised restoration plan should be submitted, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006.
EOP-005-3 | R5. | R5. Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q3 - I believe the word 'copy' implies hard copy. There are other methods and technology solutions to ensure Operators have access to the restoration plan.
EOP-005-3 | R6. | R6. Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: 6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. 6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. 6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 – Sub-requirements are confusing as it relates to context of the R6. text. Suggest rewording to: “R6. Each Transmission Operator shall verify that its restoration plan accomplishes its intended function through analysis of actual events, a combination of steady state and dynamic simulations, or testing. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify:…”
EOP-005-3 | R7. | R7. Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include:7.1. The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. 7.2. A list of required tests including: 7.2.1. The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. 7.2.2. The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. 7.3. The minimum duration of each of the required tests. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R8. | R8. Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: 8.1. System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. 8.2. Restoration priorities. 8.3. Building of cranking paths. 8.4. Synchronizing (re-energized sections of the System). 8.5. Transition of Demand and resource balance within its area to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R9. | R9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R10. | R10. Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 - Simplify this by stating "participation in drills, exercises, or simulation as requested by Reliability Coordinator.
EOP-005-3 | R11. | R11. Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 4 | 12 | Q12 – The use of “Blackstart Resource Agreements” is a proper noun that is not defined within the EOP-005-3 document nor in the NERC Glossary of Terms. Suggest changing to “Blackstart Resource agreements” and/or defining it within EOP-005-3 or in the NERC GoT.
EOP-005-3 | R12. | R12. Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R13. | R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 – GO might not know or understand that the change has affected its ability to meet the TO resotoration plan until notified by the TO or through internal analysis or testing. Suggest rewording to: “…within 24 hours of identifying such change.”
EOP-005-3 | R14. | R14.Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2 Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R15. | R15. Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: 15.1. System restoration plan including coordination with the Transmission Operator 15.2. The procedures documented in Requirement R12 | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R16. | R16. Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 - Simplify by stating "participation in drills, exercises, or simulation as requested by Reliability Coordinator.
EOP-006-3 | R1. | R1. Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: 1.1. A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. 1.2. Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. 1.3. Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. 1.4. Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.5. Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. 1.6. Criteria for transferring operations and authority back to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R2. | R2. The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C3, Q11 – Current wording is ambiguous to what approved version of the restoration plan is required for distribution. Suggest rewording to: “…within 30 calendar days of revision approval.
EOP-006-3 | R3. | R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R4. | R4. Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. 4.1. If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R5. | R5. Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. 5.1. The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R6. | R6. Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R7. | R7. Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R8. | R8. Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. 8.1. Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | 3 | 12 | C1, Q13 - There are regional drills not conducted by a single RC that could satisfy this if the language was slightly modified using "participate in" instead of conduct.
EOP-008-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: 1.1. The location and method of implementation for providing backup functionality. 1.2. A summary description of the elements required to support the backup functionality. These elements shall include: 1.2.1. Tools and applications to ensure that System Operators have situational awareness of the BES. 1.2.2. Data exchange capabilities. 1.2.3. Interpersonal Communications. 1.2.4. Power source(s). 1.2.5. Physical and cyber security. 1.3. An Operating Process for keeping the backup functionality consistent with the primary control center. 1.4. Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. 1.5. A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. 1.6. An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: 1.6.1. A list of all entities to notify when there is a change in operating locations. 1.6.2. Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. 1.6.3. Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R2. | R2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R3. | R3. Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R4. | R4. Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. 5.1. An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11 – Is there a specific need to define differing time periods for Operting Plan review? • EOP-006-3 R3. states ”R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review.” • EOP-008-2 R2.5 states “R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality.”.
EOP-008-2 | R6. | R6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 4 | 12 | Q12 - "control center" is a defined termin the NERC Got. Should be "Control Center"
EOP-008-2 | R7. | R7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R8. | R8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13

## RE
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this requirement meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
BAL-002-3 | R1. | R1. The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: 1.1 within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. 1.2 document all Reportable Balancing Contingency Events using CR Form 1. 1.3 deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity 1.3.1 is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | Q4: The BA owns no assets so although they can issues Operating Instructions, they should not be the only entity responsible for compliance and ACE recovery
BAL-002-3 | R2. | R2. Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q6: The concern with this requirement is it only requires a process to determine the MSSC and make preparations to have reserves. MSSC as the grid transforms will result in changes to how it is calculated, the amount of reserves needed etc. e.g. loss of all wind, AMI hacks disconnecting all customer load, etc. Additionally there is no data requirement or analysis to annually evaluate the process for continued validity. This standard needs to be updated in consideration of DER/VER and decarbonization.
BAL-002-3 | R3. | R3. Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: The BA owns no assets so although they can issues Operating Instructions, they should not be the only entity responsible for compliance and ACE recovery
BAL-005-1 | R1. | R1. The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R2. | R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R3. | R3. Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. 3.1 that is available a minimum of 99.95% for each calendar year; and, 3.2 with a minimum accuracy of 0.001 Hz. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R4. | R4. The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 4 | 12 | Q12: This requirement could be impoved by using the NERC defined term "System Operator" instead of the general word "operator", unless it was intentially generic.
BAL-005-1 | R5. | R5. Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | 4 | 11 | Q6, Q9: The 99.5% availability is inconsistent with the availability rate in R3.1 (99.95%). Additionally there is no guidance pertaining to acceptable system conditions when the 0.5% unavailability doesn't impact reliable operation. At light and shoulder system loads, unavailability may not be an issue but if there is an EEA or capacity shortage during unavailbility it may be more impactful to reliability.
BAL-005-1 | R6. | R6. Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R7. | R7. Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: 7.1 a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, 7.2 a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-004-4 | R1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 13 | C3: Requirement R1 contains several required inclusions within a single requirement sentence. This requirement could be improved by splitting out the different required inclusions into different subparts. C2: As the industry reacts to Order 2222 DER aggregators will assume a more important role with respect to reliability. Contempraneously, as Distribution System Operators and Platforms are deployed there should be additonal categories of functional entities created to ensure sufficient reporting is done at the distribution level.
EOP-004-4 | R2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222 DER aggregators will assume a more important role with respect to reliability. Contempraneously, as Distribution System Operators and Platforms are deployed there should be additonal categories of functional entities created to ensure sufficient reporting is done at the distribution level.
EOP-005-3 | R1. | R1. Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: 1.1. Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. 1.2. A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. 1.5. Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. 1.6. Identification of acceptable operating voltage and frequency limits during restoration. 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R2. | R2. Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | C4, Q11: Requirement R2 could be clearer. From the language, it is unclear if the intent is to provide the approved restoration plan to all entities identified in the plan, or only to those entities whose roles and specific tasks have changed.
EOP-005-3 | R3. | R3. Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3: It could be argued that requirement R3 contains two requirements - to review the plan and to submit it to its RC. The requirement could be improved by splitting it into two requirements.
EOP-005-3 | R4. | R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Doesn't require the Plan to be provided to anyone but the RC (identified entities). May be addressed in R2
EOP-005-3 | R5. | R5. Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R6. | R6. Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: 6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. 6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. 6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R7. | R7. Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include:7.1. The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. 7.2. A list of required tests including: 7.2.1. The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. 7.2.2. The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. 7.3. The minimum duration of each of the required tests. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R8. | R8. Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: 8.1. System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. 8.2. Restoration priorities. 8.3. Building of cranking paths. 8.4. Synchronizing (re-energized sections of the System). 8.5. Transition of Demand and resource balance within its area to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R9. | R9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R10. | R10. Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R11. | R11. Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3: Requirement R11 contains two specific "shall" requirements within a single requirement. This requirement could be improved by splitting out the different parts or combining into a single statement with one "shall"
EOP-005-3 | R12. | R12. Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans.
EOP-005-3 | R13. | R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans.
EOP-005-3 | R14. | R14.Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2 Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans.
EOP-005-3 | R15. | R15. Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: 15.1. System restoration plan including coordination with the Transmission Operator 15.2. The procedures documented in Requirement R12 | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans.
EOP-005-3 | R16. | R16. Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: As the industry reacts to Order 2222, DER aggregators will assume a more important role with respect to reliability and will be considered a resource supplying essential reliablity services. The are projects underway evaluating how DER may be used to support Blackstart. DER Aggregations will be considered a resource and there should be some consideration in the future to having requirements for those participating in future Blackstart plans.
EOP-006-3 | R1. | R1. Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: 1.1. A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. 1.2. Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. 1.3. Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. 1.4. Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.5. Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. 1.6. Criteria for transferring operations and authority back to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R2. | R2. The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R3. | R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R4. | R4. Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. 4.1. If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R5. | R5. Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. 5.1. The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3: Subpart 5.1 could be improved by splitting it into two subparts since it contains two separate requirements.
EOP-006-3 | R6. | R6. Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Why is control rooms used instead of Control Center? Is it intended to be more generic?
EOP-006-3 | R7. | R7. Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R8. | R8. Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. 8.1. Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: 1.1. The location and method of implementation for providing backup functionality. 1.2. A summary description of the elements required to support the backup functionality. These elements shall include: 1.2.1. Tools and applications to ensure that System Operators have situational awareness of the BES. 1.2.2. Data exchange capabilities. 1.2.3. Interpersonal Communications. 1.2.4. Power source(s). 1.2.5. Physical and cyber security. 1.3. An Operating Process for keeping the backup functionality consistent with the primary control center. 1.4. Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. 1.5. A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. 1.6. An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: 1.6.1. A list of all entities to notify when there is a change in operating locations. 1.6.2. Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. 1.6.3. Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | Q11: Large distribution requiring distribution system operators with associated systems should be subject to similar requirements as TOPs. If there are large amounts of DER on the system providing essential reliablity services to the grid, the functionality of the DSO systems are important. Additionally there will visibility, situational awareness, and telemetry issues that may exist between the DSO and TOP. Why is control center not capitalized?
EOP-008-2 | R2. | R2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: Why is control center not capitalized?
EOP-008-2 | R3. | R3. Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | Q11: Needs the word "that" added . "Reliability Standards that are applicable" control center is not capitalized No time limit on length of unplanned outage
EOP-008-2 | R4. | R4. Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 12 | Q11: control center is not capitalized No time limit on length of unplanned outage
EOP-008-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. 5.1. An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R6. | R6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: control center is not capitalized
EOP-008-2 | R7. | R7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R8. | R8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Yes | No | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 11 | C4: There is not a specific time period in which the back-up or primary facility must be restored. Q1, Q6: This requirement does not support reliablity and should be a guideline or perhaps part of the certification program. It aligns with P-81 principles and is primarily a courtesy and administrative.

## NERC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this requirement meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
BAL-002-3 | R1. | R1. The Responsible Entity experiencing a Reportable Balancing Contingency Event shall: 1.1 within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. 1.2 document all Reportable Balancing Contingency Events using CR Form 1. 1.3 deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity 1.3.1 is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that: • is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and • is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and • has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and • has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, 1.3.2 the Responsible Entity experiences: • multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 12 | (C1, Q9) R1.3 This requirement directs the BA to deploy contingency reserves irrespective of system frequency or entity Balancing Authority ACE Limit (BAAL). If for example, the BA has recovered ACE through deployment of frequency responsive or regulating reserves there is no need for the BA to deploy contingency reserves which could have an adverse impact on system frequency and BPS reliability. The requirement could be linked to recovery of ACE to within BAAL limits.
BAL-002-3 | R2. | R2. Each Responsible Entity shall develop, review and maintain annually, and implement an Operating Process as part of its Operating Plan to determine its Most Severe Single Contingency and make preparations to have Contingency Reserve equal to, or greater than the Responsible Entity’s Most Severe Single Contingency available for maintaining system reliability. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-002-3 | R3. | R3. Each Responsible Entity, following a Reportable Balancing Contingency Event, shall restore its Contingency Reserve to at least its Most Severe Single Contingency, before the end of the Contingency Reserve Restoration Period, but any Balancing Contingency Event that occurs before the end of a Contingency Reserve Restoration Period resets the beginning of the Contingency Event Recovery Period. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R1. | R1. The Balancing Authority shall use a design scan rate of no more than six seconds in acquiring data necessary to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R2. | R2. A Balancing Authority that is unable to calculate Reporting ACE for more than 30-consecutive minutes shall notify its Reliability Coordinator within 45 minutes of the beginning of the inability to calculate Reporting ACE. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | 4 | 11 | (Q9) Is there a technical basis 45 minutes? Or simply a standoff of 15 minutes after the first 30 minutes of the inability to calculate. (Q7) The measure could be more clear. It seems more correct to ensure that the entity has dated records indicating their ability to calculate for the full evidence retention period as that is better quality evidence to validate as opposed to evidence that they weren't able to calculate ACE for some period. The compliance evidence in this example seems to prove a negative.
BAL-005-1 | R3. | R3. Each Balancing Authority shall use frequency metering equipment for the calculation of Reporting ACE: 3.1. that is available a minimum of 99.95% for each calendar year; and, 3.2. with a minimum accuracy of 0.001 Hz. 3.1 that is available a minimum of 99.95% for each calendar year; and, 3.2 with a minimum accuracy of 0.001 Hz. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R4. | R4. The Balancing Authority shall make available to the operator information associated with Reporting ACE including, but not limited to, quality flags indicating missing or invalid data. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | 4 | 12 | Q12: operator should be replaced with "System Operator" which is a defined term in the NERC Glossary. Also, this requirement should be rephrased, because it's circular - requiring the BA to provide data to it's own operators. How do you distinguish between the two?
BAL-005-1 | R5. | R5. Each Balancing Authority’s system used to calculate Reporting ACE shall be available a minimum of 99.5% of each calendar year. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
BAL-005-1 | R6. | R6. Each Balancing Authority that is within a multiple Balancing Authority Interconnection shall implement an Operating Process to identify and mitigate errors affecting the accuracy of scan rate data used in the calculation of Reporting ACE for each Balancing Authority Area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: the phrase "within a multiple Balancing Authority Interconnection" should be changed, because it combines two separate Glossary terms (Balancing Authority and Interconnection) in series, giving the impression that it's one term. There is a separate term called Balancing Authority Area. Suggested change: "within an Interconnection with multiple Balancing Authority Areas"
BAL-005-1 | R7. | R7. Each Balancing Authority shall ensure that each Tie-Line, Pseudo-Tie, and Dynamic Schedule with an Adjacent Balancing Authority is equipped with: 7.1 a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, 7.2 a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-004-4 | R1. | R1. Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | (Q11) It is unclear whether or not "inverter based resources (IBR)" would be included in "Generation Loss" in Attachment 1. A definition for "monitoring or control" referenced in Attachment 1 would provide more clarity about which tools are used by RE's.
EOP-004-4 | R2. | R2. Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C2: Attachment 1, Reportable Events, should be updated for certain "Entity with Reporting Responsibility", such as: Adding GOP to Physical Threats to its BES control center, Unplanned evacuation of its BES control center, and Complete loss of monitoring or control capability at its staffed BES control center. Also, need to review the Law Enforcement flow chart for accurancy and whether its needed. Under "No", it says "ERO conducts "Investigation"" but that may or may not actually happen.
EOP-005-3 | R1. | R1. Each Transmission Operator shall develop and implement a restoration plan approved by its Reliability Coordinator. The restoration plan shall be implemented to restore the Transmission Operator’s System following a Disturbance in which one or more areas of the Bulk Electric System (BES) shuts down and the use of Blackstart Resources is required to restore the shutdown area to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage regardless of whether the Blackstart Resource is located within the Transmission Operator’s System. The restoration plan shall include: 1.1. Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. 1.2. A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. 1.3. Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. 1.4. Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. 1.5. Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. 1.6. Identification of acceptable operating voltage and frequency limits during restoration. 1.7. Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. 1.8. Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. 1.9. Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 | 11 | C3, Q4: R1.4 Include dual fuel capability if the unit is capable of Blackstart on both fuel types. Q11: The following phrase could be worded more clearly "to a state whereby the choice of the next Load to be restored is not driven by the need to control frequency or voltage.."
EOP-005-3 | R2. | R2. Each Transmission Operator shall provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the plan. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R3. | R3. Each Transmission Operator shall review its restoration plan and submit it to its Reliability Coordinator annually on a mutually-agreed, predetermined schedule. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R4. | R4. Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval, when the revision would change its ability to implement its restoration plan, as follows: 4.1. Within 90 calendar days after identifying any unplanned permanent BES modifications. 4.2. Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q6: R4.1 - 90 days seems like too long have a revised restoration plan. 30-60 days seems more appropriate.
EOP-005-3 | R5. | R5. Each Transmission Operator shall have a copy of its latest Reliability Coordinator approved restoration plan within its primary and backup control rooms so that it is available to all of its System Operators prior to its effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R6. | R6. Each Transmission Operator shall verify through analysis of actual events, a combination of steady state and dynamic simulations, or testing that its restoration plan accomplishes its intended function. This shall be completed at least once every five years. Such analysis, simulations or testing shall verify: 6.1. The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. 6.2. The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. 6.3. The capability of generating resources required to control voltages and frequency within acceptable operating limits. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R7. | R7. Each Transmission Operator shall have Blackstart Resource testing requirements to verify that each Blackstart Resource is capable of meeting the requirements of its restoration plan. These Blackstart Resource testing requirements shall include: 7.1. The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. 7.2. A list of required tests including: 7.2.1. The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. 7.2.2. The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. 7.3. The minimum duration of each of the required tests. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 12 | (C3, Q4): R7 If the unit is blackstart capable on more than one fuel type, the unit shall be tested with each fuel type once every three calendar years.
EOP-005-3 | R8. | R8. Each Transmission Operator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall include training on the following: 8.1. System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. 8.2. Restoration priorities. 8.3. Building of cranking paths. 8.4. Synchronizing (re-energized sections of the System). 8.5. Transition of Demand and resource balance within its area to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R9. | R9. Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R10. | R10. Each Transmission Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R11. | R11. Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R12. | R12. Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R13. | R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R14. | R14.Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2 Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | (Q4) R14.1 Include the type of unit and fuel type if dual fuel capable.
EOP-005-3 | R15. | R15. Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: 15.1. System restoration plan including coordination with the Transmission Operator 15.2. The procedures documented in Requirement R12 | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-005-3 | R16. | R16. Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R1. | R1. Each Reliability Coordinator shall develop and implement a Reliability Coordinator Area restoration plan. The scope of the Reliability Coordinator’s restoration plan starts when Blackstart Resources are utilized to re-energize a shutdown area of the Bulk Electric System (BES), or separation has occurred between neighboring Reliability Coordinators, or an energized island has been formed on the BES within the Reliability Coordinator Area. The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas. The restoration plan shall include: 1.1. A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. 1.2. Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. 1.3. Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. 1.4. Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. 1.5. Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. 1.6. Criteria for transferring operations and authority back to the Balancing Authority. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 12 | Q11: R1 contains the following sentence which is not a requirement but a statement: " The scope of the Reliability Coordinator’s restoration plan ends when all of its Transmission Operators are interconnected and its Reliability Coordinator Area is connected to all of its neighboring Reliability Coordinator Areas." The statement reads more like a definition than a requirement.
EOP-006-3 | R2. | R2. The Reliability Coordinator shall distribute its most recent Reliability Coordinator Area restoration plan to each of its Transmission Operators and neighboring Reliability Coordinators within 30 calendar days of creation or revision | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R3. | R3. Each Reliability Coordinator shall review its restoration plan within 13 calendar months of the last review. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R4. | R4. Each Reliability Coordinator shall review its neighboring Reliability Coordinator’s restoration plans and provide written notification of any conflicts discovered during that review within 60 calendar days of receipt. 4.1. If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R5. | R5. Each Reliability Coordinator shall review the restoration plans required by EOP-005 of the Transmission Operators within its Reliability Coordinator Area. 5.1. The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R6. | R6. Each Reliability Coordinator shall have a copy of its latest restoration plan and copies of the latest approved restoration plan of each Transmission Operator in its Reliability Coordinator Area within its primary and backup control rooms so that it is available to all of its System Operators prior to the effective date. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-006-3 | R7. | R7. Each Reliability Coordinator shall include within its operations training program, annual System restoration training for its System Operators. This training program shall address the following: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q6: R7.1 and 7.2 seem incomplete in terms of what should be included in a training program. Perhaps there should be a reference to the components of R1, at a minimum.
EOP-006-3 | R8. | R8. Each Reliability Coordinator shall conduct two System restoration drills, exercises, or simulations per calendar year, which shall include the Transmission Operators and Generator Operators as dictated by the particular scope of the drill, exercise, or simulation that is being conducted. 8.1. Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operations of the BES in the event that its primary control center functionality is lost. This Operating Plan for backup functionality shall include: 1.1. The location and method of implementation for providing backup functionality. 1.2. A summary description of the elements required to support the backup functionality. These elements shall include: 1.2.1. Tools and applications to ensure that System Operators have situational awareness of the BES. 1.2.2. Data exchange capabilities. 1.2.3. Interpersonal Communications. 1.2.4. Power source(s). 1.2.5. Physical and cyber security. 1.3. An Operating Process for keeping the backup functionality consistent with the primary control center. 1.4. Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. 1.5. A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. 1.6. An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: 1.6.1. A list of all entities to notify when there is a change in operating locations. 1.6.2. Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. 1.6.3. Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 | 11 | Q4 and Q7. For entities with peer configurations (2+ fully staffed and operating CCs that are monitoring/operating a portion of the footprint but capable of absorbing the footprint of another peer CC in the event of it's loss of capability), it is not clear which is the "Primary" and which is "Backup". From a engineering perspective they are both primary and both backups. This makes it difficult to implement consistent compliance determinations. Perhaps a clarification of defined terms would be helpful.
EOP-008-2 | R2. | R2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have a copy of its current Operating Plan for backup functionality available at its primary control center and at the location providing backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R3. | R3. Each Reliability Coordinator shall have a backup control center facility (provided through its own dedicated backup facility or at another entity’s control center staffed with certified Reliability Coordinator operators when control has been transferred to the backup facility) that provides the functionality required for maintaining compliance with all Reliability Standards are applicable to the primary control center functionality. To avoid requiring a tertiary facility, a backup facility is not required during: • Planned outages of the primary or backup facilities of two weeks or less • Unplanned outages of the primary or backup facilities | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R4. | R4. Each Balancing Authority and Transmission Operator shall have backup functionality (provided either through a facility or contracted services staffed by applicable certified operators when control has been transferred to the backup functionality location) that includes monitoring, control, logging, and alarming sufficient for maintaining compliance with all Reliability Standards that are applicable to a Balancing Authority’s and Transmission Operator’s primary control center functionality. To avoid requiring tertiary functionality, backup functionality is not required during: • Planned outages of the primary or backup functionality of two weeks or less • Unplanned outages of the primary or backup functionality | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator, shall annually review and approve its Operating Plan for backup functionality. 5.1. An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R6. | R6. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have primary and backup functionality that do not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R7. | R7. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct and document results of an annual test of its Operating Plan that demonstrates: 7.1. The coordination role of the Reliability Coordinator; and 7.2. Re-establishing the Interconnection. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
EOP-008-2 | R8. | R8. Each Reliability Coordinator, Balancing Authority, and Transmission Operator that has experienced a loss of its primary or backup functionality and that anticipates that the loss of primary or backup functionality will last for more than six calendar months shall provide a plan to its Regional Entity within six calendar months of the date when the functionality is lost, showing how it will re-establish primary or backup functionality. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13

## Resources
Questions: | Supporting Resource(s):
Supports a Reliability Objective (as defined by the Reliability Principles) | https://www.nerc.com/pa/Stand/Resources/Documents/Reliability_Principles.pdf
C2. Are the correct functional entities identified? | https://www.nerc.com/pa/Stand/Pages/FunctionalModel.aspx
Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or capability)? | https://www.nerc.com/pa/Stand/Resources/Documents/Results-Based_Reliability_Standard_Development_Guidance.pdf
Q4. Are the expectation(s) of each applicable functional entity clear? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q5. Does the requirement align with the standard's purpose statement? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q6. Does the requirement provide more than adequate protection of BPS? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q7. Can compliance be objectively measured? | https://www.nerc.com/pa/comp/Pages/ERO-Enterprise-Compliance-Auditor-Manual.aspx https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q8. Can it be practically implemented? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q9. Does it have a technical basis in engineering and operations? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q10. Does the requirement depend on external information to determine the required level of performance? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q11. Is the requirement language clear and unambiguous? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q12. Does it use consistent and current terminology? | https://www.nerc.com/files/glossary_of_terms.pdf https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | https://www.nerc.com/pa/Stand/Pages/Cost-Effective-Analysis-Process-CEAP-for-NERC-ERO-Standards.aspx