## Sheet1
Filing | Region | Registered Entity Name | NCR | NERC Violation ID | Standard | Req. | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity
2018-02-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017071 | CIP-002-5.1 | R1 | MRO_URE1 stated it was in noncompliance with CIP-002-5.1 P1.2 because it did not have an accurate listing of medium impact BES Cyber Systems at a single substation. Prior to July 1, 2016, MRO_URE1 proactively updated the CIP-002-5.1 P1.2 Medium Impact BES Cyber System list for the affected substation. MRO_URE1 listed a BES Cyber Asset (a relay) that was expected to be installed prior to July 1, 2016 instead of the relay that was currently installed. The new relay was not installed prior to July 1, 2016, and the list was inaccurate on July 1, 2016. The list remained inaccurate for approximately two and a half months, when a change in staff occurred and the discrepancy was noticed. The cause of the noncompliance was that MRO_URE1's process to create lists of medium impact BES Cyber System lacked rigor on how to treat future changes. The duration of the noncompliance was approximately two and a half months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was relatively brief (less than three months). The impacted substation was not categorized as a Critical Asset under CIP Version 3. Additionally per MRO_URE1, a comprehensive review determined the issue was limited to a single BES Cyber Asset at a single substation. Further per MRO_URE1, the affected BES Cyber Asset does not have any routable connectivity, nor does it have any interactive access. Finally, the affected BES Cyber Asset is located within a Physical Security Perimeter (PSP). No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this noncompliance, MRO_URE1: 1) updated its list of Medium Impact BES Cyber Systems; and 2) implemented a new procedure in its Cyber Asset Change Control policy. MRO verified that mitigating activities were completed.
2018-02-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017072 | CIP-004-6 | R3 | MRO_URE1stated it was in noncompliance with CIP-004-6 P3.4 because a Physical Access System (PACS) Administrator provisioned an access badge for a contractor without following the Physical Access Card issuing procedure. As a result, the contractor had unescorted physical access to the Control Center Physical Security Perimeter (PSP) before having a Personnel Risk Assessment (PRA) performed. The access remained for six days until it was discovered by a weekly access review. The cause of the noncompliance was that a PACS Administrator did not follow the procedure for provisioning an unescorted PSP access card. The duration of the noncompliance was six days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was brief due to the successful utilization of a secondary control (weekly access reviews). These weekly access reviews are much more frequent than the quarterly reviews that are required by CIP-004-6 P4.2. Additionally per MRO_URE1, the contractor remained in proximity to System Operators who were in a position to recognize any malicious activity. Further per MRO_URE1, the contractor was not granted electronic cyber access. Finally per MRO_URE1, the contractor was re-granted physical access after a PRA was conducted. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this noncompliance, MRO_URE1: 1) disabled the contractor's badge; and 2) sent an email to all of the PACS Administrators reiterating the importance of following the Physical Access Card Issuing Procedure, which was attached to the email.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017017419 | CIP-010-2 | R1. | NPCC_URE1 submitted a Self-log stating that it had discovered it was in noncompliance with CIP-010-2 R1 Part 1.2 after completing its CIP monthly configuration review. The noncompliance lasted approximately one (1) month. An IT security contractor made an undocumented baseline change to one firewall when the contractor updated the operating system of the device while they were performing assigned, documented, and approved work to move a workstation. The IT security contractor did not document or receive authorization for the adhoc baseline change, as required per CIP-010-2 R1 Part 1.2. The root cause of this noncompliance was human error related to the employee’s failure to follow formal documented procedures. | The noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. At the time of the issue, the ESP in scope had two firewalls acting as active in the membership when they should have been active/standby. The firewalls were unable to sync due to the operating system difference, with that misconfiguration if one firewall would have failed some disruption if not a total failure/downtime scenario could have occurred. In this instance, updating the operation system ensured the future reliability of the network in scope. Only one firewall required a reboot and the other firewall remained in the active state. No network disruption was observed. In the instance that the misconfiguration or update of the operating system resulted in a total failure/downtime scenario, only the communication through the corporate facing interface would have been disrupted. The EMS and operational functionalities would not have been impacted. In the event the EMS and operational functionalities at this site did experience an impact, the entity would move operations to its backup control center. No harm is known to have occurred as a result of this noncompliance. | To mitigate the issue, NPCC_URE1: 1. Created IT incident ticket to investigate the issue 2. Created emergency change order to document the change 3. Counseled and trained the responsible employee on current procedures and related NERC CIP requirements 4. Emphasized to staff the potential risk of human error when completing NERC CIP-related tasks NPCC has verified the completion of all mitigation activity.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017017420 | CIP-007-3a | R5. | NPCC_URE1 submitted a Self-Log stating that it had discovered it was in noncompliance with CIP-007-3a R5 after completing its annual vulnerability assessment. This noncompliance lasted approximately seven (7) months. The entity received its annual vulnerability report from a third party vendor. After investigating the assessment findings, the entity found that several accounts were in noncompliance. The entity found that a script had failed to run on several workstations when it performed its annual password changes. The entity failed to follow its documented procedure to confirm the script was successful. As a result, the entity was in noncompliance when it failed to change the local administrator account annually under CIP-007-3a R5.3.3 and within the 15 calendar month requirement under CIP-007-6 R5 Part 5.6. The root cause of the noncompliance was failure to follow documented processes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The accounts in scope can only be accessed locally on SCADA workstations. Local unescorted access to the workstations is limited to individuals that have received PRA, training, and authorization for access to the PSP. The workstations logically reside on a secure ESP that is monitored by an intrusion protection systems on the entity’s firewall gateways, which would alert the entity of suspicious network traffic coming from the workstations in scope. The local administrator accounts in scope do not have access to the SCADA application, and are used to install software and make Operating System (OS) level changes. The entity further performs a 15 day log review that would identify virus activity, login failures, new administrators, audit log clearing, account lockout, account creation, account deletion, account disablement, group membership changes and password changes. The workstations in scope are further protected by antivirus software that would immediately alert if suspicious software was installed. No harm is known to have occurred as a result of this noncompliance. | To mitigate this issue, NPCC_URE1 1. Changed local administrator passwords on all workstations in scope. 2. Updated procedure to include validation after password script updates are run. 3. Updated the config file used for validation of password changes to include workstations in scope. NPCC has verified the completion of all mitigation activity.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017017421 | CIP-006-6 | R2. | NPCC_URE1 submitted a Self-Log stating that it discovered it was in noncompliance with CIP-006-6 R2, while investigating a business related issue. This noncompliance lasted two (2) days. Specifically, a contractor’s initial and last exit dates and times, the visitors name, and the point of contact were not entered into the entity’s log books on two occasions, when a contractor entered and exited a High Impact PSP during a project to replace phone turrets. The root cause of the noncompliance was misunderstanding of responsibilities. Specifically, the dispatchers with CIP access at the PSP in scope mistakenly believed that a supervisor was the only person responsible for log book entries. The idea that the supervisors were the only people responsible for PSP log entries stem from control room management not wanting to disrupt the situational awareness of the dispatchers. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the contractor in scope was at all times with and in the line of sight of the control room dispatchers on both occasions. Further, the high impact BES cyber asset workstations located within the PSP in scope are not configured to allow operation of the Bulk Electric System (BES). No harm is known to have occurred during the two occurrences of noncompliance. | To mitigate the issue, NPCC_URE1: 1. Clarified the NERC Requirements and company policy with management of PSP in scope. To prevent reoccurrence of the issue, NPCC_URE1: 1. Held discussions with group involved referencing annual required CIP training and reinforced CIP responsibilities. NPCC has verified the completion of all mitigation activity.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2017017422 | CIP-006-6 | R2. | NPCC_URE2 submitted a Self-Log stating that it had an issue of CIP-006-6 R2. This noncompliance lasted one (1) day. Specifically, the entity allowed a contractor (cleaner) to enter one newly designated PSP to remove trash. The contractor (cleaner) was not continuously escorted once within the PSP. The root cause of this noncompliance was human error. The entity personnel were not accustomed to escorting visitors in this newly designated PSP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. At the time of the issue there were several High Impact engineering workstations within the PSP. The workstations are configured for read only access to provide operations support from SCADA screen development to EMS system monitoring. The contractor in scope did not have electronic access to the workstations. The contractor further did not gain unescorted access to the ESCC or the SOC. The contractor in scope had a background check which includes e-verify and criminal background checks. The entity also reviewed security video recordings. The recordings do not show the cleaner doing anything but emptying the waste baskets. No harm is known to have occurred as a result of this noncompliance. | To mitigate the issue, NPCC_URE2: 1. Communicated CIP requirements for new PSP to staff. To prevent reoccurrence of the issue, NPCC_URE2: 1. Certified the cleaner employees for CIP and granted unescorted access to PSP. NPCC has verified the completion of all mitigation activity.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2017017423 | CIP-006-6 | R1. | NPCC_URE2 submitted a Self-Log stating that it discovered it was in noncompliance with CIP-006-6 R1 part 1.3, during shift turnover when a security guard did an assessment of alarms. This noncompliance lasted approximately ten (10) hours. Specifically, an engineering technician opened multiple PSP cabinet doors to perform scheduled work. When work was completed, the engineering technician closed the cabinet doors except for one and then called the security guard to verify the doors were closed. The security guard who answered the call, due to human error, did not verify all doors were shut and gave the technician an ‘all clear’. After receiving the ‘all clear’ from the security guard, the technician left work, leaving the one PSP door open. The root cause of the noncompliance was lack of situational awareness. Specifically, the engineering technician failed to physically check that all cabinet doors were secure upon completion of work, and the security guard on shift failed to verify all doors were closed. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the PSP is located within a protected computer room that is equipped with video camera monitoring directly on the cabinet. Further, once the entity discovered the issue, the security guards monitored the PSP via the camera footage, until the PSP could be secured. Specifically, the computer room is secured with a badge access system and access is limited to a small group of company personnel and CIP certified contractors. The investigation team reviewed security camera footage and confirmed that no unauthorized individuals gained access to the PSP in scope while it was unsecured. No harm is known to have occurred as a result of this noncompliance. | To mitigate the issue, the entity: 1. Secured the PSP door To prevent reoccurrence of the issue, the entity: 1. Issued a new security turnover procedure to the security guards and their supervisors to make sure all alarms and open cabinets are resolved. 2. Modified alarm displays in the access control system so that alarms associated with CIP PSPs are now color coded and thereby more easily identified. NPCC has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017018065 | CIP-007-6 | R4 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R4. Pursuant to CIP-007-6 R4.4, the entity’s security incident monitoring process requires it to review event log summaries biweekly. The entity’s biweekly review was due but was not marked as complete in the entity’s compliance task tool until five days later. Thus, the biweekly review was five days late. The employee who completed the task included a note in the task stating that the work was completed on time, but not documented until five days later. However, the entity determined that this was a potential violation because it did not have evidence to support the note indicating the task was completed on time. Cyber Assets associated with this biweekly review are generation dispatch related assets. The review did not reveal any abnormalities on the entity’s system. The root cause was insufficient verification controls to ensure that the review tasks are completed on time. The duration of the noncompliance was approximately five days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The purpose of the biweekly review is to identify security incidents that were not caught through alerting or other real-time controls. However, here, the entity was only five days late in conducting its biweekly review, and timely completed the prior and subsequent reviews, thus reducing the time that there was any increased risk of an undetected compromise to the entity’s system. No harm is known to have occurred. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) created a re-occurring monthly meeting that will discuss and remind the Subject Matter Experts to complete a review of summary or sample of event logs on time according to the biweekly tasks; 2) created a procedure to assign a control procedure task to a Group/Team rather to an individual to ensure task coverage; 3) created a dashboard for tasks for this control procedure and published it during monthly meetings to increase visibility and help track the steps to ensure timely completion; and 4) sent out recurring biweekly emails to each team reminding them of the biweekly review task due. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017018407 | CIP-002-5.1 | R2 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2. While performing an annual review of the entity's CIP-002-5 Impact Evaluation and in preparation of the 15 month Requirement (R2.2.1) to review the identification in R1, the entity discovered that the Impact Evaluation the entity performed did not have the approval of the CIP Senior Manager as required by R2.2. Specifically, the entity could not locate a version of the Impact Evaluation signed by the CIP Senior Manager. Both the NERC Manager who prepared the Impact Evaluation and the CIP Senior Manager at the time the document was completed (and Self-Certification submitted) are no longer with the entity. The entity performed its Impact Evaluation using a template provided to the entity’s parent company by a Regional Entity. The entity’s prior NERC Compliance Manager (who was terminated by the entity) performed the Impact Evaluation. In support of that Impact Evaluation, the entity Self-Certified via the ReliabilityFirst CDMS system that the entity was “Low Impact” which is consistent with the Impact Evaluation. The root of the noncompliance is that the entity can no longer find a copy of the Impact Evaluation signed by the CIP Senior Manager. The entity’s new CIP Senior Manager performed and signed a revised Impact Evaluation that resulted in a “Low Impact” categorization. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the previous CIP Senior Manager at the entity was not properly trained to ensure that a signed copy of the Impact Evaluation was stored. Verification is involved because the entity did not have an effective internal control in place to verify that a copy of the Impact Evaluation was signed by the CIP Senior Manager and stored. That lack of an effective internal control is a root cause of this noncompliance. The duration of the noncompliance was approximately one year. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that an environment at the entity may be created where the entity is unaware of Bulk Electric System (BES) Cyber Assets that it is required to protect and that could lead to misoperation or instability in the BPS. The risk is minimized because this is primarily a documentation issue as the entity stated that it performed the Low Impact Evaluation and that it was signed by the CIP Senior Manager at that time, but the document was lost during the transition of both the NERC Manager and the CIP Senior Manager. Lastly, when the entity performed the Impact Evaluation, it confirmed that the entity is Low Impact. Because the entity is Low Impact, the entity does not have to maintain a discrete list of low impact BES Cyber Systems. No harm is known to have occurred. ReliabilityFirst considered the entity’s CIP-002-5.1 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity performed an Impact Evaluation that included the Low Impact Rating Criteria which was signed by the CIP Senior Manager. To prevent reoccurrence, the compliance manager implemented a policy of maintaining all regulatory documents on the entity's parent company's SharePoint directory. This will ensure that all documents are timely updated and stored.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017018062 | CIP-007-6 | R4 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R4. Pursuant to CIP-007-6 R4.4, the entity’s security incident monitoring process requires it to review event log summaries biweekly. The entity’s biweekly review was due but was not marked as complete in the entity’s compliance task tool until five days later. Thus, the biweekly review was five days late. The employee who completed the task included a note in the task stating that the work was completed on time, but not documented until five days later. However, the entity determined that this was a potential violation because it did not have evidence to support the note indicating the task was completed on time. Cyber Assets associated with this biweekly review are generation dispatch related assets. The review did not reveal any abnormalities on the entity’s system. The root cause was insufficient verification controls to ensure that the review tasks are completed on time, and thus this noncompliance involves the management practice of verification. The duration of the noncompliance was approximately five days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The purpose of the biweekly review is to identify security incidents that were not caught through alerting or other real-time controls. However, here, the entity was only five days late in conducting its biweekly review, and timely completed the prior and subsequent reviews, thus reducing the time that there was any increased risk of an undetected compromise to the entity’s system. No harm is known to have occurred. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) created a re-occurring monthly meeting that will discuss and remind the Subject Matter Experts to complete a review of summary or sample of event logs on time according to the biweekly tasks; 2) created a procedure to assign a control procedure task to a Group/Team rather to an individual to ensure task coverage; 3) created a dashboard for tasks for this control procedure and published it during monthly meetings to increase visibility and help track the steps to ensure timely completion; and 4) sent out recurring biweekly emails to each team reminding them of the biweekly review task due. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017018339 | CIP-004-6 | R5 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. During the entity's 15 calendar month access review, the entity identified that authorized electronic access to High Impact Bulk Electric System (BES) Cyber Systems was not removed for four users. All four of the users were part of the group which was undergoing organizational changes requiring the assignment of new position roles and permissions. Many of the permissions remained the same for the four users in the new position roles and for others, permissions were being removed due to a shift in team responsibilities. The tickets for all four of the users at issue were mistakenly closed before a follow up was completed to confirm the relevant access rights were removed for the users. Because these tickets were mistakenly closed, these four users improperly retained authorized electronic access rights. The entity also discovered a second instance when the initial automated user access report yielded two occurrences where users still had active CIP permissions accounts without any active CIP permissions after changing responsibilities on the Cyber Security team. The access changes were updated without the use of the recently implemented automated script. In both cases, the ticket did not specifically request the disabling of the respective CIP permission user accounts. The entity's records show that neither user's CIP permissions account was ever accessed after their access should have been removed. This noncompliance involves the management practices of asset and configuration management, verification, and validation. Asset and configuration management is involved because the entity did not effectively remove the authorized electronic access these users no longer required when they internally switched jobs. The entity did not have an effective process in place to ensure access that was no longer needed was timely removed and that lack of an effective process is a root cause of this noncompliance. The entity also failed to verify and validate that such access was removed. The duration of the noncompliance was approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is unauthorized individuals accessing and compromising BES Cyber Systems. The risk is minimized because the first four instances were related to trusted members of the team who subsequently retained many of the same cyber access permissions after organizational changes. All of the individuals at issue were trusted employees who had previously been provisioned such access in order to complete daily job functions. Lastly, the second noncompliance also occurred following a reorganization of departments and roles and the two trusted members of the Cyber Security team that improperly retained electronic access never accessed their CIP permissions accounts after they switched job functions. No harm is known to have occurred. ReliabilityFirst determined that the entity's compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) verified that the access change process is followed and appropriate evidence is collected; 2) submitted tickets to remove cyber access, or document the necessity to retain access; 3) conducted refresher training for staff on the revocation process for access changes. Training and ticket reviews will help ensure that the approved procedures and processes are being followed in the future; and 4) revised the procedure for access revocation and distributed that to the team. Additionally, as a detective measure, entity routinely performs reviews of access changes using automated reports and by conducting quarterly reviews. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017018160 | CIP-010-2 | R1 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1. The entity implemented a network protocol analyzer security patch without the required change ticket and without performing all of the required testing. Entity IT security approved the patch for release as part of the patch review process. The entity also installed and validated the patch on test devices. Although the patch was functionally tested on test servers, the entity did not perform the required review of the ports, services, and security controls before implementing the patch. The entity also did not complete the required change ticket for the installation of this patch. The technician responsible for assessing and implementing this patch had not previously worked on network protocol analyzer security patches and was unfamiliar with the vendor and the patching process for network protocol analyzer security patches. The technician had recently been assigned network protocol analyzer security patching responsibilities and did not realize that a change ticket and the associated testing of ports, services, and security controls was required for network protocol analyzer security patches. The entity discovered this noncompliance as part of a weekly baseline monitoring and review for unauthorized changes. This noncompliance involves the management practices of workforce management and verification. Workforce management through ineffective training is involved because the technician responsible for assessing and implementing network protocol analyzer security patches had not been properly trained on the process to follow for assessing and implementing network protocol analyzer security patches. That ineffective training is a root cause of this noncompliance. Verification is involved because the entity did not have an effective internal control in place to verify that this technician knew how to properly assess and implement network protocol analyzer security patches. The duration of the noncompliance was approximately one week. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is permitting an unauthorized patch to be implemented could adversely affect overall system security. The risk is minimized because the network protocol analyzer security patch at issue had been reviewed and approved by entity IT security prior to implementation and the patch had also been tested on like devices prior to implementation which reduces the likelihood that the patch would cause any harm once implemented. Upon discovery of the implemented patch, the entity approved a software baseline for the patch and created a change ticket so the ports, services and security controls could be evaluated retroactively. The entity had successfully processed numerous CIP change tickets without incident prior to this noncompliance. Lastly, the entity discovered this noncompliance as part of its weekly baseline monitoring and review for unauthorized changes which limited the duration to six days and demonstrates an effective detective control. No harm is known to have occurred. ReliabilityFirst determined that the entity's compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) created a software baseline for the patch; 2) created a change ticket retroactively and conducted testing retroactively to ensure that impacts to the security controls or ports and services had not been missed; 3) verbally counseled the employee. The employee later signed an attestation acknowledging the verbal counseling; 4) sent an email communication to all change ticket users reminding them of key procedural requirements related to change management; 5) developed a refresher training and guidance that would apply when an employee assumes new responsibilities related to CIP change management. Counseling and training will help ensure that the approved procedures and processes are being followed in the future. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017947 | CIP-004-6 | R5 | RFC_URE5 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. For three employees one of the entity’s joint operating companies, access was not removed within 24 hours as required. As a tool to manage access for its joint operating company’s employees, the entity sends weekly emails to its joint operating companies notifying them who has access to the entity's assets as of that week. The entity received notification from it's joint operating company that three employees still had physical access according to the weekly access review email, but that the employees should no longer have had access due to their resignations from employment. The joint operating company emailed the entity the week prior to request that access be removed for these three employees, but the entity missed the email and did not remove access as requested. Upon discovery of the error, the entity immediately revoked the employee’s physical access. Regarding the root causes, first, the entity did not have sufficient verification controls to ensure it followed up on the joint operating company’s initial email notifying the entity of the need to remove access. In response to the noncompliance, the entity identified additional verification controls that could have helped prevent the noncompliance. For future date access removals, the security specialist will flag the access removal requests for follow-up before the required access removal date, and forward the notification to the Security Specialist’s work e-mail address and create a calendar event for the future access removal. Additionally, the joint operating company failed to follow the additional step in the entity’s joint operating company work instructions that require the joint operating company to call the entity’s security center on the day of separation to verify that access is removed. The duration of the noncompliance was approximately eight days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the former employees had only physical access, and not cyber access. The entity provisioned physical access to the joint operating company employees on their joint operating company access badges, and the joint operating company recovered these badges from the employees and terminated access on the badges upon the employees’ resignations. Thus, from that time forward, the employees could not access any entity assets. Second, the entity was only eight days late in revoking access due to the entity’s detective control in the form of weekly review emails, which reduced the period of time that the BPS was put at any increased risk of being compromised as a result of the noncompliance. Third, the former employees had up-to-date training and Personnel Risk Assessments. No harm is known to have occurred. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) removed access in the entity's system; 2) provided access removal email refresher training to the joint operating company contact; 3) provided refresher training to the center which handles security for the entity; 4) provided refresher training to the security specialist and back-up personnel; and 5) revised the internal procedure to flag follow-up future access removal emails, forward the emails to an acting security specialist business email, and create calendar events as reminders to remove access.
2018-02-28 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity (SPPRE_URE1) | NCRXXXXX | SPP2017017917 | CIP-004-6 | R3; R3.5 | SPPRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3.5 because it did not conduct a Personnel Risk Assessment (PRA) for one individual with authorized electronic access within seven (7) years of the previous PRA completion date. The duration of this issue of noncompliance was 78 days, from the date the SPPRE_URE1’s employee’s PRA should have been renewed, through the date the employee’s PRA was renewed. The root cause of this noncompliance was human error, i.e. failure to follow SPPRE_URE1’s new process and perform a final assurance check to ensure all required training and PRAs were current and not about to expire prior to the SPPRE_URE1 compliance program production date. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to timely update a PRA could cause SPPRE_URE1 to miss changes in an individual’s criminal history, an element of potential risk for safety and security. Notwithstanding, the risk of noncompliance was mitigated because the employee: (1) is a long-term SPPRE_URE1 employee with no performance issues; (2) had a prior successful PRA on file; (3) completed cyber security training prior to receiving access to SPPRE_URE1’s BES Cyber Systems; (4) did not have unescorted physical access to BES Cyber Systems; and, (5) electronic access logs existed for all actions taken by the employee during the time period and no unauthorized access occurred. The updated PRA did not have any adverse findings. No harm is known to have occurred. | To mitigate this noncompliance, SPPRE_URE1: 1) disabled the employee’s electronic access upon discovery of the expired PRA; 2) completed a new PRA; 3) modified SPPRE_URE1’s access review process to confirm PRAs on a monthly basis to ensure requested renewals of PRAs are processed and completed by SPPRE_URE1’s human resources department prior to PRA expiration dates; and, 4) reviewed its access list to identify any PRAs that are due to be renewed in the current and upcoming calendar years. SPP RE has verified the completion of all mitigation activity.
2018-02-28 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity (SPPRE_URE1) | NCRXXXXX | SPP2017018074 | CIP-004-6 | R4; R4.1, R4.1.1, R4.1.2, R4.1.3 | SPPRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R4.1.1, R4.1.2, and R4.1.3. While performing SPPRE_URE1’s first quarterly electronic and physical access review, SPPRE_URE1 discovered that it had two instances of noncompliance with CIP-004-6 R4.1.1, one instance of noncompliance with R4.1.2, and one instance of noncompliance with R4.1.3. The noncompliance involved three SPPRE_URE1 employees. Two employees (Employee #1 and #2) had unauthorized electronic access (R4.1.1) to SPPRE_URE1’s BES Cyber Systems. Employee #2 also had unauthorized physical access (R4.1.2) to SPPRE_URE1’s Energy Management System (EMS) located within SPPRE_URE1’s Physical Security Perimeter (PSP). Employee #3 had unauthorized electronic access to the corporate designated storage location that houses SPPRE_URE1’s BES Cyber System Information (R4.1.3). The duration of the instance of noncompliance associated with Employee #1 was 77 days, from the date SPPRE_URE1 BES Cyber Assets were required to be compliant with CIP-004-6, thorugh the date Employee #1’s unauthorized electronic access was disabled. The duration associated with Employee #2 was 88 days, from the date SPPRE_URE1 BES Cyber Assets were required to be compliant with CIP-004-6, thorugh the date the employee’s unauthorized electronic and physical access was disabled. The duration associated with Employee #3 was 58 days, from the date unauthorized access was granted, thorugh the date Employee #3’s access to the designated storage location that houses BES Cyber System Information was properly granted. The root cause of this noncompliance was human error, i.e. failure to follow SPPRE_URE1’s process and SPPRE_URE1’s access management procedure to perform a final assurance check to ensure all required access approvals were current prior to the SPPRE_URE1 Compliance production date, and a failure to follow SPPRE_URE1’s access management procedure and access request. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-004-6 R4.1 has the potential to affect the reliable operation of the BPS by providing the opportunity for unauthorized personnel to access BES Cyber Systems and BES Cyber System information, which potentially could be used to manipulate the SPPRE_URE1 EMS or affect monitoring, alarming, and dispatching to SPPRE_URE1’s generation facilities and the Intercontrol Center Communications Protocol signal to SPPRE_URE1’s Reliability Coordinator. Notwithstanding, SPPRE_URE1 verified that Employees #1 and #2 made no attempts to access the BES Cyber Systems during the period of unauthorized access. The accesses were immediately revoked upon discovery, which were found during SPPRE_URE1’s first required quarterly access review. Regarding Employee #3, the employee had a completed personnel risk assessment and cyber security training was on file and was intended to have access to the information to perform assigned job duties and was shortly granted access after discovery. The access was inadvertently granted when Employee #3 was added to an application group. No harm is known to have occurred. | To mitigate this noncompliance, SPPRE_URE1: 1) disabled electronic access immediately upon discovery for Employees #1 and #2 who had unauthorized access to BES Cyber Assets; 2) initiated and approved a CIP access request for Employee #3; 3) reviewed its CIP-004 personnel accounts and access lists to ensure they are accurate; 4) enhanced its procedures to clarify roles and responsibilities for granting account access to BES Cyber Systems and BES Cyber System designated storage locations; and, 5) conducted training on SPPRE_URE1’s applicable access procedures. SPP RE has verified the completion of all mitigation activity.
2018-02-28 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity (SPPRE_URE1) | NCRXXXXX | SPP2017017717 | CIP-007-6 | R2; R2.1, R2.2, R2.3 | SPPRE_URE3 submitted a Self-Report to Southwest Power Pool Regional Entity (SPP RE), stating that it was in noncompliance with CIP-007-6 R2.1, R2.2, and R2.3. SPPRE_URE3’s patch management and change process management processes utilizes an automated patch management system to identify patches. The automatic patch management system did not identify all patches for four SPPRE_URE3 Cyber Assets (R2.1). Because the patches for these Cyber Assets could only be tracked by a manual process, the associated patches were not evaluated or applied within 35 calendar days (R2.2, R2.3). One of the software patches was evaluated within 35 calendar days; however, the patch was not applied to two of four servers within 35 calendar days (R2.3). The duration of this issue of noncompliance was from the date SPPRE_URE3 BES Cyber Assets were required to be compliant with CIP-007-6, through the date SPPRE_URE3 completed its mitigation of noncompliance. The root cause of this noncompliance was a process deficiency because SPPRE_URE3 lacked a defined and documented process to manually track patches, which resulted in the oversight of patches for four software components. The root cause for the software patch that was evaluated within 35 calendar days but not applied timely was human error. The software was evaluated within the 35 calendar days, however, SPPRE_URE3 employees failed to follow its verification process following implementation of a patch through its change management process and patch all intended servers within 35 calendar days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly evaluate a security patch for applicability has the potential to affect the reliability of the BPS because all known vulnerabilities may not be mitigated in a timely manner and could leave Cyber Assets vulnerable to a cyber-attack. Compromise of the SPPRE_URE3 EMS could have impacted monitoring, alarming, or dispatch to SPPRE_URE3’s generation facilities and the Inter-Control Communications Protocol (ICCP) signal to SPPRE_URE3’s Reliability Coordinator. Notwithstanding, the risk of an unknown actor gaining access to SPPRE_URE3’s BES Cyber Systems was minimal. SPPRE_URE3 has two-factor authentication at the intermediate host that provides access to the BES Cyber Systems. SPPRE_URE3’s EMS and associated Cyber Assets are continuously monitored by an intrusion protection system for any unsuccessful electronic access attempts, malicious communications, physical intrusion, and loss of functionality. No harm is known to have occurred. | To mitigate this noncompliance, SPPRE_URE3: 1) conducted an internal investigation to identify additional software components that were not patched as part of automated tools or manual processes; 2) added the applicable system software to SPPRE_URE3 patch tracker spreadsheet; 3) applied patches identified as applicable to associated software; 4) removed one of the subject applications from the four servers within the ESP; 5) installed patches and software updates to the applicable systems; 6) updated SPPRE_URE3 patch management and change management process documents to clarify the validation activities to confirm all patches were applied; 7) conducted training for SPPRE_URE3 support personnel on patch management and change management processes; and, 8) reviewed results from the current patching cycle utilizing the new process. SPP RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017017084 | CIP-006-3c | R5 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-006-3c R5. In particular, TRE_URE1 failed to immediately review unauthorized access attempts in accordance with its Physical Security Plan (PSPN) on two occasions. As part of its activities to transition to the new CIP version 5 Standards, TRE_URE1 developed a new PSPN, including a new process for responding to unauthorized entry attempts. Under TRE_URE1’s previous PSPN, all unauthorized access attempt alerts went to a designated TRE_URE1 physical security monitoring group, which would then manually determine the appropriate personnel to respond to the alert depending on specific circumstances and location. Under the revised process, however, the unauthorized access attempt alert would go directly to specifically identified response personnel as well, eliminating the need for the security team to manually relay that information. Prior to beginning the new process, the TRE_URE1 security manager erroneously informed their physical security monitoring personnel that it no longer needed to follow the existing procedure and manually relay unauthorized access attempts to the appropriate response personnel. As a result, TRE_URE1 security personnel did not immediately respond to or investigate unauthorized physical access attempts by other TRE_URE1 employees. The root cause of this noncompliance was a failure to fully communicate the timing of TRE_URE1’s transition to its new PSPN process. In particular, the TRE_URE1 security manager at issue erroneously believed that TRE_URE1 had already implemented its new alerting and response procedure prior to its effective date. The noncompliance lasted seven days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, no unauthorized access was gained. Second, TRE_URE1 experienced only two unauthorized access attempts, both of which were by TRE_URE1 employees with authorized physical access to other TRE_URE1 secure areas. In particular, the first employee at issue had authorized access to the Physical Security Perimeter at issue and the alert stemmed from an invalid card read. The second TRE_URE1 employee had authorized access to other TRE_URE1 Physical Security Perimeters, but inadvertently attempted to enter an area for which they did not have access. Third, TRE_URE1 uses a layered cyber defense approach to monitor access points to its Physical Security Perimeters on a twenty-four hours a day, seven days a week basis. As part of this layered defense, TRE_URE1 implemented a two-factor authentication process to all access points to its Physical Security Perimeters prior to the second unauthorized access alert. Fourth, the duration of the potential risk was short, lasting only seven days. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) implemented a new PSPN in compliance with CIP-006-6, including a process to ensure all unauthorized access attempts are investigated immediately; 2) installed a new electronic key card system that requires two-factor authentication at all access points to its Physical Security Perimeters; and 3) conducted CIP enhanced physical security training, including the review of the different types of alarms that could occur and information pertaining to investigation criteria and expected responses. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017018230 | CIP-002-3 | R4 | TRE_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. Texas RE subsequently determined that the duration pertaining to TRE_URE2’s failure to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems annually started earlier than July 1, 2016. Accordingly, Texas RE determined that TRE_URE2 was in noncompliance with CIP-002-3 R4, and TRE_URE2 was then in noncompliance with CIP-002-5.1 R2. Texas RE further determined that, for purposes of this noncompliance, there was no substantive change in TRE_URE2’s compliance obligations under the two applicable Standard Requirements. Pursuant to CIP-002-3 R4, TRE_URE2’s senior manager or delegate was required to approve TRE_URE2’s then-current risk-based assessment methodology, as well as its lists of Critical and Critical Cyber Assets. TRE_URE2’s designated manager performed the required review and approvals and did not identify any Critical or Critical Cyber Assets. As such, TRE_URE2 was required to perform the next review and approval within one year. However, TRE_URE2 failed to document any additional reviews of its risk-based assessment methodology or Critical and Critical Cyber Asset lists. Subsequently, TRE_URE2 did complete an impact evaluation as required. Again, however, TRE_URE2 did not obtain the required senior manager or delegate approvals. TRE_URE2 subsequently discovered the issue during an internal review and then had its designated senior manager review and approve TRE_URE2’s low-impact Bulk Electric System (BES) Cyber Asset designations, ending the issue. The root cause of this noncompliance was that TRE_URE2 lacked a process to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems. In particular, TRE_URE2 lacked an explicit written procedure to ensure the senior manager or their delegate reviewed and approved all applicable BES Cyber System designations in a timely manner. The duration of the noncompliance was approximately four years and nine months. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, the issue was largely administrative in nature, relating to the documentation for TRE_URE2’s Cyber Asset review and approval processes. In particular, TRE_URE2 provided evidence that it did not identify any Critical or Critical Cyber Assets during the issue duration. Further, TRE_URE2 timely performed the required BES Cyber Asset impact assessment and identified only assets associated with low-impact BES Cyber Systems. Second, TRE_URE2 had the appropriate controls in place for assets with low impact BES Cyber Systems by the required effective date. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE2: 1) had its designated senior manager approve the identifications as required by Requirement R1; 2) retained a new compliance director that was designated as responsible for implementing CIP-002; and 3) developed and implemented a written policy and annual review form checklist that requires the senior manager or delegate to approve the identification of all assets and associated BES Cyber Systems at least once every 15 months. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017018233 | CIP-002-3 | R4 | TRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. Texas RE subsequently determined that the duration pertaining to TRE_URE3’s failure to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems annually started earlier than July 1, 2016. Accordingly, Texas RE determined that TRE_URE3 was in noncompliance with CIP-002-3 R4, and TRE_URE3 was then in noncompliance with CIP-002-5.1 R2. Texas RE further determined that, for purposes of this noncompliance, there was no substantive change in TRE_URE3’s compliance obligations under the two applicable Standard Requirements. Pursuant to CIP-002-3 R4, TRE_URE3’s senior manager or delegate was required to approve TRE_URE3’s then-current risk-based assessment methodology, as well as its lists of Critical and Critical Cyber Assets. TRE_URE3’s designated manager performed the required review and approvals and did not identify any Critical or Critical Cyber Assets. As such, TRE_URE3 was required to perform the next review and approval within one year. However, TRE_URE3 failed to document any additional reviews of its risk-based assessment methodology or Critical and Critical Cyber Asset lists. Subsequently, TRE_URE3 did complete an impact evaluation as required. Again, however, TRE_URE3 did not obtain the required senior manager or delegate approvals. TRE_URE3 subsequently discovered the issue during an internal review and then had its designated senior manager review and approve TRE_URE3’s low-impact Bulk Electric System (BES) Cyber Asset designations, ending the issue. The root cause of this noncompliance was that TRE_URE3 lacked a process to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems. In particular, TRE_URE3 lacked an explicit written procedure to ensure the senior manager or their delegate reviewed and approved all applicable BES Cyber System designations in a timely manner. The duration of the noncompliance was approximately four years and nine months. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, the issue was largely administrative in nature, relating to the documentation for TRE_URE3’s Cyber Asset review and approval processes. In particular, TRE_URE3 provided evidence that it did not identify any Critical or Critical Cyber Assets during the issue duration. Further, TRE_URE3 timely performed the required BES Cyber Asset impact assessment and identified only assets associated with low-impact BES Cyber Systems. Second, TRE_URE3 had the appropriate controls in place for assets with low impact BES Cyber Systems by the required effective date. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE3: 1) had its designated senior manager approve the identifications as required by Requirement R1; 2) retained a new compliance director that was designated as responsible for implementing CIP-002; and 3) developed and implemented a written policy and annual review form checklist that requires the senior manager or delegate to approve the identification of all assets and associated BES Cyber Systems at least once every 15 months. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018235 | CIP-002-3 | R4 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. Texas RE subsequently determined that the duration pertaining to TRE_URE4’s failure to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems annually started earlier than July 1, 2016. Accordingly, Texas RE determined that TRE_URE4 was in noncompliance with CIP-002-3 R4, and TRE_URE4 was then in noncompliance with CIP-002-5.1 R2. Texas RE further determined that, for purposes of this noncompliance, there was no substantive change in TRE_URE4’s compliance obligations under the two applicable Standard Requirements. Pursuant to CIP-002-3 R4, TRE_URE4’s senior manager or delegate was required to approve TRE_URE4’s then-current risk-based assessment methodology, as well as its lists of Critical and Critical Cyber Assets. TRE_URE4’s designated manager performed the required review and approvals and did not identify any Critical or Critical Cyber Assets. As such, TRE_URE4 was required to perform the next review and approval within one year. However, TRE_URE4 failed to document any additional reviews of its risk-based assessment methodology or Critical and Critical Cyber Asset lists. Subsequently, TRE_URE4 did complete an impact evaluation as required. Again, however, TRE_URE4 did not obtain the required senior manager or delegate approvals. TRE_URE4 subsequently discovered the issue during an internal review and then had its designated senior manager review and approve TRE_URE4’s low-impact Bulk Electric System (BES) Cyber Asset designations, ending the issue. The root cause of this noncompliance was that TRE_URE4 lacked a process to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems. In particular, TRE_URE4 lacked an explicit written procedure to ensure the senior manager or their delegate reviewed and approved all applicable BES Cyber System designations in a timely manner. The duration of the noncompliance was approximately four years and nine months. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, the issue was largely administrative in nature, relating to the documentation for TRE_URE4’s Cyber Asset review and approval processes. In particular, TRE_URE4 provided evidence that it did not identify any Critical or Critical Cyber Assets during the issue duration. Further, TRE_URE4 timely performed the required BES Cyber Asset impact assessment and identified only assets associated with low-impact BES Cyber Systems. Second, TRE_URE4 had the appropriate controls in place for assets with low impact BES Cyber Systems by the required effective date. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) had its designated senior manager approve the identifications as required by Requirement R1; 2) retained a new compliance director that was designated as responsible for implementing CIP-002; and 3) developed and implemented a written policy and annual review form checklist that requires the senior manager or delegate to approve the identification of all assets and associated BES Cyber Systems at least once every 15 months. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE2017018237 | CIP-002-3 | R4 | TRE_URE5 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. Texas RE subsequently determined that the duration pertaining to TRE_URE5’s failure to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems annually started earlier than July 1, 2016. Accordingly, Texas RE determined that TRE_URE5 was in noncompliance with CIP-002-3 R4, and TRE_URE5 was then in noncompliance with CIP-002-5.1 R2. Texas RE further determined that, for purposes of this noncompliance, there was no substantive change in TRE_URE5’s compliance obligations under the two applicable Standard Requirements. Pursuant to CIP-002-3 R4, TRE_URE5’s senior manager or delegate was required to approve TRE_URE5’s then-current risk-based assessment methodology, as well as its lists of Critical and Critical Cyber Assets. TRE_URE5’s designated manager performed the required review and approvals and did not identify any Critical or Critical Cyber Assets. As such, TRE_URE5 was required to perform the next review and approval within one year. However, TRE_URE5 failed to document any additional reviews of its risk-based assessment methodology or Critical and Critical Cyber Asset lists. Subsequently, TRE_URE5 did complete an impact evaluation as required. Again, however, TRE_URE5 did not obtain the required senior manager or delegate approvals. TRE_URE5 subsequently discovered the issue during an internal review and then had its designated senior manager review and approve TRE_URE5’s low-impact Bulk Electric System (BES) Cyber Asset designations, ending the issue. The root cause of this noncompliance was that TRE_URE5 lacked a process to ensure the senior manager approved the identification of all assets and associated BES Cyber Systems. In particular, TRE_URE5 lacked an explicit written procedure to ensure the senior manager or their delegate reviewed and approved all applicable BES Cyber System designations in a timely manner. The duration of the noncompliance was approximately four years and nine months. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, the issue was largely administrative in nature, relating to the documentation for TRE_URE5’s Cyber Asset review and approval processes. In particular, TRE_URE5 provided evidence that it did not identify any Critical or Critical Cyber Assets during the issue duration. Further, TRE_URE5 timely performed the required BES Cyber Asset impact assessment and identified only assets associated with low-impact BES Cyber Systems. Second, TRE_URE5 had the appropriate controls in place for assets with low impact BES Cyber Systems by the required effective date. No harm is known to have occurred. Texas RE considered TRE_URE5’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE5: 1) had its designated senior manager approve the identifications as required by Requirement R1; 2) retained a new compliance director that was designated as responsible for implementing CIP-002; and 3) developed and implemented a written policy and annual review form checklist that requires the senior manager or delegate to approve the identification of all assets and associated BES Cyber Systems at least once every 15 months. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Western Electricity Coordinating Council (WECC) | Unidentifed Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017908 | CIP-005-5 | R1; P1.2 | During an audit it was determined that WECC_URE1, was in noncompliance with CIP-005-5 R1 Part 1.2. WECC_URE1 connected an ethernet cable to a switch within the Electronic Security Perimeter (ESP) to a server outside the ESP without going through an identified Electronic Access Point (EAP) as required by CIP-005-05 R1 Part1.2. Specifically, in preparation for the onsite portion of audit fieldwork, WECC_URE1 staff discovered that a server located at its control center was incorrectly cabled such that one end of an ethernet cable was connected to an active Bulk Electric System (BES) Cyber Asset (BCA) switch located within the ESP. WECC_URE1 initiated procedures to correct the issue, and informed audit staff about the issue. WECC_URE1 explained that the servers were incorrectly cabled to a digitally-disabled port of an active switch within a High Impact BES Cyber System, which inappropriately connected the server to the BCA without going through an EAP. Since the port on the switch was digitally-disabled, no traffic was exchanged between the two networks. However, audit staff noted that a pathway still existed between the ESP and non-ESP networks, inappropriately. During a call with WECC_URE1 and WECC, WECC_URE1 informed WECC of a scope expansion to include two additional cabling issues, identical in nature, in both the primary and backup Control Centers. WECC reviewed the audit noncompliance and determined that WECC_URE1 failed to ensure all External Routable Connectivity (ERC) was through an identified EAP. The root cause of the noncompliance was a mislabeled cabling cut sheet, resulting in those performing the work to do so incorrectly. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE1, and ended when WECC_URE1 re-cabled the servers to appropriate network switches, for a total of 132 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to ensure all External Routable Connectivity (ERC) was through an identified EAP. Such failure could result in attackers utilizing those paths to gain electronic access to BES Cyber Systems. In the event of a malicious actor gaining access to a Control Center, they could affect Control Center operations. If a malicious actor gained such access, it could potentially cause substantial harm to the reliability of the BES. However, WECC_URE1 implemented good preventative controls. The cables connecting the networks were attached to a digitally disabled port on the switches, and disabled and not configured network ports on the servers; therefore, no traffic was exchanged between the networks or the server. Additionally, port protectors were used to deter adding new connections. Based on the this, WECC determined that the impact had a remote likelihood of occurring. No harm is known to have occurred. WECC_URE1 has no relevant previous noncompliance with this or similar Standards and Requirements. | To mitigate this noncompliance, WECC_URE1: 1) executed an emergency change to re-cable the servers to the appropriate network switches; 2) conducted an extent of condition analysis, tracing several hundred cables across the two data centers to verify that the two instances were the only noncompliance of this issue 3) held a stand down for networking engineering that re-emphasized: a. use of pre-job brief with cross-checking/three-part communication included for these type of activities; b. peer review of cable cut sheets before implementation; c. deploying CIP tags on in-scope CIP devices as a visual cue; 4) deployed CIP signage on cabinets and port protectors on CIP devices as an additional physical protection; 5) initiated scoping of technology-based project to introduce controls to WECC_URE1's change management program and activities; and 6) implemented technology-based project based on scoping identified in (d) to introduce controls to WECC_URE1's change management program and activities.
2018-02-28 | Western Electricity Coordinating Council (WECC) | Unidentifed Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017910 | CIP-011-2 | R1; Part 1.2 | During an audit it was determined that WECC_URE1, was in noncompliance with CIP-011-2 R1 Part 1.2. WECC_URE1 did not properly identify the local servers supporting its software tool, that contained BES Cyber System Information (BCSI), as a BCSI storage location; therefore, it failed to protect and securely handle BCSI, to include storage, transit, and use of that BSCI. The servers host BCSI for undefined time periods while such information is evaluated prior to it being placed in its designated BCSI storage location. Because the servers were not the "at rest" BCSI storage location for the scan results, WECC_URE1 did not consider the them as BCSI storage locations and did not apply all the protections required by WECC_URE1's requirements. WECC reviewed the audit noncompliance and determined that WECC_URE1 failed to protect and securely handle BCSI on the server, to include storage, transit, and use of that BSCI. The root cause of the noncompliance was a less than adequate Program. Specifically, the Program did not provide sufficient clarity regarding when BCSI was considered “in transit” versus “at rest”. This ambiguity resulted in WECC_URE1 personnel believing that, because the BCSI being hosted by the servers was ultimately to be removed and placed in a designated BCSI storage location, such BCSI was "in transit" despite the time period for which it was hosted on the servers and despite the standard and Requirement being applicable to BCSI in transit. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE1, and ended when WECC_URE1 identified server as a BCSI container, which established the protection parameters of CIP-011-2 R1 Part 1.2, for a total of 171 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE1 failed to protect and securely handle BCSI on its software tool, to include storage, transit, and use of that BSCI. Such failure could potentially result in information being viewed, accessed, or removed by unauthorized personnel or malicious actors. The software tool BCSI contained IP addresses, ports, and services related to pre-production Cyber Assets. With the knowledge gained from this information a malicious actor could gain a better understanding of the WECC_URE1’s systems, and more easily compromise the ESP and/or the Physical Security Perimeter network that includes the Energy Management System (EMS) and the SCADA system. Having access to SCADA system could result in loss of visibility to multiple substations and lead to intermediate potential harm. However, WECC_URE1 implemented good preventive controls. Specifically, network intrusion detection was integrated in firewalls to assist with determining if an attacker had gained access. WECC_URE1 utilized two-factor authentication to access its network environment where CIP assets reside, and these assets themselves had additional authentication this is required to electronically access. WECC_URE1 has implemented a SIEM to log and monitor the EMS, as well as the CIP assets. Based on the controls in place, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. WECC_URE1 has no relevant previous noncompliance with this or similar Standards and Requirements. | To mitigate this noncompliance, WECC_URE1: 1) created a role in its access management tool that identified the software tool as a BCSI container, establishing the protection parameters; 2) revised its BCSI program to improve clarity regarding the potential states of BCSI and user responsibilities; 3) updated the software tool which is utilized for all stages of project approval, with checklist questions to serve as a control prior to new asset being deployed; and 4) updated its CIP activity committee checklist, used to perform an independent peer review of CIP related change management processes, to include an impact to BCSI storage locations inquiry.
2018-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2017016937 | CIP-004-6 | R4; Part 4.2 | WECC_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-6 R4 Part 4.2. Specifically, WECC_URE2 reported that its CIP-004-6 R4 and R5 processes utilized an identity management system to obtain, track, house, and verify all CIP-004-6 R4 Part 4.1.1 thru 4.1.3 authorization records. WECC_URE2 utilizes software tool reporting as an added internal control to automatically compare authorization record ID numbers from identity management system to actual electronic access and unescorted physical access to High Impact Bulk Electric System (BES) Cyber Systems (HIBCS) and Medium Impact BES Cyber Systems (MIBCS) and their associated EACMS, PCA, and PACS; however, this control was only partially functional due to a programmatic issue with the software tool reports. As a temporary measure, a process was implemented whereby designated CIP approvers were provided a quarterly report of authorized users in order to perform a manual comparison to confirm only identity management system authorized users had access to BES Cyber Systems and their associated Cyber Assets. During a review of the software tool report which compares actual access to authorization records, Subject Matter Experts (SME) identified that three individuals had access to BES Cyber Systems and associated Cyber Assets with no corresponding identity management system authorization records. Upon investigation, SMEs discovered that during the upgrade of identity management system the authorization records for three individuals were rejected. Because those three individuals had no authorization record in identity management system (even though their authorizations were stored in other locations), when the designated CIP approvers for these systems performed their quarterly comparison of actual access to authorization records verification, they should have identified and called out these discrepancies. WECC determined that WECC_URE2 failed to follow its interim process to verify it had authorization records for individuals with active electronic access or unescorted physical access at least once each calendar quarter. The root cause was insufficient training for the designated CIP approvers when performing the quarterly CIP-004-6 R4.2 verification. WECC determined that this issue began when the initial performance of this Standard and Requirement became enforceable to WECC_URE2, ended when WECC_URE2 completed verification of access records for the three individuals, for a total of 66 days of noncompliance. | WECC determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to follow its interim process to verify it had authorization records for individuals with active electronic access or unescorted physical access at least once every calendar quarter. Such failure could result in excessive privileges that could be exploited; thereby potentially affecting the reliability of the BPS. However, the individuals that had access to the HIBCS and MIBCS and their associated EACMS, PCAs and PACS were in fact authorized to have access. They simply didn’t have a record in the appropriate system and therefore quarterly review didn’t catch the discrepancy, as intended. Additionally, WECC_URE2 implemented quarterly access reviews which is what identified this issue. Based on this, WECC determined that the harm had a minimal likelihood of occurring. No harm is known to have occurred. WECC considered WECC_URE2's CIP-004 R4 compliance history in determining the disposition track and determined it should not serve as a basis for applying a penalty. | To mitigate this noncompliance, WECC_URE2: 1) updated identity management system to include the authorization records for two of the individuals and removed access for one other; 2) verified that the software tool and identity management system automated reconciliation reports are functional and completed a true-up between the two reports; and 3) performed a CIP-004-6 R4 Part 4.2 verification. WECC verified completion of mitigating activities.
2018-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entitiy 3 (WECC_URE3) | NCRXXXXX | WECC2016016547 | CIP-007-3a | R6.2, R6.3 | WECC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a, R6.2, and R6.3. Specifically, for the first instance, WECC_URE3 reported that after a tested and planned upgrade for a Security information and Event Management System (SIEM), the system was rebooted, at which time it was discovered that the log database had disappeared and could not be recovered. This database stores the encryption keys for the SIEM as well as configuration information on how and where to store logs. As a result of not having the log database, WECC_URE3 was unable to retrieve logs for the Physical Access Control System (PACS) and the SIEM, pursuant to CIP-007-3a R6.3. For the second instance, WECC_URE3 reported that the on-call personnel received an alert that a syslog server had become unresponsive. Support personnel logged in and verified the system was responding. The following day IT Security was notified that logs from other systems were not being forwarded to the SIEM and the server had become unresponsive. A system reboot returned the syslog server to expected functionality. As a result, there were no logs, monitoring or alerting for a nine-hour period, pursuant to CIP-007-3a R6.2 and R6.3 for a total of sixteen Electronic Access Control or Monitoring System (EACMS) and Physical Access Controls System (PACS) devices. WECC reviewed the Self-Report, and determined that for the first instance, WECC_URE3 failed to maintain logs for system events related to cyber security to support incident response pursuant to CIP-007-3a R6.3. For the second instance, WECC_URE3 failed to preserve, monitor and alert on security events on all applicable Cyber Assets within the ESP as well as maintain logs appropriately, pursuant to CIP-007-3a R6.2 and R6.3, respectively. Specifically, a syslog forwarding server was not properly functioning as the logs from other systems were not being forwarded to the SIEM for analysis. The root cause of the noncompliance for the first instance was a lack of technical understanding related to the management of the SIEM and logging related system assets. Specifically, personnel were not aware of the specific SIEM configuration and did not have technical details documented as related to the log database, which would have enabled the SIEM access and processing of the collected encrypted logs. The root cause for the second instance was due to an operating system error which caused the Central Processing Unit (CPU) to spike and rendered the system unresponsive. WECC determined that the first instance began when WECC_URE3 failed to maintain logs of system events, and ended when WECC_URE3 reestablished retention and access of system event logs, for a total of 52 days of noncompliance. WECC determined that the second instance began when WECC_URE3 failed to issue alerts for detected system security events for cyber assets located within the ESP, and ended when the log forwarding server was rebooted and returned to normal functionality, for a total of one day of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In the first instance, WECC_URE3 failed to manage a SIEM asset rendering it unable to decrypt long-term logs that had been collected by the system. This could potentially result in WECC_URE3 not being able to identify if and how a Cyber Security incident had occurred, or what systems and assets were compromised. Additionally, in the second instance, WECC_URE3 failed to issue alerts for detected system security events. Such failure could have allowed an attacker to gain access to systems without WECC_URE3’s knowledge or to have gone undetected. However, for the first instance, the SIEM continued to perform real-time monitoring and alerting which enabled WECC_URE3 to maintain limited visibility. There were no gaps in the logs or alerts coming from other systems including antivirus or Intrusion Protection System or Intrusion Detection System Assets (IPS/IDS) in place. Additionally, for the second instance, WECC_URE3 services teams continued to receive separate notification for abnormal system resource usage by command center personnel which was manned twenty-four hours a day. Based on the controls in place, WECC determined that the impact associated with this issue had a low likelihood of occurring. No harm is known to have occurred. WECC_URE3 has no compliance history with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE3: 1) reviewed the application recovery statement to make sure backup and recovery instructions were included, and added a backup verification process. 2) rebooted the syslog server to resume log forwarding; 3) increased short term storage for the SIEM from 21 days to 90 days to avoid any potential gaps in log storage; and 4) consolidated all components of the SIEM into a single volume so that every time a backup is made all components of the SIEM are backed up at the same time. WECC verified completion of the mitigating actives.
2018-01-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity (MRO_URE1) | NCRXXXXX | MRO2017017709 | CIP-007-6 | R2 | MRO_URE1 stated that it was in noncompliance with CIP-007-6 R2. Specifically, MRO_URE1 did not implement the mitigation plan (created under P2.3) for the patches applicable to a Cyber Asset. This occurred when MRO_URE1 did not apply the patches within the timeframe specified in the mitigation plan (P2.4) to a single Cyber Asset. The cause of the noncompliance was that MRO_URE1 relied on a software tool to apply the patches and did not have a process or control in place that confirmed that security patches were actually applied. The duration of the noncompliance was approximately five months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the patches were late in being installed, the internal controls that MRO_URE1 had outlined in the patch mitigation plan (P2.3), that would mitigate any risk until the patch was installed, remained in effect during the duration of the noncompliance. Further, the scope of the noncompliance was limited to a single Cyber Asset that does not have any direct impact on BES Operation, and runs a software application that is a detective control (as opposed to being a preventative control) used to identify malware. Additionally, the noncompliance was self-identified when an employee logged into the application used to apply patches and recognized that the list was shorter than expected, which indicates that employees are familiar with the system and sensitive to changes in it. Finally per MRO_URE1, the Cyber Asset was located in a functioning Physical Security Perimeter (PSP), was behind multiple layers of firewalls protecting the Electronic Security Perimeter (ESP), required authentication for interactive access, was protected by an intrusion detection system that monitored for malicious communication, and was logging and alerting. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this noncompliance, MRO_URE1: 1) reviewed the patching cycle to determine the scope of the patching tool's failure; 2) applied the required patches (or new variations of the patches); and 3) updated its documented process to include an internal control that verifies that a patch was successfully installed. The internal control is in the form of script that will list all patches deemed applicable by the update service that have not been installed. This script will alert MRO_URE1 and it will manually follow-up to ensure application of the patch.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017781 | CIP-007-6 | R2 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R2. During a software patch management process review, the entity discovered that the operating system information record for a remote terminal unit (RTU) was missing from the patch management tool. Upon further investigation, the entity discovered issues with 6 other RTUs. In total, the operating system for 6 RTUs and the firmware for 2 RTUs were not being patched in compliance with CIP-007 R2. The root cause of this noncompliance was issues with the entity’s management of information in the patch management tool and its relay database. For the 6 RTUs whose operating systems were not being patched, the entity only included the firmware in the patch management tool due to an oversight in the initial setup and integration between the tool and the relay database. For the 2 RTUs whose firmware was not being patched, the entity mistakenly entered the operating system information in the firmware field in the relay database instead of the actual firmware information. This major contributing factor involves the management practices of asset and configuration management, which includes controlling changes to assets and configuration items and baselines, and information management, which includes verifying validity of information items. The duration of the noncompliance was approximately one year. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, considering the entity’s total device count, the entity only missed patching a small number of assets. In other words, this noncompliance is not indicative of a systemic issue with the entity’s patch management system for its required assets. Second, the devices that the entity did miss were inherently minimal risk because they do not have external routable connectivity. Therefore, the only security concern related to physical access. These particular assets are protected according to the entity's Physical Security Plan, which includes card readers and electronic keys. Thus, any potential attacker would have to overcome these physical controls before causing any harm. No harm is known to have occurred. ReliabilityFirst considered the entity’s CIP-007-6 R2 and CIP-007 R3 (corresponding version 3 requirement) compliance history in determining the disposition track. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) manually entered missing operating system information in the patch management tool for the six affected RTUs and made corrections to the relay database and the patch management tool to correct the two RTUs that had operating system in the firmware field; 2) developed a mitigation plan with appropriate dates and compensating measures to apply the required patches; 3) implemented operating system fields integration from the relay database to the patch management tool. This includes the operating system name, operating system version, and operating system patch level; and 4) developed a document that captures the validation of data between the relay database and the patch management tool during the pre-execution CIP review prior to energization. ReliabilityFirst has verified the completion of all mitigation activity.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017948 | CIP-003-6 | R2 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-003-6 R2. As part of its required cyber security plan for its low impact Bulk Electric System (BES) Cyber Systems, the entity established a Cyber Security Incident Response Plan (CSIRP). In order to demonstrate that it had actually implemented the CSIRP, the entity conducted a test of the plan, using an actual event that had occurred. However, that actual event did not result in a Reportable Cyber Security Incident (CSI). As a result, the entity did not test the portion of its CSIRP that dealt with actually reporting a CSI. The root cause of this noncompliance was the entity’s failure to fully understand the testing requirements of CIP-003-6 R2. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the entity proactively identified this noncompliance by reaching out to ReliabilityFirst to verify whether its initial test was sufficient. When ReliabilityFirst indicated that it was not, the entity immediately took steps to correct the noncompliance. Second, once the entity conducted a test of its entire CSIRP, no changes were required. ReliabilityFirst also notes that no potential CSIs were experienced during the time period in question. No harm is known to have occurred. ReliabilityFirst considered the entity’s CIP-003-6 R2 and CIP-003-3 R1 (corresponding version 3 requirement) compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) performed a test of its CSIRP with a training scenario that would have hypothetically resulted in a Reportable CSI. Thus, the entity was able to fully test is CSIRP; and 2) adopted and updated its CSIRP and corresponding test/exercise form to clarify process steps, as well as test form response fields, to ensure that future tests of the CSIRP would result in a full evaluation of the plan.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017782 | CIP-004-6 | R4 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R4. The entity used a primarily manual process for uploading electronic and physical access control records to the entity's access management system for review. The employee primarily responsible for performing this manual process left the company. Because the entity did not document the complete process end-to-end and because management did not have direct oversight over the process, the entity failed to perform three quarterly reviews of its electronic and physical access list. The root cause of this noncompliance was the entity’s failure to document this manual process. This major contributing factor involves the management practices of verification, in that the quarterly review process is a verification check, and workforce management, which includes managing employment status changes. The duration of the noncompliance was approximately one year. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact this verification step was a redundant control. The entity removes physical and electronic access within 24 hours of an employee’s departure, which reduces the likelihood that an unauthorized individual could have gained access. ReliabilityFirst also notes that the entity discovered no discrepancies when it completed its reviews. No harm is known to have occurred. ReliabilityFirst considered the entity's CIP-004-6 R4 and corresponding version 3 requirements (i.e., CIP-003 R5; CIP-004 R4, and CIP-006 R1) compliance history in determining the disposition track. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) documented the entity flat file process to allow for continuation in the event of employee rotation; 2) automated the entity flat file process to store on appropriate CIP Information Repository (CIR) to be ready for processing; 3) performed an analysis using the last upload file the entity produced to the access management system against every month of raw data produced from the entity’s Energy Management System for nine months; and 4) performed a monthly comparison of all actual access files received to the list of expected files. The entity notified performers and its compliance personnel of monthly file upload results. ReliabilityFirst has verified the completion of all mitigation activity.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017766 | CIP-005-5 | R1 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-005-5 R1. The hardware running a virtual Bulk Electric System Cyber Asset (BCA) had a failure that caused the BCA to become unresponsive and unable to provide application functionality. As a result, as intended, all application functions were automatically transferred to a different BCA virtual server without any service interruption. In the process of troubleshooting the source of the initial failure, the entity was asked by the vendor to connect a certain server management technology port to determine the source of the failure. Thus, in order to quickly resolve the failure, the entity configured the server management technology with an IP address and connected the port into a firewalled non-Electronic Security Perimeter (ESP) network in violation of CIP-005-5 R1. The port was connected to the non-ESP port for approximately five hours throughout the duration of the troubleshooting and recovery process. Upon completion of the troubleshooting effort, the entity disconnected the server management technology port and restored the network configuration to its original state. The cause was lack of controls to ensure that the entity’s emergency procedures to recover the asset were fully compliant with the NERC Standards and Requirements. This noncompliance involves asset and configuration management, as the entity’s processes lacked sufficient controls to manage the effects of implementing changes to the asset. The duration of the noncompliance was approximately five hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is unauthorized access or vulnerabilities into the ESP. However, this risk was mitigated here because of the multiple other security controls in place. The server management technology port, which is used only for disaster recovery, only grants access to the server hardware via approved credentials as controlled through the entity’s access management program. The steps required in order to access the server management technology port include a VPN, multi-factor authentication, an Electronic Access Control or Monitoring System-ID, and an additional authentication step. Additionally, the server management technology port cannot be used to access the virtual servers or the applications hosted by the virtual servers. Lastly, the entity quickly mitigated the noncompliance, thus reducing the time period that the asset was at risk of being compromised. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. It should also be noted that immediately following the noncompliance, the entity checked the baseline (through automated scans) and determined no baseline changes were made during the period of the outage. No harm is known to have occurred. ReliabilityFirst considered the entity's CIP-005 R1 compliance history in determining the disposition track. ReliabilityFirst determined that the entity's compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) removed the server management technology from the network to end the noncompliance; 2) confirmed there were no security impacts to the BCA; 3) met with subject matter experts to determine feasibility of applying CIP controls to the server management technology devices; 4) documented which CIP controls and procedures needed to be modified to accommodate server management technologies being placed in an ESP in the event of the failure of an asset running virtual BCAs. Output of the mapping was the roadmap for testing feasibility in the next milestone; 5) used non-CIP-scoped assets, tested each combination of server management technology type, firmware and operating system to determine feasibility of integrating server management technology compliance with the entity's tool and processes; and 6) updated procedures and other documentation to allow server management technologies to be added into an ESP in the event of the failure of an asset running virtual BCAs.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017018518 | CIP-004-3a | R4 R4.1 | RFC_URE5 submitted a self-log stating that it was in noncompliance with CIP-004-3a R4.1. The entity Information Technology (IT) applied two Active Directory groups incorrectly which resulted in unauthorized electronic access to NERC Electronic Access Control or Monitoring Systems (EACMS) Cyber Assets and a Bulk Electric System Cyber System Information (BCSI) repository. The entity IT group inadvertently provisioned access to 15 individuals to NERC EACMS Cyber Assets and to 21 individuals to the BCSI repository. The entity IT group used AD groups that are typically used to administer similar infrastructure in the corporate environment. By applying the incorrect AD groups, individuals had unauthorized access permissions that they did not require. The cause of this potential violation was from a variety of reasons, including: 1. IT did not include detailed tasks in the project plan to sufficiently address the additional tasks for creating and applying the new NERC AD groups in the new NERC EACMS domain prior to production. 2. The existing IT pre-production checklist was not sufficiently detailed to identify that an incorrect AD group was applied to the NERC EACMS. 3. IT individual failed to verify all compliance steps were complete prior to configuring the monitoring tool, i.e. the BCSI repository. This noncompliance involves the management practice of workforce management through ineffective training because an entity individual incorrectly provisioned access to the wrong individuals. Ineffective training is a root cause of this noncompliance. The duration of the noncompliance was approximately nineteen months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to none. The inappropriate access was granted to a NERC EACMS and BCSI environment, which are segregated from the BCS environments. The inappropriate access provided no interactive access to any BCAs or caused adverse impact to BCAs through the access that was granted. No harm is known to have occurred. The harm level was unlikely to be realized for the following reasons: • Inappropriate access granted to a NERC EACMS and BCSI environment, which are segregated from the BCS environments. • Inappropriate access provided no interactive access to any BCAs or caused adverse impact to BCAs through the access that was granted. There are several internal controls in place to detect or prevent violation occurrence, including: • An IT pre-production sign-off process to verify all compliance requirements are implemented prior to assets being placed into production. • The IT Security Compliance group has centralized oversight for the AD Group creation process for NERC CIP Assets. While the current controls did not prevent the issue, the IT personnel identified and reported the issue when performing a design review for an upgrade project of the Cyber Assets. | To mitigate this noncompliance, the entity: 1) removed the incorrect AD group from the EACMS Cyber Asset; 2) removed the incorrect AD group from the BCSI repository; 3) created new AD groups and authorized access via security request system tickets; 4) performed a comprehensive review of AD groups and entitlements for all NERC access to identify any additional unauthorized access issues associated with AD Groups; 5) reviewed and updated the existing pre-production checklist to add necessary detailed steps to ensure compliance prior to production (e.g. human performance checks); and 6) performed a review of AD groups and entitlements for all NERC access to new assets put into production after the comprehensive review to identify any additional unauthorized access issues associated with AD groups until implementation of pre-production checklist enhancements.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017018519 | CIP-007-6 | R2.3 | RFC_URE5 submitted a self-log stating that it was in noncompliance with CIP-007-6 R2.3. The vendor released a security patch for an Electronic Access Control or Monitoring Systems (EACMS) Cyber Asset. An entity IT individual performed the patch assessment following the documented process and identified that the vendor released new code. The entity IT individual documented their assessment on the patch assessment tracker and indicated that there were no applicable security patches released by the vendor. During a patch assessment cycle, an entity IT individual identified the incorrect patch assessment. Due to the incorrect determination, the entity IT did not apply the security patch within the required 35 days. The cause of this potential violation was from a variety of reasons, including: 1. Entity IT did not apply the patch within 35 days of assessment because the patch was not identified as a security patch. 2. The entity IT individual is no longer employed at the entity so it is unclear how he made his determination. 3. Entity IT peer check process did not include a detailed review of each patch assessment. This noncompliance involves the management practice of workforce management through ineffective training because an entity individual performed an incorrect patch assessment. Ineffective training is a root cause of this noncompliance. The duration of the noncompliance was approximately forty days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to none. This asset is an EACMS asset, not a Bulk Electric System asset. This patch addressed an http cross scripting issue. This asset only uses https and was therefore unsusceptible to this issue. Furthermore, this asset was protected by two firewalls and two factor authentication, further reducing any risk. This issue would also have been addressed in a subsequent code release. No harm is known to have occurred. The harm level was minimal to unlikely to be realized for the following reasons: • This patch addressed an http cross scripting issue. This asset only uses https and was therefore unsusceptible to this issue. • This issue would also have been addressed in a subsequent code release. There are several internal controls in place to detect or prevent violation occurrence, including: • Internal processes and procedures in place for released patches require monthly review of patch and reporting back in a group setting. • The late patch assessment was identified during the next patch cycle and implemented promptly (40 days late). | To mitigate this noncompliance, the entity: 1) implemented the security patch; 2) updated its patch management procedure to incorporate a peer check of vendor release notes in its patching process; and 3) reinforced expectations to ensure security patches are properly identified, documented and applied per the NERC CIP V6 requirements.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017018520 | CIP-011-2 | R1.2 | RFC_URE5 submitted a self-log stating that it was in noncompliance with CIP-011-2 R1.2. Entity IT sent several network topology diagrams to a contractor. The documents were labeled “Confidential CIP Asset Information (CCAI)” because the documents contained Bulk Electric System Cyber System Information (BCSI). The contract firm was not established under the entity program as being permitted to hold CCAI outside the entity environment. The information was sent to six individuals and placed on their network. The data was transmitted using a secure file transfer protocol. The cause of this potential violation was from a variety of reasons, including: 1. Lack of adherence to documented policy and training. 2. The contractors who received the NERC CCAI had completed the entity NERC Cyber Security Training and had a current background check. This noncompliance involves the management practices of external interdependencies and workforce management. Both management practices are implicated because an entity employee incorrectly sent information to a contractor that is not established under the entity program as being permitted to hold CCAI outside the entity environment. Ineffective training and insufficient vendor management are both root causes of this noncompliance. The duration of the noncompliance was approximately five months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to substantial. While the information that was shared was a network topology diagram, the contract firm who received the documents is under a Confidentiality Agreement with the entity. No harm is known to have occurred. The harm level was minimal to not likely to be realized for the following reasons: • The contract firm who received the documents is under a Confidentiality Agreement with the entity. • The duration of the time the contract firm had the document was limited and they destroyed all copies at the entity's request. There are several internal controls in place to detect or prevent violation occurrence, including: • Entity Cyber Security Policy and Information Protection procedure includes specific information and process steps and is available to all entity employees and contractors who have access to NERC CIP Confidential CIP Asset Information CCAI/BCSI. • Information Protection is included in the NERC Cyber Security Training as well as in specific information handling training. • The contractors who received the NERC CCAI had completed entity NERC Cyber Security Training and had a current background check. While the current controls did not prevent the issue, the issue was self-identified by a co-worker during a meeting on a new project which demonstrates understanding and culture of compliance. | To mitigate this noncompliance, the entity: 1) permanently deleted all copies of the information; 2) provided personalized instruction to staff regarding NERC information protection expectations; 3) sent a communication to all NERC CIP Cleared individuals to clarify expectations on information protection requirements; 4) updated training on information protection to clarify expectation; 5) reduced the number of employees and contractors involved in work involving NERC CIP Assets; and 6) changed its work process to no longer use vendors to perform work tasks that require unattended view of BCSI.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017018521 | CIP-004-3 | R4.1 | RFC_URE5 submitted a self-log stating that it was in noncompliance with CIP-004-3 R4.1. As part of the extent of condition to address another self-logged issue, entity IT identified seven individuals without appropriate authorization to NERC CIP Assets via the entity security request system. Entity IT provisioned access via the security request system process, but the individuals did not receive appropriate approval because the security request system workflow did not include an approval step by the NERC CIP access authorizer due to a null value in a required attribute field. A. 1 Individual with electronic access to Physical Access Control Systems Cyber Assets B. 2 Individuals with electronic access to Electronic Access Control or Monitoring Systems (EACMS) Cyber Assets Entity IT identified individuals that were authorized for access for one role, but were also provisioned for another role for which authorization was not given. A. 1 Individual with electronic access to an EACMS Cyber Asset B. 3 Individuals with electronic access to electronic storage locations containing Confidential CIP Asset Information/Bulk Electric System Cyber System Information (BCSI). Although there were no security request system authorization records for provisioned access, each individual’s access was reviewed by the individual’s supervisor and the NERC CIP access authorizer during the quarterly access validation. Each individual had completed NERC CIP cyber security training and had a successful personnel risk assessment (PRA) at that time access was provisioned. The cause of this potential violation was from a variety of reasons, including: 1. Entity IT did not have a control to verify provisioned access at the role level to the authorization record at the role level. 2. Entity IT had not configured the access control systems to require setting a field value which would have prevented this issue. 3. Entity IT did not follow documented process for provisioning access. This noncompliance involves the management practice of verification because the entity did not verify that all individuals received the appropriate approval before receiving access and did not verify that all individuals were given proper access for their roles. This failure to verify is a root cause of this noncompliance. The duration of the noncompliance was approximately four years. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to none. In all cases, each individual had completed NERC CIP cyber security training and had a successful PRA at the time access was provisioned. Each individual’s access was reviewed by the individual’s supervisor and the NERC CIP access Authorizer during the entity’s Quarterly Validations and the access was either approved or removed at that time. No harm is known to have occurred. The harm level was minimal to be realized for the following reasons: • Access was deemed appropriate by the NERC CIP Authorizer during the quarterly validations. • Each individual had completed NERC CIP cyber security training and had a successful PRA at the time access was provisioned. There are several internal controls in place to detect or prevent violation occurrence, including: • Entity IT performs a review quarterly of all accesses to NERC CIP assets, systems and BCSI repositories. • Entity IT uses its security request system for requesting, authorizing and processing all security permissions for NERC CIP assets, systems and BCSI repositories. • Entity IT implemented a new daily control that reconciles access permissions to access authorization records for all automated access. While the current controls did not prevent the issue, the first and third controls identified the initial set of issues. The new daily reconciliation control assures any unauthorized automated access will be identified promptly for corrective action limiting risk to entity NERC CIP assets. | To mitigate this noncompliance, the entity: 1) submitted security request system tickets in the entity Security Request System to authorize or revoke each access as appropriate; 2) implemented changes to the new access request reconciliation process which generates a daily report identifying individuals with NERC CIP Access and no authorization tickets in the entity Security Request System at the role level. The reports are reviewed by IT daily; 3) reinforced expectations to IT individuals provisioning NERC CIP Accesses; 4) updated the application to require setting the necessary field value to ensure approval by the NERC CIP Authorizer; and 5) conducted a review of the NERC CIP access control process to identify any additional corrective actions or preventative or detective controls.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017018522 | CIP-004-3a | R4.2 | RFC_URE5 submitted a self-log stating that it was in noncompliance with CIP-004-3a R4.2. The entity failed to revoke physical access for two individuals for a total of six Physical Security Perimeters (PSPs) within the required timeframe. For one of the individuals, the access was not revoked once the supervisor determined that access was no longer needed. The supervisor determined that an employee on disability no longer needed access and did not initiate the revocation process. The physical access was removed. For the second individual the access was not revoked upon retirement. The cause of this potential violation was from a variety of reasons, including: 1. Intermittent time off by the employee due to use of Family Medical Leave Act policy. 2. Lack of adherence to documented process and training. 3. Human performance error to not enter the security request system ticket at the same time the access determination was made. This noncompliance involves the management practice of verification because the entity did not verify that it timely revoked access for the two individuals at issue in the noncompliance. This failure to verify is a root cause of this noncompliance. The duration of the noncompliance was approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to none. The individuals retained access to six PSPs. The individuals had completed NERC CIP cyber security training and had successful personnel risk assessment (PRA) while the access was retained and understood the importance of the devices. No harm is known to have occurred. The harm level was unlikely to be realized for the following reasons: • The individuals had completed NERC CIP cyber security training and had successful PRAs at the time access was retained. • The individuals had valid business needs and were authorized for access prior to going on leave and retirement from the entity. • The individuals did not use the access during the period of late revocation. There are several internal controls in place to detect or prevent violation occurrence, including: • Entity Supervisors review all physical and electronic access to NERC CIP Assets for their direct reports on a quarterly basis. • Entity Compliance reviews quarterly access validation results as an independent verification and self-assessment. • The supervisors were NERC CIP Cleared (PRA and security awareness training). • The supervisors received annual NERC CIP training which includes information on access revocation requirements • All Supervisors of personnel with physical and/or electronic access to NERC CIP Assets complete training of their responsibilities, including access revocation. • Procedures document access requirements, including business need and access revocation requirements. While the current controls did not prevent the issue, the first control prompted the need for revocation and second control identified the potential violation. A new control to be implemented will identify the potential need for revocation within days. | To mitigate this noncompliance, the entity: 1) removed all NERC CIP Access for Individual one; 2) removed all Accesses for Individual two; 3) reviewed expectations for NERC CIP Access revocation with all supervisors; 4) Supervisors of individual one and two re-took training courses; 5) delivered message to all Supervisors of NERC CIP Cleared individuals reinforcing expectations for having NERC CIP Access; 6) reviewed all individual accesses for additional revocation of accesses; 7) developed a new control to enhance monitoring of NERC CIP Cleared employees with access to NERC CIP Assets to ensure timely revocation, e.g. any employee reporting 3 consecutive days of non-work, non-vacation time and notify immediate and skip level supervisor to confirm employee access is correct. Implementation date will be set based upon control design; and 8) researched to enhance monitoring of NERC CIP Cleared contractor access to NERC CIP Assets to ensure timely revocation.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017017359 | CIP-008-5 | R3; R3.1, R3.1.3 | SPPRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-008-5 R3.1.3. After testing its cybersecurity incident response plan (CIRP), SPPRE_URE1 did not notify each person or group with a defined role in the CIRP of the documented lessons learned within 90 calendar days. The duration of this issue of noncompliance was five days, beginning the date SPPRE_URE1 should have communicated CIRP lessons learned to appropriate SPPRE_URE1 personnel, and ending the date CIRP lessons learned were communicated to the appropriate SPPRE_URE1 personnel. The root cause of this noncompliance was a misunderstanding of the process by the SPPRE_URE1 subject matter expert (SME) that was responsible for distributing the CIRP lessons learned to applicable staff. This was a new requirement and the first CIRP test conducted under Version 5 of the CIP standards that required the SME to communicate CIRP lessons learned. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-008-5 R3.1.3 has the potential to affect the reliability of the BPS because had an incident occurred and the appropriate SPPRE_URE1 employees were unaware of changes to the CIRP, incident response could have been delayed. Notwithstanding, SPPRE_URE1 did not have an event that required the use of its CIRP during the time of noncompliance. The issue was reported internally by the SME that is responsible for communicating the lessons learned, and subsequently, the CIRP lessons learned were promptly distributed to the appropriate SPPRE_URE1 personnel. No harm is known to have occurred. SPPRE considered SPPRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SPPRE_URE1: 1) communicated lessons learned to the applicable SPPRE_URE1 employees; and, 2) implemented an automated monthly task that requires the SME to check for updates to the CIRP and notify the appropriate personnel of any changes. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017017349 | CIP-006-6 | R1; R1.2 | SPPRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R1.2. Two contractors were working in a SPPRE_URE1 Physical Security Perimeter (PSP). One of the contractors had authorized access to the PSP (Contractor #1). The other contractor did not have authorized access to the PSP, i.e. a visitor (Contractor #2). Contractor #1 gave his access credentials, i.e. badge and PIN, to Contractor #2, who left the PSP and used Contractor #1’s credentials to regain entry to the same PSP. The duration of this issue of noncompliance was three days, beginning the date Contractor #1 gave Contractor #2 his PSP access credentials, and ending the date Contractor #1’s PIN was reset. The root cause of this noncompliance was human error. By giving access credentials to a person who was unauthorized to have access to SPPRE_URE1’s PSP, Contractor #1 did not follow SPPRE_URE1’s PSP process. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-006-6 R1.2 has the potential to affect the reliability of the BPS because a person with malicious intent could access the PSP and disrupt operations via unauthorized physical or electronic access to BES Cyber Systems. Notwithstanding, Contractor #1’s credentials were not used by Contractor #2 to access any other SPPRE_URE1 PSP. Contractor #2 was continuously escorted inside the PSP by Contractor #1, who was authorized to access the PSP, and Contractor #2 had a current Personnel Risk Assessment and cyber security training on file. The issue was discovered by observation of another SPPRE_URE1 employee, immediately reported, and action to mitigate was taken promptly, including immediately resetting Contractor #1’s PIN and reinforcing PSP access training. No harm is known to have occurred. SPPRE considered SPPRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SPPRE_URE1: 1) reset Contractor #1’s PIN; and, 2) conducted training for both contractors and their supervisor on the applicable SPPRE_URE1 cyber security policies. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2017017101 | CIP-004-6 | R4; R4.1, R4.1.3 | SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-6 R4.1 and R4.1.3. During an internal review, SPPRE_URE2 discovered that an SPPRE_URE2 employee (Employee #1) had been given access to Critical Electric Infrastructure Information (CEII) (R4.1.3) electronic storage locations prior to the completion of the appropriate authorization form (R4.1). The system administrator (SA) responsible for implementing the access change did not follow the SPPRE_URE2 process that requires the SA to grant only the access that is indicated on the form provided by the SPPRE_URE2 Help Desk. The form provided to the SA did not contain CEII access approvals. The duration of this instance of noncompliance was eight days, beginning the date Employee #1 was given access to the CEII electronic storage locations, and ending the date access to the CEII electronic storage locations were removed for Employee #1. Additionally, SPPRE_URE2 submitted another instance of CIP-004-6 R4.1.3. During an internal review, SPPRE_URE2 discovered that a second SPPRE_URE2 employee (Employee #2) had been given access to CEII electronic storage locations (R4.1.3) prior to the completion of the authorized access form. The SPPRE_URE2 Help Desk did not follow the SPPRE_URE2 process and provided an incomplete authorized access form to the SA responsible for granting access (R4.1). Subsequently, the SA granted CEII access to Employee #2 based on the incomplete access form. The duration of this instance of noncompliance was 121 days, beginning the date Employee #2 was given access to the CEII electronic storage locations, and ending the date access to the CEII electronic storage locations was removed for the Employee #2. The root cause of this instance of noncompliance was a combination of human error and insufficient training on the access request process. In both instances the steps were performed did not follow the SPPRE_URE2’s process. Additionally, assumptions were made by the SPPRE_URE2 SA that the prior steps had been completed by the SPPRE_URE2 Help Desk, without the SA confirming that was the case before granting CEII access. Regarding insufficient training, the SA did not follow the process by granting more access than was indicated on the authorization form for Employee #1. Further, the work package the SPPRE_URE2 Help Desk sent the SA that contained the access authorization forms for Employee #2 did not accurately reflect what work was to be completed at the time it was assigned; therefore, creating room for error. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to restrict electronic access to SPPRE_URE2’s CEII electronic storage locations to only those employees with a business need has the potential to affect the reliability of the BPS by providing employees without an identified business need with access to protected information, which could be misused and compromise a BES cyber system. Notwithstanding, Employee #1 only had access for seven days and was not aware of the access until the day access was removed. The employee was tasked with duties unrelated to the CEII storage location and did not access the CEII storage during the seven days the employee had access. Additionally, Employee #1 had a completed Personnel Risk Assessment on file and was authorized for electronic access to SPPRE_URE2’s CEII electronic storage locations. Employee #2 also did not access the CEII storage during the noncompliance. However, if Employee #2 had accessed the CEII storage, there were no files in the storage location for Employee #2 to access. No harm is known to have occurred. SPPRE considered SPPRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) removed electronic access to the CEII storage location for Employee #1; 2) revised the general access form to add CEII access approvals to limit confusion by identifying all needed general access on one authorization form; 3) removed electronic access to the CEII storage location for Employee #2; and 4) reinforced and trained affected staff on the access request process steps. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | SPPRE_Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2017016852 | CIP-006-6 | R2; R2.1, R2.2 | SPPRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R2.1 and R2.2. SPPRE_URE3 identified two instances where the same employee had not been properly escorted (R2.1) or logged into (R2.2) a Physical Security Perimeter (PSP). On two instances, an employee unsuccessfully attempted to access the PSP by swiping his access badge. The employee subsequently followed an authorized individual (tailgated) into the PSP without utilizing his access badge. The employee was not escorted (R2.1) nor logged into the PSP (R2.2) as a visitor. He remained in the PSP for six minutes on the first occasion and 19 minutes on the second occasion. The duration of this issue of noncompliance was 12 days, from the first date the employee entered the PSP without being properly escorted and logged, through the last date the employee exited the PSP after not being escorted or logged. The root cause of this noncompliance was the employee’s failure to follow SPPRE_URE3’s visitor control program, which prohibits tailgating. The employee believed he had authorized unescorted access to all PSPs at the location he worked, but he was granted access to only 11 of the 12 PSPs. When the employee’s badge did not allow him access to the 12th PSP, the employee was required to inquire about the denied access per SPPRE_URE3’s visitor control program. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly escort and log in visitors at a PSP has the potential to affect the reliability of the BPS by providing the opportunity for visitors with malicious intent to access Cyber Assets within the PSP. Notwithstanding, the employee had successfully passed a Personnel Risk Assessment and had unescorted access to 11 of the 12 PSPs. In addition, the employee was not a visitor but a known employee with a business need to access the PSP. Access to the PSP was subsequently granted to the employee. No harm is known to have occurred. SPPRE considered SPPRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3 required the Employee to again complete the annual NERC CIP training. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017752 | CIP-004-6 | R.3: P3.5 | WECC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3 Part 3.5. Specifically, WECC_URE1 reported that it updated its internal documentation of Bulk Electric System (BES) Cyber System authorized users and discovered that the personnel risk assessment (PRA) interval for one individual with authorized unescorted physical access to certain WECC_URE1 Physical Security Perimeters (PSPs) containing High Impact BES Cyber System (HIBCS) had exceeded the maximum seven-year interval by one day. WECC_URE1 performed an internal review and learned that WECC_URE1’s Human Resource (HR) department, which was responsible for the management of PRAs, went through organizational and personnel changes prior to the noncompliance, including changes in management responsibility for PRAs. Specifically, the HR position that performs tasks related to PRAs was unfilled for several months and activities were temporarily assigned to other individuals within HR until the vacant HR position was filled. A report was generated from the HR database which identified the due dates for upcoming PRAs in the next quarter. HR staff completed PRAs for individuals with PRAs due dates in that quarter. A new hire assumed the previously vacant HR position, however they were not trained on the importance of NERC CIP requirements and PRA due dates and therefore failed to ensure this individual’s PRA was renewed in a timely manner which fell into the next quarter. One day after the PRA renewal due date, the identity check and history check were completed by a third party and WECC_URE1 completed the risk assessment, exceeding the compliance. WECC reviewed the Self-Report and, after further discussions with WECC_URE1 and analysis of data request responses, determined that WECC_URE1 failed to ensure that one individual with unescorted physical access had its PRA completed within the seven-year timeframe as required by Part 3.5. The root cause of the noncompliance was a lack of effective management controls to ensure that requirements were clearly communicated, understood, and met during periods of organizational change. This noncompliance started when a PRA for one individual expired and ended when the PRA was completed, for a total of one day of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure that one individual with unescorted physical access had its PRA completed within the seven-year timeframe as required by Part 3.5. Such failure could present a risk of unauthorized access to WECC_URE1’s HIBCS which could be exploited to cause damage or outages, thereby potentially affecting the reliability of the BES. However, the individual had been employed with WECC_URE1 for seven years, their access was limited to physical access only with no electronic access, and since the individual had previously been approved for unescorted physical access, they were aware of the security requirements associated with the PSPs. Additionally, the length of this noncompliance was only one day. Based on the controls in place and the length of the noncompliance, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE1: 1) completed the expired PRA; 2) improved its PRA report to be automatically generated and distributed to multiple individuals who are responsible for ensuring PRAs are completed within the required time frame; and 3) updated its PRA program documents to include a detailed procedure to ensure PRAs are completed within the seven-year timeframe and ensured that the staff were made aware of the mandatory requirements and timelines within the program. WECC_URE1 has verified the completion of all mitigation activity.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2017018397 | CIP-006-6 | R1; Part 1.8 | WECC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R1 Part 1.8. Specifically, WECC_URE2 reported that fumes from a roof repair at its Control Center containing Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) were so strong that WECC_URE2 had to prop open the Physical Security Perimeter (PSP) door to the Control Center to get ventilation. WECC_URE2’s System Operator placed a call to the IT Manager who, authorized the door to be propped open and actively monitored until it no longer needed to be opened. A similar incident occurred involving the same location where WECC_URE2 propped open the PSP door for ventilation. Even though the PSP door was monitored for access during the times the PSP door was propped open, WECC_URE2 did not log entry of each individual with authorized unescorted physical access into the PSP pursuant to CIP-006-6 R1 Part 1.8. WECC reviewed the Self-Report and determined WECC_URE2 failed to log entry of everyone with authorized unescorted physical access into a PSP at its Control Center containing MIBCS. The root cause of the noncompliance was personnel not fully understanding the requirements for logging access during such situations. WECC determined that this issue began when access logging should have occurred, and ended when WECC_URE2 closed the PSP door, for a total of one hour and 40 minutes for the first instance and one hour and 45 minutes for the second instance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to log entry of everyone with authorized unescorted physical access into a PSP at its Control Center containing MIBCS. Such failure could result in unauthorized access of individuals to WECC_URE2’s Control Center containing MIBCS. Once inside the Control Center, an unauthorized individual could compromise systems operated by WECC_URE2.. However, the harm had a low likelihood of occurring. The PSP at the Control Center was monitored by visual observation performed by WECC_URE2 personnel with authorized access. This issue is a documentation error where WECC_URE2 did not log entry into the PSP. WECC_URE2 confirmed that the only individuals who accessed the PSP during the short time it was propped open were authorized to do so. Additionally, No harm is known to have occurred. WECC_URE2 has no compliance history with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE2: 1) updated its Physical Access Procedure to address such instances where a PSP door may be propped open and what to do to remain compliant. WECC verified WECC_URE2's mitigating activities.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2017018434 | CIP-010-2 | R3; Part 3.1 | WECC_URE2 submitted a Self-Report stating that, it was in noncompliance with CIP-010-2 R3 Part 3.1. Specifically, WECC_URE2 reported that it did not conduct a paper or active vulnerability assessment by the mandatory and enforceable date of CIP-010-2 R3 Part 3.1. WECC_URE2 discovered this noncompliance while it was conducting its yearly review of the documents and procedures that comprise WECC_URE2’s CIP program. The scope of this noncompliance includes MIBCS and associated Electronic Access or Monitoring Systems (EACMS), Physical Access Controls Systems (PACS), and Protected Cyber Assets (PCA) at its Control Center. WECC_URE2 experienced a turnover of its management, and believes this is the reason for not performing the vulnerability assessment. Additionally, WECC_URE2 believed that the vulnerability assessment should have been performed on the mandatory and enforceable date of the Standard and Requirement, when in fact the initial performance of R3 part 3.1 was a different date per NERC’s Version 5 Implementation Plan dated October 23, 2015. WECC reviewed the Self-Report and determined that WECC_URE2 failed to conduct a paper or active vulnerability assessment by the mandatory and enforceable date of the Standard and Requirement. The root cause of the noncompliance was management policy guidance or expectations not well-defined, understood, or enforced. Specifically, during WECC_URE2’s transition between managers, the requirement to conduct the paper or active vulnerability assessment was missed. WECC determined that this issue began when a paper or active vulnerability assessment should have been conducted, and ended when WECC_URE2 conducted a paper vulnerability assessment, for a total of 81 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to conduct a paper or active vulnerability assessment by the mandatory and enforceable date of the Standard and Requirement. Such failure could result in WECC_URE2 not being able to identify current security patches that may prevent malware, viruses and malicious code from being installed on its systems. Additionally, not conducting a vulnerability assessment could result in not identifying unjustified open ports that may affect the SCADA System used for monitoring and control, the HMI that controls the SCADA, the data acquisition server used for monitoring and control of the SCADA, the data interchange ICCP link server and switches that control the inter-entity real-time coordination between entities. The vulnerability assessment performed by the entity found no vulnerabilities. WECC determined that the harm associated with this noncompliance had a low likelihood of occurring. No harm is known to have occurred. WECC_URE2 has no compliance history with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE2: 1) a. conducted a paper vulnerability assessment. WECC verified WECC_URE2's mitigating activities.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2017018173 | CIP-007-6 | R2; Part 2.2 | WECC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R2 Part 2.2. Specifically, WECC_URE2 reported that on two separate instances it did not evaluate security patches for applicability within 35 calendars of the last evaluation. During the implementation of CIP Version 5, WECC_URE2 believed it could schedule its evaluation of security patches on a monthly calendar basis, however did not take into consideration the effect that months with 30 and 31 days, and holidays, and that weekends would have on meeting the requirement to evaluate security patches for applicability at least once every 35 calendar days from its last evaluation. Additionally, WECC_URE2 did not consider how its dependence on a single individual to perform the security patch evaluation could negatively impact its CIP compliance obligations. The scope of this noncompliance includes EACMS, PACS, PCAs and BES Cyber Assets (BCAs) associated with the MIBCS at its Control Center. WECC reviewed the Self-Report and determined that WECC_URE2 failed to evaluate security patches at least once every 35 calendar days pursuant to CIP-007-6 R2 Part 2.2. The root cause of the noncompliance was due to a lack of controls to timely monitor security patch evaluation dates. Specifically, the technician responsible for evaluating security patches was relying on memory when doing the evaluation, thus missing the 35-calendar day review requirement. WECC determined that this issue began when WECC_URE2 should have evaluated security patches for applicability, and ended when WECC_URE2 completed its security patch evaluations, for a total of two days for the first instance and three days for the second instance of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to evaluate the release of security patches for applicability within 35 calendar days from the last evaluation. Such failure could result in missing critical security patches released to prevent malware, viruses, or malicious code from being installed in its MIBCS. Failure to review these patches may affect the SCADA System used for monitoring and control, the HMI that controls the SCADA, the data acquisition server used for monitoring and control of the SCADA, the data interchange ICCP link server, and switches that control the inter-entity real-time coordination between entities. WECC_URE2 had weak internal controls in place to prevent or detect this issue. WECC determined that the harm associated with this noncompliance had a low likelihood of occurring. No harm is known to have occurred. WECC_URE2 has no compliance history with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE2: 1) evaluated security patches released by its listed sources for the devices in scope.; 2) updated its excel patch source workbook to include a designated date for evaluating security patches; and 3) updated its security patch management procedures to include what needs to be evaluated for security patches and when; WECC verified WECC_URE2's mitigating activities.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2018018920 | CIP-010-2 | R1: P1.3 | WECC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R2. Specifically, WECC_URE3 reported that it discovered that the configuration data was outdated in its management system. This system is used to automatically detect and update changes to baseline configuration data. Further investigation of the issue determined that the management system's configuration collections processes running on twelve assets had failed, and the baseline configuration data for those assets was not being uploaded. As a result, baseline configurations were not updated within the required 30 calendar days of completing a change as required in CIP-010-2 R1 Part 1.3. After the management system's processes were restarted, the configuration collection processes resumed. WECC reviewed the Self-Report and after further discussions with WECC_URE3 and analysis of data request responses, determined that WECC_URE3 had four instances of noncompliance in which baseline configurations were not monitored for changes every 35 calendar days as required by CIP-010-2 R2 Part 2.1 (WECC2016016647) and therefore baseline configurations were not updated within 30 calendar days of the changes as required by CIP-010-2 R1 Part 1.3 (WECC2018018920). These instances affected Protected Cyber Assets (PCAs) and Electronic Access or Monitoring Systems (EACMS) associated with WECC_URE3’s High Impact Bulk Electric System (BES) Cyber System (HIBCS). The root cause of the noncompliance was the management system's client software that performs updates to the baselines failed and stopped performing updates on the devices and WECC_URE3 did not have any controls to monitor the software client. The four instances of noncompliance started when baseline configurations were not monitored for changes every 35 calendar days nor were changes updated within 30 calendar days, and ended on when the baseline configuration was again monitored, with the longest incident lasting approximately 80 days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to monitor baseline configurations for changes every 35 calendar days as required by CIP-010-2 R2 Part 2.1 and therefore baseline configurations were not updated within 30 calendar days of the changes as required by CIP-010-2 R1 Part 1.3 on PCAs and EACMS located within facilities containing HIBCS. Such failure could potentially result in not identifying unauthorized changes to these assets such as the installation of malicious or unauthorized vulnerable software. This could potentially lead to the compromise of one or more of these devices which could in turn lead to other network compromises ultimately leading to negatively affecting BES Cyber Systems and the BES operational state. However, these devices are protected with a defense-in-depth strategy which includes the placement of protection mechanisms, procedures, and policies which are intended to increase the dependability of the system where multiple layers of defense prevent unauthorized access and direct attacks against critical systems. These include, segregated networks, strict access controls, access monitoring, malicious code monitoring, logging of all access, and change control procedures. Based on the controls in place, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE3: 1) restarted the management system's agent configuration collections processes for the impacted assets, and configuration collection resumed; 2) evaluated changes to the baselines configurations and determined that no unauthorized changes occurred during the outage period; and 3) implemented a new process to review, and respond as needed, the active state of all the management system's agent configuration collections processes, weekly.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016647 | CIP-010-2 | R2: P2.1 | WECC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R2. Specifically, WECC_URE3 reported that it discovered that the configuration data was outdated in its management system. This system is used to automatically detect and update changes to baseline configuration data. Further investigation of the issue determined that the management system's configuration collections processes running on twelve assets had failed, and the baseline configuration data for those assets was not being uploaded. As a result, monitoring for unauthorized changes was not conducted within 35 calendar days as required in CIP-010-2 R2 Part 2.1. After the management system's processes were restarted, the configuration collection processes resumed. WECC reviewed the Self-Report and after further discussions with WECC_URE3 and analysis of data request responses, determined that WECC_URE3 had four instances of noncompliance in which baseline configurations were not monitored for changes every 35 calendar days as required by CIP-010-2 R2 Part 2.1 (WECC2016016647) and therefore baseline configurations were not updated within 30 calendar days of the changes as required by CIP-010-2 R1 Part 1.3 (WECC2018018920). These instances affected Protected Cyber Assets (PCAs) and Electronic Access or Monitoring Systems (EACMS) associated with WECC_URE3’s High Impact Bulk Electric System (BES) Cyber System (HIBCS). The root cause of the noncompliance was the management system's client software that performs updates to the baselines failed and stopped performing updates on the devices and WECC_URE3 did not have any controls to monitor the software client. The four instances of noncompliance started when baseline configurations were not monitored for changes every 35 calendar days nor were changes updated within 30 calendar days, and ended on when the baseline configuration was again monitored, with the longest incident lasting approximately 80 days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to monitor baseline configurations for changes every 35 calendar days as required by CIP-010-2 R2 Part 2.1 and therefore baseline configurations were not updated within 30 calendar days of the changes as required by CIP-010-2 R1 Part 1.3 on PCAs and EACMS located within facilities containing HIBCS. Such failure could potentially result in not identifying unauthorized changes to these assets such as the installation of malicious or unauthorized vulnerable software. This could potentially lead to the compromise of one or more of these devices which could in turn lead to other network compromises ultimately leading to negatively affecting BES Cyber Systems and the BES operational state. However, these devices are protected with a defense in depth strategy which includes the placement of protection mechanisms, procedures, and policies which are intended to increase the dependability of the system where multiple layers of defense prevent unauthorized access and direct attacks against critical systems. These include, segregated networks, strict access controls, access monitoring, malicious code monitoring, logging of all access, and change control procedures. Based on the controls in place, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE3: 1) restarted the management system's agent configuration collections processes for the impacted assets, and configuration collection resumed; 2) evaluated changes to the baselines configurations and determined that no unauthorized changes occurred during the outage period; and 3) implemented a new process to review, and respond as needed, the active state of all the management system's agent configuration collections processes, weekly.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016465 | CIP-007-6 | R5: P5.4 | WECC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R5 Part 5.4. Specifically, WECC_URE3 reported that it did not change the default passwords on three protection relays at substations containing Medium Impact Bulk Electric System (BES) Cyber Systems (MIBCS) without external routable connectivity (ERC). These issues were discovered during a field assessment associated with a NERC CIP Vulnerability Assessment made by WECC_URE3's employees. After this discovery, WECC_URE3's employees instructed a test crew to change the default password and complete a checklist for passwords. These activities were completed for all relays. WECC_URE3 discovered that it had a second instance in which it did not change the default password on a programmable logic controller (PLC) at a substation containing MIBCS without ERC, because it was previously out of scope based in prior versions of the CIP standards. The PLC was later determined to be in-scope, requiring its default password to be changed. The default password was changed and all relevant documentation was updated. WECC reviewed the Self-Report and after further discussions with WECC_URE3 and analysis of data request responses, determined that WECC_URE3 failed to change default passwords on four devices located at substations containing MIBCS, as required by CIP-007-6 R5 Part 5.4. The root cause of the noncompliance was a less than adequate procedure. Specifically, WECC_URE3’s procedure did not include a process for how to handle new scope related to projects and changing default passwords, as required by CIP-007-6 R5 Part 5.4. This first instances of noncompliance started when the Standard and Requirement became mandatory and enforceable to WECC_URE3, and ended when the last password was changed on a protection relay, for a total of approximately 50 days of noncompliance. The second instance on noncompliance started when WECC_URE3 failed to change the default password on a PLC that had been reconfigured and was now in scope for this Standard and Requirement, and ended when the last password was changed on the PLC, for a total of approximately 20 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to change the default password on four devices. Such failure could increase the risk of unauthorized access and potential changes to its MIBCS. Because the passwords were default, WECC_URE3 would not have the capability to identify who used the password which could result in adverse impacts to WECC_URE3’s registered functional obligations in coordinating and communicating, as well as monitoring, controlling and operating its facilities; thereby potentially affecting the reliability of the BES. However, none of the devices have remote access and are not externally routable, so all actions must be done at the devices themselves. WECC_URE3 also utilizes a process in which local passwords are verified on all BES Cyber Assets on an annual basis. Additionally, one of the relays has a redundant protection relay that would have provided protection in the case of loss or misuse of the relay with the default password and for two of the other relays, they have UFLS protections providing automated sub-second response to system disturbances. The PLC also resides in a security zone where each door is equipped with an alarm and alert for any unauthorized physical access attempts. Based on the controls in place, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE3: 1) changed all default passwords; 2) conducted training for all technicians who deal with compliance for CIP-007-6 and CIP-010-2; 3) implemented an application to provide specific details on a per device basis as to what accounts/passwords exist and to assist with password changes (copy/paste passwords); 4) updated its procedure to expand the change management process to evaluate and assess projects at NERC-impacted facilities with both programmable and non-programmable equipment; and 5) holds monthly meetings to keep employees current on NERC CIP requirements and processes. WECC has verified the completion of all mitigation activity.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2017017107 | CIP-004-6 | R5: P5.2 | WECC_URE4 submitted a Self-Certification stating that it was in noncompliance with CIP-004-6 R5 Part 5.2. Specifically, WECC_URE4 reported that it did not revoke electronic or unescorted physical access for two employees that transferred to different job roles by the next calendar day following the date that WECC_URE4 determined that they no longer required said access. In the first instance, a manager submitted a request to have the employee’s electronic access to its High Impact Bulk Electric System (BES) Cyber System (HIBCS) revoked. Due to a misconfiguration of WECC_URE4’s tracking system, the tasks to revoke the access were assigned to the wrong personnel, therefore the revocation did not occur in a timely manner. In reviewing the root cause of the first instance of noncompliance, WECC_URE4 discovered an additional instance of noncompliance. A request was made for a transferred employee’s unescorted physical access to two Medium Impact BES Cyber Systems (MIBCS) to be revoked. According to WECC_URE4’s process, its tracking system assigns a revocation task to a primary and secondary point of contact. If the task is not completed within 12 hours, the tracking system escalates the task to a primary escalation point of contact. However, in this instance the tracking system did not escalate the task and instead cancelled the task and sent a cancellation notice to the primary and secondary point of contact. Both of these individuals assumed that the other one had completed the revocation task and therefore no action was taken. The second instance was discovered and the employee’s access was revoked on the same day. WECC reviewed the Self-Certification and determined that in two separate instances, WECC_URE4 failed to revoke a transferring employee’s electronic or unescorted physical access by the end of the next calendar day following the date that WECC_URE4 determined that the two employees no longer required said access. The root cause for the first instance of noncompliance was an untimely response by WECC_URE4 to correct a known repetitive problem within the tracking system. Specifically, WECC_URE4 was aware that the tracking system did not appropriately assign tasks regarding its HIBCS, however they had yet to update the tracking system and so this revocation was missed. The root cause for the second instance of noncompliance was a less than adequate testing of design and installation of the tracking system. Specifically, the tracking system did not perform as designed and caused a revocation task to be cancelled instead of escalated. This first noncompliance started when electronic access was not revoked for a transferred employee within one calendar day, and ended when the employee’s electronic access was revoked, for a total of approximately five days of noncompliance. This second noncompliance started when unescorted physical access was not revoked for a transferred employee within one calendar day, and ended when the employee’s unescorted physical access was revoked, for a total of approximately 130 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In two separate instances, WECC_URE4 failed to revoke electronic access to its HIBCS and unescorted physical access to two MIBCS in a timely manner. Such failure could present a risk of unauthorized access to WECC_URE4’s HIBCS and MIBCS. Such unauthorized access could be exploited to alter or tamper with the Control Center, transmission, generation, and substations causing damage or outages, thereby potentially affecting BES transmission lines and generation in the western interconnection. However, both employees were transferred within WECC_URE4. Additionally, both employees had been authorized and provisioned either electronic or unescorted physical access prior to their transfer. The employee with electronic access had previously worked in a group where he had knowledge of the EMS system and associated security patches. The employee with unescorted physical access had previously worked in a group where he had knowledge of substations and associated security patches. Based on the controls in place, WECC determined that the harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE4: 1) revoked both the electronic and unescorted physical access; 2) updated how the tracking system assigns tasks associated with its Energy Management System; 3) fixed escalation process within the tracking system so that tasks are not cancelled, but instead escalate properly; 4) resolved daily notification reporting bug within the HR reports; 5) finalized requirements for the automatic revocation of physical security access; and 6) implemented the automatic revocation for physical access between the tracking system and WECC_URE4’s program used for physical security access. WECC has verified the completion of all mitigation activity.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014453 | CIP-006-3c | R4 | WECC_URE5 submitted a Self-Report stating that it was in noncompliance with CIP-006-3c R4. Specifically, WECC_URE5 reported that during a quarterly review of its Physical Access Control System (PACS) it discovered two key fobs that were enabled and identified as “dispatch” and not associated with a specific individual. The key fobs were originally enabled during testing and system changes that WECC_URE5 was performing, and then placed in a locked box as a back-up in case an employee with authorized unescorted physical access forgot their access badge. WECC_URE5 failed to implement operational and procedural controls to manage physical access to all access points to the Physical Security Perimeter (PSP) protecting its Control Center, when they did not adequately account for the key fobs. WECC reviewed the Self-Report determined that WECC_URE5 failed to document and implement the operational and procedural controls to manage physical access at all access points to the PSP pursuant to CIP-006-3c R4. The root cause of the noncompliance was a lack of education and training of the CIP requirements. Specifically, supervisors and other employees were aware of the key fobs; however, the connection was never made that their miss-use represented a CIP compliance issue. WECC determined that this issue began when WECC_URE5 did not log use of the key fob, and ended when WECC_URE5 disabled the two key fobs in its PACS, for a total of 164 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to document and implement the operational and procedural controls to manage physical access at all access points to the PSP pursuant to CIP-006-3c R4. Such failure could result in a bad actor gaining unauthorized physical access to the Control Center and affecting generation and/or transmission within the Western Interconnection. However, to access the key fob, three other doors had to be traversed, each with its own card reader and required access. The final door required CIP access authorization. Therefore, an individual had to either have their own CIP authorized badge in the first place to access the key fob in the operations area, or be admitted by another authorized person. Visitors were required to be escorted, so the only person likely to have been admitted without their own badge would have been someone recognized as being authorized to be in the area. Based on these facts and the controls analyzed, WECC determined that the risk associated with this noncompliance had a low likelihood of occurring. No harm is known to have occurred. WECC considered WECC_URE5's compliance history with CIP-006-3c R4. WECC_URE5 had no relevant previous noncompliance with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE5: 1) disabled the PACS key fobs that were not individually assigned; and 2) informed and discussed at a senior level meeting to provide education and emphasize that the personal badge each person possessed is the only allowed method to access a PSP. WECC verified completion of WECC_URE5's Mitigation Plan.
2017-12-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2017018545 | CIP-004-6 | R4; R4.1 | FRCC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R4 (Part 4.1). This noncompliance started when FRCC_URE1 failed to authorize employees prior to granting them electronic access to the designated storage locations for BES Cyber System Information (BCSI) and ended when proper authorization was granted. Specifically, FRCC_URE1 failed to authorize based on need for Access to designated storage locations, whether physical or electronic, for BCSI, as required by CIP-004-6 R4 (R4.1). FRCC_URE1’s program authorizes access based on roles. FRCC_URE1 verified the extent of condition to the instances identified. The roles in question provided Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP) access but not BCSI storage access. FRCC_URE1 recognized the roles in question should have had BCSI access in the procedure. The root cause for this noncompliance was that FRCC_URE1 did not follow the procedure to correctly provision access. The individuals responsible for granting access assumed that because the employees in question were already assigned to roles with more critical access, that those roles also afforded BCSI storage access. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1’s failure to properly authorize individuals before granting access to BCSI could potentially result in release of secure information to employees who are not trained in proper handling of BCSI. The risk was reduced because the employees were authorized for access to more sensitive areas (PSP/ESP). These employees also had the required background screening and training, which included proper handling of BCSI. No harm is known to have occurred. FRCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, FRCC_URE1: 1) completed authorization process retroactively for the two employees provisioned with BCSI storage location access; 2) verified that all other persons with access to BCSI storage locations were properly authorized; 3) revised the process; 4) retrained applicable employees on the process; and 5) set up internal controls for annual re-training on access authorization process.
2017-12-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017442 | CIP-007-6 | R5: P4.2 and P5.4 | MRO_URE1 identified two instances of noncompliance. The first instance of noncompliance involved a default password discovered on a BES Cyber Asset (Ethernet switch) discovered during an annual vulnerability assessment. MRO_URE1 conducted an extent of conditions analysis and discovered additional default passwords on 49 Medium Impact BES Cyber Assets (BCAs) and 14 Protected Cyber Assets (PCAs) associated with a Medium Impact BES Cyber System. The second instance of noncompliance involved two devices that had their password requirements removed via Windows registry changes. The first instance of noncompliance was caused by staff not following MRO_URE1's documented process to change known default passwords. The second instance of noncompliance was caused by field personnel not documenting the operational reason for granting local operators the ability to respond to alarms without password authentication. This noncompliance lasted approximately five months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the first instance of noncompliance, per MRO_URE1, the issue was detected by a secondary control not required by the CIP standards. This secondary control limited the duration of the noncompliance to approximately four months. Additionally per MRO_URE1, the 64 BCAs and PCAs that were impacted by the noncompliance were network communications equipment and not Cyber Assets that can exert direct control of Transmission Facilities. Further per MRO_URE1, the 64 devices resided within a Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP) and were protected by an Intermediate System against an adversary trying to employ Interactive Remote Access on the devices. Finally per MRO_URE1, the affected devices were located in substations and Control Centers were not impacted. For the second instance of noncompliance, per MRO_URE1, the issue was discovered by a technician conducting a secondary review of the asset configuration, which limited the duration of the noncompliance. Further per MRO_URE1, the two devices were located within a PSP and access to the devices was limited to personnel who are required to comply with the requirements of CIP-004-6 (including Personnel Risk Assessments and annual CIP training). Finally, the issue was a documentation issue as it was mitigated by documenting the configuration, or alternatively could have been resolved through submission of a TFE. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this noncompliance, MRO_URE1: For the first instance of noncompliance: 1) changed the default password on all affected devices, and 2) conducted training for relevant staff on the process for changing default passwords. For the second instance of noncompliance: 3) documented the operational reasons that non-administrative accounts can bypass login for these two devices, and 4) to prevent reoccurrence, changed field personnel accounts to non-administrative accounts so that configuration changes could not be made by field personnel. MRO_URE1 stated that mitigating activities.
2017-12-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017016863 | CIP-002-5.1 | R1 | MRO_URE2 stated that a Medium Impact BES Cyber Asset was installed at a substation without being identified as a Medium Impact BES Cyber Asset. The issue was caused by a failure to train personnel associated with a specific type of equipment on MRO_URE2's CIP Version 5 field work procedures. This noncompliance last approximately three weeks. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was self-identified that resulted in the duration being limited to three weeks. Per MRO_URE2, the BES Cyber Asset in question is a component of an RTU that was already identified as a BES Cyber Asset. It is not required by the Standard and Requirement that an RTU and its components be recorded as separate BES Cyber Assets, and this level of granularity is not typical utility practice. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this noncompliance, MRO_URE2: 1) added the I/O module to its BES Cyber Asset List; 2) updated baseline documentation for the affected BES Cyber System; 3) distributed an email to all personnel authorized to work on Medium Impact BES Cyber Systems to clarify and reinforce all relevant policy and procedures; and 4) provided training all personnel authorized to work on Medium Impact BES Cyber Systems on the relevant CIP Version 5 policies and procedures and "lessons learned." MRO_URE2 stated that mitigating activities were complete.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017018388 | CIP-003-6 | R1. | NPCC_URE1 submitted a self-report stating that it was in noncompliance with CIP-003-6 R1. During a third-party review of NERC CIP compliance, it was discovered the required cyber security policies was not fully developed, reviewed and signed by CIP Senior Manager in accordance with CIP-003-06 R1 Part 1.2. NPCC_URE1 is classified as containing low impact BES Cyber Systems. This was as a result of inadequate resources at NPCC_URE1 to understand and implement the NERC CIP requirements for low impact BES Cyber Systems. The noncompliance lasted approximately 4 months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 is classified as containing low impact BES Cyber Systems. NPCC_URE1 is located in a sparsely populated region. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the NPCC_URE1's compliance history and determined there are no relevant instances of noncompliance | To mitigate this noncompliance, NPCC_URE1: 1) drafted CIP cyber security policy for low impact BES Cyber Systems addressing security awareness, physical security controls, electronic access controls and Cyber Security Incident response; 2) reviewed policy for completeness and implementation ability; 3) approved CIP cyber security policy for low impact BES Cyber Systems by a CIP senior manager; 4) made the policy available to personnel; and 5) contracted an experienced third-party resource to develop and assist with implementation of NERC CIP Program to meet compliance with all applicable requirements for low impact BES Cyber Systems including cyber security policy for low impact BES Cyber Systems to address security awareness, physical security controls, electronic access control, and Cyber Security Incident response. NPCC has verified the completion of all mitigation activity.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2017017900 | CIP-006-6 | R1. | NPCC_URE2 submitted a self-log stating that it was in noncompliance with CIP-006-6 R1. A contractor working at NPCC_URE2's Substation was removing material via a door. During the pre-job briefing, the contractor was informed by the NPCC_URE2's permit holder that the contractor was not permitted to exit the facility in this manner without the permit holder in attendance. During the course of the morning, members of the contractor crew were removing material through the door with the permit holder in attendance. However, during a half-hour period the contractor opened the door and was removing material without the permit holder in attendance. The contractor was approached by a NPCC_URE2 employee who was passing by the substation and observed the open door. The employee stopped the work and notified the permit holder. The Substation is a medium impact facility for cyber security compliance and the door in question is a perimeter access point. CIP-006-6 R1 requires the Company to document and implement a plan to restrict access to BES Cyber Systems. The Company plan stipulates that “leaving an opened perimeter access point unattended is prohibited”. Video records confirm that the contractor periodically entered and exited via the door while removing material from the substation. There were periods where no one was visibly present at the open door. The root cause of the issue was the failure of the contractor to follow clear directions from the permit holder. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Video records confirm that no one entered the substation via the open door, other than contractor and Company personnel. A NPCC_URE2 employee observed the open door and facilitating a rapid resolution of the issue. Also, there are additional doors/walls separating the Substation BES Cyber Assets from the perimeter access point. Risk was also limited by the short duration that the perimeter access point was open and unattended. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the NPCC_URE2's compliance history and determined there are no relevant instances of noncompliance | To mitigate this issue, NPCC_URE2: 1) Created an Action Line Complaint against the contractor in the NPCC_URE2 Oversight System. The contractor was advised on the issue and the contractor agreed that, on an on-going basis, they will direct their personnel via toolbox talks and pre-job briefings of security procedures and the requirement that no one is to enter/exit without substation personnel escorting them. This remediation plan was accepted by the Company's committee that oversees contractors. 2) revised their CIP-006 Procedure to clarify that an authorized person must be in attendance when a perimeter access point is left open. 3) sent an Awareness Email (Security Notice) to relevant employees stating that contractors shall follow the physical security rules. 4) had a quarterly meeting to discuss the event. 5) reviewed the CIP-006 issue by the vice president at an expanded staff meeting. NPCC has verified the completion of all mitigation activity.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2017017398 | CIP-004-6 | R3. | NPCC_URE3 submitted a self-log stating that it was in noncompliance with CIP-004-6 R3. NPCC_URE3 failed to conduct a Personnel Risk Assessment (PRA) for one individual with authorized unescorted physical access within 7 calendar years of the previous PRA completion date. The noncompliance lasted approximately 1 month. The root cause of the noncompliance was due to a gap in the entity’s process for identifying PRA’s that are expiring soon when granting unescorted physical access rights. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the individual is an employee and has worked with the entity for more than 10 years and is still currently employed by the entity. The employee had a prior PRA and up to date CIP training. The individual further did not have electronic access rights to the BES Cyber Systems. Additionally, the individuals PRA was renewed with no adverse findings. The individual in scope had access to several PSPs classified as Medium impact facilities. During the period where the PRA had lapsed the individual in scope accessed one substation on two days for the performance of assigned substation maintenance tasks. If the systems at this facility would have been compromised line protection may still be provided by protection relays at connecting substations. Further, if remote substation monitoring and remote substation control was lost, the entity would dispatch an investigation team and the substation would be manned. No harm is known to have occurred during the noncompliance period. NPCC considered NPCC_URE3’s compliance history and determined there are no relevant instances of noncompliance. | To mitigate the issue, the entity: 1) Revoked unescorted physical access for the individual in scope 2) Performed a PRA on the individual in scope To prevent reoccurrence of the issue, the entity: 1) Updated its Corporate Security procedures to notify its internal compliance group when access is granted and the PRA for the individual will expire within the next six months. NPCC has verified the completion of all mitigation activity.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2017017396 | CIP-010-2 | R2. | NPCC_URE4 submitted a self-log stating that it was in noncompliance with CIP-010-2 R2. NPCC_URE4 failed to monitor for, investigate, and document detected unauthorized changes to the baseline at least once every 35 calendar days for several PCAs. The noncompliance lasted approximately 2 days. The root cause of the noncompliance was human error. The individual responsible for performing the review received a reminder at the beginning of the month and forgot to complete the task by the end of the month. A contributing factor to the issue is the Governance, Risk and Compliance (GRC) system used to send email notifications to complete the required monitoring was not able to alert in 30 day increments. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the entity has intrusion detection systems on the network in scope that would alert personnel if malicious packets carrying known signatures crossed the network to the PCAs in scope. The entity further mitigated the risk by completing the baseline configuration monitoring one day late for several PCAs and two days late for the remaining PCAs. No unauthorized changes to baseline configurations were detected. No harm is known to have occurred during the two day noncompliance period. NPCC considered NPCC_URE4’s compliance history and determined there are no relevant instances of noncompliance. | To mitigate this issue, the entity: 1) Completed the baseline configuration monitoring for the several PCAs in scope. To prevent reoccurrence of the issue, the entity: 1) Configured software to automatically monitor the baseline configuration for the PCAs in scope. 2) Enhanced its GRC system to issue 30-day reminders. NPCC has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017499 | CIP-004-6 | R5 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. Beginning with a routine internal review, and continued through an extent of condition analysis, RFC_URE1 identified a several instances where shared account passwords for NERC CIP shared accounts were not changed within 30 days of an individual’s termination. The length of time that these passwords remained unchanged ranged from 2 days to 53 days. Generally, RFC_URE1 uses their access management system to track the relationships between an individual user and the shared accounts known to the user. The access management system is configured with role based access control roles that form the relationship between an individual user and the shared accounts known to that user. When an individual is removed from an role based access control role, all related access is revoked and all shared accounts included with that role are disassociated from the removed user. In these cases, the access management system automatically generates notifications to inform the assigned performers that the password for each impacted shared account must be changed. The root cause of this noncompliance was a misconfiguration within the access management system where many of the shared accounts at issue did not have assigned performers. Consequently, performers did not receive notifications to change passwords after a termination. Another factor contributing to the cause of this noncompliance was the performers’ failure to act in a timely manner on notifications that were assigned by the access management system. These major contributing factors involve the management practices of verification, in that RFC_URE1 failed to verify that all shared accounts had assigned performers within the access management system, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately four months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, in each of the terminations, physical and logical access had been removed within 24 hours of the termination, removing the individual’s ability to access the shared accounts in question and utilize the known passwords. Second, RFC_URE1 adheres to a 90-day password change cycle for most shared account passwords, including those identified in this matter. This additional control helped limit the duration of the missed password changes and the amount of time that they could have been used. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE1: 1) changed all of the relevant passwords; 2) conducted individual briefing for one specific performer who missed multiple password changes; 3) documented and established a monitoring protocol for RFC_URE1 to track the status and age of Shared Account User manual fulfillment tasks in the access management system, including a periodicity of review and protocol for following up on the reported tasks to ensure timely closure in support of ongoing compliance to NERC Standard CIP-004-5 R5 Part 5.5; 4) designed and delivered an access management system report to support the monitoring protocol. The report will show the status and age of the shared account user manual fulfillment tasks; 5) enhanced the email generated by the access management system for the shared account password change task to include, or provide a link to, sufficient information for the tasks to be performed, the timeframe in which to complete the task as well as the affected shared account; 6) verified that all production shared accounts associated with High-Impact Bulk Electric System Cyber Systems and their associated Electronic Access Control or Monitoring System devices are uniquely represented in the access management system. RFC_URE1 also validated every shared account object in the access management system and updated to include correct performers where needed; 7) corrected each of the shared accounts with missing or empty performer groups by adding or updating the performer group where necessary; and 8) delivered reinforcement communications for shared account owners, performers and IT managers that addresses Shared Account password change responsibilities and associated access management system functionality. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017567 | CIP-004-6 | R5 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. While performing an internal check of access discrepancy reports, RFC_URE1 discovered that an employee’s electronic access was not terminated in a timely manner following the employee’s transfer to a different department. The employee’s access was removed 27 days late. RFC_URE1 then conducted an extent of condition review and discovered additional instances where an employee’s electronic access was not removed in a timely manner. The length of time that those employees’ access rights remained active ranged from 1 day to 8 days. The root cause of this noncompliance where the employee’s access rights remained active for more than 7 days was the responsible individuals’ failure to track and execute the removal task within the required timeframe. For the remaining instances where the access rights were active for less than 7 days, the major contributing factor was an out-of-date job aid that was not updated to reflect the new timing requirements of CIP v5 (CIP v5 changed the timing requirement from 7 days to the next calendar day). These major contributing factors involve the management practices of verification, in that RFC_URE1 failed to verify that its job aids were up-to-date, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately six months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although RFC_URE1’s preventative controls failed to prevent this issue from occurring, RFC_URE1 self-identified the issue through an internal control and subsequent extent of condition review. Second, in all of these instances, the employees involved were trusted individuals with current CIP training and Personnel Risk Assessments, who had been transferred to different roles within the organization. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE1: 1) updated RFC_URE1 logical access training documentation to show updated verbiage to match the current CIP-004-6 R5, Part 5.2 requirement. RFC_URE1 also updated RFC_URE1 IT documentation, detailing updated process to meet the removal of access for an employee transfer; 2) communicated changes to the RFC_URE1 access training documentation and the RFC_URE1 IT documentation to RFC_URE1 IT support team members; 3) educated RFC_URE1 IT support team in the current NERC CIP requirement to remove users via transfer; and 4) enabled RFC_URE1's compliance operations department to receive communications from the access management system to provide additional oversight of all access removal notifications. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017646 | CIP-004-6 | R5 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. RFC_URE1 discovered that users who had recently been provided access to Physical Security Perimeters (PSPs) were not able to physically enter the space using their credentials. Upon investigation, RFC_URE1 determined that there was a folder in the entity's badging system, that had reached capacity with temporary files and was unable to store new information. This problem caused the connection between the badging system and the access management system tool to stop syncing information. As a result, not only were the grants of physical access not processed, but physical access revocation requests were also not processed for a period of 8 days. Specifically, physical access revocation request tickets were not processed within the required time frame. The delay in revocation for these individuals ranged from 3 days to 6 days. All revocation requests were processed upon discovery. The root cause of this noncompliance was a process gap related to RFC_URE1’s failure to realize that there was a storage limitation on the temporary file for data interchange between the badging system and the access management system. This major contributing factor involves the management practices of information management, in that RFC_URE1 failed to realize storage limitations with respect to this information, validation, in that RFC_URE1 failed to validate that the method by which this information was stored and transferred was sufficient to meet their needs, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliances was approximately five days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Of the four individuals involved, three were employees in good standing, who maintained a NERC CIP Personnel Risk Assessment and active NERC CIP training and had their access removed because they no longer needed it to complete their job duties. The fourth employee was terminated by RFC_URE1, but RFC_URE1 collected his badge and disabled his physical access profile. Thus, this user would not have been able to access the location to utilize the access rights retained beyond the removal deadline. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE1: 1) removed access from the users in question; 2) assessed file space and removed old files to allow the access management system activity to run properly; and 3) implemented a process that consists of an automated periodic cleanup task to delete unused temporary files. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017502 | CIP-004-6 | R5 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. Beginning with a routine internal review, and continued through an extent of condition analysis, RFC_URE2 identified a several instances where shared account passwords for NERC CIP shared accounts were not changed within 30 days of an individual’s termination. The length of time that these passwords remained unchanged ranged from 2 days to 53 days. Generally, RFC_URE2 uses their access management system to track the relationships between an individual user and the shared accounts known to the user. The access management system is configured with role based access control roles that form the relationship between an individual user and the shared accounts known to that user. When an individual is removed from a role based access control role, all related access is revoked and all shared accounts included with that role are disassociated from the removed user. In these cases, the access management system automatically generates notifications to inform the assigned performers that the password for each impacted shared account must be changed. The root cause of this noncompliance was a misconfiguration within the access management system where many of the shared accounts at issue did not have assigned performers. Consequently, performers did not receive notifications to change passwords after a termination. Another factor contributing to the cause of this noncompliance was the performers’ failure to act in a timely manner on notifications that were assigned by the access management system. These major contributing factors involve the management practices of verification, in that RFC_URE2 failed to verify that all shared accounts had assigned performers within the access management system, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately four months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, in each of the terminations, physical and logical access had been removed within 24 hours of the termination, removing the individual’s ability to access the shared accounts in question and utilize the known passwords. Second, RFC_URE2 adheres to a 90-day password change cycle for most shared account passwords, including those identified in this matter. This additional control helped limit the duration of the missed password changes and the amount of time that they could have been used. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE2: 1) changed all of the relevant passwords; 2) conducted individual briefing for one specific performer who missed multiple password changes; 3) documented and established a monitoring protocol for RFC_URE2 to track the status and age of Shared Account User manual fulfillment tasks in the access management system, including a periodicity of review and protocol for following up on the reported tasks to ensure timely closure in support of ongoing compliance to NERC Standard CIP-004-5 R5 Part 5.5; 4) designed and delivered an access management system report to support the monitoring protocol. The report will show the status and age of the Shared Account User manual fulfillment tasks; 5) enhanced the email generated by the access management system for the shared account password change task to include, or provide a link to, sufficient information for the tasks to be performed, the timeframe in which to complete the task as well as the affected shared account; 6) verified that all production shared accounts associated with High-Impact Bulk Electric System Cyber Systems and their associated Electronic Access Control or Monitoring System devices are uniquely represented in the access management system. RFC_URE2 also validated every shared account object in the access management system and updated to include correct performers where needed; 7) corrected each of the shared accounts with missing or empty performer groups by adding or updating the performer group where necessary; and 8) delivered reinforcement communications for shared account owners, performers and IT managers that addresses Shared Account password change responsibilities and associated access management system functionality. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017648 | CIP-004-6 | R5 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. RFC_URE2 discovered that users who had recently been provided access to Physical Security Perimeters (PSPs) were not able to physically enter the space using their credentials. Upon investigation, RFC_URE2 determined that there was a folder in the entities’ badging system, that had reached capacity with temporary files and was unable to store new information. This problem caused the connection between the badging system and the access management system tool to stop syncing information. As a result, not only were the grants of physical access not processed, but physical access revocation requests were also not processed for a period of 8 days. Specifically, physical access revocation request tickets were not processed within the required time frame. The delay in revocation for these individuals ranged from 3 days to 6 days. All revocation requests were processed upon discovery. The root cause of this noncompliance was a process gap related to RFC_URE2’s failure to realize that there was a storage limitation on the temporary file for data interchange between the badging system and the access management system. This major contributing factor involves the management practices of information management, in that RFC_URE2 failed to realize storage limitations with respect to this information, validation, in that RFC_URE2 failed to validate that the method by which this information was stored and transferred was sufficient to meet their needs, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliances was approximately five days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Of the four individuals involved, three were employees in good standing, who maintained a NERC CIP Personnel Risk Assessment and active NERC CIP training and had their access removed because they no longer needed it to complete their job duties. The fourth employee was terminated by RFC_URE2, but RFC_URE2 collected his badge and disabled his physical access profile. Thus, this user would not have been able to access the location to utilize the access rights retained beyond the removal deadline. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE2: 1) removed access from the users in question; 2) assessed file space and removed old files to allow the access management system activity to run properly; and 3) implemented a process that consists of an automated periodic cleanup task to delete unused temporary files. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017647 | CIP-004-6 | R5 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. RFC_URE3 timely removed a contractor’s cyber and physical access as required by the NERC CIP Revocation Procedure. The contractor had access to a certain user account that had a shared password and RFC_URE3 did not change the password within 30 days of employment separation as required. RFC_URE3 changed the password 16 days late. The shared password account is accessed by control room System Supervisors in RFC_URE3’s control center. The account allows System Supervisors access to the Windows Domain to log into the Energy Management System (EMS) workstation. This shared password to access the workstations does not provide direct access to the EMS. After logging into the shared account, the System Supervisors must log into the system using their individual password in order to have direct access to the EMS application. The cause was that responsibilities regarding changing the password were not clearly defined. The SCADA support staff expected the control center to change the shared password for the account as personnel changes occurred while the control center expected SCADA support staff to change shared password because SCADA support staff receives email notifications regarding access revocations. As a result, neither group changed the password. This noncompliance involves the management practice of verification, which includes having steps to ensure that changes, such as changes in employment status, are conducted according to the relevant process. The duration of the noncompliance was approximately sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is allowing the opportunity for a former contractor to access, and potentially compromise, Bulk Electric System Cyber Systems. The risk is minimized here because the former contractor would have needed additional access to utilize the unchanged password. Within 24 hours of the contractor’s separation, RFC_URE3 removed the contractor’s cyber and physical access. To access the EMS, the former contractor would have needed physical access to the workstation (which he did not have) and cyber access (which he did not have). Accordingly, it was very unlikely that the former contractor could have gained access to the shared account. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE3: 1) defined the responsibility for the account until such time that the account is no longer needed. When an access revocation request is sent to the support group (via a workflow), the support group owns the responsibility to initiate a password change on the account. This password change will be coordinated with the on-shift control center senior; 2) analyzed all shared password control center accounts and identified the owner for each account; 3) made a system hardware upgrade that resulted in no longer needing the shared password account, so RFC_URE3 eliminated the shared password account; 4) generated a report of the control center personnel and operations center personnel revocation requests associated with the access system's revocation requests. RFC_URE3 reviewed the data and validated that no other occurrences of possible noncompliance of the 30-day password change exists; and 5) held Compliance Cyber Security Stand Downs. These Stand Downs addressed the NERC requirements to manage shared password accounts. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017500 | CIP-004-6 | R5 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. Beginning with a routine internal review, and continued through an extent of condition analysis, RFC_URE4 identified a several instances where shared account passwords for NERC CIP shared accounts were not changed within 30 days of an individual’s termination. The length of time that these passwords remained unchanged ranged from 2 days to 53 days. Generally, RFC_URE4 uses their access management system to track the relationships between an individual user and the shared accounts known to the user. The access management system is configured with role based access control roles that form the relationship between an individual user and the shared accounts known to that user. When an individual is removed from a role based access control role, all related access is revoked and all shared accounts included with that role are disassociated from the removed user. In these cases, the access management system automatically generates notifications to inform the assigned performers that the password for each impacted shared account must be changed. The root cause of this noncompliance was a misconfiguration within the access management system where many of the shared accounts at issue did not have assigned performers. Consequently, performers did not receive notifications to change passwords after a termination. Another factor contributing to the cause of this noncompliance was the performers’ failure to act in a timely manner on notifications that were assigned by the access management system. These major contributing factors involve the management practices of verification, in that RFC_URE4 failed to verify that all shared accounts had assigned performers within the access management system, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately four months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, in each of the terminations, physical and logical access had been removed within 24 hours of the termination, removing the individual’s ability to access the shared accounts in question and utilize the known passwords. Second, RFC_URE4 adheres to a 90-day password change cycle for most shared account passwords, including those identified in this matter. This additional control helped limit the duration of the missed password changes and the amount of time that they could have been used. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE4: 1) changed all of the relevant passwords; 2) conducted individual briefing for one specific performer who missed multiple password changes; 3) documented and established a monitoring protocol for RFC_URE4 to track the status and age of Shared Account User manual fulfillment tasks in the access management system, including a periodicity of review and protocol for following up on the reported tasks to ensure timely closure in support of ongoing compliance to NERC Standard CIP-004-5 R5 Part 5.5; 4) designed and delivered an access management system report to support the monitoring protocol. The report will show the status and age of the Shared Account User manual fulfillment tasks; 5) enhanced the email generated by the access management system for the shared account password change task to include, or provide a link to, sufficient information for the tasks to be performed, the timeframe in which to complete the task as well as the affected shared account; 6) verified that all production shared accounts associated with High-Impact Bulk Electric System Cyber Systems and their associated Electronic Access Control or Monitoring System devices are uniquely represented in the access management system. RFC_URE4 also validated every shared account object in the access management system and updated to include correct performers where needed; 7) corrected each of the shared accounts with missing or empty performer groups by adding or updating the performer group where necessary; and 8) delivered reinforcement communications for shared account owners, performers and IT Managers that addresses Shared Account password change responsibilities and associated access management system functionality. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017501 | CIP-004-6 | R5 | RFC_URE5 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. Beginning with a routine internal review, and continued through an extent of condition analysis, RFC_URE5 identified a several instances where shared account passwords for NERC CIP shared accounts were not changed within 30 days of an individual’s termination. The length of time that these passwords remained unchanged ranged from 2 days to 53 days. Generally, RFC_URE5 uses their access management system to track the relationships between an individual user and the shared accounts known to the user. The access management system is configured with role based access control roles that form the relationship between an individual user and the shared accounts known to that user. When an individual is removed from a role based access control role, all related access is revoked and all shared accounts included with that role are disassociated from the removed user. In these cases, the access management system automatically generates notifications to inform the assigned performers that the password for each impacted shared account must be changed. The root cause of this noncompliance was a misconfiguration within the access management system where many of the shared accounts at issue did not have assigned performers. Consequently, performers did not receive notifications to change passwords after a termination. Another factor contributing to the cause of this noncompliance was the performers’ failure to act in a timely manner on notifications that were assigned by the access management system. These major contributing factors involve the management practices of verification, in that RFC_URE5 failed to verify that all shared accounts had assigned performers within the access management system, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately four months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, in each of the terminations, physical and logical access had been removed within 24 hours of the termination, removing the individual’s ability to access the shared accounts in question and utilize the known passwords. Second, RFC_URE5 adheres to a 90-day password change cycle for most shared account passwords, including those identified in this matter. This additional control helped limit the duration of the missed password changes and the amount of time that they could have been used. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE5: 1) changed all of the relevant passwords; 2) conducted individual briefing for one specific performer who missed multiple password changes; 3) documented and established a monitoring protocol for RFC_URE5 to track the status and age of Shared Account User manual fulfillment tasks in the access management system, including a periodicity of review and protocol for following up on the reported tasks to ensure timely closure in support of ongoing compliance to NERC Standard CIP-004-5 R5 Part 5.5; 4) designed and delivered an access management system report to support the monitoring protocol. The report will show the status and age of the Shared Account User manual fulfillment tasks; 5) enhanced the email generated by the access management system for the shared account password change task to include, or provide a link to, sufficient information for the tasks to be performed, the timeframe in which to complete the task as well as the affected shared account; 6) verified that all production shared accounts associated with High-Impact Bulk Electric System Cyber Systems and their associated Electronic Access Control or Monitoring System devices are uniquely represented in the access management system. RFC_URE5 also validated every shared account object in the access management system and updated to include correct performers where needed; 7) corrected each of the shared accounts with missing or empty performer groups by adding or updating the performer group where necessary; and 8) delivered reinforcement communications for shared account owners, performers and IT managers that addresses Shared Account password change responsibilities and associated access management system functionality. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017151 | CIP-007-6 | R5 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it was in noncompliance with CIP-007-6 R5. During an internal review, RFC_URE5 discovered that a numeric PIN pad code used only for local access to the front panel display of several identical relays were not changed from the manufacturer specific default value. (The relays also have an management port, which is used to control configuration baselines. This port requires passwords for access to the management port. These management port passwords were changed by RFC_URE5 from the manufacturer default passwords.) This PIN pad code is used to access the settings menu from the front panel display. However, the PIN pad code cannot be used to change relay logic, firmware, passwords, communications settings, or the device configuration baseline. The root cause of this noncompliance was the fact that the engineer, who created the device configuration guide for changing default passwords, incorrectly believed that the PIN pad code was not a password because he believed that the front panel provided read only local access. Therefore, this engineer did not include the PIN pad code on the list of passwords to be changed. This major contributing factor involves the management practice of asset and configuration management in that RFC_URE5 failed to properly configure the PIN pad code prior to putting the device into service. The duration of the noncompliance was approximately eight months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, physical access would have been required before someone could make changes at the device panel, and this device panel was secured within a Medium Impact substation facility. Second, the default baseline configuration, such as relay logic, firmware, access passwords, or alternative communication protocols, cannot be altered from the relay front panel. In addition, RFC_URE5 regularly checks relay settings, during which it would have identified any potential changes to the relays at issue. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE5: 1) changed the default Man-Machine interface (MMI) keypad PINs for the protection relays; 2) updated the relay configuration guide to include instructions to change the default MMI PIN code value; and 3) provided training to protection and control personnel and CIP Engineering. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017649 | CIP-007-6 | R5 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it was in noncompliance with CIP-007-6 R5. During its annual Cyber Vulnerability Assessment, RFC_URE5 discovered that the password used to initiate the “calibration” command for a specific relay type was not properly recorded in RFC_URE5’s inventory of default accounts. It should have been included in the inventory of default accounts because RFC_URE5 considers password protected commands in protection relays to be ‘accounts.” Although this password was not inventoried, it was, in fact, changed from its default value. The root cause of this noncompliance was the fact that, in developing its inventory of known default accounts, RFC_URE5 relied on the vendor manuals to identify these types of accounts. In this case, the vendor’s instruction manual indicated that the vendor did not publish a default password for the calibration command for this type of relay. Therefore, RFC_URE5 did not know to include it in its inventory. This major contributing factor involves the management practices of asset and configuration management, which includes identifying assets and configuration items inventory, and external interdependencies, which includes managing risks due to external interdependencies. The duration of the noncompliance was approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, considering the fact that the password at issue was changed, despite not being properly inventoried, this noncompliance is primarily a documentation issue. Second, RFC_URE5 regularly checks relay settings, during which it would have identified any potential changes to the relays at issue. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE5: 1) updated relevant documentation to include Calibration access level in the inventory of default accounts; 2) updated database password template to include Calibration access level; and 3) provided communication to RFC_URE5 CIP personnel regarding the unpublished default password in the relay instructions manual. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017619 | CIP-004-6 | R5 | RFC_URE6 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. An employee left RFC_URE6’s employment. Pursuant to CIP-004-6 R5, passwords for any shared accounts utilized by the employee were required to have been changed within thirty days. While the employee’s unescorted physical and cyber perimeter access was disabled within 24 hours of separation, the password for the shared account was not changed until thirty-three days later when RFC_URE6 discovered the noncompliance during a routine review of user access and immediately changed the password. The causes were a failure to follow the applicable procedure to create a ticket for the necessary password change, and lack of verification controls to ensure the procedure was followed. This noncompliance involves the management practice of workforce management as additional training could have helped prevent the noncompliance. Additionally, this noncompliance involves the management practice of verification, which includes having steps to ensure that changes, such as changes in employment status, are conducted according to the relevant process. The duration of the noncompliance was approximately three days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is allowing the opportunity for a former employee to access, and potentially compromise, Bulk Electric System Cyber Systems. The risk is minimized here because the former employee would have needed physical and cyber access to utilize the shared account. And, within 24 hours of the employee’s separation, RFC_URE6 removed the employee’s cyber and physical access and, in addition, two-factor authentication was required to remotely access CIP assets. Accordingly, it was very unlikely that the former employee could have gained access to the shared account. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE6: 1) enacted the process to change the password immediately; 2) updated its training program for department personnel to include a periodic review of department procedures and control activities related to CIP requirements. The training covered the procedure for shared account password changes summarizing the importance to always adhere to this procedure by always entering a ticket for tracking to closure all shared account password changes; and 3) implemented a peer review process for shared account password changes. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017018504 | CIP-004-3a | R4.1 | RFC_URE7 submitted a self-log stating that it was in noncompliance with CIP-004-3a R4.1. The Electronic Access Control or Monitoring Systems (EACMS) asset was placed into production. RFC_URE7 Information Technology (RFC_URE7 IT) identified an Active Directory (AD) group that was incorrectly applied to a NERC EACMS asset, inadvertently granting several people access to blade server infrastructure used in the NERC EACMS environment. The AD group that was incorrectly applied is used to administer similar infrastructure in the corporate environment, where access for the individuals is appropriate. Although there are no NERC authorization records for provisioned access, each individual’s access to the corporate AD group was approved by the data owner for the infrastructure devices, which is the same individual as the NERC CIP Access Authorizer. Each individual had completed NERC CIP cyber security training and had a successful personnel risk assessment during the period. This noncompliance involves the management practice of workforce management through ineffective training because RFC_URE7 IT inadvertently granted several people access to blade server infrastructure. Ineffective training is a root cause of this noncompliance. The duration of the noncompliance is approximately six months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors: 1) All individuals were properly NERC CIP Cleared; 2) All individuals who had access are familiar with NERC CIP process and recognize anomalies; 3) This specific access provided no ability to log onto a Bulk Electric System (BES) asset; and 4) This environment manages security controls but no impact to BES assets. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE7: 1) removed the incorrect AD group; and 2) created a new AD group with controls specific to the NERC environment (authorized approval, NERC clearance check) and applied to the infrastructure, and users have been authorized for access. Mitigation activities that fix the issue and also prevent recurrence: 1) A comprehensive review of AD groups and entitlements for all NERC access was performed to identify other latent issues associated with incorrect AD group. No additional instances were found; and 2) Formalized verification steps were added to existing pre-production process that requires technical Subject Matter Experts to provide evidentiary proof of AD groups applied.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017018505 | CIP-007-6 | R2 P2.3 | RFC_URE7 submitted a self-log stating that it was in noncompliance with CIP-007-6 R2 P2.3. The vendor released a security patch for an Electronic Access Control or Monitoring Systems (EACMS) Cyber Asset. RFC_URE7 Information Technology (RFC_URE7 IT) individual performed the patch assessment following the documented process and identified that the vendor released new code. The RFC_URE7 IT individual documented their assessment on the Patch Assessment Spreadsheet and indicated that there were no applicable security patches released by the vendor. During a patch assessment cycle, another RFC_URE7 IT individual identified the incorrect patch assessment. Due to the incorrect determination, RFC_URE7 IT did not apply the patch within the required 35 days. The patch was to address multiple vulnerabilities which are considered a Medium severity. The vulnerabilities covered by this patch were not exploited on the servers between the time that the patch was released and the time that the patch was installed. This noncompliance involves the management practices of workforce management through ineffective training and verification because RFC_URE7 IT did not apply the patch within 35 days. Ineffective training is involved because a RFC_URE7 employee incorrectly determined that there were no applicable security patches released by the vendor. Verification is involved, and is the root cause of the noncompliance, because RFC_URE7 did not have a process in place to verify that the correct patching determination was made. The duration of the noncompliance was approximately one month. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors: 1) This asset was protected by two firewalls and two factor authentication, leverages VPN remote access that disables internet access when connected, and administrator access is limited to a select group, therefore reducing the risk of this issue being exploited; 2) Internal processes and procedures in place for released patches require monthly review of patch and reporting back in a group setting; and 3) The late patch assessment was identified during the next patch cycle and implemented promptly. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE7 implemented the security patch. Mitigation activities that fix the issue and also prevent recurrence: 1) RFC_URE7 IT updated its procedure to incorporate a peer check of vendor release notes in its patching process; 2) A meeting was held with the patching team to reinforce the process; and 3) RFC_URE7 IT directors reinforced the need to ensure security patches are properly identified, documented and applied.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017018506 | CIP-010-2 | R1.2 | RFC_URE7 submitted a self-log stating that it was in noncompliance with CIP-010-2 R1.2. Microsoft released a security patch (Rev A) which RFC_URE7 Information Technology (RFC_URE7 IT) assessed per the RFC_URE7 IT patch assessment process. RFC_URE7 IT attempted to install the patch, but the patch was defective and could not be implemented. Microsoft released an update to the security patch (Rev B) and RFC_URE7 IT assessed per the RFC_URE7 IT patch assessment procedure. The security patch was applicable to RFC_URE7 assets and staged for deployment to Development and Production, however unbeknownst the patch was not installed. Microsoft released an update to the Rev B security patch (Rev C) under the same number with notes indicating that no action was needed if the Rev B patch was already installed. Based on guidance in the release notes, RFC_URE7 IT determined no further action was needed because RFC_URE7 IT believed the security patch was already deployed. A software deployment tool downloaded the updated security patch (Rev C) and automatically deployed the security patch (Rev C) update. The software deployment tool took this automated action because the configuration had an expiration parameter of 35 days. Since the security patch was issued under the original number, logic determined this patch to be 35 days old and took action to install. The automated installation of the update bypassed baseline authorization and Cyber Security Testing. This noncompliance involves the management practice of asset and configuration management because RFC_URE7 did not have an effective process in place to ensure that patches that were initially defective when released, were timely installed after an update to the security patch was released. This lack of an effective process to assess and implement updated/revised security patches is a root cause of this noncompliance. The duration of the noncompliance was approximately one day. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors: 1) The patch was intended to be installed on these devices; and 2) The patch had been installed in the corporate environment first. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE7 uninstalled the security patch from the devices. To mitigate this noncompliance and also prevent recurrence, RFC_URE7 reconfigured the configuration tool to no longer do the automatic installation upon expiration.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017018507 | CIP-004-3a | R4.1 | RFC_URE7 submitted a self-log stating that it was in noncompliance with CIP-004-3a R4.1. As part of the extent of condition, RFC_URE7 Information Technology (RFC_URE7 IT) identified the following conditions without an authorization record in the current RFC_URE7 security request system: A. 1 Individual with electronic access to Physical Access Control Systems Cyber Assets B. 2 Individuals with electronic access to Electronic Access Control or Monitoring Systems Cyber Assets C. 3 Individuals with electronic access to an electronic storage locations containing Critical Cyber Asset Information/Bulk Electric System Cyber System Information For each instance, access was provisioned via the NERC authorization process but did not receive appropriate approval by the authorizer. Although there are no NERC authorization records for provisioned access, each individual’s access was reviewed by the individual’s supervisor and the NERC CIP Access Authorizer during RFC_URE7’s Quarterly Validations. Each individual had completed NERC CIP cyber security training and had a successful personnel risk assessment at that time. This noncompliance involves the management practices of workforce management through ineffective training and verification because RFC_URE7 IT provisioned access to employees that did not have the proper authorization records. Ineffective training is involved because a RFC_URE7 employee incorrectly provisioned access to employees that did not have the proper authorization records. Verification is involved, and is the root cause of the noncompliance, because RFC_URE7 did not have a process in place to verify that access would only be given to employees with proper authorization records. The duration of the noncompliance was approximately six months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors: 1) This was more of a procedure noncompliance; and 2) Individuals were properly NERC CIP Cleared. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE7 submitted NERC authorization tickets in RFC_URE7’s security request system to authorize or revoke each access as appropriate. To mitigate this noncompliance and also prevent recurrence, RFC_URE7 corrected control mismatch script to include additional criteria.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2017017692 | CIP-007-6 | R5 | RFC_URE8 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R5. RFC_URE8 replaced a redundant pair of relays at its substation, which was identified as a medium impact substation. During the installation and commissioning of the new relays, RFC_URE8 failed to change the default passwords for the relays. RFC_URE8 identified the issue when the engineering team verified the settings of the relays when they were synced to the relay configuration database. The root cause of this noncompliance was the relay technician’s failure to properly follow the written process for commissioning the relays. Another contributing factor was a process flaw in that the engineering team did not verify the settings until after the relays were active. These major contributing factors involve the management practices of implementation, in that the field technician did not follow established protocols for implementing new equipment, and verification, in that the engineering team did not verify the settings until after the relays were active. The duration of the noncompliance was approximately ten days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, default passwords present a security threat if the asset can be accessed. In this case, the relays do not have external routable connectivity, which prevents a remote cyber attack from leveraging the default passwords. Second, the facility in question requires two factor authentication in the form of a proximity badge and a personal 5-digit PIN to obtain physical access. Third, activity in the control building and substation yard is monitored by motion sensors, which are monitored continuously by a centralized security operations center. Fourth, RFC_URE8 identified and corrected the issue quickly, which minimized the potential risk. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE8: 1) changed the default passwords on the relays that were commissioned; 2) ran a report from the Physical Access Control Systems solution used to secure the substation control building to verify there were no unauthorized access events recorded during the timeframe where the passwords had not been reset; 3) detailed steps to be taken prior to the commissioning of a substation Bulk Electric System (BES) Cyber Asset. Included in these steps is verification that the password was changed from the vendor default. There is also a detailed step for verification of the settings, including the password change, from a supervisor or manager. This step occurs earlier in the commissioning process, before the device is activated; 4) created a manual checklist that contains all of the requirements for commissioning a new BES Cyber Asset for a substation and includes verification by a manager or supervisor as part of the process; and 5) provided face to face training to review the checklist process with test department and utilized an attendance sheet to ensure all testers attended training. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2017017667 | CIP-002-5.1 | R2 | SERC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. SERC_URE1 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months. SERC_URE1 implemented a process to consider and identify required assets and/or Bulk Electric System (BES) Cyber Systems. SERC_URE1 documented this identification in the “Applicable Facilities” list of its CIP-002-5.1 BES Cyber Systems identification and categorization methodology document. SERC_URE1’s Methodology identified one asset that contains a low impact BES Cyber System. SERC_URE1’s president approved and signed the methodology documentation, but the SERC_URE1 president was not the CIP Senior Manager or an approved delegate. Ten days later, SERC_URE1’s CIP Senior Manager arrived onsite and approved the “Applicable Facilities” list generated by SERC_URE1’s methodology document, as required by CIP-002-5.1 R2.2. Approximately ten months later, SERC_URE1 discovered this error while preparing the response to SERC’s CIP-002 Guided Self-Certification. The root cause of this noncompliance was a lack of training for SERC_URE1’s CIP Senior Manager. This noncompliance lasted for approximately ten days, starting when the Standard became mandatory and enforceable on SERC_URE1, and ending when SERC_URE1’s CIP Senior Manager approved the BES Cyber System identifications. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to have its CIP Senior Manager or delegate approve its BES Cyber Asset list could lead to inadequate or non-existent cyber security controls for those BES Cyber Assets, which could result in the compromise or misuse of those Cyber Assets and affect the real-time operation of the BPS. However, this noncompliance was an administrative failure in which the SERC_URE1 president approved the BES Cyber System identifications instead of the CIP Senior Manager or delegate. SERC_URE1’s CIP Senior Manager approved the ‘Applicable Facilities’ list ten days after the Standard became mandatory and enforceable on SERC_URE1 and there were no changes to the BES Cyber System list required. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE1: 1) had its CIP Senior Manager sign the Applicable Facilities list; 2) added a work order to execute the CIP-002 methodology on an annual basis. This will ensure that SERC_URE1 addresses CIP-002-5.1 R2.2 at least once every 15 calendar months; and 3) ensured that the CIP Senior Manager understands that a signature is not required but approval of the CIP methodology is. Going forward, SERC_URE1 will create a meeting request and have senior managers reply that CIP-002 methodology was completed and approved. SERC_URE1 documented an annual work order to address this milestone.
2017-12-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2017017242 | CIP-004-6 | R4; P4.1 | SERC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R4.1. SERC_URE2 did not implement a process to authorize or approve an individual who it gave authorized unescorted physical access to a PSP. SERC_URE2 processed a bulk access request for several SERC_URE2 security guards to have access to SERC_URE2’s Data Center PSP. SERC_URE2’s normal process is to grant the same access rights to all its security guards. During the request for access, SERC_URE2 management approved all security guards to have access to the primary access door to the PSP. However, SERC_URE2 management made a clerical error and failed to document its approval for one of the security guards to have access to a secondary access door into the same PSP. The clerical error went unnoticed and SERC_URE2’s Physical Access Control System (PACS) administrator granted access to the primary and secondary access doors for all of the security guards, despite the lack of documentation of approval for the one security guard to the secondary access door. Approximately two and a half months later, SERC_URE2 discovered the clerical error during its periodic access review, as required under CIP-004-6 R4.3. SERC_URE2 conducted an extent-of-condition during its periodic access review, and concluded that this was the only discrepancy found. Approximately two weeks later, SERC_URE2 management corrected the clerical error and processed the security guard for approved authorization into the secondary access door into the PSP. SERC_URE2 determined the root cause to be SERC_URE2’s inadequate process for granting bulk authorization. For bulk processing of similar authorizations, SERC_URE2’s process has the potential to miss distinct alternate authorization requests. This noncompliance lasted for approximately three months, starting when SERC_URE2 granted a security guard access to a PSP’s secondary access door without following its documented process, and ending when SERC_URE2 management corrected the clerical error and processed the security guard for approved authorization into the secondary access door into the PSP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure to implement its process for authorization into a PSP, could result in unauthorized personnel accessing the PSP and allow them to take action that would negatively impact the reliability of the BPS. However, the SERC_URE2 guard already had authorized access into the PSP through the primary access door and SERC_URE2 intended to grant access to the secondary access door but failed to adequately document that access for a single security guard. In addition, the security guard only had physical access into the data center PSP and could not access SERC_URE2 Cyber Assets that were inside locked server cabinets inside the PSP. In addition, all required network ports on the switches are protected using port-security technology. This allows SERC_URE2 to define which media access control (MAC) address can function on each port. In addition, SERC_URE2 has turned off all non-required network ports on the switches using the interface shutdown command, which prevents rogue devices from establishing unauthorized connections. Lastly, SERC_URE2 has configured software which monitors for any changes to the baseline. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-004 compliance history in determining the disposition track. SERC determined that SERC_URE2’s CIP-004-6 R2 compliance history should not serve as a basis for applying a penalty. The mitigating activities for the prior noncompliance would not have prevented the instant noncompliance. | To mitigate this noncompliance, SERC_URE2: 1) commissioned a new access management solution integrated with its PACS so that there is no human interaction in the process that could misinterpret the specific granted authorizations; and 2) designed the automated system so that the PACS can only execute management approved specific accesses, so PACS cannot have an opportunity to grant unauthorized physical access.
2017-12-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2017017362 | CIP-004-6 | R5; P5.2 | SERC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5.2. SERC_URE2 did not revoke an individual’s unescorted physical access that it determined was not necessary by the end of the next calendar day following the date that SERC_URE2 determined access was not necessary. A SERC_URE2 employee was transferred to a position that did not require unescorted physical access to any Physical Security Perimeters (PSPs), but the supervisor forgot to initiate a revocation action on SERC_URE2’s access processing system and the access was not terminated by the end of the next calendar day. The transferred employee had physical access permissions to SERC_URE2’s supervisory control and data acquisition (SCADA) control room PSP and backup SCADA control room PSP. Approximately one and a half months later, SERC_URE2 captured the transferred employee’s unauthorized unescorted physical access rights through a training control process, which reminds managers of their employees’ upcoming NERC CIP training requirements. This alerted the transferred employee’s new manager to the mistake. During this NERC CIP training requirement notification, SERC_URE2 discovered no other instances of transferred employees maintaining access rights unnecessarily. SERC_URE2 determined that the root cause of this noncompliance was lack of training. The transferred employee’s direct supervisor thought that he initiated a future revocation on the access processing system, but the direct supervisor did not. This noncompliance lasted approximately a month and a half, starting the day after the transferred employee’s physical access rights should have been removed, and ending when SERC_URE2 revoked the transferred employee’s physical access rights. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure to revoke authorized unescorted physical access when no longer required could permit an individual who no longer required access to use that access to negatively impact the reliability of the BPS. However, SERC_URE2 confirmed that the transferred employee did not access the PSPs after his transfer. In addition, the transferred employee did not have electronic access to Bulk Electric System (BES) Cyber Systems and only had physical access to two PSPs, lessoning the chance of an undetected attack on BES Cyber Systems. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-004 compliance history in determining the disposition track. SERC determined that SERC_URE2’s CIP-004-6 R2 compliance history should not serve as a basis for applying a penalty. The mitigating activities for the prior noncompliance would not have prevented the instant noncompliance. | To mitigate this noncompliance, SERC_URE2: 1) issued training for all management, supervisor and above, as well as their clerical staff and those in the HR Employment Services area, on the proper procedures to follow when staff is transferred or terminated. It clearly reminds management of their responsibility to initiate appropriate action when informed by Employee Services that the individual had access to PSPs or BES Cyber Systems; and 2) trained Employment Services CIP-004 SMEs to confirm the completed revocation by the date due.
2017-12-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2017018105 | CIP-004-6 | R5; P5.1 | SERC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5.1. SERC_URE2 did not revoke a vendor’s authorized Interactive Remote Access within 24 hours of a termination. On a Friday, at 2:00 p.m., a SERC_URE2 vendor terminated an employee that had authorized access to one of SERC_URE2’s Bulk Electric System (BES) Cyber Systems. The vendor had authorized Interactive Remove Access to multiple Medium Impact Bulk Electric System (BES) Cyber Assets and Protective Cyber Assets. At approximately 5:30 p.m., the SERC_URE2 vendor sent an e-mail to notify SERC_URE2 that one of its employees no longer worked at the firm. The vendor sent the notification to SERC_URE2’s software implementation team instead of SERC_URE2’s manager who is responsible administering the vendor’s contract. At approximately 7:20 p.m., the implementation team read the message and forwarded it to that manager’s designee to initiate the access revocation. On the following Monday, SERC_URE2’s system administrator, who received the original access revocation email from the vendor, noticed that the SERC_URE2 manager had not submitted an access revocation request over the weekend and immediately used SERC_URE2’s access management system’s "urgent termination process" that bypasses the department’s management to revoke access. After SERC_URE2’s system administrator initiated the revocation process, the system administrator contacted the department management responsible for the revocation to ensure proper documentation of the effort. At approximately 5:00 p.m., SERC_URE2 completed the last system revocation from the vendor’s access revocation request. SERC_URE2 conducted an extent-of-condition using its contractor contact list, which lists all contractors, past and present, who have required access. SERC_URE2 concluded that SERC_URE2 handled all other terminations from its vendors within the required 24-hour time-period. SERC_URE2 determined the root cause to be that SERC_URE2 has not established a process for regular communication with its vendors and contractors with access to SERC_URE2's BES Cyber Systems and BES Cyber System Information instructing them how and to whom to communicate regarding terminations. SERC_URE2 had informed its vendor and contractors of the need for timely notifications of vendor or contractor employee terminations. In addition, SERC_URE2’s work practices of these key SERC_URE2 personnel do not universally include routine checking for communications outside normal working hours. The noncompliance lasted for two days, starting 24 hours after SERC_URE2’s vendor terminated the employee, and ending when SERC_URE2 removed the terminated vendor employee’s access. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure to revoke access for a terminated vendor employee within 24 hours of the termination could allow that individual to use the retained access to negatively impact the reliability of the BPS. However, the individual could not remotely access any of SERC_URE2's BES Cyber Systems, including the access management software that would have allowed the revocation or granting of physical access to the Physical Security Perimeters (PSPs). SERC_URE2 controls the physical fob for virtual private network access to this system. Whenever this vendor needs access to the system, the vendor must call SERC_URE2 to receive the number displayed on the fob. In addition, the individual did not have physical access to SERC_URE2's PSPs. The individual was authorized for access to SERC_URE2's "jump server," the access management system application, and the Physical Access Control Systems (PACS) devices. SERC_URE2 removed the unauthorized access permissions the next business day after the employee no longer needed access to the BES Cyber Systems. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-004 compliance history in determining the disposition track. SERC determined that SERC_URE2’s CIP-004-6 R2 compliance history should not serve as a basis for applying a penalty. The mitigating activities for the prior noncompliance would not have prevented the instant noncompliance. | To mitigate this noncompliance, SERC_URE2: 1) revoked the vendor employee’s Interactive Remote Access once SERC_URE2 personnel were informed of the end of the individual’s employment; 2) reminded SERC_URE2 personnel of the importance of receiving and acting upon communication about vendor personnel changes in a timely manner; and 3) communicated with vendors regarding the revocation process and 24 hour requirement for revocation.
2017-12-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2016016336 | CIP-006-6 | R1; P1.3 | SERC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R1.3. SERC_URE3 did not utilize two or more different physical access controls to restrict physical access into Physical Security Perimeters (PSPs) to only those individuals who have authorized unescorted physical access. At approximately 10:45 a.m., a SERC_URE3 employee unlatched the double doors at the system operation center computer room while taking delivery of a rack. The employee brought the rack just within the double door, the doors closed, and a few minutes later, the employee left the room without securing the double doors. Approximately one week later, a contractor exiting the system operations center (SOC) computer room, which contained High Impact Bulk Electric System (BES) Cyber Systems, discovered one side of the double doors unlatched. The top and bottom pins of the stationary double doors, secured from within the PSP, were in a non-secure state. The contractor immediately secured the latches and notified SERC_URE3 personnel. The next day, SERC_URE3 discovered that with the one side of the double doors unsecured, the primary door would latch and secure, requiring an authorized security badge and finger print to open. However, if an individual pushed both doors inward, the doors would separate and open without requiring the badge and fingerprint presentation. This action would also trigger a forced entry alarm that would go to the SERC_URE3 security console. SERC_URE3 conducted an extent-of-condition assessment by reviewing all doors for any similar locking configurations. SERC_URE3 found no additional instances of two door intermeshed configurations, where the second door required mechanical physical latches be engaged in order to assure the primary security mechanism (the mag-lock) could be successfully engaged. SERC_URE3 determined that the root cause of this noncompliance was a lack of training, resulting in the SERC_URE3 employee not following SERC_URE3 security policies. This noncompliance lasted one week, starting when the SERC_URE3 employee unlatched the double door, and ending when the contractor secured the double door upon exit. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE3’s failure to secure the double door could have permitted unauthorized individuals to gain access to the data center and High Impact BES Cyber Systems by pushing both doors simultaneously. However, if an individual opened the double doors without an authorized badge presentation, SERC_URE3 security would have received a forced entry alarm and immediately investigated. SERC_URE3 monitors the SOC computer room 24 hours per day, seven days per week through a closed-circuit television feed to on-site armed corporate security staff. The SOC is within a physically secured building, patrolled by on-site armed security, reducing the risk of unauthorized individuals gaining access to the PSP. SERC_URE3 received no forced entry alarms during the noncompliance. No harm is known to have occurred. SERC considered SERC_URE3's compliance history in determining the disposition track. SERC determined that SERC_URE3's compliance history should not serve as a basis for applying a penalty. The prior mitigating activities would not have prevented the instant noncompliance. | To mitigate this noncompliance, SERC_URE3: 1) re-secured the top and bottom latch on the SOC computer room double door that does not have an electric strike installed to secure the door; 2) sent an email communication to all employees and contractors with unescorted physical access to PSPs to reinforce security policies and procedures; 3) ensured that no other PSPs had similar double door configurations; and 4) sent an email communication to all relevant employees and contractors to reinforce security policies and procedures.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016107 | CIP-005-5 | R1; R1.3, R1.5 | During a Compliance Spot Check, SPP RE determined that SPPRE_URE1 was not compliant with CIP-005-5 R1.3, R1.5. CIP-005-5 R1.3 requires SPPRE_URE1 to implement a process that requires inbound and outbound access permissions of Electronic Security Perimeter (ESP) traffic and denies all other access by default. SPPRE_URE1’s Access Control Process provides that “[a]ccess control devices such as firewalls, and/or similar appliances, shall be configured to deny access by default, such that explicit access permissions must be specified.” SPPRE_URE1’s high speed encryptors, are Electronic Access Points to SPPRE_URE1’s primary and backup control center ESPs, and established a point-to-point encrypted tunnel between the two control center ESPs. These encryptors were not performing access control of traffic between the two control center ESPs per CIP-005-5 R1.3 and SPPRE_URE1’s Access Control Process. CIP-005-5 R1.5 requires SPPRE_URE1 to implement a method for detecting known or suspected malicious communications for both inbound and outbound ESP communications. SPPRE_URE1’s Network Intrusion Detection System (NIDS) sensors were not configured to monitor traffic between the two high speed encryptors, which were Electronic Access Points to SPPRE_URE1’s primary and backup control center ESPs. The root cause of both instances of noncompliance was a misinterpretation of the standard. Regarding CIP-005-5 R1.3, SPPRE_URE1 believed that the high speed encryptors met the standard and performed access control of traffic flowing between the primary and secondary control center ESPs because the traffic was encrypted. Regarding CIP-005-5 R1.5, because SPPRE_URE1 believed that the encryptors met CIP-005-5 R1.3, and SPPRE_URE1’s NIDS is incapable of monitoring encrypted traffic, SPPRE_URE1 believed it met the standard by configuring the NIDS sensors to monitor traffic within the boundaries of each separate ESP. The duration of this instance of noncompliance was 13.5 months, from the effective date of the standard through the date SPPRE_URE1 completed its mitigation of the noncompliance. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform access control and monitoring of traffic between the primary and backup control center ESPs has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of BES Cyber Systems to occur, which could lead to misoperation or instability of the BES. Notwithstanding, SPPRE_URE1 utilized a firewall at each separate ESP (primary and backup control centers). All traffic between the two high speed encryptors at each ESP was encrypted and forced into a sub-interface on the firewalls for rules processing. The firewalls contained restrictive controls for each interface, thus ensuring only specific access was allowed based upon Internet Protocol (IP) addresses and specific ports and services. Additionally, both ESPs were continuously monitored and protected by an intrusion preventative/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on BES Cyber Systems within the ESP. SPPRE_URE1 implemented additional protective measures to protect BES Cyber Systems inside the ESPs, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions; network and host based anti-malware systems; password and lockout policies; and personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this noncompliance, SPPRE_URE1: 1) upgraded the software on its SCADA/EMS network (CIP-005-5 R1.3 and R1.5); and 2) installed new network hardware and firewalls (CIP-005-5 R1.3 and R1.5); a. declassified the two high speed encryptors as Electronic Access Points to the primary and backup control center ESPs (CIP-005-5 R1.3); b. classified the new firewalls as Electronic Access Points to the primary and backup control center ESPs (CIP-005-5 R1.3); c. configured the new firewalls to perform the Intrusion Detection System function for all traffic entering and leaving the primary and backup control center ESPs (CIP-005-5 R1.5). SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016109 | CIP-005-3a | R2; R2.4 | During a Compliance Spot Check, SPP RE determined that SPPRE_URE1 was not compliant with CIP-005-3a R2.4 because it did not implement strong technical controls for external interactive access into the Electronic Security Perimeter (ESP) to ensure authenticity of the accessing party. Specifically, 41 individuals with authorized interactive access to SPPRE_URE1’s ESP were able to gain access to the ESP by remotely logging onto SPPRE_URE1’s jump host, i.e., virtual server, by utilizing their individual domain usernames and passwords. Although access to a target host, i.e., another device within the ESP, required an additional login with the user’s same individual domain username and password, the SPP RE audit team determined that the use of this single-factor authentication process to access the ESP via the jump host did not constitute strong technical controls to ensure authenticity of the accessing party. This noncompliance was initially identified during a prior Compliance Audit. To mitigate the noncompliance, SPPRE_URE1 implemented an additional layer of technical controls, which it believed to be multi-factor authentication for external interactive access into its ESP. More specifically, the last step to gain access to the ESP required individuals to retrieve a software security token via their individual email account, and enter the token code or password prior to gaining interactive access to the ESP. SPPRE_URE1’s mitigation plan for this prior issue was verified as complete. Nevertheless, during the most recent Spot Check, the SPP RE audit team determined that the use of the security tokens described in SPPRE_URE1’s mitigation plan did not constitute multi-factor authentication to ensure the authenticity of the accessing user. Although software security tokens were required, the security tokens were sent to the user’s email, something the user knows, instead of something the user has, e.g. a SMS text message to the user’s cell phone. As a result, SPPRE_URE1’s multi-point authentication sequence equated to two consecutive single-factor authentications, something the user knows, and there was no way to ensure that the person receiving the token was the authorized user. But for SPP RE erroneously approving and verifying completion of SPPRE_URE1’s mitigation plan for the prior issue, the noncompliance would not have been identified during the subsequent Spot Check. The duration of this instance of noncompliance was 59.9 months, starting the date after the conclusion of the prior Compliance Audit, and ending the date SPPRE_URE1 completed its Mitigation Plan. The root cause of this noncompliance was SPPRE_URE1’s reliance on SPP RE’s erroneous acceptance and verification of SPPRE_URE1’s mitigation plan for the prior issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R2.4 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized access to Cyber Assets inside the PSP. The risk was mitigated by SPPRE_URE1’s use of the jump host. Additionally, although two single-factor authentications (login credentials, and four-digit PIN) were required to access the ESP, these two factors are both something the user knew. The risk that a user’s login credentials would be compromised was mitigated by the second authentication factor requiring the user’s unique four-digit PIN in order to request a token be emailed. Moreover, all Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this noncompliance, SPPRE_URE1: 1) implemented hardware and software upgrades to the SCADA system, which includes new: a. internal ESP network switches; b. ESP firewalls; c. SCADA domain controllers; d. intermediate system to control Interactive Remote Access to devices inside the ESP; 2) installed a new jump host outside the ESP firewalls; and 3) implemented multi-factor authentication for all Interactive Remote Access into its ESP by utilizing hard tokens, which is something only authorized users have. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2017016807 | CIP-010-2 | R1; R1.4.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 was not compliant with CIP-010-2 R1.4.2 following changes that deviated from SPPRE_URE2’s baseline configuration. Specifically, when the same change was made to multiple Cyber Assets with similar functions and running the same applications, SPPRE_URE2 conducted a verification test of only one Cyber Asset, which served as a representative for all the Cyber Assets. However, in most cases, the grouped Cyber Assets were not identically configured. As a result, SPPRE_URE2 was unable to verify that cyber security controls for the individual Cyber Asset had not been adversely affected following a change that deviated from SPPRE_URE2’s baseline configuration. The duration of this instance of noncompliance was 7.4 months, from the effective date of the standard through the date SPPRE_URE2 verified the cyber security controls for each Cyber Asset following a change that deviated from SPPRE_URE2’s baseline configuration. The root cause of this noncompliance was a misinterpretation of the standard. According to SPPRE_URE2, its misinterpretation of the standard was due to the following language from the Guidelines and Technical Basis section of the standard: “[T]he Responsible Entity should note that wherever a test environment (or production environment where the test is performed in a manner that minimizes adverse effects) is mentioned, the requirement is to “model” the baseline configuration and not duplicate it exactly.” SPPRE_URE2 interpreted this language to mean that verification testing of cyber security controls could be performed on a representative group of “like” Cyber Assets, i.e., two separate Cyber Assets with similar functions and running the same types of applications. Therefore, SPPRE_URE2 believed that for a group of “like” Cyber Assets with similar baselines, the verification of cyber security controls for one Cyber Asset in a group could be used to represent all Cyber Assets in the group. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to maintain accurate configuration baselines has the potential to affect the reliability of the BPS by providing an opportunity for unauthorized and undetected modifications to be made to applicable Cyber Assets, which could introduce system instability or affect the functionality of such assets. All “like” Cyber Assets had similar functions and were running the same types of applications as the Cyber Asset that was tested. Therefore, the baselines of the “like” Cyber Assets and the tested Cyber Asset were reasonably similar, and all such assets required the change, which significantly reduced the risk that an adverse impact would occur on a “like” Cyber Asset. Additionally, the installed security patches on all Cyber Assets were being tracked, evaluated, and up-to-date. Moreover, SPPRE_URE2’s High and Medium Impact BES Cyber Systems and their associated Cyber Assets were continuously monitored and protected by an intrusion prevention/detection system, which provides real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the Electronic Security Perimeter. No harm is known to have occurred. SPP RE considered SPPRE_URE2’s compliance history and determined that the instant nponcompliance was appropriate for Compliance Exception treatment. | To mitigate this noncompliance, SPPRE_URE2: 1) following a change, for each individual device, verified that required cyber security controls determined in R1.4.1 were not adversely affected; and 2) trained all affected personnel on the new requirement to conduct verification of cyber security controls for each individual device. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016387 | CIP-005-3a | R3; R3.2 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-005-3a R3. In particular, TRE_URE1 failed to implement its documented process for monitoring and logging access at access points to its Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. TRE_URE1 transferred its centralized logging and alerting system from its existing facility to a new data center. During the six-hour transfer process, however, TRE_URE1 lost the ability to automatically log system events, as well as issue alerts for unauthorized access attempts. The issue ended when TRE_URE1 personnel completed the planned transfer of the centralized logging and alerting system to the new data center and restored all logging and alerting functionality. The root cause of this noncompliance was an insufficient process to ensure compliance during the transfer of TRE_URE1’s centralized logging and alerting system. In particular, TRE_URE1 lacked a clear process to identify localized logging sources, as well as request that the individual business units responsible for affected Cyber Assets manually review logs and issue any alerts as appropriate during the planned system outage. The duration of the noncompliance was approximately six hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue, TRE_URE1 operations personnel continuously monitored all applicable cyber security systems for possible abnormal activity. Second, throughout the duration of the noncompliance, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unidentified security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) completed its scheduled move of its centralized logging and alerting tool, which made logging and alerting functional again; 2) completed the relocation to the newly constructed data center to improve reliability of the equipment; 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system; 4) clarified that other intrusion detection products located outside of designated Electronic Security Perimeters could be used for the detection and logging of malicious code to satisfy the requirements of the current NERC Reliability Standards during future outages; and 5) established a new process to send email notifications to all affected business units informing them of the need to manually review Cyber Asset logs during outages of the centralized logging and alerting system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016388 | CIP-007-3a | R5; R5.3.3 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a R5.3.3. In particular, TRE_URE1 identified a number of accounts with passwords that were not changed within the preceding 15 months. Texas RE subsequently determined the duration of this noncompliance was approximately two years. Accordingly, Texas RE determined that TRE_URE1 was in noncompliance with CIP-007-3a R5.3.3, and subsequently was in noncompliance with CIP-007-6 R5, P5.6. Texas RE further determined that, for purposes of this issue, there was no substantive change in TRE_URE1's compliance obligations under the applicable CIP-007 versions at issue. TRE_URE1 performed a periodic check of password aging and discovered that multiple account passwords were not changed as required. The accounts at issue consisted of default account, generic accounts, and interactive accounts. Following this discovery, TRE_URE1 required individuals to change their passwords upon their next login to the accounts at issue. Because certain accounts were seldom utilized, TRE_URE1 did not update all the affected passwords in a timely manner. The root cause of this noncompliance was that TRE_URE1 did not have an adequate control to ensure that passwords were changed as required. Specifically, TRE_URE1 relied on a manual password review to ensure that passwords were changed as required. The duration of the noncompliance was approximately two years and two months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the passwords met the complexity requirements, reducing the likelihood of compromise. Second, the individuals had authorized access to the domain or network at issue. Third, the majority of accounts at issue did not have domain administration group access. Lastly, throughout the noncompliance duration, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) changed the expired passwords; and 2) implemented a daily script for interactive accounts that automatically notifies users that their password is close to expiring at 90 days and automatically disables any account user IDs with passwords older than 180 days. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016389 | CIP-007-3a | R6 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a R6. In particular, TRE_URE1 failed to monitor and manage security events affecting Cyber Assets within an Electronic Security Perimeter (ESP) because event logs were neither processed nor retained during a 90-minute service disruption. Network support personnel discovered that a secondary firewall deployed between its centralized logging and alerting tool and ESPs containing CIP Cyber Assets was out of sync with its primary firewall. The following day, TRE_URE1 network support personnel attempted to address the firewall synchronization issue by rebooting the secondary firewall. However, when TRE_URE1 personnel rebooted the secondary firewall, the two firewalls began to compete to replicate their configurations. This conflict in turn disrupted traffic to the centralized logging and alerting system. TRE_URE1 personnel resolved the issue by erasing the secondary firewall’s configuration, restoring data traffic to the centralized security event logging and alerting system 90 minutes after the initial disruption. The root cause of this noncompliance was a software issue with the secondary firewall. In particular, when TRE_URE1 personnel rebooted the secondary firewall to address the synchronization issue, TRE_URE1 believes that software issues caused the firewalls to behave differently than anticipated. The duration of the noncompliance was approximately 90 minutes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Throughout the noncompliance duration, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unintended security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) erased the configuration on the secondary firewall, synchronizing with the primary firewall and restoring data traffic to its centralized security event logging and alerting system; 2) replaced the firewalls at issue; and 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017018759 | CIP-007-3a | R6 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-005-3a R3. In particular, TRE_URE1 failed to implement its documented process for monitoring and logging access at access points to the Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. Subsequently, Texas RE determined that the issue described in TRE_URE1's CIP-005-3a R3 Self-Report was also a noncompliance pertaining to CIP-007-3a R6 for TRE_URE1. In particular, TRE_URE1 failed to implement automated tools to monitor system events related to Cyber Assets within an ESP. For approximately six hours, the automated tool to monitor system events was not available. Therefore, TRE_URE1 could not monitor system events. TRE_URE1 transferred its centralized logging and alerting system from its existing facility to a new data center. During the six hour transfer process, however, TRE_URE1 lost the ability to automatically log system events, as well as issue alerts for unauthorized access attempts. The issue ended when TRE_URE1 personnel completed the planned transfer of the centralized logging and alerting system to the new data center and restored all logging and alerting functionality. The root cause of this noncompliance was an insufficient process to ensure compliance during the transfer of TRE_URE1’s centralized logging and alerting system. In particular, TRE_URE1 lacked a clear process to identify localized logging sources, as well as request that the individual business units responsible for affected Cyber Assets manually review logs and issue any alerts as appropriate during the planned system outage. The duration of the noncompliance was approximately six hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue, TRE_URE1 operations personnel continuously monitored all applicable cyber security systems for possible abnormal activity. Second, throughout the duration of the noncompliance, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unidentified security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) completed its scheduled move of its centralized logging and alerting tool, which made it possible to monitor system events again; 2) completed the relocation to the newly constructed data center to improve reliability of the equipment; 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system; 4) clarified that other intrusion detection products located outside of designated Electronic Security Perimeters could be used for the detection and logging of malicious code to satisfy the requirements of the current NERC Reliability Standards during future outages; and 5) established a new process to send email notifications to all affected business units informing them of the need to manually review Cyber Asset logs during outages of the centralized logging and alerting system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017018758 | CIP-005-3a | R3 | TRE_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a R6. In particular, TRE_URE1 failed to monitor and manage security events affecting Cyber Assets within an Electronic Security Perimeter (ESP) because event logs were neither processed nor retained during a 90-minute service disruption. Subsequently, Texas RE determined that the issue described in TRE_URE1's CIP-007-3a R6 Self-Report was also a noncompliance pertaining to CIP-005-3a R3 for TRE_URE1. In particular, TRE_URE1 failed to implement its documented process for monitoring and logging access at access points to its ESPs twenty-four hours a day, seven days a week. Network support personnel discovered that a secondary firewall deployed between its centralized logging and alerting tool and ESPs containing CIP Cyber Assets was out of sync with its primary firewall. The following day, TRE_URE1 network support personnel attempted to address the firewall synchronization issue by rebooting the secondary firewall. However, when TRE_URE1 personnel rebooted the secondary firewall, the two firewalls began to compete to replicate their configurations. This conflict in turn disrupted traffic to the centralized logging and alerting system. TRE_URE1 personnel resolved the issue by erasing the secondary firewall’s configuration, restoring data traffic to the centralized security event logging and alerting system 90 minutes after the initial disruption. The root cause of this noncompliance was a software issue with the secondary firewall. In particular, when TRE_URE1 personnel rebooted the secondary firewall to address the synchronization issue, TRE_URE1 believes that software issues caused the firewalls to behave differently than anticipated. The duration of this noncompliance was approximately 90 minutes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Throughout the noncompliance duration, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unintended security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE1: 1) erased the configuration on the secondary firewall, synchronizing with the primary firewall and restoring data traffic to its centralized security event logging and alerting system; 2) replaced the firewalls at issue; and 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017017473 | CIP-004-6 | R2; P2.2 | TRE_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE2 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE2’s assets included a Control Center containing a Medium Impact Bulk Electric System (BES) Cyber System (MIBSC). On TRE_URE2’s registration date, two TRE_URE2 employees had electronic and/or unescorted physical access rights without prior cyber security training as required. Both individuals worked non-traditional schedules such that TRE_URE2 had issues scheduling the requisite training. TRE_URE2 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the newly applicable CIP version 5 Standards. In particular, TRE_URE2’s training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE2 did not ensure all employees with electronic or physical access rights had the requisite training. The duration of the noncompliance was approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE2’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE2: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017017918 | CIP-004-6 | R3; P3.2 | TRE_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE2 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE2’s assets included a Control Center containing a Medium Impact Bulk Electric System (BES) Cyber System (MIBSC). On TRE_URE2’s registration date, one individual had authorized unescorted physical access to the TRE_URE2 Control Center without possessing a valid PRA. TRE_URE2 subsequently completed the missing PRA for the single employee, ending the issue. The root cause of the issue was that TRE_URE2 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE2’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the NERC CIP Senior Manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE2 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE2 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE2’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE2: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the CIP Senior Manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2016016390 | CIP-005-3a | R3; R3.2 | TRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-005-3a R3. In particular, TRE_URE3 failed to implement its documented process for monitoring and logging access at access points to its Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. TRE_URE3 transferred its centralized logging and alerting system from its existing facility to a new data center. During the six-hour transfer process, however, TRE_URE3 lost the ability to automatically log system events, as well as issue alerts for unauthorized access attempts. The issue ended when TRE_URE3 personnel completed the planned transfer of the centralized logging and alerting system to the new data center and restored all logging and alerting functionality. The root cause of this noncompliance was an insufficient process to ensure compliance during the transfer of TRE_URE3’s centralized logging and alerting system. In particular, TRE_URE3 lacked a clear process to identify localized logging sources, as well as request that the individual business units responsible for affected Cyber Assets manually review logs and issue any alerts as appropriate during the planned system outage. The duration of this noncompliance was approximately six hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue, TRE_URE3 operations personnel continuously monitored all applicable cyber security systems for possible abnormal activity. Second, throughout the duration of the noncompliance, TRE_URE3 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unidentified security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE3: 1) completed its scheduled move of its centralized logging and alerting tool, which made logging and alerting functional again; 2) completed the relocation to the newly constructed data center to improve reliability of the equipment; 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system; 4) clarified that other intrusion detection products located outside of designated Electronic Security Perimeters could be used for the detection and logging of malicious code to satisfy the requirements of the current NERC Reliability Standards during future outages; and 5) established a new process to send email notifications to all affected business units informing them of the need to manually review Cyber Asset logs during outages of the centralized logging and alerting system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2016016392 | CIP-007-3a | R6 | TRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a R6. In particular, TRE_URE3 failed to monitor and manage security events affecting Cyber Assets within an Electronic Security Perimeter (ESP) because event logs were neither processed nor retained during a 90-minute service disruption. Network support personnel discovered that a secondary firewall deployed between its centralized logging and alerting tool and ESPs containing CIP Cyber Assets was out of sync with its primary firewall. The following day, TRE_URE3 network support personnel attempted to address the firewall synchronization issue by rebooting the secondary firewall. However, when TRE_URE3 personnel rebooted the secondary firewall, the two firewalls began to compete to replicate their configurations. This conflict in turn disrupted traffic to the centralized logging and alerting system. TRE_URE3 personnel resolved the issue by erasing the secondary firewall’s configuration, restoring data traffic to the centralized security event logging and alerting system 90 minutes after the initial disruption. The root cause of this noncompliance was a software issue with the secondary firewall. In particular, when TRE_URE3 personnel rebooted the secondary firewall to address the synchronization issue, TRE_URE3 believes that software issues caused the firewalls to behave differently than anticipated. The duration of the noncompliance was approximately 90 minutes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Throughout the noncompliance duration, TRE_URE3 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unintended security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE3: 1) erased the configuration on the secondary firewall, synchronizing with the primary firewall and restoring data traffic to its centralized security event logging and alerting system; 2) replaced the firewalls at issue; and 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017018764 | CIP-007-3a | R6 | TRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-005-3a R3. In particular, TRE_URE3 failed to implement its documented process for monitoring and logging access at access points to the Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. Subsequently, Texas RE determined that the issue described in TRE_URE3's CIP-005-3a R3 Self-Report was also a noncompliance pertaining to CIP-007-3a R6 for TRE_URE3. In particular, TRE_URE3 failed to implement automated tools to monitor system events related to Cyber Assets within an ESP. For approximately six hours, the automated tool to monitor system events was not available. Therefore, TRE_URE3 could not monitor system events. TRE_URE3 transferred its centralized logging and alerting system from its existing facility to a new data center. During the six-hour transfer process, however, TRE_URE3 lost the ability to automatically log system events, as well as issue alerts for unauthorized access attempts. The issue ended when TRE_URE3 personnel completed the planned transfer of the centralized logging and alerting system to the new data center and restored all logging and alerting functionality. The root cause of this noncompliance was an insufficient process to ensure compliance during the transfer of TRE_URE3’s centralized logging and alerting system. In particular, TRE_URE3 lacked a clear process to identify localized logging sources, as well as request that the individual business units responsible for affected Cyber Assets manually review logs and issue any alerts as appropriate during the planned system outage. The duration of the noncompliance was approximately six hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue, TRE_URE3 operations personnel continuously monitored all applicable cyber security systems for possible abnormal activity. Second, throughout the duration of the noncompliance, TRE_URE3 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unidentified security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE3: 1) completed its scheduled move of its centralized logging and alerting tool, which made it possible to monitor system events again; 2) completed the relocation to the newly constructed data center to improve reliability of the equipment; 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system; 4) clarified that other intrusion detection products located outside of designated Electronic Security Perimeters could be used for the detection and logging of malicious code to satisfy the requirements of the current NERC Reliability Standards during future outages; and 5) established a new process to send email notifications to all affected business units informing them of the need to manually review Cyber Asset logs during outages of the centralized logging and alerting system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017018762 | CIP-005-3a | R3 | TRE_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-3a R6. In particular, TRE_URE3 failed to monitor and manage security events affecting Cyber Assets within an Electronic Security Perimeter (ESP) because event logs were neither processed nor retained during a 90-minute service disruption. Subsequently, Texas RE determined that the issue described in TRE_URE3's CIP-007-3a R6 Self-Report was also a noncompliance pertaining to CIP-005-3a R3 for TRE_URE3. In particular, TRE_URE3 failed to implement its documented process for monitoring and logging access at access points to its ESPs twenty-four hours a day, seven days a week. Network support personnel discovered that a secondary firewall deployed between its centralized logging and alerting tool and ESPs containing CIP Cyber Assets was out of sync with its primary firewall. The following day, TRE_URE3 network support personnel attempted to address the firewall synchronization issue by rebooting the secondary firewall. However, when TRE_URE3 personnel rebooted the secondary firewall, the two firewalls began to replicate their configurations. This conflict in turn disrupted traffic to the centralized logging and alerting system. TRE_URE3 personnel resolved the issue by erasing the secondary firewall’s configuration, restoring data traffic to the centralized security event logging and alerting system 90 minutes after the initial disruption. The root cause of this noncompliance was a software issue with the secondary firewall. In particular, when TRE_URE3 personnel rebooted the secondary firewall to address the synchronization issue, TRE_URE3 believes that software issues caused the firewalls to behave differently than anticipated. The duration of this noncompliance was approximately 90 minutes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Throughout the noncompliance duration, TRE_URE3 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring ESPs for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unintended security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate this noncompliance, TRE_URE3: 1) erased the configuration on the secondary firewall, synchronizing with the primary firewall and restoring data traffic to its centralized security event logging and alerting system; 2) replaced the firewalls at issue; and 3) modified its Security Event Monitoring to include language that personnel will also monitor the central system at all times and alert support personnel if they detect a failure of the logging system. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018779 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018780 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018781 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018782 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018783 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018784 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018785 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018786 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018787 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018788 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018789 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018790 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018791 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018792 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018793 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018794 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018795 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018796 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018797 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018798 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018799 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018800 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018801 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018802 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018803 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018804 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018805 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018806 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018807 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018808 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018809 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018810 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018811 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018812 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018813 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018814 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018815 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018816 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018817 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018818 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018819 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018820 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018821 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018822 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018823 | CIP-004-6 | R2; P2.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R2, P2.2. In particular, TRE_URE4 granted authorized electronic and/or unescorted physical access to six employees without those individuals first completing the required cyber security training. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 personnel were required to complete specific Cyber Security training prior to obtaining authorized electronic access and/or unescorted physical access to the Control Center. Five TRE_URE4 employees had electronic and/or unescorted physical access rights without prior training. TRE_URE4 performed the required training for three of these employees. Subsequently, one additional employee obtained authorized unescorted physical access to the Control Center at issue without first completing the required Cyber Security training. This employee subsequently completed that training. Regarding the final two employees at issue, both individuals worked non-traditional schedules such that TRE_URE4 had issues scheduling the requisite training. TRE_URE4 completed this training for the final two employees, ending the issue. The root cause of the noncompliance was an insufficient process to implement Cyber Security training requirements under the new CIP version 5 Standards. In particular, TRE_URE4’s previous training process relied solely on a single individual tracking all in-person training sessions. As a result, TRE_URE4 did not ensure all employees with electronic or physical access rights had the requisite training prior to the effective date of the Standard. The duration of the noncompliance was approximately four months and sixteen days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was brief, lasting less than five days for the majority of the instances. Second, all affected individuals were long-term employees and in good standing throughout the issue duration. Third, five of the six individuals at issue had valid PRAs throughout the issue duration. Regarding the other employee, that individual had only authorized unescorted physical access rights and did not in fact physically access the Control Center prior to receiving the required Cyber Security training. Finally, TRE_URE4’s Control Center had a number of additional electronic and physical protections in place throughout the issue duration, including 24/7 monitoring, malicious code detection, and alerting systems. Collectively, these additional controls reduced the risk that the employees at issue could introduce vulnerabilities into the Control Center systems. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the cyber security training for the applicable personnel at issue; 2) implemented bi-monthly meetings with subject matter experts to track NERC compliance deadlines and ensure compliance obligations; 3) provided training to the subject matter expert responsible for access approval on the correct process and reinforced that the notes within its ticketing system would no longer be utilized; 4) implemented a new learning management system that automatically tracks and notifies applicable staff members of upcoming training deadlines; 5) implemented a third-party cyber security awareness course program, which can be completed off-site and at any time of the day; and 6) implemented a new process to track all NERC Reliability Standards within a database in order to ensure that all Standards are tracked in a more systematic way. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017018824 | CIP-004-6 | R3; P3.2 | TRE_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R3, P3.2. In particular, TRE_URE4 did not attain or retain a personnel risk assessment (PRA) for a single employee as required. TRE_URE4’s Control Center became a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). As such, TRE_URE4 was required to attain and retain PRAs for all personnel with authorized electronic or unescorted physical access to the Control Center by July 1, 2016. However, TRE_URE4 granted unescorted physical access to a single employee without attaining or retaining a PRA for that individual after the effective date of the Standard. TRE_URE4 then completed the missing PRA, ending the issue. The root cause of the issue was that TRE_URE4 did not possess an adequate process to ensure that all personnel possessed valid PRAs prior to receiving authorized electronic or unescorted physical access. Specifically, TRE_URE4’s process relied upon its Human Resources (HR) department to provide the date on which a PRA for authorized personnel was completed. In this instance, HR personnel incorrectly recorded the date that a PRA was conducted, and the date was subsequently provided in a report to the applicable manager without an additional review or verification. The duration of the noncompliance was approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the single individual at issue was a long-term employee and in good standing throughout the issue duration. Second, the completed PRA revealed no security issues, and TRE_URE4 subsequently restored unescorted physical access to the single individual at issue. Third, TRE_URE4 did not have any reportable Cyber Security Incidents for the time period at issue. Fourth, the employee possessed only physical access rights to Cyber Assets and did not have corresponding electronic access rights, limiting the scope of potential risk from any potential malicious activities. Finally, TRE_URE4’s Control Center was continuously monitored throughout the issue duration, reducing the risk that the single employee at issue could enter the physical security perimeter and damage or disrupt equipment. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TRE_URE4: 1) completed the PRA for the single individual at issue; 2) approved its revised BCS Personnel Risk Assessment Procedure that provides an additional PRA review process by the applicable manager for verification that a valid PRA is on record before approving access requests; and 3) counseled HR and compliance team members on how to verify the completion of all PRAs. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017340 | CIP-009-6 | R1; Part 1.3 | WECC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-009-6 R1 Part 1.3. Specifically, WECC_URE1 reported that a server, classified as a Bulk Electric System (BES) Cyber Asset associated with a Medium Impact BES Cyber System (MIBCS), had a hardware error. During the troubleshooting process, WECC_URE1’s operations technology department Subject Matter Experts (SME) identified that this server, as well as four additional servers associated with four different MIBCS, did not have a specific process documented or implemented for the backup and storage of information required to recover BES Cyber System functionality. In addition, the specific server manufacturer for the five servers in question was not explicitly listed in the Recovery Plans. Therefore, the servers were not backed up. The root cause of this issue was less than adequate communication between work groups. The compliance responsibility for certain BES Cyber Assets associated with MIBCS, which were not in scope under prior versions of the CIP Reliability Standards, were shared between two different operations departments. WECC determined that WECC_URE1 did not include five servers in its Recovery Plan, resulting in the failure to backup and store information required to recover MIBCS functionality. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE1, and when WECC_URE1 added the five servers to its backup schedule and to its Recovery Plan, for a total of 272 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to have a process documented or implemented for the backup and storage of information required to recover MIBCS functionality for five servers. Such failure could result in loss of relay setting information, visibility, or control. Additionally, personnel may not be able to respond appropriately to effectively recover BES Cyber Assets in the event of a failure; thereby potentially affecting the reliability of the BES. However, the servers housed applications and capabilities which were duplicated and available in WECC_URE1’s Demilitarized Zone (DZ). The DZ is the primary method for accessing such applications remotely. The servers were used as human machine interface within substations. The servers housed applications which were relatively easy to re-install, with minimal data loss should the servers fail. The backup process for the servers would be identical to other servers, which were explicitly addressed in the Recovery Plans. Based on this, the likelihood of the harm occurring is low. No harm is known to have occurred. WECC_URE1 does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance, WECC_URE1 will complete the following mitigation activities: 1) add servers to backup Schedule and ensure successful backup; 2) add servers to NERC CIP-009-6 Recovery Plans; 3) update NERC CIP-009-6 Recovery Plans to clarify roles and responsibilities; 4) add steps to its enterprise wide operations configuration change (EWOCC) training for CIP-009-6 and update business unit procedures for alignment; and 5) train SMEs on roles and responsibilities and on the new EWOCC training steps.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016470 | CIP-010-2 | R1; Part 1.1.5 | WECC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1 Part 1.1.5. This noncompliance was identified by WECC auditors during WECC_URE2’s audit. As WECC_URE2’s audit period ended prior to the mandatory and enforceable date for CIP-010-2 R1 Part 1.1.5, WECC auditors determined to provide WECC_URE2 with an Area of Concern in accordance with guidance provided by NERC for CIP Version 5 transitional audits. WECC_URE2 self-reported the noncompliance after receiving the audit report knowing that the noncompliance was still occurring. Specifically, WECC_URE2 reported that during its audit it was discovered that WECC_URE2 did not include a list of applied security patches for the operating systems of the several devices pursuant to CIP-010-2 R1 Part 1.1.5. WECC_URE2 had been using an automated discovery tool to scan devices and populate a Configuration Management Database (CMDB) with information about software and security patches applied to devices. This information is used to generate device configuration baselines. When the discovery tool was deployed, comparisons of cyber assets and the lists of installed software created by the discovery tool seemed to indicate that all installed patches were being detected and recorded in the CMDB. However, WECC_URE2 learned that OS-level patches were recorded in a registry path that was not among the default registry paths used for discovery by the discovery tool The scope of devices affected by WECC_URE2’s failure to document and apply security patches were devices classified as High Impact Bulk Electric System (BES) Cyber Systems (HIBCS) and Medium Impact BES Cyber Systems (MIBCS). These devices included domain controllers; file servers; servers; and workstations used in WECC_URE2’s Energy Management System, as well as electronic access monitoring and physical access control servers. WECC determined that WECC_URE2 failed to document applied security patches on several devices when developing baseline configurations, when CIP-010-2 R1 became mandatory and enforceable. The root cause of the noncompliance was less than adequate testing of system software. Specifically, WECC_URE2’s configuration baseline tool, was not configured to consider all registry paths when developing baseline configuration for devices with applied security patches. OS-level patches were recorded in a registry path that was not among the default registry paths used for discovery by the discovery tool. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE2, and ended on when WECC_URE2 began collecting OS-level patch information and recorded that information in the CMDB, for a total of 81 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE2 failed to document applied security patches on several devices when developing baseline configurations. Such failure could allow exposures and vulnerabilities or disruption to the operations and control of HIBCS or MIBCS and associated Cyber Assets, resulting in damage of equipment; data leakage; compromise of physical access points; power cycling; or shutting down equipment. However, the likelihood of the harm occurring was low. WECC_URE2 utilized an automated discovery tool to scan devices for baseline configuration and populate a CMDB with information with four of the five subparts of CIP-010-2 R1 Part 1.1. WECC_URE2 had multiple technical, procedural, and administrative compensating controls in place to reduce and mitigate risk, to include change management with multiple levels of review and security patch management which included the devices in scope as validated during WECC_URE2’s prior WECC audit. WECC_URE2 did not experience any physical security events or incidents, anomalous system events, cyber events, or impacts to the BES during the noncompliance. No harm is known to have occurred. WECC_URE2 has no relevant compliance history with this Standard and Requirement. | To mitigate this noncompliance, WECC_URE2: 1) modified software to collect OS-level patch information; and 2) verified the new patch information was being sent to the CMDB. WECC verified completion of the Mitigation Plan.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2017016738 | CIP-007-6 | R5; Parts 5.2 and 5.4 | WECC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R5 Parts 5.2 and 5.4. Specifically, WECC_URE3 reported it replaced two existing electro-mechanical relays with microprocessor relays. The new relays were part of a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) with no External Routable Connectivity (ERC). The default accounts were not added to WECC_URE3’s inventory list of default accounts and the default passwords were not changed prior to commissioning pursuant to CIP-007-6 R5 Parts 5.2 and 5.4. The system protection engineer responsible for ensuring compliance for the new relays did not request that the construction substation technician change the passwords at the time of commissioning. Typically, the system protection engineers would change the passwords remotely at or prior to the commissioning. However, since there was no remote access to these relays, the passwords needed to be changed by someone in the field. The system protection engineer knew the passwords had to be changed, but did not clearly understand that this had to be done prior to commissioning, and instead had planned to dispatch someone out to change the passwords shortly thereafter, but got distracted by other critical tasks and failed to get back to the passwords as he had intended. WECC_URE3 discovered this issue of noncompliance during a substation inspection. WECC determined that the WECC_URE3 failed to identify and inventory all known enabled default account types and failed to change a known default password, per Cyber Asset capability on two relays within its MIBCS. The root cause was job scoping that did not identify special circumstances and/or conditions to prevent noncompliance. Specifically, the system protection engineer responsible for ensuring compliance for the new relays did not request that the construction substation technician change the passwords at the time of commissioning. Normally, the system protection engineer would change the password remotely, but this site had no remote access to the relays; therefore, the password change task was forgotten. WECC determined that this issue began when the two new relays were commissioned and ended when WECC_URE3 changed the passwords on the two relays and updated its inventory list of default accounts, for a total of 19 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE3 failed to change the default passwords and update default account documentation for two relays at one Transmission substation containing MIBCS with no ERC. Such failure could allow unauthorized access to the two relays which could result in a complete shutdown or configuration changes that could have severe negative effects on the substation and connected BES. Once connected, a bad actor could take the transformer off line, or make the primary protection for the transformer unavailable. However, the likelihood of this harm occurring was reduced by the internal controls that WECC_URE3 had in place. Specifically, the MIBCS was within a Physical Security Perimeter (PSP). To exploit the vulnerability provided by the existence of default passwords at the MIBCS without ERC, a bad actor would have to gain physical access through the secure PSP to the substation control house where the relays reside. PSP access was controlled and monitored 24/7. Additionally, because the MIBCS had no ERC, the new relays were serially connected. Once inside the control house, to gain electronic access, the bad actor would need to make a direct serial connection to the specific relays that had the unchanged default password. The two relays were monitored, and direct serial access would have been identified immediately upon connecting to the device. WECC_URE3 also performs scheduled substation inspections, which was how this noncompliance was discovered. Based on the this, WECC determined that the risk had a low likelihood of occurring. No harm is known to have occurred. WECC_URE3 does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance, WECC_URE3: 1) changed the default account password on the two relays and updated its inventory documentation accordingly; 2) provided additional instruction to construction supervisors and substation technicians regarding the necessity of changing default passwords prior to commissioning devices; and 3) updated system protection procedures to clarify what actions are required to be taken and when prior to commissioning devices. WECC has verified the completion of all mitigation activity.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016650 | CIP-008-5 | R3; Part 3.2, Part 3.2.1, Part 3.2.2 | WECC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-008-5 R3 Part 3.2. Specifically, WECC_URE4 reported that it discovered that there had been three instances in which changes were made to its roles and responsibilities with individuals involved with its Incident Response Plan and WECC_URE4 failed to update the plan within 60 days of the changes or notify applicable personnel. The three instances included a senior manager; a senior information security analyst who left WECC_URE4; and a senior information security analyst. WECC determined that in three instances, WECC_URE4 failed to update its Incident Response plan and notify the applicable parties of the changes within 60 calendar days. The root cause for all instances of noncompliance was a less than adequate process in which management failed to assign personnel to actively manage the Incident Response Plan’s roles and responsibilities as required in CIP-008-5 R3 Part 3.2. This noncompliance started 61 days after the first individual’s role had changed and the Incident Response Plan was not updated, and ended when all three individual’s roles were updated in the Incident Response Plan and appropriate personnel were notified of the changes, for a total of 117 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to update its Incident Response Plan and notify the applicable parties of the changes within 60 calendar days. A failure to keep accurate roles and responsibility information could potentially result in confusion and delays in responding to an incident due to personnel not understanding the roles and responsibilities for response efforts. The resulting response delays could potentially allow for the incident to spread to other locations or affect more devices; thereby, having a potentially greater overall impact on WECC_URE4 and the operating BES environment. However, WECC_URE4 has assigned multiple people the responsibility for responding to an incident. If an incident occurred, multiple people within its Incident Response Plan still would have been able to respond. Based on this, the likelihood of the harm occurring is low. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE4: 1) updated the roles and responsibilities section for the three individuals; 2) implemented a new process assigning a specific role to manage the roles and responsibilities and ensure that all changes are documented and communicated; and 3) designated that at the last Incident Response meeting of each month appropriate personnel will review the Incident Response Plan for accuracy. WECC has verified the completion of all mitigation activity.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016651 | CIP-004-6 | R5: P5.1, P5.3 | WECC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5 Parts 5.1 and 5.3. Specifically, WECC_URE4 reported that in one instance it did not initiate the removal of a contractor’s unescorted physical access and Interactive Remote Access to its Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) located at its primary and backup Control Centers, within 24 hours of termination as required by CIP-004-6 R5 Part 5.1. WECC_URE4 was notified that a contractor, with authorized unescorted physical and electronic access, was leaving the following week. WECC_URE4’s IT Service Desk was not notified of the contractor’s termination until 11 days later, at which time WECC_URE4 terminated the contractor’s unescorted physical and electronic access. Additionally, WECC_URE4 reported that it did not revoke access to a designated storage location containing BES Cyber System Information (BCSI) as required by CIP-004-6 R5 Part 5.3 for three contractors. Three contractors, with access to BCSI, were terminated and the IT Service Desk was not notified. When the noncompliance was discovered, two of the contractors’ access was terminated that same day and a third contractor’s access was terminated later. WECC determined an increase in scope to what was originally self-reported by WECC_URE4 was warranted. In one instance, WECC_URE4 failed to initiate the removal of a contractor’s unescorted physical access and Interactive Remote Access to its MIBCS associated with its primary and backup Control Centers within 24 hours of termination as well as the individuals access to designated storage locations containing BCSI, by the next calendar day. Additionally, WECC determined that WECC_URE4 failed to revoke eight contractors’ access to its designated storage location containing BCSI by the next calendar day, rather than just three contractors as originally self-reported by WECC_URE4. The root cause for all instances of noncompliance was a less than adequate process and training relating to the termination of contractors. An additional causal factor was the Service Desk did not have access to the directory needed to remove BCSI access. This noncompliance started when WECC_URE4 failed to revoke unescorted physical access within 24 hours of termination, and ended when WECC_URE4 came back into compliance with the last instance. The remaining instances of noncompliance occurred within this time period with various lengths of noncompliance lasting from two days to 153 days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to revoke unescorted physical access to its MIBCS located at its primary and backup Control Centers with 24 hours of their termination. WECC_URE4 also failed to revoke several contractors’ access to its BCSI by the next calendar day following termination. Such failure could present a risk of unauthorized access to WECC_URE4’s MIBCS. Such unauthorized access could be exploited to cause damage or outages, thereby potentially affecting the reliability of the BES. However, WECC_URE4 performed the required quarterly access reviews, annual BCSI access reviews, and performed spot checks for all Standards. Additionally, WECC_URE4’s Control Center operates as monitor only and has no control function because its SCADA design utilizes a distributed model of control. For six of the instances, no physical access was provided to the contractors. None of the contractors had control system or operator access. None of the contractors used their access after they had been terminated. Based on this, the likelihood of the harm occurring was minimal. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE4: 1) implemented a new process to include a termination form which details the specific access the contractor has; steps that need to be taken when there is a termination, which includes collecting all company issued equipment from the terminated contractor; date of termination; and the manager’s signature; 2) implemented additional training for all managers who are responsible for contractor access and for all individuals who could violate this Standard. The training includes steps on how to properly terminate and transfer employees and contractors that have NERC CIP access; and 3) added contractors to the HR system so that HR can oversee contractor hiring and termination. WECC has verified the completion of all mitigation activity.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016652 | CIP-007-6 | R2 | WECC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R2. Specifically, for two instances, WECC_URE4 reported that it did not take action to apply applicable patches, create a dated mitigation plan, or revise an existing mitigation plan pursuant to CIP-007-6 R2 Part 2.3 for Electronic Access Control or Monitoring Systems (EACMS) associated with its MIBCS located at its primary and backup Control Centers. For the first instance, WECC_URE4 identified a patch that should have been applied to its EACMS. WECC_URE4 applied the patch to two EACMS to ensure the patch was safe to apply; however, did not taken action pursuant to CIP-007-6 R2.3 for the remaining EACMS within 35 calendar days of the day a patch was deemed as applicable. For the second instance, WECC_URE4 did not take action pursuant to CIP-007-6 R2.3 within 35 calendar days of the day a patch was deemed applicable to its EACMS. In both instances WECC_URE4 applied the patch to the EACMS. WECC_URE4 reported a separate issue where it did not evaluate security patches for applicability at least 35 calendar days from the last evaluation for one Protected Cyber Asset (PCA). WECC_URE4 shut off the PCA, but did not immediately decommission the PCA from operation. During the interim, two patches were released and were not assessed for applicability. Additionally, WECC_URE4 reported that it created an internal mitigation plan for a security patch on one EACMS that could not be patched within the 35 calendar day timeframe. When completing the last step in the mitigation plan, complete the required patch, WECC_URE4 encountered an unexpected error with the software and had to work with the manufacturer to resolve the error. This error resulted with WECC_URE4 not installing the patch. As a result, they did not submit a revised internal mitigation plan by the proposed completion date. WECC determined that there was an increase in scope from what was originally self-reported by WECC_URE4. WECC_URE4 did not identify patch sources for some of its EACMS and some of its BCAs associated with its MIBCS located at its primary and backup Control Centers, as required by CIP-007-6 R2 Part 2.1. Additionally, WECC determined that the instance in regards to the PCA was not a noncompliance because WECC_URE4 applied the patches within 34 calendar days. In total, there were eleven instances of noncompliance. The root cause of all instances of noncompliance was a lack of communication on who was responsible for the tasks associated with WECC_URE4’s process to ensure compliance with CIP-007-6 R2. WECC determined that the fourth, fifth, and sixth instances of noncompliance began when cyber security patch sources were identified; all security patches were evaluated; and WECC_URE4 took action pursuant to CIP-007-6 R2.3, for a total of 402 days of noncompliance. All additional issues of noncompliance fell within this timeframe. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to follow its documented security patch program to install applicable patches within 35 calendar days for EACMS and BCAs associated with its MIBCS located at its primary and backup Control Centers in eight separate instances, Part 2.3. Additionally, WECC_URE4 failed to identify its patching sources, Part 2.1. WECC_URE4 also failed to install the patch by the due date listed in the mitigation plan or have a CIP Senior Manager sign an extension, Part 2.4. Failure to identify, evaluate and install security patches in a timely manner could potentially result in an attacker gaining access to WECC_URE4’s MIBCS to cause disruptions to its operating capabilities potentially affecting over 600 MW of generation in the western interconnection. However, WECC_URE4’s Control Center operates as monitor-only and has no control function because its SCADA design utilizes a distributed model of control. WECC_URE4 performs weekly vulnerability scans on all CIP networks and performs a weekly review of the results. WECC_URE4 performed a spot check which is how it identified these instances of noncompliance. WECC_URE4 has also implemented segregated networks based on function, with access controls, to restrict traffic to only authorized traffic. Based on this, the likelihood of the harm occurring is low. No harm is known to have occurred. | To mitigate this noncompliance, WECC_URE4: 1) identified all patch sources, evaluated all applicable patches, installed all applicable patches and decommissioned the one PCA; 2) updated its patch management procedure to include monthly reviews of patch reports and to also include a peer review ensuring that the new patch version for the monthly patch reports matches the previous month’s report; 3) trained applicable individuals on the mitigation process and what steps are needed for a mitigation extension; 4) updated request for change forms to include a “delete from disk date” no longer than one week from the shutdown point; 5) developed an application that automatically alerts the patch management team when a patch due date is close; and 6) hired a third-party vendor to manage the evaluation of applicability of security patches.
2017-12-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2017017386 | CIP-004-6 | R5; Part 5.1 | During a Compliance Audit, WECC determined that WECC_URE5, had an issue with CIP-004-6 R5 Part 5.1. WECC_URE5 was unable to provide evidence to demonstrate that unescorted physical access for two terminated employees with physical access to High Impact Bulk Electric System (BES) Cyber Systems (HIBCS) was removed within 24-hours of a termination action. According to WECC_URE5’s Access Control Procedure, the first step when revoking access is the responsibility of its “Leaders”, in this case a supervisor. The supervisor notifies Human Resources, preferably in writing via email, of the departure of the employee to include their name, employee ID, and their final date of service with WECC_URE5. That action is a manual one, and is necessary for any further steps in the process to commence. Supervisors receive training and education on this process and the importance of its timeliness. While the majority of the remaining steps are automated, this first step remains a manual action. The root cause was a supervisor not following WECC_URE5’s documented processes for revocation of physical access. WECC determined that this issue began when unescorted physical access should have been revoked for two employees, and ended on when WECC_URE5 revoked the access, for a total of 25 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to revoke unescorted physical access for two employees within 24-hours of a termination action. Failure to revoke unescorted physical access to BES Cyber Systems could allow unauthorized individuals to compromise the security of the BES Cyber Assets that control the BES. This unauthorized access could be exploited to cause damage or widespread outages of the BES, thereby, potentially affecting the reliability of the bulk power system (BPS). However, the likelihood of the harm occurring was minimal. WECC_URE5 utilized an automated Physical Access Control System (PACS) for the completion of revocations for terminations actions, reassignments, or transfers based on future dates. Additionally, WECC_URE5 implemented its access management quarterly review of unescorted physical access. All entrances to the Physical Security Perimeter of the HIBCS were monitored and controlled by the PACS. No harm is known to have occurred. WECC considered WECC_URE5's CIP-004 compliance history in determining the disposition track. WECC_URE5 had no relevant prior noncompliance with CIP-004. | To mitigate this issue, WECC_URE5: 1) revoked physical access for the two terminated individuals; 2) placed the supervisor on suspension, pending review; and 3) terminated the supervisor’s employment.
2017-11-30 | Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2017018428 | CIP-006-6 | R2. | FRCC_URE1 submitted a Self-Log stating that it had an issue of CIP-006-6 R2 (Part 2.2). This issue started when a visitor exited from a Physical Security Perimeter (PSP) without being logged and ended when the visitor log was updated with the correct time the visitor exited the PSP. FRCC_URE1 did not implement its documented visitor control program as required under CIP-006-6, Part 2.2 to manually or automatically log visitor entries into and out of a PSP, including the date and time of initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor on one (1) occasion at a PSP. The root cause for this violation was failure to follow the procedure. Additionally, it was determined that the Visitor Access Log was cluttered due to its continuous nature and did not lend itself to quick review and was therefore a contributing factor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk of not logging visitors in and out of a PSP could lead to unauthorized access to Cyber Assets. The risk was reduced because the visitor was escorted for the entirety of their physical access to the PSP and this error was administrative in nature. No harm is known to have occurred. FRCC determined that this issue was appropriate for CE treatment because it posed a minimal risk and FRCC_URE1 self-logged the issue. Additionally, FRCC_URE1 has no relevant prior noncompliance. | To mitigate this issue, FRCC_URE1: 1. corrected the visitor log by signing the log when visitor actually exited the PSP; 2. performed Visitor Access Control refresher training for the visitor escort and peer group, reiterating the steps of and importance of the Visitor Access Control procedures; 3. modified the Visitor Access Log to have one date per page; 4. implemented an Internal Control daily Visitor Log check; 5. implemented a weekly Visitor Log check internal control; 6. documented (formalized) the monthly log check internal control procedure; and 7. performed comprehensive, entity wide refresher training during Fall Compliance SME Update meeting.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017573 | CIP-006-6 | R2 | MRO_URE1 reported that it had an issue with CIP-006-6 P2.1. Specifically, MRO_URE1 identified two instances where individuals gained unauthorized, unescorted access to a Physical Security Perimeter (PSP). For the first instance, an employee asked a Emergency and Security Control Operator (ESCO) to remotely open the PSP door to the Back-up Control Center so that the employee could check on a reported pre-fire alarm. In the second instance, during a training exercise, three System Operators obtained unauthorized, unescorted access to a substation that has a Medium Impact BES Cyber System from an ESCO. The cause of the noncompliance was a failure of operators to follow MRO_URE1's established access control procedures. The total duration of the noncompliance was less than a month, but each individual instance lasted one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For instance number one, the individual who gained the access was a current employee who had gone through a corporate background check. Additionally, MRO_URE1 conducted a review of the cyber system logs at the facility and confirmed there were no other access attempts while the employee was in the facility. For instance number two, the System Operators who gained the improper access have up-to-date Personal Risk Assessments, have completed CIP-004 training, and are approved to have unescorted physical access to PSPs that contain High Impact BES Cyber Systems. Finally, for both instances, per MRO_URE1, it reviewed the security video and the Emergency and Security Operations Center telephone audio recordings to confirm that only the employees described in the Self-Report actually entered the facilities. No harm is known to have occurred. MRO_URE1 has no relevant history with CIP-006-6 R2. | To mitigate this issue, MRO_URE1: For the first instance of noncompliance: 1) secured the facility; 2) reviewed logs to ensure the were no additional access attempts; 3) included this on a Lessons Learned for ESCOs; and 4) created a new PSP Fire Alarm Checklist, and provided training to ESCOs on that augmented checklist. For the second instance of noncompliance: 5) secured the facility; 6) included this on a Lessons Learned for ESCOs; and 7) created a new Emergency Key Box Checklist, and provided training to ESCOs on that augmented checklist.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016857 | CIP-007-6 | R3 | MRO_URE1 reported that it had an issue with CIP-007-6 R3. MRO_URE1 utilized a software application as one of its methods to deter, detect, or prevent malicious code in accordance with CIP-007-6 P3.1. MRO_URE1 detected that it failed to update its documented process for updating and testing the software application's anti-virus signatures or patterns as required by CIP-007-6 P3.3. The cause of the noncompliance was that staff did not realize that the process documentation for this particular software application was not sufficient to meet the new requirements for CIP v5. The duration of the noncompliance was approximately eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Per MRO_URE1, the noncompliance was related only to documentation as the software application MRO_URE1 was using had up-to-date signatures with updates being timely applied to the application. Additionally, the software application does not have the ability to directly impact BES operations, it is a detective control meant to detect malware, and is not a preventive control that could prevent the installation of malware. No harm is known to have occurred. MRO_URE1 has no relevant history with CIP-007-6 R3. | To mitigate this issue, MRO_URE1: 1) updated the software application's process documentation to include antivirus signature updates; and 2) provided training to staff on the updated documentation.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016865 | CIP-010-2 | R1 | MRO_URE1 reported that it had an issue with CIP-010-2 R1. MRO_URE1 identified four instances of noncompliance. In the first instance of noncompliance, MRO_URE1 identified two devices that had incomplete baselines. The operating system software and patches were included in the baseline, but not all off-the-shelf software, and none of the custom software was included in the baseline. The cause of the noncompliance was that staff did not understand what was required for the baseline under CIP v5. In the second instance of noncompliance, MRO_URE1 identified that its baseline information was incomplete, as the firmware level had not been documented for two devices. The two devices were spares and had not been deployed in the field. The cause of the noncompliance was staff failed to follow MRO_URE1's documented procedure for creating baselines. In the third instance of noncompliance, MRO_URE1 identified four devices (switches) that had incomplete baselines as the information regarding network accessible TCP/IP ports was missing. The cause of the noncompliance was staff failed to follow MRO_URE1's documented procedure for creating baselines. In the fourth instance of noncompliance, MRO_URE1 identified an RTU whose baseline was updated 35 days after an update, as opposed to the required 30 days. The cause of the noncompliance was deficient training for the staff member responsible for updating the baseline on this device. The duration of the noncompliance was approximately seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the first instance, the duration was brief, as the issue was identified during a review to confirm appropriate baselines for Cyber Assets that transitioned from CIP v3 to CIP v5, and promptly corrected. For the second instance of noncompliance, the devices were spares that had not been placed into the field during the duration of the noncompliance. For the third instance of noncompliance, the noncompliance was self-identified by a detective control and was limited to documentation of enabled ports, as no changes to the configuration of the devices was required. For the fourth instance of noncompliance, the duration of the noncompliance was brief, as the update was only five days late. No harm is known to have occurred. MRO_URE1 has no relevant history with CIP-010-2 R1. | To mitigate this issue, MRO_URE1: For the first instance of noncompliance: 1) completed the baselines for the two devices; and 2) the asset supervisor and the asset administrator provided additional guidance to staff to reinforce the expectations for baseline documentation under CIP v5. For the second instance of noncompliance: 3) completed the baselines for the two devices; and 4) provided reinforcement training on applicable procedures related to baselines. For the third instance of noncompliance: 5) completed the baselines for the four devices; 6) conducted an extent of condition to review baselines for all high and medium impact BES Cyber Assets; 7) updated a subsection of the applicable Device Management procedure; 8) provided training to all applicable personnel on the updated Device Management procedure; and 9) sent an email to all Asset Supervisors and Asset Administrators on the importance of accurate baselines. For the fourth instance of noncompliance: 10) updated the baseline the device; 11) provided training to all applicable personnel on the change management process requirements; 12) discussed the issue with all Asset Supervisors and Asset Administrators to verify they were following the 30-day update requirement for baselines; 13) conducted a spot check of 15 sample change log entries to confirm the baselines were timely updated; and 14) sent requests for additional information to relevant Subject Matter Experts, reviewed the responses to identify issues, and updated baselines and reinforced the change management process with applicable personnel
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016856 | CIP-006-6 | R1 | MRO_URE1 reported that it had an issue with CIP-006-6 P1.4 and P1.6. Specifically, MRO_URE1 failed to monitor for a forced door entry into two Physical Security Perimeters (PSP) at a single substation and failed to monitor for unauthorized access to the associated Physical Access Control System (PACS). The cause of the noncompliance was a hardware failure with the primary small form-factor pluggable transceiver on the Synchronous Optical Networking (SONET) system at the substation which resulted in a communication failure. The duration of the noncompliance was approximately three hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance only lasted three and a half hours due to MRO_URE1's situational awareness and the timely dispatching of maintenance personnel. Additionally, during the loss of the monitoring for forced door entry, the on-site physical access controls were still functional only allowing authorized personnel to enter. Further, logging of the door open events remained active during the communication outage as evidenced by the four recorded door events that coincided with the dispatched personnel. Moreover, the PACS was located within a PSP, which is an additional security control not required by the standard. Finally, MRO_URE1's event analysis did not find any evidence of forced entry at either PSP. No harm is known to have occurred. MRO_URE1 has no relevant history with CIP-006-6 R1. | To mitigate this issue, MRO_URE1 re-established communication used for monitoring.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017017437 | CIP-002-5.1 | R1 | MRO_URE2 reported that it had an issue with CIP-002-5.1 R1. Specifically, MRO_URE2 did not identify an asset (substation) that contained a low impact BES Cyber System. Subsequently, MRO_URE2 reported an additional instance of noncompliance related to the failure to identify a Medium Impact BES Cyber Asset (a 230 kV breaker failure relay) at a substation. The first instance was caused by an inconsistent application of BES Asset due to differences in methodologies and forms that were used by different departments. The second instance was caused by human performance, as the relay is quite small and is seated next to a nearly identical relay, and the two relays were identified as a single relay. The duration of the noncompliance was approximately four and a half months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both instances can be described as documentation errors and the scope was limited to one Low Impact asset and one Medium Impact BES Cyber Asset. Additionally, for instance number one, the CIP Standards and Requirements associated with the protection of low impact BES Cyber Systems were not enforceable during the noncompliance. Further, for instance number two, the relay was password protected, current in regard to security patches, and was protected by all applicable CIP protections. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE2: 1) added the asset to its low impact BES Cyber Asset spreadsheet; 2) added the asset to its Medium Impact BES Cyber Assets List; and 3) to prevent reoccurrence MRO_URE2 will use a standardized form and accompanying guideline ("facility verification form") as a consistent resource to identify assets that need to be included on its low impact BES Cyber Asset spreadsheet.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2016015993 | CIP-004-3a | R3 | MRO_URE2 reported that it had an issue with CIP-004-3a R3.2. MRO_URE2 identified two instances of noncompliance. Specifically, in instance number one, MRO_URE2 did not update each personnel risk assessment (PRA) at least every seven years. The PRA update was conducted over appoximately six weeks late. For instance number two, MRO_URE2 granted electronic access to a vendor's employee before a PRA was fully completed. The first instance was caused by human error as the original PRA date was incorrectly entered into the database as the date the employee was granted access. The second instance was caused by issues related to migrating from one system to another system during CIP v5 transition. The duration of the noncompliance was approximately three and a half months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For instance number one, the employee had a previous PRA and was up-to-date on CIP training. Additionally, the duration was reduced because the noncompliance was identified by a secondary control. Further, during the time that the employee's PRA was expired, the employee only gained entry to one medium impact substation on a single occasion and did not attempt to log into the system that is used to control and monitor access to a substation's Electronic Security Perimeter or Critical Cyber Assets (CCAs). For instance number two, the issue was limited to a single vendor employee, and the duration of the incomplete PRA was limited to four and a half months. Additionally, the vendor's employee had up-to-date CIP training. Finally, a review of logs establish that the account was never used. No harm is known to have occurred. MRO considered MRO_URE2’s CIP-004-3a R3 compliance history in determining the disposition track. MRO_URE2's relevant prior noncompliance with CIP-004-3a R3 includes: NERC Violation ID MRO2016015555 (CIP-004-3a R3) that was resolved as a Compliance Exception. MRO determined that MRO_URE2's compliance history should not serve as a basis for applying a penalty because the current noncompliance was not caused by a failure to mitigate the prior noncompliance. | To mitigate this issue, MRO_URE2: For instance number one: 1) revoked access of the employee; and 2) to prevent reoccurrence, made changes to automate population of the PRA date in its database. For instance number two: 3) disabled access for the account of the vendor's employee; and 4) implemented a new Identity and Access Management tool to automate the provisioning and de-provisioning access that also has the capability to act as a detective control. This tool includes capabilities to verify PRAs and CIP training.
2017-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017017440 | CIP-006-6 | R2 | MRO_URE2 reported that it had an issue with CIP-006-6 R2. MRO_URE2 identified three instances of noncompliance. Regarding instance one, a visitor was not continuously escorted for approximately 90 seconds while in the Control Center. The second instance involved two employees who did not have access permission rights to enter a medium impact substation, but were able to use their badges to enter the Physical Security Perimeter (PSP) to, per MRO_URE2, perform routine maintenance, due to a hardware failure. The third instance involved two unauthorized contractors who were left unescorted for approximately one hour in a medium impact substation. The first instance was caused by human error as the person who opened the door for the contractor did not recognize the importance of continuously escorting the contractor as the contractor passed through the PSP. The second instance was caused by a hardware failure. The third instance of noncompliance was caused by human performance as the escort did not perform the job duties in the manner that the escort was trained. The total duration of the noncompliance was approximately three months, although each individual instance of noncompliance lasted less than one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All three instances were promptly detected by secondary controls and the noncompliance was quickly mitigated. For instance number one, the contractor was only unescorted for 90 seconds and was monitored by Security Operations Center (SOC) cameras while unescorted. Additionally, the contractor was initially escorted and properly signed in and out of the PSP. For instance number two, the SOC was able to promptly detect that the employees entered the substation without access rights, was able to immediately call the substation and inform the employees that they did not have access and ask that they leave, verify by video that the employees were only in the PSP for four minutes, and generated a work order and repaired the faulty door on the same day of the noncompliance. For instance number three, the SOC became aware of the noncompliance by an inappropriate scan of a badge and took immediate action to investigate and correct the situation. Additionally, MRO_URE2 revoked access from the escort on the day that it occurred and conducted a vulnerability assessment at the site that revealed no issues. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE2: For instance number one: 1) provided training on access policies to the employee who opened the door for the contractor; and 2) distributed an email memo from the compliance office describing the incident and reinforcing policies regarding the escort of visitors. For instance number two: 3) the SOC directed the employees to leave the substation; 4) repaired the malfunctioning door that improperly gave access; and 5) sent an "e-Bulletin" to applicable employees reminding them to be aware of their own access levels prior to attempting to enter a facility, or to contact SOC to confirm access levels. For instance number three: 6) the SOC directed the contractors to secure the site and leave; 7) revoked the escort's CIP substation access; 8) conducted a vulnerability assessment on the affected substation; and 9) modified the "scope of work" for escorts to clarify their job duties.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017492 | CIP-006-6 | R2 | RFC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R2. An employee escorted a security contractor, who was not authorized for unescorted access, into a Physical Security Perimeter (PSP) so that the contractor could work on the security fence system. While the contractor was on the phone advising the Security Operations that work was going to begin on the security system, the employee stepped outside of the control house leaving the contractor unescorted. During the conversation, the Security Operations operator discovered the contractor was inside the control house unescorted. The Security Operations operator also determined that a visitor log was not opened and instructed the contractor to leave the control house. The contractor exited immediately and met the employee outside, where the employee was advised of what had occurred. The contractor was alone for approximately one to three minutes. The employee stated that he had never escorted someone into a NERC Site and made a mistake. The cause was insufficient training and reminders regarding escort responsibilities. Accordingly, this noncompliance involves the management practice of workforce management. The duration of the noncompliance was approximately five minutes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The contractor is a trusted contractor and was on the phone with the Security Operations operator throughout the one to three minutes that he was alone in the PSP. Additionally, RFC_URE1’s Security Operations operator quickly identified the noncompliance and instructed the contractor to exit the PSP, which he immediately did. Accordingly, there was little opportunity for the contractor to act in a way that could compromise the BPS and there was no indication of any intent other than to complete the task for which he was there. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE1: 1) conducted supplemental training with the employee in addition to his required 2017 NERC CIP Training; 2) conducted a training class with slides from the 2017 NERC CIP Training relating to “Escorting Visitors” to their service technicians, in order that they would be aware that they should always have an escort while in a PSP; 3) generated electronic posters to explain to employees the responsibilities of escorting visitors/employees in a PSP; and 4) sent an email communication to all transmission employees explaining the duties of escorts within a PSP.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017329 | CIP-011-2 | R1 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-011-2 R1. During a review of printer and scanner settings, RFC_URE2 identified a potential issue where a shared folder was being used as a temporary repository for scanned field revisions of substation and system protection prints, (These types of prints were not considered Bulk Electric System (BES) Cyber System Information (BCSI) until CIP v5 took effect on July 1, 2016.) but was not designated as a CIP Information Repository (CIR). The shared folder is used to hold the scanned files until they are filed to their appropriate CIR. RFC_URE2 investigated the field revisions log dating back to the implementation date of CIP v5 (i.e., July 1, 2016) and discovered several CIP-protected substation and system protection prints that contain BCSI and were scanned to the shared folder. (Three of the files were removed within 5 minutes of being placed in the shared folder. One of the files remained in the shared folder for 9 days. That file contained BES cyber system network topology.) Several RFC_URE2 employees have authorized access to the corporate data network, which would have allowed them to access this shared folder. Of those employees, more than half are not CIP-trained, but are trusted company personnel. The root cause of this noncompliance was a gap in RFC_URE2’s process for controlling the scanning of this type of information. During the CIP v5 transition, RFC_URE2 failed to identify that this type of information was scanned to this temporary shared folder prior to being moved to its CIR. This major contributing factor involves the management practice of information management, which includes protecting information items and managing information item confidentiality and privacy. The duration of the noncompliance was approximately four months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, most of the files were removed from the shared folder within minutes of being scanned, minimizing the likelihood that any unauthorized person could have obtained the information. Second, although the fourth file resided on the shared folder for 9 days, only trusted company personnel had access to the shared folder, making it unlikely that a malicious actor would have obtained the information. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE2 : 1) held training sessions to remind CIP personnel of the proper use and handling procedures of CIP Protected Information; 2) sent reinforcing communication to ensure scanning of CIP protected substation and system protection prints is halted until completion of corrective actions to properly configure current scanner or purchase a new scanner; 3) displayed signage around the scanner to remind personnel of the restrictions regarding CIP Protected Information; 4) researched scanner capabilities and implemented a solution to allow scanning directly into a CIR; 5) updated relevant procedures according to final outcome of the above milestone activity implementing a solution to allow scanning directly to a CIR; and 6) held training session regarding new process measures and new applicable BCSI controls being instituted per the revised procedures. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017328 | CIP-010-2 | R1 | RFC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1. During a review of their configuration baseline change management process, RFC_URE2 discovered a change management ticket showing that two baseline configuration changes were updated 5 days after the 30 calendar day deadline for completing the changes. The ticket at issue was created to update two database servers with the new approved security patches and software upgrades. While the update to the two baseline configuration changes occurred late, the change ticket was properly submitted and authorized for the security patches and software updates to be performed. During the same review of the configuration baseline changes management process, RFC_URE2 also discovered that an application was installed to help facilitate a change in PIN codes for RFC_URE2’s Physical Access Control systems (PACS), but the change ticket was never submitted to the group responsible for baseline updates. As a result, the baseline update was completed 8 days late. The root cause of this noncompliance was the fact that RFC_URE2's process for monitoring baseline changes for its PACs systems was not proactive enough from a preventative control perspective. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of first noncompliance was approximately five days. The duration of the second noncompliance was approximately seven days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk presented by this noncompliance relates to the fact that the baseline configurations were out-of-date, which could hinder RFC_URE2's ability to properly test planned changes or respond to unexpected changes to its system. The fact that RFC_URE2 quickly detected and corrected the issues through effective internal controls minimized the window of time that out-of-date baselines could have hindered RFC_URE2's ability to analyze unexpected changes to the system. Second, these planned changes were properly authorized prior to being implemented, which minimized the likelihood that they could have had an adverse effect on RFC_URE2's system. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE2: 1) conducted training with impacted personnel. Lessons learned will be shared to keep track of the changes and the 30 calendar day window of opportunity and to create awareness on the applicable aspects of this standard CIP-010; 2) implemented reporting to monitor PACS baseline on a bi-weekly basis to make their preventative controls more proactive in nature; 3) created or updated the Job Aid for Baseline Impacting Changes; and 4) communicated to other staff within the RFC_URE2 Compliance Team. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017248 | CIP-002-5.1 | R1 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R1. During an internal review, RFC_URE3 determined that several substation devices were not listed as “production” BCAs in the CIP devices system-of-record for a duration ranging from 3 to 6 months. RFC_URE3 tracks all of its in-scope CIP devices in this system, which gets automated feeds from a RFC_URE3 engineering database to collect “planned” devices, which undergo assessments to determine CIP applicability. Applicable CIP devices are kept in a “staging state” in this system until a commissioning confirmation is received from the field through an automated feed from the engineering database. Once it is confirmed that a device has been brought “in-service,” the applicable planned device is moved to the “production” Master Device List (MDL) managed and generated by this system. The listing of a device on the MDL signifies that the device is a CIP device (i.e., BCA, PCA, EACMS). In this case, RFC_URE3 discovered that several devices remained in the “staging state” in this system, as their commissioning confirmations were not received, which would have triggered their placement on the MDL. (During the investigation, RFC_URE3 reviewed impacts to other CIP Reliability Standards, but did not identify additional potential issues with these devices. All devices were included within RFC_URE3 programs for applicable electronic and physical security requirements specified in the CIP Standards 003 through 011.) During its extent of condition review, RFC_URE3 also identified an additional device that was placed in-service as an emergency replacement. This device’s data was placed in the engineering database later than its actual in-service date, and consequently, its entry in the MDL was also delayed. (RFC_URE3 identified a default password change issue with this device, which was the subject of another self-report.) The root cause of this noncompliance was the lack of a more frequently occurring verification of the information in the CIP devices system-of-record. This major contributing factor involves the management practices of verification and information management, which includes verifying the validity of information items. The duration of the noncompliance was approximately six months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. This noncompliance is a documentation issue because it involves a misclassification of devices that were, nevertheless afforded all of the applicable electronic and physical security requirements contained in the CIP Standards. For instance, all of the devices in question were in a physical zone managed by RFC_URE3 to ensure access was restricted to only authorized personnel. In fact, ReliabilityFirst verified that this issue did not result in any cyber, physical, or operational impact to the BPS as these devices continued to operate in a normal state during the period of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE3: 1) performed weekly review of planned devices in Engineering Database; 2) corrected all records in the Engineering Database and assessment completion in NERC CIP Asset system of record; 3) performed frequent (3-4 times a week) review of “pre-production” device list in this system; 4) held a discussion with relevant personnel on (a) Sequence of CIP Reviews for new and existing devices and (b) Workflow enhancement possibilities; 5) held a discussion with relevant personnel on (a) Timing of CIP Reviews for new and existing devices and (b) Workflow enhancement possibilities; 6) held a discussion with relevant personnel on (a) Sequence of CIP Reviews and (b) Workflow enhancement possibilities; 7) provided Engineering Database upgrade to improve functionality including a fix to the faulty device transition; 8) reviewed system and Master Device List (MDL) functionality with system Subject Matter Expert and RFC_URE3's engineers; 9) updated batch process to read the records from RFC_URE3’s tables in a common time zone format; 10) ensured inclusion of all devices in the Master CIP Device List; 11) enhanced the process and its documentation related to CIP device commission to (a) Identify and document the “Operational In-Service” and “CIP In-Scope” dates correctly, (b) Identify commissioning roles and responsibilities more clearly, (c) Identify the timing and dependency requirements for roles and their responsibilities correctly, and (d) Identify process for emergency commissioning of CIP devices and their placement in the MDL; 12) added to appropriate sections in Commissioning Checklist(s) to address CIP device representation in MDL; 13) created and provided trainings on the enhanced CIP Device Commissioning process to all relevant personnel; and 14) added to appropriate sections in the Enhanced Procedural and/or Technical measures, to address completion time and obtain approvals for CIP device.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017016912 | CIP-010-2 | R1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in noncompliance with CIP-010-2 R1. During a routine review of baseline updates, RFC_URE3 discovered that, while it was upgrading data switches, it failed to properly record the replacement of two switches in the asset management database system within 30 days of the changes being completed. Because the device statuses were not changed in the asset management database system, the baseline configuration was not updated within 30 days of the field changes. The root cause of this noncompliance was the loss of personnel and a delayed turnover process. The individual who had been responsible for performing the task retired from RFC_URE3 with no backup in place. This major contributing factor involves the management practices of workforce management, which includes managing succession plans, and asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately one month. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE3 identified the late baseline updates through an internal control, which limited the amount of time that the baselines were out of date. Second, the devices at issue were new switches that were tested and then installed with the latest firmware patches and mitigating security controls in place. Considering the fact that these were new devices with the latest patches and security controls, together with the fact that the baselines were out of date for a short period of time, minimizes the likelihood of any harm occurring. Additionally, ReliabilityFirst notes that the devices at issue continued to operate in a normal state during the period in question, and that no security patch updates for the devices were missed. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE3: 1) processed the final approvals for the asset management database records for the respective switches; 2) reviewed and discussed the CIP-010 standard and program expectations with all relevant personnel; 3) assigned secondary personnel structure to assist with the asset management database baseline configuration change approvals; 4) developed a quality assurance (QA) report for the monthly Manager’s Meeting; 5) established a standing agenda item to the monthly manager’s meeting to review the QA Report and reinforce expectations and reviewed the current QA report; 6) updated procedure to move clearly define the roles and responsibilities and timing requirements; and 7) provided training to all relevant personnel on the revised Testing Group procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017503 | CIP-007-6 | R4 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R4. RFC_URE3 conducted its regular review of event logging information in the detective tool and discovered that the automated log repository was not properly processing event data resulting in the loss of ability to generate alerts for detected malicious code and the loss of event logs required to be retained under CIP-007-6 R4 Part 4.3. RFC_URE3 uses the detective tool to log security events for a number of Bulk Electric System (BES) Cyber System devices. Special applications collect Security Event logs either directly from the BES Cyber Systems or from the detective tool agents installed on the BES Cyber Systems. The applications then forward the logs to a centralized log repository that aggregates and correlates the Security Event logs. The repository also generates security alerts and event reporting to support monitoring. In this case, a problem occurred with two of the background processes that feed information to the repository. While correcting these issues, the hard drive for the primary repository tasked with aggregating and alerting on events failed, which slowed recovery. RFC_URE3 completed all the necessary repairs. Notably, during the time that these issues were occurring, the devices at issue did not lose the ability to detect and quarantine malicious code. Rather, it was just the ability to generate alerts that was impacted. Moreover, many of the devices at issue were still logging security events locally and sending them to one of the applications at issue. The problem related to the retention of those logs for the requisite length of time. The root cause of this noncompliance were various technical issues with the detective tool, including, configuration issues, and software and hardware failures. These major contributing factors involve the management practices of information management, which includes the backup and retention of information items, and verification, including verifying the background processes feeding information to the repository. The duration of the noncompliance was approximately twenty days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the devices at issue still had the ability to detect and quarantine malicious code. Second, all of the devices at issue were still logging events locally. Third, during the approximately three weeks that this issue was occurring, RFC_URE3 was fully aware of the issue and could have quickly detected any issues that occurred. Fourth, RFC_URE3’s defense in depth strategy protects these devices with multiple firewalls and two-factor authentication. Therefore, configuration changes to a single firewall would not grant access to an external user. This setup increases the complexity of any attempts to compromise RFC_URE3’s systems through a single configuration change. Overall, a detailed knowledge of RFC_URE3’s network design, topology and navigation through multiple firewalls would have been necessary to gain access to the BES Cyber Systems at issue. Additionally, ReliabilityFirst notes that no malicious baseline changes and no reported operational or security impacts occurred during the time period in question. No harm is known to have occurred. RFC_URE3 has taken the following steps to mitigate risk while the mitigation plan is successfully completed: (1) the actions already completed have returned the detective tool system to reliable operation; (2) RFC_URE3 has completed a document detailing its process for performing device reporting validation to the security event logging system; and, (3) RFC_URE3's defense-in-depth strategy, described above, will also mitigate ongoing risks. | To mitigate this noncompliance, RFC_URE3 will complete the following mitigation activities: 1) validated that devices are logging to RFC_URE3 detective tool; 2) created/updated document detailing the RFC_URE3 process for performing device reporting validation to the security event logging system; 3) executed the process for performing device reporting validation to the security event logging system; 4) created/updated document detailing the process to verify the system health of the applications and repository; 5) executed the process to verify the system health of the detective tool applications and repository; and 6) will perform a review of the other RFC_URE3 detective tool Instances. RFC_URE3 will deliver recommendations for expanding device reporting and detective tool health check processes to include these instances. RFC_URE3 requires this length of time to complete these mitigation activities because milestone 6 in particular will take this time to complete due to the breadth and detail required.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017334 | CIP-010-2 | R1 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1. During a review of their configuration baseline change management process, RFC_URE3 discovered a change management ticket showing that two baseline configuration changes were updated 5 days after the 30 calendar day deadline for completing the changes. The ticket at issue was created to update two database servers with the new approved security patches and software upgrades. While the update to the two baseline configuration changes occurred late, the change ticket was properly submitted and authorized for the security patches and software updates to be performed. During the same review of the configuration baseline changes management process, RFC_URE3 also discovered that an application was installed to help facilitate a change in PIN codes for RFC_URE3’s Physical Access Control systems (PACS), but the change ticket was never submitted to the group responsible for baseline updates. As a result, the baseline update was completed 8 days late. The root cause of this noncompliance was the fact that RFC_URE3's process for monitoring baseline changes for its PACs systems was not proactive enough from a preventative control perspective. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of first noncompliance was approximately five days. The duration of the second noncompliance was approximately seven days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk presented by this noncompliance relates to the fact that the baseline configurations were out-of-date, which could hinder RFC_URE3's ability to properly test planned changes or respond to unexpected changes to its system. The fact that RFC_URE3 quickly detected and corrected the issues through effective internal controls minimized the window of time that out-of-date baselines could have hindered RFC_URE3's ability to analyze unexpected changes to the system. Second, these planned changes were properly authorized prior to being implemented, which minimized the likelihood that they could have had an adverse effect on RFC_URE3's system. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE3: 1) conducted training with impacted personnel. Lessons learned will be shared to keep track of the changes and the 30 calendar day window of opportunity and to create awareness on the applicable aspects of this standard CIP-010; 2) implemented reporting to monitor PACS baseline on a bi-weekly basis to make their preventative controls more proactive in nature; 3) created or updated the Job Aid for Baseline Impacting Changes; and 4) communicated to other staff within the RFC_URE3 Compliance Team. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017249 | CIP-011-2 | R1 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-011-2 R1. An IT manager found a document at a printer. The document contained log-in instructions and passwords for RFC_URE3 assets, one of which was associated with an in-scope BES Cyber Asset. The individual immediately provided the document to leadership to securely store. RFC_URE3 later determined that the document was printed by a database administrator, who had authorized access to the data, a current Personnel Risk Assessment, and CIP training. Furthermore, the database administrator had stored the document on his company-issued laptop and not in a CIP Information Repository (CIR) as required. The root cause of this noncompliance was the fact that RFC_URE3’s procedure for handling BES Cyber System Information did not include specific language related to password management. This lack of specificity resulted in the database administrator not taking appropriate steps to secure the information. This major contributing factor involves the management practice of information management, which includes ensuring the confidentiality of information items. The duration of the noncompliance was approximately one day. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE3 identified and corrected the issue quickly. Although the IT manager did not discover the document through a formal internal control, the fact that he quickly identified this as an issue and took it to his supervisor demonstrates a strong culture of compliance at RFC_URE3. Second, the document was on a printer that was located in a building with several layers of physical security. Third, even if a bad actor had obtained the document, the passwords alone would not have been enough to actually access the assets at issue because RFC_URE3 utilizes multi-factor authentication to grant access. No harm is known to have occurred. While the mitigation plan is being completed, RFC_URE3 has a number of mitigating measures in place to minimize risk such as: (1) elevated rights accounts on BES Cyber Assets require multi-factor authentication; (2) defined thresholds for unsuccessful authentication events and lockout parameters for the BES Cyber Asset; (3) failed authentication attempts which exceed the defined threshold are forwarded to the security event monitoring solution for logging and alerting notification; (4) logged security events that issue an alert prompt an investigation each business day and enable appropriate action; (5) in-scope Cyber Assets are configured to enforce a password change, or the obligation to change, at least every 15 calendar months; and, (6) physical security badges control access to buildings and floors. | To mitigate this noncompliance, RFC_URE3 will complete the following mitigation activities: 1) held a stand down on interim password management and storage options to the impacted department including all Database Administrators (DBAs) that can be implemented immediately; 2) created an action plan to evaluate password management solution(s) including: identification of key stakeholders and evaluation criteria; 3) will conduct an evaluation of password management solution(s), present the evaluation and recommendations to key stake holders, and select password management solution(s); 4) will generate a password management Training and Reference Material describing password management solution(s); 5) will generate a training deck on the password management solution(s) and provide training to individuals with access to passwords to elevated rights accounts on BES Cyber Assets; and 6) will review and update the relevant procedure to include language specific to password management. RFC_URE3 requires this time frame to complete the mitigating activities because the steps must be completed consecutively, rather than concurrently.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017504 | CIP-011-2 | R1 | RFC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-011-2 R1. During its first annual Transmission & Substation Cyber Vulnerability Assessment (CVA), RFC_URE3 discovered that a particular schematic was not identified as BES Cyber System Information (BCSI), and, consequently, was not labeled or stored appropriately. (The schematic depicts the port-table of one Ethernet switch.) The root cause of this noncompliance was the fact that this particular schematic was missed during RFC_URE3’s field verification walk-down of applicable systems in preparation for CIP v5. Because it was missed in this review, it was not identified as BCSI. This cause involves the management practice of information management, which includes classifying and protecting information items, and verification, in that RFC_URE3 failed to verify that it had included all applicable systems in its walk-down. The duration of the noncompliance was approximately eight months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the information contained in the schematic would only have allowed a bad actor to identify the site and connectivity of equipment there. The schematic did not contain any IP addresses, passwords, or other addition information needed to compromise the facility. Second, the schematic was stored on organization owned infrastructure accessible only to trusted employees or contractors performing work for RFC_URE3. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE3: 1) properly identified the missed schematic as BES Cyber System Information (BCSI) related to a Medium Impact BES Cyber System; 2) properly labeled the missed schematic containing BCSI as “CIP Protected Information”; 3) moved the schematic labeled as CIP Protected Information to the secure vault 4) created approach and define scope of a management system for engineering drawings to ensure that all BCSI meets program requirements; 5) performed analysis of this management system according to approach and scope identified in MS04; and 6) documented findings of management system analysis according to MS05 and, if applicable, implement a mitigation plan for identified areas of improvement.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017411 | CIP-004-6 | R4 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R4. For its quarterly access review, RFC_URE4 supervisors and Bulk Electric System Cyber Asset owners determine who should have access and the level of access based on the individual’s job function. RFC_URE4 then completes a “true-up” process that compares the personnel listed within the quarterly access review with the personnel listed in RFC_URE4’s access granting and revocation tracking system that identifies personnel with NERC access and also includes the associated authorization records. For discrepancies between the quarterly access review and access system lists, further reviews are conducted. During an internal quality assurance review, RFC_URE4 discovered that the fourth quarter review was not complete for a portion of the access records. More specifically, the security group, responsible for conducting the quarterly access review, requested the authorized access request records from the SCADA support group. RFC_URE4 then conducted its true-up process. However, prior to the SCADA support group submitting its data for the quarterly access review, it changed some access names (to designate type of access) for personnel without notifying the Administrator responsible for performing the true-up process. This change led to the inability of the Administrator to validate the access privileges of several High Impact users within the SCADA support group. As a result, the Administrator marked the true-up as incomplete until such time when the Administrator could verify the discrepancies, which occurred after the fourth quarter. The root cause was that the true-up process did not clearly define whether or not resolving these types of discrepancies were part of the quarterly verification and thus must be completed within the quarter. The noncompliance involves workforce management because additional training and clarity in the procedure could have helped prevent the noncompliance. The duration of the noncompliance was approximately two months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk of not completing a quarterly review is that the review would not identify previous errors in provisioning or removing access. The risk is mitigated here because RFC_URE4 quickly identified and mitigated the noncompliance, thus reducing the amount of time that there was an increased risk as a result of this noncompliance. Additionally, the SCADA support group did not change any access privileges. Rather, it changed only its naming conventions for types of access. Thus, there was no increased risk as a result of the change that unauthorized individuals would obtain access. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE4: 1) conducted an off-cycle quarterly access review true-up process; 2) updated the NERC Type Names to match the entitlement names in the access system and 3) updated the true-up review process to indicate when the review is deemed as complete. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017327 | CIP-004-6 | R5 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5. A contract employee of RFC_URE4 requested and was granted an extended leave of absence. Three days after the employee's last day of work prior to the leave of absence, the leader in charge of the contract worker determined that the contract employee’s NERC access should be revoked during the leave of absence. Thus, the leader requested that the employee’s access be terminated and, in the request, backdated the termination date to the employee's last day. The access revocation was completed, which was more than 24 hours after the contract employee’s termination date. The root cause was an unclear revocation process related to extended leaves of absence. This noncompliance involves the management practice of workforce management because additional training regarding specific scenarios when access revocation is necessary could have prevented this noncompliance from occurring. The duration of the noncompliance was approximately two days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that an individual who is no longer permitted to have access will use that access in a manner that will compromise the BPS. However, this risk was mitigated here because RFC_URE4 self-identified and mitigated the noncompliance within one day, thus reducing the amount of time the BPS was potentially put at an increased risk due to the noncompliance. Additionally, the reason for the employee’s termination was a leave of absence as opposed to a wrongful act that caused the employee to be terminated, thus reducing the likelihood that the employee would act in a way to compromise the BPS. Lastly, the employee had a current personnel risk assessment and his training was up to date. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE4: 1) updated the existing access evocation process to include specific scenarios, such as extended leave of absence, employee death, etc. so that the business unit leaders will know when access revocations are required and how to execute access revocations; and 2) communicated the updated access revocation process to all the business unit leaders to inform them of when and how to properly execute the access revocation process based on the scenarios from Milestone 1. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017373 | CIP-007-6 | R2 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-007-6 R2. RFC_URE4 determined that a planned outage at a power plant may be delayed. The purpose of the planned outage was to make changes to NERC-protected equipment. The subject matter expert determined that because of the delay, the mitigation plan for certain devices would not be completed by the due date. Upon this determination, the employee updated the mitigation plan with a new completion date and requested review and signature from the asset owner. RFC_URE4’s process requires the signature of both the asset owner and the CIP Senior Manager for any mitigation plan extension. However, regarding the root cause, the employee was unaware of the need for the signature from the CIP Senior Manager or delegate and therefore did not request the necessary signature until seven days later. This noncompliance involves the management practice of workforce management because additional training, along with a checklist or work instructions, could have prevented this occurrence. The duration of the noncompliance was approximately two days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, RFC_URE4 identified and mitigated the noncompliance within only two days of occurrence. Additionally, the RFC_URE4 expert completed most of the steps to extend the mitigation plan on time, including updating the mitigation plan prior to its expiration and having the asset owner approve and sign the updated Mitigation Plan. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) requested a mitigation plan extension; 2) reviewed the Potential Violation Lessons Learned during its weekly meeting and included the review of any future patching mitigation plans as a standing mitigating item on the weekly agenda; 3) created an onboarding checklist to better educate new hires of pertinent compliance requirements; and 4) completed the initial mitigation plan. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017374 | CIP-009-6 | R3 | RFC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-009-6 R3. RFC_URE4 failed to document and communicate lessons learned within the 90-day deadline. More specifically, RFC_URE4 tested several recovery plans using paper drills. RFC_URE4 documented those drills and informally shared the results with the drill participants. RFC_URE4 was required to update the recovery plans and notify relevant personnel of the updates 90 days from the date RFC_URE4 completed the drills. However, in calculating the deadline, the recovery procedure owner calculated three months from the date of the drills rather than 90 days. RFC_URE4 completed the updates and communicated the updates to the relevant personnel. The root causes were not having the CIP-009 R1 tasks in RFC_URE4’s NERC automatic task tracking and escalation process at the time the drills were completed. The drills were completed earlier than expected and thus the personnel responsible for updating the tracking system did not yet complete their task of including the CIP-009 tasks in the tracking system. This noncompliance involves the management practices of asset and configuration management and verification because RFC_URE4 failed to timely implement measures to verify manually calculated deadlines relating to its configuration items. The duration of the noncompliance was approximately four days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is prevention or delay in an entity’s response to a cyber-security incident as a result of not updating and communicating an up-to-date recovery plan within 90 days. However, RFC_URE4 was only two days late in updating its recovery plans and formally communicating the updates to relevant personnel. Additionally, RFC_URE4 informally communicated the results of the drills two days after completing the drills, thus reducing the potential that relevant personnel were not aware of lessons learned from the drills. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE4: 1) integrated the Recovery Plan workbook with the project schedule. Within the project, RFC_URE4 integrated the excel workbook specific to CIP 009 Recovery Plan tasks, into the project schedule; 2) modified the NERC task tracking mechanism to ensure that CIP 009 requirements are structured as interdependent tasks with due dates for successor tasks incorporated, tracked and visible once an initiating task has occurred; and 3) updated the Recovery Plan Program exercise templates. The CIP 009 templates act as both a checklist and evidence for recovery plan activities. Updating the templates to include CIP 009 R3 requirements will ensure clear expectations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017331 | CIP-010-2 | R1 | RFC_URE5 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1. During a review of their configuration baseline change management process, RFC_URE5 discovered a change management ticket showing that two baseline configuration changes were updated 5 days after the 30 calendar day deadline for completing the changes. The ticket at issue was created to update two database servers with the new approved security patches and software upgrades. While the update to the two baseline configuration changes occurred late, the change ticket was properly submitted and authorized for the security patches and software updates to be performed. During the same review of the configuration baseline changes management process, RFC_URE5 also discovered that an application was installed to help facilitate a change in PIN codes for RFC_URE5’s Physical Access Control systems (PACS), but the change ticket was never submitted to the group responsible for baseline updates. As a result, the baseline update was completed 8 days late. The root cause of this noncompliance was the fact that RFC_URE5's process for monitoring baseline changes for its PACs systems was not proactive enough from a preventative control perspective. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of first noncompliance was approximately five days. The duration of the second noncompliance was approximately seven days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk presented by this noncompliance relates to the fact that the baseline configurations were out-of-date, which could hinder RFC_URE5's ability to properly test planned changes or respond to unexpected changes to its system. The fact that RFC_URE5 quickly detected and corrected the issues through effective internal controls minimized the window of time that out-of-date baselines could have hindered RFC_URE5's ability to analyze unexpected changes to the system. Second, these planned changes were properly authorized prior to being implemented, which minimized the likelihood that they could have had an adverse effect on RFC_URE5's system. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE5: 1) conducted training with impacted personnel. Lessons learned will be shared to keep track of the changes and the 30 calendar day window of opportunity and to create awareness on the applicable aspects of this standard CIP-010; 2) implemented reporting to monitor PACS baseline on a bi-weekly basis to make their preventative controls more proactive in nature; 3) created or updated the Job Aid for Baseline Impacting Changes; and 4) communicated to other staff within the RFC_URE5 Compliance Team. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017447 | CIP-006-6 | R2 | RFC_URE6 submitted a Self-Report stating that it was in noncompliance with CIP-006-6 R2. An RFC_URE6 contracted cleaning vendor employee who was authorized for unescorted physical access to CIP Physical Security Perimeters (PSPs) did not continuously escort his supervisor, an unauthorized party, for sixty-eight seconds in a Control Center administrative office/support area. The cleaning vendor employee accidentally left his supervisor unescorted while he briefly left the room for 68 seconds. The cleaning vendor employee’s supervisor was a visitor and not authorized for unescorted physical access in that area. RFC_URE6 security personnel identified this noncompliance within eight hours after the incident during a review of security camera recordings for an unrelated investigation of cleaning supplies left in a hallway. This noncompliance involves the management practices of external interdependencies management, and workforce management. External interdependencies management is involved because RFC_URE6’s cleaning vendor was responsible for the breach of procedure and the RFC_URE6 cleaning vendor employee did not follow RFC_URE6’s visitor escorting procedure. Workforce management is involved because RFC_URE6 staff failed to properly train contractor employees regarding unescorted physical access. That failure to properly train is the root cause of this noncompliance. The duration of the noncompliance was approximately one day. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is permitting unauthorized individuals to access Bulk Electric System (BES) Cyber Systems without supervision. The risk is minimized because the supervisor was left unsupervised for a short amount of time, only sixty-eight seconds, in the Control Center administrative office/support area. Given the short amount of time the supervisor was left unsupervised and that he was left unsupervised in an administrative office area, it would have been very difficult for the supervisor to access BES Cyber Systems and cause any damage. Additionally, the supervisor had passed a criminal background check and a drug screening. RFC_URE6’s detective controls are working effectively as they were able to identify a noncompliance that lasted only a little longer than one minute and RFC_URE6 security personnel discovered this issue within eight hours after the noncompliance occurred. No harm is known to have occurred. | As an immediate corrective action, RFC_URE6 management informed the cleaning vendor supervisors that their cleaning personnel were prohibited from escorting visitors in RFC_URE6 PSPs until the issue was investigated and resolved. Cleaning Vendor supervisors notified their cleaning personnel of this prohibition. On-shift cleaning personnel were immediately notified, and other cleaning personnel were notified before they started cleaning duties on their next shifts. This escorting prohibition stayed in place until applicable preventive measures were completed. To mitigate this noncompliance, RFC_URE6: 1) required the cleaning vendor personnel with PSP access to retake the two training presentations that included PSP visitor escorting and access requirements; 2) provided a written notification to the contracted cleaning vendor that another escorting or access incident would result in immediate removal of the responsible individual’s access to RFC_URE6 facilities and the individual would not be permitted to perform work for RFC_URE6; and 3) conducted an “all hands” meeting with cleaning vendor personnel to emphasize the importance of following company procedures especially related to Escorting and Visitor access. This meeting underscored the need to obtain approval from RFC_URE6 management for any visitors entering the Control Center.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017017506 | CIP-004-3a | R2 | RFC_URE7 submitted a Self-Report stating that it was in noncompliance with CIP-004-3a R2. The online training center Administrator validated a joint operating company employee’s Cyber and Physical Security training as having been completed, although the employee did not complete his annual security training. The Administrator accidentally used the employee’s brother’s training date. The brother, who is also an employee of the joint operating company, had completed the training, and thus the Administrator incorrectly entered that training date to validate training for the first employee. A replacement badge request prompted a review of the employee’s training transcript, which led to the discovery of the invalid training date. Upon discovery, access was revoked. Subsequently, the individual completed his annual training for the following year and RFC_URE7 restored his access. The cause of the noncompliance was lack of verification controls to prevent improper training validation when multiple individuals have the same last name. This noncompliance involves the management practice of verification, which includes having steps to confirm that information is accurate before taking an action based on that information. The duration of the noncompliance was approximately seven months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This was a trusted employee who completed annual security training four times prior. Additionally, in addition to the annual security training, employees are trained through other means throughout the year on CIP-related topics. For the year in question, RFC_URE7 held eight training sessions on various CIP topics for the group in which the employee at issue worked. Lastly, RFC_URE7 self-identified and mitigated the noncompliance within six months, thus reducing the period of time that there was any increased risk as a result of the noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE7: 1) created a training validation policy and included cross reference of full name and online training center ID; 2) published an updated document to Policies and Procedures SharePoint; 3) trained staff on updated process; and 4) evaluated the potential to do periodic training data comparisons between training and access request systems.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2017017330 | CIP-010-2 | R1 | RFC_URE8 submitted a Self-Report stating that it was in noncompliance with CIP-010-2 R1. During a review of their configuration baseline change management process, RFC_URE8 discovered a change management ticket showing that two baseline configuration changes were updated 5 days after the 30 calendar day deadline for completing the changes. The ticket at issue was created to update two database servers with the new approved security patches and software upgrades. While the update to the two baseline configuration changes occurred late, the change ticket was properly submitted and authorized for the security patches and software updates to be performed. During the same review of the configuration baseline changes management process, RFC_URE8 also discovered that an application was installed to help facilitate a change in PIN codes for RFC_URE8’s Physical Access Control systems (PACS), but the change ticket was never submitted to the group responsible for baseline updates. As a result, the baseline update was completed 8 days late. The root cause of this noncompliance was the fact that RFC_URE8's process for monitoring baseline changes for its PACs systems was not proactive enough from a preventative control perspective. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of first noncompliance was approximately five days. The duration of the second noncompliance was approximately seven days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk presented by this noncompliance relates to the fact that the baseline configurations were out-of-date, which could hinder RFC_URE8's ability to properly test planned changes or respond to unexpected changes to its system. The fact that RFC_URE8 quickly detected and corrected the issues through effective internal controls minimized the window of time that out-of-date baselines could have hindered RFC_URE8's ability to analyze unexpected changes to the system. Second, these planned changes were properly authorized prior to being implemented, which minimized the likelihood that they could have had an adverse effect on RFC_URE8's system. No harm is known to have occurred. | To mitigate this noncompliance, RFC_URE8: 1) conducted training with impacted personnel. Lessons learned will be shared to keep track of the changes and the 30 calendar day window of opportunity and to create awareness on the applicable aspects of this standard CIP-010; 2) implemented reporting to monitor PACS baseline on a bi-weekly basis to make their preventative controls more proactive in nature; 3) created or updated the Job Aid for Baseline Impacting Changes; and 4) communicated to other staff within the RFC_URE8 Compliance Team. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2017017453 | CIP-002-5.1 | R2; R2.2 | SERC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. SERC_URE1 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months. SERC_URE1’s compliance and operations contractor initiated its annual internal assessment of SERC_URE1’s existing CIP Version 5 compliance evidence. A few days later, SERC_URE1's compliance and operations contractor discovered SERC_URE1 had performed an evaluation of its assets, but its impact evaluation document incorrectly listed the facility manager as the approval authority instead of the CIP Senior Manager or delegate. However, SERC_URE1’s overarching procedure required the CIP Senior Manager to review and approve the impact evaluation. On the same day, SERC_URE1's compliance and operations contractor conducted an extent of condition review. As required by its internal control procedure, the contractor's reliability compliance managers conducted internal assessments of all applicable NERC Reliability Standards that require CIP Senior Manager oversight or approval, for all registered entities that the contractor provided compliance services for. The contractor found similar noncompliances at multiple other entities, including some registered in the SERC region. The impacted registered entities self-reported these discovered noncompliances, as well. Approximately two weeks later, SERC_URE1 updated its impact evaluation document and SERC_URE1’s CIP Senior Manager signed it. The root cause of this noncompliance was SERC_URE1’s lack of management oversight, inadequate procedures, and lack of suitable internal controls (e.g., reminders or alerts), to ensure that SERC_URE1 adhered to the time-sensitive approval. This noncompliance lasted approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to have its CIP Senior Manager or delegate approve its Bulk Electric System (BES) Cyber System list could indicate inadequate cyber security controls that could lead to compromise or misuse that could affect the real-time operation of the BPS. However, this noncompliance was an administrative failure since the facility manager reviewed and signed the identifications and there were no changes to the list when the CIP Senior Manager reviewed and signed it. SERC_URE1 periodically reviewed the list of BES Cyber Systems to ensure the proper identification and categorization of Cyber Assets. SERC_URE1 only has one Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE1: 1) completed the BES Cyber Systems identification document and had its CIP Senior Manager approve it; 2) implemented a new impact evaluation tool and revised the CIP-002 procedure to incorporate the tool. Both clearly state that the CIP Senior Manager (or delegate) is the approval authority; 3) trained plant personnel, owner's asset managers, and compliance staff on this issue; 4) reviewed signature requirements for CIP-002 and CIP-003 for facilities with Low Impact BES Cyber Systems; 5) revised the conflicting documentation guidance, in the CIP-002 procedure, to delineate the required signatories; 6) implemented an "at-a-glance" dashboard to help all concerned personnel quickly review compliance status; and 7) implemented a recurring calendar item for its CIP Senior Manager to review the dashboard on a monthly basis and send out reminders of upcoming due dates to the facility (within 3 months of being due).
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2017017540 | CIP-004-6 | R5; P5.1 | SERC_URE2 submitted a Self-Report stating that it was in noncompliance with CIP-004-6 R5.1. SERC_URE2 did not initiate the removal of an individual’s unescorted physical access permissions upon resignation, and did not complete the removals within 24 hours of the resignation. The SERC_URE2 NERC compliance officer discovered that SERC_URE2 did not revoke unescorted physical access for an employee who voluntarily resigned from SERC_URE2 approximately one week earlier. The resigned employee’s manager approached the NERC compliance officer about how to relinquish the badge, which he had retrieved from the employee on the same day as the resignation. SERC_URE2 maintained an access management program, which required the manager, upon any termination, to initiate access revocations through all applicable systems. The manager held the badge, but did not act to revoke access permissions or document any actions taken to initiate the removal of the ability to access. This employee had physical access to a few Medium Impact Systems split between a primary control center system and a backup control center system. SERC_URE2 conducted an extent-of-condition assessment by having all supervisors with employees or personnel having access to PSPs review all termination actions. SERC_URE2 concluded that it properly revoked access permissions for all other termination actions within the prescribed timeframes. The cause of this noncompliance was insufficient training which led to the manager failing to follow the SERC_URE2 access revocation process and initiate access revocations. This noncompliance lasted approximately five days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2's failure to revoke access permissions within 24 hours of resignation gave a former employee the opportunity to access the SERC_URE2 control centers and the energy management system, either of which the former employee could have compromised or manipulated to negatively impact the BPS. However, SERC_URE2 retrieved the resigning employee’s access badge upon resignation and the employee did not have remote interactive access rights. SERC_URE2 only took five extra days to revoke all physical access permissions for the resigning employee. The resigning employee only had physical access, was current on cyber security training, had a valid personnel risk assessment, and was in good standing with SERC_URE2. SERC_URE2 had established Physical Security Perimeters with logging an alerting, as well as established Electronic Security Perimeters to alert upon any unauthorized access or physical reconfigurations of Bulk Electric System (BES) Cyber Systems or BES Cyber Assets. No harm is known to have occurred. SERC considered SERC_URE2’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE2: 1) reinforced the mandates of CIP-004-6 R5.1 and of the relevant SERC_URE2 procedure. The responsible manager completed the access revocation form and revoked the employee’s access; and 2) provided reinforcement training to all personnel that are required to maintain compliance with the NERC CIP standards concerning access management.
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2017017489 | CIP-002-5.1 | R2; R2.2 | SERC_URE3 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. SERC_URE3 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months. SERC_URE3’s compliance and operations contractor, initiated its annual internal assessment of SERC_URE3’s existing CIP Version 5 compliance evidence. Two days later, SERC_URE3's compliance and operations contractor discovered SERC_URE3 had performed an evaluation of its assets, but its impact evaluation document incorrectly listed the facility manager as the approval authority instead of the CIP Senior Manager or delegate. However, SERC_URE3’s overarching procedure required the CIP Senior Manager to review and approve the impact evaluation. On the same day, SERC_URE3's compliance and operations contractor conducted an extent of condition review. As required by its internal control procedure, the contractor's reliability compliance managers conducted internal assessments of all applicable NERC Reliability Standards that require CIP Senior Manager oversight or approval, for all registered entities that the contractor provided compliance services for. The contractor found similar noncompliances at multiple other entities, including some registered in the SERC region. The impacted registered entities self-reported these discovered noncompliances, as well. Approximately two weeks later, SERC_URE3 updated its impact evaluation document and SERC_URE3’s CIP Senior Manager signed it. The root cause of this noncompliance was SERC_URE3’s lack of management oversight, inadequate procedures and lack of suitable internal controls, to ensure that SERC_URE3 adhered to the time-sensitive approval. This noncompliance lasted approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE3’s failure to have its CIP Senior Manager or delegate approve its Bulk Electric System (BES) Cyber System list could indicate inadequate cyber security controls that could lead to compromise or misuse that could affect the real-time operation of the BPS. However, this noncompliance was an administrative failure since the facility manager reviewed and signed the identifications, and there were no changes to the list when the CIP Senior Manager reviewed and signed it. SERC_URE3 has one Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE3’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE3: 1) completed the BES Cyber Systems identification document and had its CIP Senior Manager approve it; 2) implemented a new impact evaluation tool and revised the CIP-002 procedure to incorporate the tool. Both clearly state that the CIP Senior Manager (or delegate) is the approval authority; 3) implemented an "at-a-glance" dashboard to help all concerned personnel quickly review compliance status; and 4) implemented a recurring calendar item for its CIP Senior Manager to review the dashboard on a monthly basis and send out reminders of upcoming due dates to the facility (within three months of being due).
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2017017478 | CIP-002-5.1a | R2; R2.2 | SERC_URE4 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1a R2.2. SERC_URE4 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 within 15 months of the previous approval. Approximately 1.5 years earlier, SERC_URE4’s CIP Senior Manager approved the identifications of its Bulk Electric System (BES) Cyber Systems, by signing its impact evaluation form. However, SERC_URE4 failed to have its CIP Senior Manager approve the impact evaluation form within 15 calendar months thereafter. SERC_URE4 discovered this noncompliance when conducting an extent of condition review in response to a similar noncompliance discovered at another facility managed by SERC_URE4’s compliance and operations contractor. That same day, SERC_URE4’s CIP Senior Manager approved the identifications of its BES Cyber Systems by signing the impact evaluation form, approximately three months late. The apparent cause of this noncompliance was SERC_URE4’s lack of management oversight and inadequate proactive internal controls. This noncompliance lasted approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4’s failure to have its CIP Senior Manager or delegate approve its BES Cyber System list at least once every 15 calendar months could indicate inadequate cyber security controls that could lead to compromise or misuse that could affect the real-time operation of the BPS. However, this was an administrative failure because the CIP Senior Manager signed the identification list late, but SERC_URE4 did not make any changes to its list when the CIP Senior Manager reviewed and signed it. SERC_URE4 has only Low Impact BES Cyber Systems. No harm is known to have occurred. SERC considered SERC_URE4’s CIP-002-3 R1 compliance history in determining the disposition track. SERC determined that SERC_URE4’s CIP-002-3 R1 compliance history should not serve as a basis for applying a penalty. The mitigating activities for the prior noncompliance would not have prevented the instant noncompliance. | To mitigate this noncompliance, SERC_URE4: 1) had its CIP Senior Manager approve and sign the impact evaluation evidence form; 2) implemented a new impact evaluation tool and revised the CIP-002 procedure to incorporate the tool; 3) implemented an "at-a-glance" dashboard to help all concerned personnel quickly review compliance status; 4) implemented a recurring calendar reminder for its CIP Senior Manager to review the dashboard on a monthly basis, and send out reminders of upcoming due dates to the facility (within three months of being due); 5) established a recurring maintenance item in its computerized maintenance management system to ensure the completion of the new evaluations within the 15-month window of the previous approval; and 6) trained managers, compliance staff, and plant personnel on this issue, and reviewed signature requirements for CIP-002 and CIP-003 for facilities with Low Impact BES Cyber Systems.
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2017017670 | CIP-003-6 | R1 | SERC_URE5 submitted a Self-Certification stating that it was in noncompliance with CIP-003-6 R1.2. SERC_URE5 did not have CIP Senior Manager approval for its Low Impact Bulk Electric System (BES) Cyber System policies. SERC_URE5 tasked a few employees to create a compliance program in order to meet the CIP-003-6 R1.2 compliance effective date. The tasked employees left SERC_URE5 prior to the compliance effective date. SERC_URE5 held its annual CIP-002 review meeting. In that meeting, SERC_URE5 discussed the approaching deadline for the upcoming CIP requirements. The next month, SERC_URE5 conducted a separate meeting to discuss the outcome of a supervisory control and data acquisition (SCADA) assessment that included electronic access to the Low Impact site, where attention was again brought up to the CIP requirements that were coming into effect. SERC_URE5 has one BES Cyber System at one Low Impact site. SERC_URE5 did not have a cyber security policy approved by its CIP Senior Manager, as required in CIP-003-6 R1.2 by the compliance effective date. Approximately two months later, SERC_URE5 created its cyber security plan. This cyber security plan did not have a Cyber Security Incident Response plan that referenced BES Cyber Security and its requirements, but instead referenced its EOP-004-2 Event Reporting Procedure. In addition, SERC_URE5’s Chief Operating Officer signed the cyber security plan, but its CIP Senior Manager did not, as required under CIP-003-6 R1.2. SERC_URE5 designated its manager of electric systems operations as its CIP Senior Manager. The apparent cause of this noncompliance is lack of management oversight and confusion about what the CIP-003-6 R1.2 Standard required. This noncompliance lasted approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE5’s failure to have its CIP Senior Manager or delegate’s approval for its Low Impact BES Cyber System cyber security policies, could lead to the application of inadequate or non-existent cyber security controls that could result in compromise or misuse of BES Cyber Systems and thereby affect the real-time operation of the BPS. However, SERC_URE5’s Low Impact BES Cyber System does not have External Routable Connectivity and any risk to the BES would require physical access. Physical controls were in place but not documented. In the event of a misoperation, SERC_URE5 designed its Low Impact BES Cyber System to trip upstream for protection, isolating the same segment of the BPS. Multiple misoperations would be required to impact more than SERC_URE5's Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE5’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE5: 1) applied to deregister one of its registered functions. 2) has an annually reviewed Internal Compliance Program (ICP). SERC_URE5 changes that would require them to re-register one of its currently registered functions would be captured in this review.
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2017017671 | CIP-003-6 | R2 | SERC_URE5 submitted a Self-Certification stating that it was in noncompliance with CIP-003-6 R2. SERC_URE5 did not implement one or more documented cyber security plan(s) for its Low Impact Bulk Electric System (BES) Cyber System(s) that include the sections in Attachment 1. SERC_URE5 tasked a few employees to create a compliance program in order to meet the CIP-003-6 R1.2 compliance effective date. The tasked employees left SERC_URE5 prior to the compliance effective date. SERC_URE5 held its annual CIP-002 review meeting. In that meeting, SERC_URE5 discussed the approaching deadline for the upcoming CIP requirements. The next month, SERC_URE5 conducted a separate meeting to discuss the outcome of a supervisory control and data acquisition (SCADA) assessment that included electronic access to the Low Impact site, where attention was again brought up to the CIP requirements that were coming into effect. SERC_URE5 has one BES Cyber System at one Low Impact site. SERC_URE5 did not have any documented cyber security plans for its low impact BES Cyber Systems that included the sections in Attachment 1, as required in CIP-003-6 R2 by the compliance effective date. Approximately two months later, SERC_URE5 created its cyber security plan. This cyber security plan did not have a Cyber Security Incident Response plan that referenced BES Cyber Security and its requirements, but instead referenced its EOP-004-2 Event Reporting Procedure. The apparent cause of this noncompliance is lack of management oversight and confusion about what the CIP-003-6 R2 Standard required. This noncompliance lasted approximately three months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE5’s failure to implement a documented cyber security plan for its Low Impact BES Cyber System could lead to the application of inadequate or non-existent cyber security controls that could result in compromise or misuse of BES Cyber Systems and thereby affect the real-time operation of the BPS. However, SERC_URE5’s Low Impact BES Cyber System does not have External Routable Connectivity and any risk to the BES would require physical access. Physical controls were in place but not documented. In the event of a misoperation, SERC_URE5 designed its Low Impact BES Cyber System to trip upstream for protection, isolating the same segment of the BPS. Multiple misoperations would be required to impact more than SERC_URE5's Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE5’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE5: 1) applied to deregister one of its registered functions. 2) has an annually reviewed Internal Compliance Program (ICP). SERC_URE5 changes that would require them to re-register one of its currently registered functions would be captured in this review.
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 6 (SERC_URE6) | NCRXXXXX | SERC2017017490 | CIP-002-5.1 | R2; R2.2 | SERC_URE6 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. SERC_URE6 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months. SERC_URE6’s compliance and operations contractor initiated its annual internal assessment of SERC_URE6’s existing CIP Version 5 compliance evidence. A few days later, SERC_URE6's compliance and operations contractor discovered SERC_URE6 had performed an evaluation of its Bulk Electric System (BES) assets, but SERC_URE6’s CIP Senior Manager did not approve the list by signing the impact evaluation document. SERC_URE6’s impact evaluation document template, as well as SERC_URE6's overarching procedure, required the CIP Senior Manager to review and approve the impact evaluation, but the facility manager had signed the evidence document instead of the CIP Senior Manager. On the same day, SERC_URE6's compliance and operations contractor conducted an extent of condition review. As required by its internal control procedure, the contractor's reliability compliance managers conducted internal assessments of all applicable NERC Reliability Standards that require CIP Senior Manager oversight or approval, for all registered entities that the contractor provided compliance services for. The contractor found similar noncompliances at multiple other entities, including some registered in the SERC region. The impacted registered entities self-reported these discovered noncompliances, as well. Approximately two weeks later, SERC_URE6’s CIP Senior Manager approved and signed the impact evaluation evidence document. The root cause of this noncompliance was SERC_URE6’s lack of management oversight and lack of suitable internal controls, to ensure that SERC_URE6 adhered to the time-sensitive approval. This noncompliance lasted approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE6’s failure to have its CIP Senior Manager or delegate approve its BES Cyber System list could indicate inadequate cyber security controls that could lead to compromise or misuse that could affect the real-time operation of the BPS. However, this was an administrative failure since the facility manager reviewed and signed the identifications and there were no changes to the list when the CIP Senior Manager reviewed and signed it. SERC_URE6 has one Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE6’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE6: 1) had its CIP Senior Manager complete and approve the impact evaluation evidence document; 2) implemented a new impact evaluation tool and revised the CIP-002 procedure to incorporate the tool. Both clearly state that the CIP Senior Manager (or delegate) is the approval authority; 3) implemented an "at-a-glance" dashboard to help all concerned personnel quickly review compliance status; and 4) had its CIP Senior Manager implement a recurring calendar item to review the dashboard on a monthly basis to send out reminders of upcoming due dates to the facility (within three months of being due).
2017-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 7 (SERC_URE7) | NCRXXXXX | SERC2017017491 | CIP-002-5.1 | R2; R2.2 | SERC_URE7 submitted a Self-Report stating that it was in noncompliance with CIP-002-5.1 R2.2. SERC_URE7 did not have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months. SERC_URE7’s compliance and operations contractor initiated its annual internal assessment of SERC_URE7’s existing CIP Version 5 compliance evidence. A few days later, SERC_URE7's compliance and operations contractor discovered SERC_URE7 had performed an evaluation of its Bulk Electric System (BES) assets, but SERC_URE7’s CIP Senior Manager did not approve the list by signing the impact evaluation document. SERC_URE7’s impact evaluation document template, as well as, SERC_URE7's overarching procedure required the CIP Senior Manager to review and approve the impact evaluation, but the facility manager had signed the evidence document instead of the CIP Senior Manager. On the same day, SERC_URE7's compliance and operations contractor conducted an extent of condition review. As required by its internal control procedure, the contractor's reliability compliance managers conducted internal assessments of all applicable NERC Reliability Standards that require CIP Senior Manager oversight or approval, for all registered entities that the contractor provided compliance services for. The contractor found similar noncompliances at multiple other entities, including some registered in the SERC region. The impacted registered entities self-reported these discovered noncompliances, as well. Approximately two weeks later, SERC_URE7’s CIP Senior Manager approved and signed the impact evaluation evidence document. The root cause of this noncompliance was SERC_URE7’s lack of management oversight and lack of suitable internal controls, to ensure that SERC_URE7 adhered to the time-sensitive approval. This noncompliance lasted approximately ten months. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE7’s failure to have its list of identified BES assets approved by the CIP Senior Manager or delegate could indicate inadequate cyber security controls that could lead to compromise or misuse that could affect the real-time operation of the BPS. However, this noncompliance was an administrative failure since the facility manager reviewed and signed the identifications and there were no changes to the list when the CIP Senior Manager reviewed and signed it. SERC_URE7 has one Low Impact BES Cyber System. No harm is known to have occurred. SERC considered SERC_URE7’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SERC_URE7: 1) had its CIP Senior Manager complete and approve the impact evaluation evidence document; 2) implemented a new impact evaluation tool and revised the CIP-002 procedure to incorporate the tool. Both clearly state that the CIP Senior Manager (or delegate) is the approval authority; 3) implemented an "at-a-glance" dashboard to help all concerned personnel quickly review compliance status; and 4) had its CIP Senior Manager implement a recurring calendar item to review the dashboard on a monthly basis to send out reminders of upcoming due dates to the facility (within three months of being due).
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017017220 | CIP-011-2 | R1; R1.2 | SPPRE_URE1 submitted a Self-Report stating that, as a Transmission Owner and Transmission Operator, it had an issue of noncompliance with CIP-011-2 R1.2 because an SPPRE_URE1 CIP contractor did not protect SPPRE_URE1 BES Cyber System Information in accordance with SPPRE_URE1’s CIP information protection program (Program). SPPRE_URE1’s Program requires BES Cyber System Information that is transmitted to authorized end users via email to be encrypted, or include a link to a file containing such information, which can be retrieved only by end users who have authorized access to the file. One of two SPPRE_URE1 Contractors that frequently work together on SPPRE_URE1 CIP-related projects (Contractor #1) transmitted BES Cyber System Information, i.e., SCADA information associated with a substation with a medium impact rating, in unencrypted form via an email attachment to the other contractor (Contractor #2). Contractor #1 had authorized access to the BES Cyber System Information. Although Contractor #2 was previously authorized to have access to the CIP information, his access had been revoked approximately two months prior to the transmittal of the email because he transferred to a position that did not require access to such information. At the time of the email transmittal, both contractors were working together on general scoping issues related to the same project. Contractor #1 requested a more thorough assessment from Contractor #2 and transmitted the BES Cyber System Information to Contractor #2 so that the project scope could be finalized. Contractor #1 did not adhere to SPPRE_URE1’s Program because the BES Cyber System Information he transmitted to Contractor #2 was unencrypted, and Contractor #2 was not authorized to have access to such information. The duration of this instance of noncompliance is one day, beginning and ending on the date Contractor #1 transmitted the BES Cyber System Information via email to Contractor #2, who no longer had authorized access to such information. The root cause of this instance of noncompliance was human error due to SPPRE_URE1's contractors not adhering to SPPRE_URE1’s Program. The contractors were retrained on SPPRE_URE1’s Program, which included the type of CIP information that must be protected and the procedures to protect such information. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to protect all BES Cyber System Information has the potential to affect the reliable operation of the BPS by providing an opportunity for BES Cyber System Information to be revealed to unauthorized individuals, which could compromise BES Cyber Systems and lead to misoperation or instability in the BES. Notwithstanding, Contractor #2, had recently left SPPRE_URE1 employment to work for the SPPRE_URE1 contractor company; a current Personnel Risk Assessment was on file for Contractor #2; Contractor #2 had completed the most recent NERC CIP security training; and he had authorized access to BES Cyber System Information approximately two months prior to receiving such information. Additionally, the BES Cyber System Information was transmitted between two SPPRE_URE1 email addresses utilizing Transport Layer Security, which reduced the risk of third-party access to the information. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) gave a presentation to all SPPRE_URE1 contractors who might come in contact with BES Cyber System Information regarding data loss prevention; 2) published a newsletter entitled “Data Loss Prevention”, which emphasized the importance of correctly handling confidential information, and where to get additional information regarding the Program; and 3) retrained Contractors #1 and #2 by requiring them to retake its NERC CIP Information Protection Program course. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2017016828 | CIP-004-6 | R5 | SPPRE_URE2 submitted a Self-Report stating that, it had an issue of noncompliance with CIP-004-6 R5.1 because it did not revoke Interactive Remote Access privileges for a summer intern within 24 hours of termination. The root cause of this instance of noncompliance was that the protocol for access revocation for summer interns was different than the process used for staff terminations and did not account for the 24 hour revocation timeline when personnel are unavailable to revoke access during weekends and holidays. For standard employee terminations, the Human Resources (HR) department submits a notice via an electronic paging application, which begins the account deactivation and alerts IT Security of the termination and access revocation. However, when summer interns end employment, the HR department sends a notice through its HR application to the IT Help Desk. When a summer intern terminated her employment with SPPRE_URE2 and the HR department sent notice through the HR application to the IT Help Desk on a Friday, the IT Help Desk was not aware of the notice of termination until the following Monday. The intern’s Interactive Remote Access was disabled at that time. The duration of this instance of noncompliance was three days, from 24 hours after the summer intern’s termination actions occurred, through the date the summer intern’s Interactive Remote Access was removed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to remove an employee’s Interactive Remote Access within 24 hours of termination could lead to unauthorized access to critical cyber assets. Notwithstanding, the summer intern never had physical or electronic access to any CIP assets while employed at SPPRE_URE2. She was granted an Active Directory account, which allowed her read-only access to SPPRE_URE2’s CIP documents. Upon termination, even though her Active Directory account was not disabled, she had no electronic means to access any CIP information or CIP assets. Additionally, the summer intern was not fired for cause, but left to return to school. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2 modified its Summer Intern Termination/Exit Process to follow the standard Employee Termination Process. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2017017433 | CIP-002-5.1 | R2 R2.2 | SPPRE_URE3 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-5.1 R2.2. Although SPPRE_URE3’s procedure governing its BES Cyber System impact evaluation correctly identified the CIP Senior Manager as the responsible party for approving the evaluation of BES Cyber Systems, the template used by SPPRE_URE3 to document the evaluation incorrectly identified its facility manager as the approval authority. As a result, SPPRE_URE3’s facility manager and not its CIP Senior Manager, approved the impact evaluation of its BES Cyber Systems. The duration of this instance of noncompliance was approximately 9.8 months, from the date CIP-002-5.1 became mandatory and enforceable, through the date SPPRE_URE3 completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was a documentation error in the template used by SPPRE_URE3 to document compliance with CIP-002-5.1 R2.1. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to have the CIP Senior Manager approve the impact evaluation of BES Cyber Systems has the potential to affect the reliability of the BPS by increasing the risk that BES Cyber Systems will not be identified and afforded the protections required by the CIP Reliability Standards. Here, but for the administrative error resulting in the impact evaluation being approved by the facility manager and not the CIP Senior Manager, the impact evaluation was performed consistent with the requirements of CIP-002-5.1 R2.1. The results of the impact evaluation did not change due to the administrative error and only low impact BES facilities were identified. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) implemented an impact evaluation tool for CIP-002 requiring approval by the CIP Senior Manager; 2) revised its CIP-002 procedure to clearly indicate that CIP Senior Manager approval of the impact evaluation is required; 3) completed an impact evaluation that was approved by the CIP Senior Manager; 4) created an “at-a-glance” dashboard to increase awareness of compliance status and required the Headquarters (HQ) NERC CIP Manager to review the dashboard on a monthly basis; and 5) implemented a requirement for the HQ NERC CIP Manager to send out reminders of upcoming compliance due dates to facilities (within 3 months of being due). SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2017017048 | CIP-003-3 | R2; R2.2 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-003-3 R2.2 because it did not properly document a change in the assignment of the CIP Senior Manager within thirty calendar days. The duration of this instance of noncompliance was approximately 9.8 months, from the date by which SPPRE_URE4 should have documented its change in the assignment of the CIP Senior Manager, through the date SPPRE_URE4 completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was a lack of process controls requiring changes in the assignment of the CIP Senior Manager to be formally documented within thirty calendar days from a change. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely document a change to the assignment of the CIP Senior Manager has the potential to affect the reliability of the BPS by increasing the potential that an organization’s cyber security program will not receive the prominence necessary to ensure the security of cyber assets and the BPS. Notwithstanding SPPRE_URE4’s failure to properly document the assignment of its CIP Senior Manager, it was SPPRE_URE4’s intent to designate its General Manager as its CIP Senior Manager, and for the duration of the noncompliance, the General Manager was performing the duties of the CIP Senior Manager. The risk to the BPS was further mitigated because the General Manager is the chief executive officer of the organization, and SPPRE_URE4 corrected the documentation error immediately after its discovery during an internal review. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE4: 1) documented the assignment of the CIP Senior Manager; and 2) documented a requirement for changes in the assignment of the Senior CIP Manager to be documented within 30 calendar days of the effective date of the change. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017387 | CIP-010-2 | R1; Part 1.3 | During a Compliance Audit, WECC determined that WECC_URE1,had an issue with CIP-010-2 R1 Part 1.3. During WECC_URE1’s CIP audit, it was identified that WECC_URE1 failed to update the baseline configuration as necessary within 30 calendar days of completing a change that deviated from the baseline configuration for one port on a BES Cyber Asset (BCA) at a HIBCS. The auditors determined that the open port, was not documented on WECC_URE1’s ports and services list submitted as audit evidence. WECC_URE1 made a change relating to the port that did not transition to the baseline configuration because the individual responsible for manually entering port data into the CIP SharePoint database did not enter the specific port; therefore, did not get added to the list of ports and services. The port on the BCA was necessary to monitor connectivity to the EMS servers and workstations. The root cause of this issue was a process design flaw. Specifically, WECC_URE1 used a monthly automated port comparison process that cannot find discrepancies because it compares to the previous month and not the SharePoint data (baseline). WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable and ended when WECC_URE1 updated its CIP SharePoint database to correctly indicate the portas ‘in-service’, for a total of 283 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to update the baseline configuration as necessary within 30 calendar days of completing a change that deviated from the baseline configuration for one device in its HIBCS. Such failure could result in BES Cyber Assets ports and services being either enabled or disabled as they would not be accounted for on the approved baselines. Additionally, this failure could result in WECC_URE1 failing to detect malicious applications and/or malicious communications. This would lead to substantial effects on the application functionality of a BES Cyber Asset and its communication with applications and other BES Cyber Assets, which could potentially affect the reliability of the BES. However, WECC_URE1 had implemented documented processes for updating changes to the baseline configuration and also utilized a SharePoint workflow. Each logical network accessible port was needed for legitimate application or services in the support of the Cyber Assets that support BES functions. This issue is simply a documentation error and considered administrative in nature because WECC_URE1 did not update or maintain its baseline documentation to reference the running ports and services. For these reasons, WECC determined that the risk had a minimal likelihood of occurring. No harm is known to have occurred. WECC_URE1 had no prior noncompliance with this Standard and Requirement. | To mitigate this issue, WECC_URE1: 1) updated its CIP SharePoint database to correctly indicate the port in question as ‘in-service’; 2) performed a review of all baseline entries listed in its CIP SharePoint database against its most recent baseline scans to ensure the accuracy of documentation; and 3) updated its change management procedure to include any addition or removal of ports as a change, which will automatically send an email notification to the designated approver to take action.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016460 | CIP-007-6 | R5; Part 5.4 | During a Compliance Audit, WECC determined that WECC_URE2 had an issue with CIP-007-6 R5 Part 5.4. WECC_URE2 failed to change the default passwords on two digital fault recorders classified as Protected Cyber Assets (PCAs) and one relay classified as a Bulk Electric System (BES) Cyber Asset (BCA) located at substations containing Medium Impact BES Cyber Systems (MIBCS). The root cause of this issue was a lack of understanding regarding the applicability of CIP-007-6 R5 Part 5.4 on the Cyber Assets in scope. WECC reviewed the Audit Finding and, after further discussions with WECC_URE2 and analysis of data request responses, determined that WECC_URE2 had a scope increase from the audit finding and failed to change the default password on a total of 54 digital fault recorder PCAs and one relay BCA at substations containing MIBCS. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable on WECC_URE2, and ended when WECC_URE2 changed the default passwords on the Cyber Assets in scope, for a total of 109 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to change the default password on a total of 55 Cyber Assets by the mandatory and enforceable date of the Standard and Requirement. Such failure could increase the risk of unauthorized access and potential changes to WECC_URE2’s MIBCS. Because the passwords were default, WECC_URE2 would not have the capability to identify who used the password which could result in adverse impacts to WECC_URE2’s registered functional obligations in coordinating and communicating, as well as monitoring, controlling and operating its critical Facilities; thereby potentially affecting the reliability of the BES. However, none of the Cyber Assets in scope had electronic remote access. Additionally, both physical and electronic access is restricted to only those individuals who have been authorized. WECC_URE2 had implemented documented procedures to ensure default passwords were changed. WECC determined that the risk associated with this issue had a minimal likelihood of occurring. No harm is known to have occurred. WECC considered WECC_URE2's CIP-007 compliance history in determining the disposition track. WECC_URE2 had no relevant prior noncompliance with CIP-007. | To mitigate this issue, WECC_URE2: 1) Changed the default passwords on the Cyber Assets in scope; and 2) Communicated with all applicable employees to reinforce the policy that all default passwords are to be changed prior to placing devices into service.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2017016764 | CIP-005-5 | R2; Parts 2.1, 2.2, 2.3 | WECC_URE3 submitted a Self-Report stating that, it had an issue with CIP-005-5 R2 Parts 2.1, 2.2, and 2.3. Specifically, WECC_URE3 reported that during preparation for its audit, along with a 3rd party CIP consultant, it discovered that it had not documented a process for its Interactive Remote Access (IRA). Prior to this, WECC_URE3 understood that CIP-005-5 R2 applied only to contractors and 3rd party vendors trying to remotely access Medium Impact BES Cyber Assets (BCAs) from outside of WECC_URE3 and not to WECC_URE3 personnel inside the company trying to remotely access into the Electronic Security Perimeter (ESP) containing Medium Impact BCAs. Since WECC_URE3 did not allow IRA for contractors and 3rd party vendors, it considered itself compliant with CIP-005-5 R2. The root cause was a misunderstanding of CIP-005-5 R2 and its applicability to WECC_URE3 personnel who utilized IRA into the ESP. WECC reviewed the Self-Report and, after further discussions with WECC_URE3, determined that it had 11 remote hosts outside the ESP that had IRA into the ESP containing Medium Impact BCAs, without the implementation of a documented process that collectively included utilizing an Intermediate System (IS); encryption that terminated at an IS; and that required multi-factor authentication for the IRA session, pursuant to CIP-005-5 R2 Parts 2.1, 2.2, and 2.3. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable on WECC_URE3, and ended when WECC_URE3 removed the firewall rules which allowed IRA into the ESP, for a total of 247 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to document and implement a process that collectively included utilizing an Intermediate System (IS); encryption that terminated at an IS; and that required multi-factor authentication for the IRA session when allowing IRA into the ESP. Such failure, could result in a malicious actor gaining access to WECC_URE3’s Control Center containing Medium Impact BES Cyber Systems, to disrupt WECC_URE3’s operational capabilities and loss of visibility or unintended loss.; thereby potentially affecting the reliability of the bulk power system. However, WECC_URE3 did not permit IRA for contractors or 3rd party vendors. IRA into the ESP was only allowed by internal support staff who had completed personnel risk assessments. Internal support staff could only IRA into ESP from electronically and physically secured workstations inside WECC_URE3, which utilized protocol encryption. Based on this, WECC determined that the harm had a minimal likelihood of occurring. No harm is known to have occurred. WECC considered WECC_URE3's CIP-005 compliance history in determining the disposition track. WECC_URE3 had no relevant prior noncompliance with CIP-005. | To mitigate this issue, WECC_URE3: 1) removed the firewall rules which allowed IRA into the ESP; 2) updated documentation to no longer allow IRA for any one; and 3) trained staff on the new IRA procedures.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014022 | CIP-007-3a | R5 | WECC_URE4 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R5.2.3 and R5.3.3. Specifically, WECC_URE4 reported that during a mock audit it discovered that it had shared accounts where the usage was not logged in SCADA, resulting in WECC_URE4 not having an audit trail of the shared account use. The shared accounts were associated with CCAs at WECC_URE4’s primary and backup Control Centers, and substations. Additionally, WECC_URE4 reported that it did not change a password for local shared accounts associated with CCAs at the same locations, within a calendar year. The root cause was a less than adequate process to ensure compliance with CIP-007-3a R5.2.3 and R5.3.3. WECC reviewed the Self-Report and determined that WECC_URE4 had two issues of noncompliance; one with R5.2.3 and one with R5.3.3. In the first issue, WECC_URE4 failed to have an audit trail of its shared accounts use. In the second issue, WECC_URE4 failed to change a password on a shared account at least annually. This issue started when WECC_URE4 did not have an audit trail of its shared account use and ended when WECC_URE4 implemented a manual process as an audit trail of shared account use for a total of 921 days of noncompliance. The second issue fell within this timeframe as WECC_URE4 failed to change the aforementioned passwords, throughout an entire calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to provide an audit trail of account use for its shared accounts and to change passwords on CCAs at least annually. Such failure could allow unauthorized access to the CCAs to go unnoticed and unchecked, potentially allowing malicious access to these assets; thereby, potentially affecting the reliability of the Bulk Electric System (BES). However, the likelihood of the harm occurring was reduced by the controls WECC_URE4 had implemented. The physical and logical controls for these devices are limited to its personnel that have been provisioned access via its change control and management process, Personnel Risk Assessment, and CIP training programs. WECC_URE4 established strong technical and procedural controls that limit the risk of exposure to the CCAs identified. Additionally, WECC_URE4’s networking equipment was logging and alerting for any suspicious activity, and devices were generating security event alerts for each individual incorrect password entered. No harm is known to have occurred. | To mitigate this issue, WECC_URE4: 1) implemented a manual process as an audit trail of shared account use; 2) scheduled a quarterly reoccurring calendar event as a reminder to gather shared account logs for review; 3) changed the passwords on all the applicable local shared accounts; and 4) scheduled a reminder to populate on the anniversary of the last password change to remind appropriate personnel to change the passwords WECC_URE4 has verified the completion of all mitigation activity.
2017-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015634 | CIP-007-3a | R6.5 | MRO_URE1 stated that it had an issue with CIP-007-3a R6.5. MRO_URE1 reported that logs related to two Critical Cyber Assets (CCAs), network switches that support MRO_URE1's Backup Energy Management System, were not being reviewed in accordance with MRO_URE1's procedures. The cause of the noncompliance was a system configuration error. The CCAs sent their logs to a "CIP log" that resided on a syslog server. The automation logic used to filter logs contained incorrect definitions for the two affected CCAs. As a result, log information for the two CCAs were not included in the aggregated log information being reviewed. The duration of the issue was approximately 15 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was limited to the failure to include two CCAs in the aggregated log review, and the risk of the noncompliance was reduced because the logs were retained and were reviewed after the noncompliance was discovered. Logs for other CCAs in the backup control center were being timely reviewed. Additionally, the CCAs only affected the availability of the backup system, which could not impact normal operations and any un-availability of the backup system would have been immediately discovered. Further, per MRO_URE1, the CCAs resided within a Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP) which reduced the likelihood that an adversary could obtain unauthorized access to the CCAs. Moreover, the review of logs is a detective control and does not prevent attempts at unauthorized access. Finally, per MRO_URE1, no cyber security events were discovered when the logs were reviewed after the issue was detected. No harm is known to have occurred. MRO considered MRO_URE1's CIP-007-3a R6 compliance history in determining the disposition track. MRO_URE1’s relevant prior noncompliance with CIP-007-3a R6 include: NERC Violation ID MRO2012009816 (CIP-007-3a R6.4). The prior issue involves an instance of noncompliance where event logs were corrupted when five workstations that log user access and security events had an issue with their operating system. As a result MRO_URE1 was unable to retain all required logs for 90 calendar days. MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The prior noncompliance involved maintaining logs, which is not an issue in the current noncompliance, and the current noncompliance was not caused by a failure to mitigate the prior noncompliance. | To mitigate this issue, MRO_URE1: 1) corrected the syslog filters; 2) reviewed the logs for the two CCAs that were not included in the aggregated view; 3) verified the scope of the issue by causing failed logins on all CCAs followed by a log review to confirm that all failed logins were being correctly filtered; and 4) reviewed its NERC CIP Security Log Procedure and other relevant documentation to confirm that it included testing for proper syslog operation. MRO_URE1 stated that mitigating activities were complete.
2017-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016858 | CIP-014-2 | R4 | MRO_URE1 stated that it had an issue with CIP-014-2 R4. Specifically, MRO_URE1 stated that it failed to conduct an evaluation of potential threats and vulnerabilities of a physical attack within 120 days of completing its requirements under R2 as described in CIP-014-2 R2. The cause of the noncompliance was MRO_URE1's reliance on guidance from NERC that included a "no later than" date for compliance with CIP-014-2 R4. MRO_URE1 failed to verify the operative date, which was provided in the implementation plan and was listed as within 120 days of the verification described in CIP-014-2 R2. The duration of the issue was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was quickly self-identified and mitigated promptly, limiting the duration of the noncompliance to approximately one month. Further, per MRO_URE1, the activities described in CIP-014-2 R4 and R5 were completed in advance of the "no later than" guidance that NERC had provided. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE1 completed the evaluation of potential threats and vulnerabilities of a physical attack as required by CIP-014-2 R4. MRO_URE1 stated that mitigating activities were complete.
2017-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017016907 | CIP-014-2 | R1 | During a Compliance Audit, MRO determined that MRO_URE2, had an issue with CIP-014-2 R1. MRO_URE2 failed to perform an initial risk assessment of all Transmission substations that met the criteria identified in applicability sections 4.1.1.2. Specifically, the entity failed to identify a single substation in its initial risk assessment. The cause of the noncompliance was MRO_URE2's process for the identification of all Transmission substations failed to include all BES Transmission Lines because its process documents defined a substation as consisting "of only one bus voltage and the Facilities connected to that bus." This resulted in substations having a lower aggregate weighted value. The duration of the noncompliance was approximately 22 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE2's BES applicability determination was complete and thorough, and the noncompliance was the result of MRO_URE2's definition of a substation in its process documents. The scope of the noncompliance was also limited to not including one substation in its initial risk assessment, which did not have an actual impact on reliability as when MRO_URE2 re-conducted its initial risk assessment to include the affected substation, the assessment did not result in the identification of that substation as a critical substation. Additionally, the noncompliance did not impact the categorization of the other substations that were identified in the initial risk assessment. Further, the miscategorization of future substations through the same cause is prevented through the mitigation of CIP-002 MRO2017016899 (CIP-002-5.1). No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE2: 1) performed an initial risk determination for the affected substation; and 2) committed to changing the definition of substation in its process documents through the Mitigation Plan associated with MRO2017016899 (CIP-002-5.1). MRO verified that mitigating activities were complete .
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (URE1) | NCRXXXXX | NPCC2017017006 | CIP-004-6 | R5. | During a Compliance Audit, NPCC determined that URE1 had an issue of CIP-004-6 R5. During a review of the evidence gathered for the audit, NPCC identified a potential noncompliance that took place during a transfer of an employee. Two (2) shared ID passwords were not reset within 30 calendar days following the date that the employee no longer required retention of that access. The first password was not changed for approximately 90 days and the second password duration was not changed for approximately 139 days. The root cause of the noncompliance was human error. The individual responsible for changing the password did not follow procedure and did not follow up with the appropriate SME(s) as required by the procedure. Specifically, the individual used an out-of-date list that did not have all of the IDs listed when changing passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the BPS. The termination action was an internal transfer. The shared accounts were inaccessible to the employee after his transfer. On his date of transfer, the employee’s physical access, access to all the CIP areas, domain accounts in the CIP areas, and his CIP remote access was removed. No harm is known to have occurred as a result of this issue of noncompliance. | To mitigate this issue, URE1: 1. Reset passwords for the shared IDs 2. Incorporated a quality assurance review into the process 3. Retrained the individual responsible for changing passwords on the correct procedure/process that is to be followed for transfers and/or terminations.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (URE2) | NCRXXXXX | NPCC2017017285 | CIP-004-6 | R4. | URE2 submitted a Self-Report stating that it had an issue of CIP-004-6 R4. A drill was held in the control center's conference room which is located within URE2’s NERC defined Physical Security Perimeter (PSP). In attendance were personnel from various groups. When one supervisor attempted to enter the PSP through the turnstile, he could not enter because he did not have a pin number for the turnstile access control pad. The supervisor contacted one of the CIP team employees who activated the supervisor’s ID card and pin number in the physical access control system. This activation occurred without checking whether the supervisor had been granted unescorted access. The employee was granted unescorted access and attended the drill. However, the supervisor did not have the authority to enter the PSP unescorted because (1) he had not yet completed all the required training for obtaining unescorted access to the PSP; and (2) the request and approval process for such unescorted access had not yet been initiated. The supervisor needed to finish one additional course to complete this training. In addition, although the review of the supervisor’s criminal history records had been completed by Human Resources, it had not been completed as part of the CIP team access approval process. The root cause was individual human performance. The CIP team employee frequently works with the supervisor and incorrectly assumed he was authorized for unescorted PSP access. The noncompliance lasted approximately two hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee was in line-of-sight of an authorized employee throughout the visit, only accessed the conference room, and had access for approximately two (2) hours. The employee did not access the control room floor. The employee had a completed NERC background check, and had partially completed the required training. The employee was appropriately granted unescorted physical access approximately three (3) days later. No harm is known to have occurred as a result of this issue of noncompliance. | To mitigate this issue, URE2: 1. Disabled access for the supervisor 2. Reviewed the event to identify process improvements which would make it less susceptible to a recurrent event, 3. Held a training session with all CIP team members in charge of granting access to review and reinforce the onboarding process and to discuss human performance improvement tools that can be used by individuals to make them less susceptible in making similar errors 4. Completed the review and training requirements to grant access for the substation supervisor's unescorted access to the PSP.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (URE2) | NCRXXXXX | NPCC2017017978 | CIP-006-6 | R1. | URE2 submitted a Self-Report stating that it had an issue of CIP-006-6 R1 Part 1.8. Storm mobilization was activated due to thunderstorms occurring across the service territory. In support of this effort, unescorted physical access to the control center was activated for two (2) support employees. The access authorization was processed and approved in the computer system that documents and tracks such items for both employees. However, although access was authorized for both employees, there was a failure to activate one of the employee’s ID card (badge) and access 4 digit personal identification number (pin) because the employee failed to come to the control center to have this process completed. The employee contacted the control center to gain access. The control center sent an authorized service operator to the service center lobby to escort the employee to the control center. When the service operator and the employee arrived at the main door, the employee swiped his badge but it did not allow entrance since the badge had not been enabled for unescorted access. The service operator then swiped his employee ID badge, entered the main door, and allowed the employee to enter the door as well. The service operator then proceeded to the front entrance turnstile (the Physical Security Perimeter (PSP) entrance point), swiped his badge, entered his pin (two-factor) and allowed the employee to enter the PSP. The service operator then again swiped his badge at the turnstile, entered his pin and entered the PSP under his own credentials. Once inside the PSP, the manager immediately confronted the service operator and employee. The manager instructed the service operator and employee to immediately exit and obtain the proper visitor/escort badges from the Security Operations Center (SOC). The service operator and employee then exited the PSP using the service operator’s badge twice, and proceeded to the SOC to log-in and obtain the correct visitor/escort badges. The service operator and employee then returned and entered the PSP, appropriately logged. This noncompliance lasted for approximately 6 minutes. The root cause of this instance of noncompliance was the employee’s failure to complete the process to activate his badge and pin, which are used for logging entry into the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the entry into the PSP, the un-logged employee was only within the PSP for a minute or two before the manager required the service operator and the employee to leave and to follow the appropriate procedures. The employee had been successfully and appropriately granted unescorted physical access. Additionally, the employee was in line-of-sight of another authorized employee throughout the visit, only accessed the control center hallway, and did not access the control room floor. No harm is known to have occurred as a result of this issue of noncompliance. | To mitigate this issue, URE2: 1. Logged the employee as a visitor. 2. Re-trained all individuals involved in the proper procedures to follow when escorting or being escorted into the control center. 3. As part of the quarterly unescorted access review, employee-sponsors for unescorted access have been requested to review the control center Physical Security – Access Control procedure with their sponsored employees. 4. Communicated this incident to all employees with unescorted access via the quarterly Cyber Security awareness email. 5. Created and placed a quick reference card in the front entrance displaying the salient points of the visitor entrance/exit procedure that can be used by authorized employees when escorting visitors.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentifed Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017226 | CIP-007-6 | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-6 R2. This noncompliance involves three separate instances. In the first instance, RFC_URE1’s application support team did not complete patch source review for software supported by a Protected Cyber Asset. The root cause of the noncompliance was that the application was out of support and thus the vendor no longer provided patches for the software. As a result, the application support team mistakenly thought they were no longer required to perform recurring patch source reviews. However, the application support team was required to perform these reviews until they requested and were granted an exemption due to the support status of the software. Second, RFC_URE1’s patch management standard requires manual security patch sources to be monitored at least every 35 days for available security patches. RFC_URE1 completed a patch availability review for the logging and alerting application, but the employee responsible for the review was on vacation when the 35 calendar day limit was exceeded. When he returned from vacation, he immediately checked the patch source and found that no security patches were released. The root cause was that the notifications of the upcoming reviews were being sent to only that employee and thus, no one else on the team was notified to review the source. Third, RFC_URE1 was alerted to a software vulnerability affecting an Electronic Access Control or Monitoring System-classified Windows server used to protect Windows critical infrastructure from malicious software. Two days later, the Cybersecurity group assessed the security patch accompanying the vulnerability and determined the patch to be applicable. As a result, the patch would need to be implemented within 35 days. However, RFC_URE1 did not implement the patch until 79 days later, when RFC_URE1’s system sent the responsible employee a notification alerting him of the late patch application. The root cause was insufficient detective controls and insufficient visibility into the status of outstanding items (i.e. patches). This noncompliance involves the management practice of asset and configuration management because RFC_URE1’s patch management process lacked sufficient controls to manage changes and potential changes to assets. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Regarding the first instance, this is mostly a documentation error as RFC_URE1’s application support team knew that the application was no longer supported by the vendor and, as a result, the vendor would not release any patches. And, as expected, there were no security patches for the application during the time the source was not being monitored. Regarding the second instance, RFC_URE1 was only two days late in checking the patch source. RFC_URE1 quickly detected and mitigated the noncompliance. Regarding the third instance, because RFC_URE1 was quick to assess the patch (within two days of release), RFC_URE1’s deadline for applying the patch was shorter than it would have been had RFC_URE1 waited the maximum allowable time under the Standard to assess patches. Though RFC_URE1 was 32 days late in applying the patch, it was unlikely that the vulnerability could have been exploited because the software vulnerability could only be exploited by an insider on the same network as the Windows server and would have required the insider to intercept and degrade encrypted communications between the client and server. RFC_URE1 still applied the patch within 79 days of release, thus reducing the time period during which there was any potential risk to the system. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) converted manual patch source to automated feed; 2) contacted the vendor to determine the security patch status of the application and adjusted accordingly; 3) installed the security patch and modified the personal dashboard to include “ready to implement” patches; 4) modified existing or created new reports to more closely reflect all patches in all states; 5) monitored control reports and documented results. RFC_URE1 also incorporated improvements to controls if needed; 6) updated its Security Patch Management document to require physical documentation of the absence of security patches for manual patch source checks; 7) communicated the new procedure to all affected areas; and 8) analyzed results of past control reviews and implemented necessary process improvements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentifed Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017224 | CIP-007-6 | R2 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-6 R2. This noncompliance involves three separate instances. In the first instance, RFC_URE2’s application support team did not complete patch source review for software supported by a Protected Cyber Asset. The root cause of the noncompliance was that the application was out of support and thus the vendor no longer provided patches for the software. As a result, the application support team mistakenly thought they were no longer required to perform recurring patch source reviews. However, the application support team was required to perform these reviews until they requested and were granted an exemption due to the support status of the software. Second, RFC_URE2’s patch management standard requires manual security patch sources to be monitored at least every 35 days for available security patches. RFC_URE2 completed a patch availability review for the logging and alerting application, but the employee responsible for the review was on vacation when the 35 calendar day limit was exceeded. When he returned from vacation, he immediately checked the patch source and found that no security patches were released. The root cause was that the notifications of the upcoming reviews were being sent to only that employee and thus, no one else on the team was notified to review the source. Third, RFC_URE2 was alerted to a software vulnerability affecting an Electronic Access Control or Monitoring System-classified Windows server used to protect Windows critical infrastructure from malicious software. Two days later, the Cybersecurity group assessed the security patch accompanying the vulnerability and determined the patch to be applicable. As a result, the patch would need to be implemented within 35 days. However, RFC_URE2 did not implement the patch until 79 days later, when RFC_URE2’s system sent the responsible employee a notification alerting him of the late patch application. The root cause was insufficient detective controls and insufficient visibility into the status of outstanding items (i.e. patches). This noncompliance involves the management practice of asset and configuration management because RFC_URE2’s patch management process lacked sufficient controls to manage changes and potential changes to assets. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Regarding the first instance, this is mostly a documentation error as RFC_URE2’s application support team knew that the application was no longer supported by the vendor and, as a result, the vendor would not release any patches. And, as expected, there were no security patches for the application during the time the source was not being monitored. Regarding the second instance, RFC_URE2 was only two days late in checking the patch source. RFC_URE2 quickly detected and mitigated the noncompliance. Regarding the third instance, because RFC_URE2 was quick to assess the patch (within two days of release), RFC_URE2’s deadline for applying the patch was shorter than it would have been had RFC_URE2 waited the maximum allowable time under the Standard to assess patches. Though RFC_URE2 was 32 days late in applying the patch, it was unlikely that the vulnerability could have been exploited because the software vulnerability could only be exploited by an insider on the same network as the Windows server and would have required the insider to intercept and degrade encrypted communications between the client and server. RFC_URE2 still applied the patch within 79 days of release, thus reducing the time period during which there was any potential risk to the system. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) converted manual patch source to automated feed; 2) contacted the vendor to determine the security patch status of the application and adjusted accordingly; 3) installed the security patch and modified the personal dashboard to include “ready to implement” patches; 4) modified existing or created new reports to more closely reflect all patches in all states; 5) monitored control reports and documented results. RFC_URE2 also incorporated improvements to controls if needed; 6) updated its Security Patch Management document to require physical documentation of the absence of security patches for manual patch source checks; 7) communicated the new procedure to all affected areas; and 8) analyzed results of past control reviews and implemented necessary process improvements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentifed Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017149 | CIP-004-6 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-6 R5. A contractor from a custodial services company gave their two week voluntary termination notice. This individual returned their physical ID badge to the security desk of the operations building after completing their final shift. Four days later, the responsible group received a call from the backup facilities coordinator indicating uncertainty about whether an official off-boarding process had been initiated for the contractor. Upon review of the contractor’s record, RFC_URE3 discovered that the contractor’s end date in RFC_URE3’s HR System had not been updated by the facilities coordinator. As a result, the contractor’s unescorted physical access remained in place for approximately three days beyond the removal deadline. The responsible group immediately updated HR System and ensured access was removed. The root cause of this noncompliance was the fact that the facilities coordinators did not know how to future-date a voluntary termination in the HR System. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately two days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the contractor turned his badge over to RFC_URE3 after his last shift, which prevented him from being able to gain physical entry to a CIP designated Physical Security Perimeter (PSP) in order to utilize the provisioned access rights which had not been removed. Second, although the badge remained active during the period in question, the badge was under the control of RFC_URE3 security and two-factor authentication consisting of the contractor’s ID badge and PIN would have been required for others to gain unauthorized access to the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed the access from the contractor in question; 2) sent awareness communication to leadership in RFC_URE3 responsible group 3) emphasized RFC_URE3’s policies to vendor and provide reinforcement to affected individuals; 4) provided reinforcement revocation communication to personnel accountable for contractors/employees with NERC access; and 5) developed awareness training, posted on portal page, and communicated to participants to ensure that managers who are responsible for those with NERC access are aware of the proper process for access removal. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentifed Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016539 | CIP-010-2 | R1 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-010-2 R1. RFC_URE4 had three IT Security PCs with baselines that did not get updated/promoted in RFC_URE4’s detective tool baseline within 30 calendar days of completing the change (patching) on these three IT Security PCs. RFC_URE4’s IT Consultant was processing baseline changes and realized that RFC_URE4 IT Security had not initiated the connection to install the patches. The IT Consultant found the IT Security employee on call and made an in person request that the machines be updated as soon as possible to complete the change since the change window had passed. The patches were installed and the machines were updated before the target date. Approximately one month later, RFC_URE4 discovered (while processing the prior patching configuration updates) that the patches installed on the workstations had not been promoted to the baseline in the detective tool. The installed patches were promoted to baseline ten days late for the three IT Security PCs. The noncompliance is that RFC_URE4 did not update the baseline configuration within 30 calendar days of completing a change (patching) that deviated from the existing baseline configuration. (CIP-010-2 R1 Part 1.3 applies to Electronic Access Control or Monitoring Systems (EACMS), Physical Access Control Systems and Protected Cyber Assets. The assets in question are IT workstations, which are identified as Intermediate Systems, which by definition are EACMS, thus the requirement is applicable to them. RFC_URE4 maintains Cyber Asset Configuration baselines in the detective tool and when the "actual" baseline experiences a change which is different from the "baseline" recorded in the detective tool an exception is generated. The exception continues to be reported as the "actual" baseline of the asset.) This noncompliance involves the management practice of asset and configuration management because RFC_URE4 had insufficient monitoring reports and controls in place to identify the noncompliance. These insufficient monitoring reports are a root cause of the noncompliance. RFC_URE4 staff completed the workflows for installing the patches on these three IT Security PCs without realizing that the baselines on the three PCs had not yet been promoted. The duration of the noncompliance was approximately nine days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that permitting an undocumented change could adversely affect system security from incorrect baselines that do not have updated information. The risk is minimized because this is primarily a documentation issue. RFC_URE4 timely assessed and installed the security patches on the three EACMS assets at issue meaning the EACMS assets were always up-to-date with appropriate protections. RFC_URE4 simply failed to document that assessment by updating/promoting the baseline in a timely manner as required by CIP-010-2 R1. The risk is further minimized because the noncompliance has a short duration of only nine days. Lastly, the EACMS assets (three IT Security PC workstations) were within both an electronic and physical security perimeter and are located within a RFC_URE4 corporate facility with controlled access and intrusion detection at the approved access points. All of those protections reduce the risk that a bad actor could exploit a baseline that was not timely updated. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) promoted the baseline for the three assets; 2) recommended corrective feedback for the employee implicated that included a discussion of the importance of attention to detail; 3) created a weekly exception report and report notes which will serve as the last step confirmation of baseline update/promotion; 4) included in the System Administration > Audit Log a comment field which is where the authorizing change request is recorded. Filtered by asset group, this provides a quick and easy verification that all members of a group have experienced the same promotion event for the same change request. This report should also be used to automate updating of the CIP-010- List: "Last Date Baseline Promoted" by allowing for the automatic mapping of baseline promotion dates to the change request number. The report should only be saved and imported to the CIP-010-List when it has been verified that ALL assets have been promoted; 5) updated Change Management/Baseline exception monitoring to require Compliance Team members to schedule reviews of baseline exceptions at least once per week and maintain these as high priority tasks which cannot be re-scheduled to accommodate other assignments; and 6) enhanced process documentation for creating and reviewing the new report. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017016873 | CIP-007-6 | R4; 4.1.1, 4.1.2. 4.2.2 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-6 R4.1.1, R4.1.2, and R4.2.2. An unexpected network interruption occurred during SPPRE_URE1 scheduled maintenance. A network switch was rebooted during maintenance, causing the storage volumes of the centralized logging servers to change to a read-only state, which prevented certain assets, firewalls, and switches from saving logs for 12 Electronic Access Control and Monitoring System (EACMS) Cyber Assets per CIP-007-6 R4.1.1 and R4.1.2. The network interruption also affected SPPRE_URE1’s security events alerting system, rendering it incapable of detecting and generating alerts for failure of event logging on the 12 EACMS Cyber Assets per CIP-007-6 R4.2.2. The duration of this instance of noncompliance was 14 hours, from the time the SPPRE_URE1 syslog servers ceased detecting, logging, and alerting security events on the 12 affected EACMS Cyber Assets, through the time logging and alerting was restored. The root cause of this instance of noncompliance was a combination of a lack of a detailed process describing steps necessary for rebooting the switch and having one physical server for its security alerting system which resulted in a single point of failure for the security alerting and logging capabilities of the EACMS. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-6 R4 has the potential to affect the reliable operation of the BPS by allowing Critical Cyber Assets to be compromised and other system cyber security events to occur without SPPRE_URE1’s knowledge. Had a cyber-incident occurred during the server outage, any valuable diagnostic or forensic logs would have been lost. Additionally, SPPRE_URE1 would have been unable to review security event logs on firewalls and switches that would be useful to analyze the security event. Notwithstanding, detection and alerting for malicious code on the 12 Cyber Assets that were not retaining logs was still functioning and no Cyber Security events happened during the noncompliance. SPPRE_URE1 self-identified the issue and mitigated promptly. No harm is known to have occurred. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) rebooted the syslog servers and security event logging resumed; 2) replaced the redundant virtual syslog server with a physical server at both EACMS locations; 3) added an additional alert for monitoring the logs for a specific error related to disk access interruption and storage subsystem errors; 4) created a new documented process for developing a quality assurance checklist for maintenance activities that impact the power or communications of Cyber Assets in the protected networks; and, 5) distributed the documented process to all applicable IT personnel. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2016016161 | CIP-005-5 | R1; R1.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had an issue of noncompliance with CIP-005-5 R1.3 because some of the firewall outbound access permissions for SPPRE_URE2’s Primary Control Center (PCC) and Backup Control Center (BUCC) Electronic Security Perimeters (ESPs) were unjustified. The duration of this instance of noncompliance was approximately 10.6 months, from the effective date of the standard through the date SPPRE_URE2 completed its mitigation of the noncompliance. The root cause of the instance of noncompliance with CIP-005-5 R1.3 was a misinterpretation of the standard. SPPRE_URE2 interpreted the standard to apply only to external network communications and not to internal network communications. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Maintaining unjustified ESP firewall access permissions has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Bulk Electric System (BES) Cyber Systems to occur, which could lead to misoperation or instability in the BES. Notwithstanding, the noncompliance involved only outbound network communications between SPPRE_URE2 devices; all PCC and BUCC firewall inbound access permissions were justified. SPPRE_URE2’s BES Cyber Systems and their associated Cyber Assets were continuously monitored and protected by an intrusion prevention/detection system, which provides real-time log analysis, event alerting, and blocking of malicious transmissions on Cyber Assets within the ESP. SPPRE_URE2 had an effective security patch management program, and access to the Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. SPP RE considered SPPRE_URE2’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) reviewed all firewall access permissions and confirmed that there were no additional unjustified firewall access permissions; 2) updated the firewall outbound access permissions to include the justified outbound access permissions for the PCC and BUCC ESPs; and 3) revised its ESP Procedure to indicate that internal network communications apply to the standard and that only specific IPs with corresponding ports required for operation are allowed. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2017017074 | CIP-003-6 | R4 | SPPRE_URE3 submitted a Self-Certification stating that it had an issue of noncompliance with CIP-003-6 R4. SPPRE_URE3’s reporting chain for some CIP compliance responsibilities was shifted in response to a reorganization, and the revisions were not properly documented within 30 days of the delegation changes. The duration of this instance of noncompliance was approximately 6 months, from the day after the SPPRE_URE3 CIP delegation document should have been updated, through the date the SPPRE_URE3 CIP delegation document was updated to reflect the changes. The root cause of this instance of noncompliance was that SPPRE_URE3 did not have a formal review process in place that includes instructions to update the delegation document when changes to CIP compliance responsibilities occur. Additionally, SPPRE_URE3 did not have internal controls in place that would trigger an update of its CIP delegation document within 30 days of any delegation or responsibilities changes or ensure that the CIP delegation document was reviewed timely to ensure all changes were timely documented. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-003-6 R4 has the potential to affect the reliability of the BPS by creating the risk that the responsible Subject Matter Experts (SMEs) would be unaware of responsibilities related to the CIP Standards that have been delegated to them. As a result, the protective measures required by the CIP standards may not be adequately implemented for SPPRE_URE3’s Critical Assets and Critical Cyber Assets essential to the operation of the BPS. Notwithstanding, this was a documentation deficiency, as the responsible SMEs subject to the delegation of responsibility changes were aware of their CIP responsibilities and performing the duties as required. The CIP senior manager had approved the delegations, minimizing the potential of unauthorized security actions outside of the approved processes. No harm is known to have occurred. SPP RE considered SPPRE_URE3’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) revised, reviewed, and signed the CIP delegation document reflecting the current CIP compliance responsibilities; 2) implemented a formal process to include sending the delegation document to managers on a monthly basis for managers to review for changes in their departments; and, 3) implemented a process to utilize the work order system to track and document the review of the delegation document. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2017017076 | CIP-005-3a | R3; R3.2 | SPPRE_URE3 submitted a Self-Certification stating that it had an issue of noncompliance with CIP-005-3a R3.2. One of SPPRE_URE3's firewall was not configured to detect or alert for attempts at or actual unauthorized access at one access point into the SPPRE_URE3 Electronic Security Perimeter (ESP). The duration of this instance of noncompliance was approximately 43.4 months, from the date the firewall was placed in service and was not detecting and alerting for attempts at or actual unauthorized access, through the date SPPRE_URE3 completed its mitigating activities. The root cause of this instance of noncompliance was a combination of human error and lack of internal controls. When the firewall was placed into service, the SPPRE_URE3 employee did not confirm that the firewall had the proper ruleset and was detecting and alerting attempts or actual unauthorized access into the ESP. Also, SPPRE_URE3’s Configuration Management Plan did not include a process for post-change review after firewalls are installed to ensure that firewall rule sets were properly configured. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to review and alert for unauthorized access attempts could have created a situation where unauthorized access attempts or actual unauthorized access to the ESP would not have been recognized or investigated, potentially allowing the function and capability of the Cyber Assets to be degraded or compromised. Notwithstanding, no unauthorized electronic access occurred. Only one firewall to one ESP access point was affected. The electronic asset resides within an access controlled Physical Security Perimeter that has port locks and tamper tape in place. SPPRE_URE3 has a network intrusion detection system that is used to monitor traffic and cyber assets that can host anti-malware. Additionally, the personnel with authorized unescorted access have met the CIP-004 access requirements. No harm is known to have occurred. SPP RE considered SPPRE_URE3’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) updated the firewall device configuration, allowing the firewall device to detect and alert attempts into the ESP; 2) reviewed the logs for all 12 Supervisory Control and Data Acquisition (SCADA) network devices and determined that this one instance was the full scope of the noncompliance; and, 3) updated its Configuration Management Plan to require a post-change review of all network baseline changes in the SCADA environment. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2016016319 | CIP-007-6 | R5; R5.7 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-6 R5.7. During an internal assessment, SPPRE_URE4 discovered that the an application installed on an electronic access control and monitoring (EACM) server is not technically capable of limiting the number of unsuccessful authentication attempts or alerting after a threshold of failed logon attempts, and a Technical Feasibility Exception (TFE) had not been requested. The duration of this instance of noncompliance was approximately 4.8 months, from the effective date of the standard through the SPP RE approval date of SPPRE_URE4’s submitted TFE. The root cause of this instance of noncompliance was a misinterpretation of the standard. SPPRE_URE4 viewed the requirement from a system perspective, and thus, did not believe the standard applied at the application level. Specifically, access to the EACM server is controlled by Windows Active Directory, a centralized directory service system that automates network management of user data, security, and distributed resources for distributed networking environments. Because Windows Active Directory limited the number of logon attempts to the EACM server, SPPRE_URE4 believed it was compliant with the standard. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-6 R5.7 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized system access, providing the potential for undetected compromise of BES Cyber Systems, which could lead to misoperation or instability in the Bulk Electric System (BES). Notwithstanding, with the exception of an approved TFE, SPPRE_URE4 confirmed that the application and associated EACM server were compliant with the CIP standards, and were afforded the required protective measures, including physical and electronic access controls. For example, the application subject to this issue of noncompliance is installed on the EACM server, which is located inside a Physical Security Perimeter (PSP) and restricted to individuals with authorized access to the PSP. For electronic access, only a select few individuals have the ability to remotely access the application by authenticating to the EACM, server, which is set to lock out accounts after five failed logon attempts. Regardless, the application does not allow any monitoring or controlling of any Cyber Asset. Moreover, SPPRE_URE4’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. No harm is known to have occurred. SPP RE considered SPPRE_URE4’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE4: 1) discussed with each affected personnel that the standard applies to the application level; 2) confirmed that the scope of the noncompliance did not extend beyond the application; and 3) submitted a TFE for the application, which was approved by SPP RE. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016386 | CIP-003-3 | R6 | TRE_URE1 submitted a Self-Report to Texas RE after receiving notice of an upcoming Compliance Audit stating that it had discovered multiple instances of noncompliance with CIP-003-3 R6. In particular, TRE_URE1 failed to follow its change control process when making software changes to its Critical Cyber Assets (CCAs) on three occasions. Regarding the first instance, TRE_URE1 Information Technology (IT) personnel conducted a planned installation of printer logic software on select TRE_URE1 workstations. In the process of installing this software, however, TRE_URE1 IT personnel inadvertently installed the printer logic software on additional dispatcher workstations that were not within the approved software installation scope. TRE_URE1 IT personnel removed the printer logic software from the additional workstations at issue, ending the issue. Regarding the second instance, TRE_URE1 IT personnel inadvertently installed a system diagnostic tool on the same dispatcher workstations as the previous instance. A TRE_URE1 system administrator determined that the software was accidentally installed when he attempted to restart one of the affected workstations and contacted the IT administrator conducting the installation to stop the installations. TRE_URE1 IT personnel then proceeded to immediately uninstall the diagnostic tool from the applicable devices, ending the issue on the same day as the initial inadvertent installation. Regarding the third instance, a TRE_URE1 IT contractor with the appropriate physical and electronic access approvals inadvertently installed a notepad application on multiple servers. In this instance, the notepad application had been installed on TRE_URE1 servers in TRE_URE1’s test environment, but TRE_URE1 had not approved the installation of the notepad application on servers in the production environment. TRE_URE1 detected the issue during its daily review of its baseline configuration changes. TRE_URE1 personnel removed the software from the BES Cyber Assets at issue, ending the final instance. The root cause of these instances of noncompliance was that TRE_URE1 lacked a process to ensure that its IT personnel properly applied all software installations to the correct devices or groups of devices. In particular, TRE_URE1 lacked sufficient managerial controls to ensure that all software changes did not inadvertently propagate to cyber assets beyond the scope of the approved installation. In addition, TRE_URE1 did not provide adequate training to TRE_URE1 IT personnel tasked with deploying software to ensure proper scopes were selected. The duration of the noncompliance was approximately nine months. | These issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Regarding the first two instances, the software at issue was either entirely nonfunctional or merely diagnostic in nature. As such, TRE_URE1 stated that neither software would have an operational impact on the devices to which they were inadvertently deployed. Regarding the third instance, the software was installed on a test server without issue and the software type had no known operational issues or vulnerabilities. Second, the duration of the issue was short. In particular, TRE_URE1 quickly detected the issues and removed the software at issue within three days or less of the inadvertent installations. Third, TRE_URE1 did not identify any operational or security issues, including any issues with its CIP-005 and CIP-007 security controls, associated with any of the software installations. Finally, throughout the issue duration, TRE_URE1 had a number of defense-in-depth protections in place, including distributed intrusion detection and intrusion prevention systems monitoring Electronic Security Perimeters (ESPs) for malicious activity, advanced persistent threat tools monitoring intrusions from the external Internet, host intrusion prevention and antivirus protections against malware infection, two-factor authentication for critical systems, and firewalls and other tools securing the network perimeter to allow only traffic intended to flow to and between ESPs. Collectively, these additional protections reduced the risk associated with any unintended security vulnerability in the unlikely event one occurred in these circumstances. No harm is known to have occurred. | To mitigate these instances of noncompliance, TRE_URE1: 1) uninstalled the software on all devices beyond the approved software installation scope; 2) performed a post-change assessment to ensure existing security controls were not adversely affected after the first instance of noncompliance occurred; 3) created separately defined software installation zones for the software push processes at issue to automatically isolate NERC Cyber Assets from unintended software pushes; 4) provided guidance on proper software change management procedures to the single TRE_URE1 contractor at issue; 5) developed a learning module to ensure that personnel responsible for change management are aware of the configuration change management process; and 6) implemented a process which requires that the baseline management tool monitors changes daily as an additional detective control. Texas RE has verified the completion of all mitigation activity.
2017-10-31 | Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017017380 | CIP-006-6 | R1; P1.10 | During a Compliance Audit, Texas RE determined that TRE_URE2 had an issue with CIP-006-6 R1. Specifically, TRE_URE2 did not document a process that addresses CIP-006-6 R1, Part 1.10 in its physical security plan. The root cause of this issue was that TRE_URE2 did not understand the need to include CIP-006-6 R1, Part 1.10 in its physical security plan process document by the required date of July 1, 2016. In particular, TRE_URE2 did not have cabling and nonprogrammable communications components located outside of a PSP and therefore did not have to implement any additional physical access restrictions under CIP-006-6 R1, Part 1.10. The duration of the noncompliance was approximately seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This noncompliance was documentary in nature. In particular, all of TRE_URE2’s applicable cabling and nonprogrammable communications components were located inside a PSP. Therefore, TRE_URE2 did not have to implement any additional physical access restrictions specified in CIP-006-6 R1, Part 1.10 for its medium impact BES Cyber Systems. Furthermore, once the issue was identified, TRE_URE2 quickly revised its physical security plan to comply with CIP-006-6 R1, Part 1.10. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) modified its physical security plan document to comply with CIP-006-6 R1, Part 1.10; and 2) provided its revised physical security plan document to affected staff. Texas RE has verified the completion of all mitigation activity.
2017-10-31 | Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017017383 | CIP-009-6 | R1; P1.3; P1.4 | During a Compliance Audit, Texas RE determined that TRE_URE2 had an issue with CIP-009-6 R1. Specifically, TRE_URE2 did not fully address all aspects of CIP-009-6 R1, Parts 1.3 and 1.4 in its documented recovery plan. The root cause of this issue was an insufficient process to ensure all aspects of TRE_URE2’s recovery plan were adequately documented. In particular, TRE_URE2’s applicable recovery plan did not specifically address storage of information required to recover BES Cyber System functionality and the process for responding to backup failures. The duration of the noncompliance was approximately seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This noncompliance was documentary in nature. Specifically, during the Compliance Audit, Texas RE determined that TRE_URE2 has implemented specific processes to receive alerts and log backup failures, as well as processes to store data necessary to recover BES Cyber System functionality. While TRE_URE2 personnel understood and tested these processes (including through a live demonstration during the audit), TRE_URE2 did not document these procedures within its associated recovery plan. Furthermore, while TRE_URE2’s recovery plan did not include all required information, TRE_URE2’s process document did partially address aspects of CIP-009-6 R1, Parts 1.3 and 1.4 by referencing the backup of information required to recover BES Cyber System functionality and verification of the backup processes, limiting the scope of TRE_URE2’s documentation issues. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) modified its recovery plan to fully comply with CIP-009-6 R1, Parts 1.3 and 1.4; and 2) provided its revised recovery plan process document to affected staff. Texas RE has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016622 | CIP-006-3c | R2 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-006-3c R2.2. Specifically, WECC_URE1 failed to implement a process for the update of anti-virus and malware prevention signatures for two Physical Access Control Systems (PACS) according to CIP-007-3a R4, as required by CIP-006-3c R2.2. WECC_URE1 determined it needed to update its anti-virus software and initiated a project to perform this update. The PACS Subject Matter Expert (SME) discovered that the PACS servers in scope were not visible in either the new or the old anti-virus programs. Upon further review by the PACS SME, WECC_URE1 determined the only anti-virus installed on the PACS servers was the expired old anti-virus program and no real-time protection was being provided. During this project, the responsibility of anti-virus administration changed to a new internal organization. The support staff that was responsible for installing the new anti-virus was not provided access to the new anti-virus management console to verify successful agent installations. The common tool used for verification was undergoing an upgrade during this time and was also unavailable. Additionally, the technical complexity of the PACS environment required coordination by multiple organizations for implementation and configuration of the new anti-virus. The root cause of this issue was that the personnel/department interactions were not considered. WECC determined that this issue began when support for the previous anti-virus program was no longer available and that the issue ended when WECC_URE1 utilized a new anti-virus system. The duration of noncompliance was approximately two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to implement a process for the update of antivirus and malware prevention signatures for two PACS. Failure to update anti-virus and malware prevention signatures could potentially result in viruses or malware spreading to other systems or compromising the PACS. A compromised PACS could prevent authorized access or allow unauthorized individuals to access Critical Cyber Assets. However, WECC_URE1 implemented good controls to prevent a compromise from happening. WECC_URE1’s PACS are isolated from the rest of the network. Access to the Internet from the PACS environment is restricted and file transfers are tightly controlled. Desktop connections are all virtualized requiring two-factor authentication. Additionally, WECC_URE1 implemented good detective controls to detect any possible compromise. Based on the controls in place, WECC determined that the risk had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) replaced the PACS and ensured the anti-virus was updated, mitigating the threat of malicious code; and 2) created a procedure to ensure PACS are updated and mitigating the threat of malicious code. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016623 | CIP-007-6 | R4 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-6 R4, Part 4.2. Specifically, WECC_URE1 failed to generate alerts for security events, as required by the Standard for two PACS. WECC_URE1 determined it needed to update its anti-virus software and initiated a project to perform this update. The PACS SME discovered that the PACS servers in scope were not visible in either the new or the old anti-virus programs. Upon further review by the PACS SME, WECC_URE1 determined the only anti-virus installed on the PACS servers was the expired old anti-virus program and no real-time protection was being provided. Because of this, WECC_URE1 determined that the PACS were not alerting security events, as required. During this project, the responsibility of anti-virus administration changed to a new internal organization. The support staff that was responsible for installing the new anti-virus was not provided access to the new anti-virus management console to verify successful agent installations. The common tool used for verification was undergoing an upgrade during this time and was also unavailable. The root cause of this issue was that the personnel/department interactions were not considered. WECC determined that this issue began when the Standard became mandatory and enforceable, and ended when WECC_URE1 ensured the new anti-virus system was alerting. The duration of noncompliance was approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to alert for detected malicious code, or detected failure of malicious code event logging on two PACS. Failure to alert for detected malicious code could result in viruses or malware spreading to other systems or compromising the PACS. A compromised PACS could prevent authorized access or allow unauthorized individuals access to BES Cyber Assets. However, WECC_URE1 implemented good controls to prevent a compromise from happening. PACS are isolated from the rest of the network. Access to the Internet from the PACS environment is restricted and file transfers are tightly controlled. Desktop connections are all virtualized requiring two-factor-authentication. Additionally, WECC_URE1 implemented good detective controls to detect any possible compromise. Based on the controls in place, WECC determined that the risk had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) replaced the PACS and ensured it included an anti-virus system for alerting; and 2) created a procedure to ensure PACS have antivirus and alerting capabilities. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017092 | CIP-004-6 | R3 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-6 R3 Part 3.5. Specifically, WECC_URE1 failed to adequately implement its Personnel Risk Assessment (PRA) program when it failed to have current PRAs for two individuals with authorized electronic access to a High Impact BES Cyber Systems (HIBCS). The two individuals in scope were unresponsive to recurring PRA communications by a security officer to renew their PRAs. The security officer sent an email to notify relevant personnel of these PRA expirations. The relevant personnel received the email; however, this was the first PRA expiration that required access revocation for the Control Center, and they were unclear on the actions required to be taken. The PRAs expired for the two individuals in scope. The security officer performed a spot check and discovered that the two employees still had authorized electronic access to the HIBCS even though their PRAs had expired. The root cause of this issue was the lack of an adequate process for notifying other stakeholders about expired, or about to expire, PRAs and the steps to perform. WECC determined that this issue began when the PRA for the two individuals expired and ended when WECC_URE1 revoked electronic access for the two individuals in scope. The duration of noncompliance was approximately five days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to implement a process to ensure that individuals with authorized electronic access had a personnel risk assessment completed within the last seven years. Specifically, the PRAs for two employees expired and WECC_URE1 failed to revoke authorized electronic access to the BES Cyber Assets at the Control Center. Failure to renew PRAs increases the risk of a bad actor obtaining electronic access to the HIBCS. However, WECC_URE1 implemented strong detective controls to detect the expired PRAs. Specifically, WECC_URE1 performed an internal spot check of the notification and access revocation process one day after the PRAs had expired. During this spot check, WECC_URE1 made a timely discovery that the revocation had not been completed as per procedure. Based on the controls in place, WECC determined that the risk had a low likelihood of occurring. Additionally, WECC_URE1 reviewed access logs to confirm that the individuals in scope did not access the BES Cyber Systems without a current PRA and timely removed the individuals’ electronic access. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) revoked authorized electronic access for the two personnel in scope; 2) developed an escalation process for instances where an individual opts out of the PRA process or fails to respond to a renewal notice; 3) enumerated the steps for the subsequent revocation of authorized electronic and unescorted physical access to BES Cyber Assets; and 4) updated email templates to clarify PRA expiration dates and next steps. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016715 | CIP-007-6 | R4; Part 4.2 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-6 R4 Parts 4.1, 4.2, and 4.4. Specifically, regarding CIP-007-6 R4 Part 4.1, WECC_URE2 reported that logged events on its Intrusion Protection System (IPS) devices, which were placed in service for CIP Version 5 compliance, did not retain logged events. Regarding CIP-007-6 R4 Part 4.2, WECC_URE2 reported that its software, used to collect logged events for Cyber Assets in its High Impact Bulk Electric System (BES) Cyber System (HIBCS) located at its control center, suffered a partial failure. WECC_URE2 discovered this issue during its normal log review process. WECC_URE2 determined that some generated security events alerts were collected by the software, but not all of them. Regarding CIP-007-6 R4 Part 4.4, WECC_URE2 reported that it did not review logged events at intervals no greater than 15 calendar days for seven devices. WECC reviewed the Self-Report and, after further discussions with WECC_URE2 and analysis of data request responses, determined that the original Self-Report submitted by WECC_URE2 should have a decrease in scope. WECC_URE2 was able to provide evidence of compliance with CIP-007-6 R4 Parts 4.1 and 4.4. However, WECC determined that WECC_URE2 did fail to generate alerts for security events for 18 Cyber Assets located at its control center pursuant to CIP-007-6 R4 Part 4.2. The root cause of this violation was less than adequate controls to monitor software performance, and identify performance issues when Cyber Assets stopped sending generated alerts for security events to the software. WECC determined that this issue began when alerts for security events were no longer being sent to the software, and ended, when WECC_URE2 performed a reboot of the system and confirmed security events were alerting and were being collected and sent to the software, for a total of 13 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to generate alerts for security events on 18 Cyber Assets located at its control center. Such failure could result in the loss of visibility to malicious events taking place on the Cyber Assets, which could result in systems within or adjacent to WECC_URE2’s control center being vulnerable. Loss of alerts can also result in loss of visibility to operational performance issues, resulting in degradation or service outages. Malicious activity could result in complete control (installation of software, exfiltration of data, remote control, etc.) of the affected system; thereby potentially affecting the reliability of the BES. WECC_URE2 utilized a logging architecture that included data aggregation, analysis, and alerting capabilities. Although WECC_URE2 did not have performance of log monitoring on the system, it had monitoring on its end point devices to ensure they were sending logs. WECC_URE2 had implemented strong compensating controls to prevent the exploitation of the systems where alerting visibility had been lost at the control center. These systems were restricted by Cyber Asset protections including an Electronic Security Perimeter; anti-malware and, monitoring protections. Additionally, Cyber Assets were protected with physical access controls for unescorted physical access and a method to authenticate for interactive remote user access, which requires two-factor authentication. Unescorted physical access is protected by the implementation of Personnel Risk Assessments and cyber security training programs. Based on the controls in place, WECC determined that the risk associated with this violation had a minimal likelihood of occurring. No harm is known to have occurred. WECC_URE2 has no relevant prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE2 will complete the following mitigation activities by March 14, 2018: 1) collect data from the system for use by the vendor for investigation of the problem; 2) determine method to ensure that all instances of system logging failure can be identified when they occur; 3) identify and document all controls that would resolve the root cause; d. identify and update any CIP-007 review processes or procedures that need to be updated; 4) train personnel on any CIP-007 procedural changes; 5) train personnel to use any new controls identified; and 6) assign monthly review that the controls have been implemented and followed for one quarter. .
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2017017456 | CIP-007-6 | R2 | WECC_URE3 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-6 R2 Part 2.3. Specifically, WECC_URE3 reported that a Microsoft update was not applied on its Physical Access Control Systems (PACS) workstations associated with WECC_URE3’s High Impact Bulk Electric System (BES) Cyber System (HIBCS) and Medium Impact BES Cyber System (MIBCS) within 35 calendar days per CIP-007-6 R2 Part 2.3. In October of 2016, Microsoft changed the manner in which patches were released from individual patches to a bundling of patches into a single executable. WECC_URE3’s Subject Matter Expert (SME) was unfamiliar with the new patch format and missed installing the patch within the required timeframe. WECC reviewed the Self-Report and, after further discussions with WECC_URE3 and analysis of data request responses, determined that in addition to the self-reported issue, WECC_URE3 had a scope increase of three additional issues of noncompliance with CIP-007-6 R2 Part 2.2. All three instances of noncompliance involved Microsoft patches that were released out of band. WECC_URE3 did not have an adequate process to address out of band patches and consequently failed to evaluate three patches within the required 35 calendar day timeframe. The root cause was a less than adequate process for identifying, assessing, and timely installation of released security patches. This issue started when a patch was not evaluated for applicability within the required 35 calendar day timeframe, and ended when the patch was evaluated for applicability, for a total of 322 days of noncompliance. The three additional instances of noncompliance fell within the timeframe of the first instance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to evaluate security patches for applicability within 35 calendar days and, and for security patches assessed as applicable, failed to take action pursuant to CIP-007-6 R2 Part 2.3 within the required 35 days after evaluating them for applicability. Such failure could potentially result in an attacker gaining access to WECC_URE3’s HIBCS and MIBCS to cause disruptions to its operation capabilities; thereby, affecting the reliability of the BES. However, WECC_URE3 implemented controls to reduce the likelihood of the risk from occurring. Specifically, PACs workstations are physically protected and access controlled. They reside on a separate network that is access protected and is limited to those with a business need to access the PACs workstations. Additionally, the PACS workstations are backed up regularly, and if necessary, a new machine could be put in service quickly via a backup image. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) evaluated patches for applicability; 2) applied applicable patch; 3) added a new task step to its patch management process that will prompt SMEs to verify that the patch install or mitigation dates been filled in with the date the patches were applied for Windows workstations and servers; and 4) added an agenda item to its bi-monthly group meetings to discuss any changes in patch releases from patching sources and how they will be addressed to ensure robust continuity of patch application. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Register Entity 4 (WECC_URE4) | NCRXXXXX | WECC2017017238 | CIP-003-6 | R4 | WECC_URE4 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-003-6 R4. Specifically, WECC_URE4 reported that during performance of its annual self-certification process, it discovered that the CIP-003-6 R4 CIP Senior Manager delegation of authority document in place from the mandatory and enforceable date of the Standard and Requirement, included delegation authority for approval of the CIP-003 R1 cyber security policies to someone other than the CIP Senior Manager. CIP-003-6 R1 does not allow for delegation of authority. The root cause was a misunderstanding regarding the application of delegation related to CIP-003-6 R1. WECC reviewed the Self-Report and determined that WECC_URE4 failed to implement a documented process that included delegation authority only where allowed by the CIP Standards. CIP-003-6 R1 states that the CIP Senior Manager is the signing authority for documented cyber security policies; therefore, the delegation of that authority is not allowed in the CIP Standards. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE4, and ended when WECC_URE4 updated its documentation process and removed the CIP-003 R1 delegation authority, for a total of 120 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to implement a documented process that included delegation authority only where allowed by the CIP Standards. Such failure could cause an unclear line of authority and ownership for security matters, which could translate into communication issues or incorrect CIP process training for personnel. However, each of WECC_URE4’s cyber security policies contained a specific approval line which indicated that only the CIP Senior Manager was authorized to approve, and not a delegate. WECC_URE4 verified that no delegated authority signed its cyber security policies. WECC_URE4 discovered this issue during a compliance review. This is simply a documentation issue and not related to any cyber security issues. No harm is known to have occurred. WECC_URE4 has no prior relevant compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE4 1) updated its delegation of authority documentation by removing the incorrect delegation, which was then reviewed and approved by the CIP Senior Manager; and 2) reviewed all effective cyber security policies to verify that only the CIP Senior Manager had signed them.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2017017389 | CIP-007-6 | R4; Part 4.1 | During a Compliance Audit WECC determined that WECC_URE5 had possible issue of noncompliance with CIP-007-6 R4 Part 4.1. Specifically, WECC_URE5 failed to log events to detect successful login attempts; failed access attempts and failed login attempts; and malicious code for one Human Machine Interface (HMI) on a series capacitor classified as a Bulk Electric System (BES) Cyber Asset (BCA) at a Medium Impact BES Cyber System (MIBCS) without External Routable Connectivity (ERC) and without dial-up access. WECC_URE5 had been initially informed by the manufacturer that WECC_URE5 did not have the ability to adjust any settings on this specific BCA, therefore WECC_URE5 did not enable security event logging pursuant to R4 Part 4.1. While WECC_URE5 was gathering evidence for an audit data request, WECC_URE5 contacted the manufacturer for further evidence to demonstrate the manufacturer’s previous claim. The manufacturer responded that they do not recommend changing any control and protection settings without first consulting them as such action would void the warranty. This was a different response than what was originally told to WECC_URE5. The root cause of this issue was a misunderstanding between WECC_URE5 and the manufacturer of the BCA regarding the capabilities of the device. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE5, and ended when enabled security event logging on the BCA in scope, for a total of 241 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to log events on one BCA to detect successful login attempts; detect failed access attempts and failed login attempts; and malicious code. Such failure could result in WECC_URE5 not being able to identify or perform after-the-fact investigations of Cyber Security Incidents or act on the alerts generated based on the logs. This could potentially further prevent WECC_URE5 from being able to identify how an attacker compromised a system to prevent the same or similar attacks in the future. However, this issue was limited to a single BCA that was isolated physically and electronically to a single MIBCS without ERC at a substation. Based on this, WECC determined that the risk had a minimal likelihood of occurring. No harm is known to have occurred. No harm is known to have occurred. WECC_URE5 had not relevant prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE5: 1) enabled security event logging on the BCA in scope; 2) confirmed that the BCA was generating security event logs; 3) developed and distributed guidelines for preferred evidence to demonstrate compliance; 4) reviewed its tool during substation and technical operations safety meetings to stress the importance of having a questioning attitude when discussing compliance related issues; and 5) reviewed its three-way communications tool during substation and technical operations safety meetings to stress the importance of using three-way communications when discussing compliance related issues. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2015014929 | CIP-004-3 | R4 | WECC_URE6 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3 R4. Specifically, WECC_URE6 failed to revoke physical access to Critical Cyber Assets (CCAs) within seven calendar days for one individual who no longer required such access. The individual in scope returned to their original position at a separate internal position and no longer required physical access to WECC_URE6 CCAs, but WECC_URE6 failed to remove the individual's access or to update the access list within the required timeframe. The root cause of the violation was inadequate processes and procedures. The duration of the issue was approximately 15 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE6 failed to revoke physical access for one individual within the required 7 days of no longer requiring such access. Failure to revoke access to Critical Cyber Assets in a timely manner could allow unauthorized individuals to have malicious physical access to the Critical Cyber Assets. This unauthorized physical access could compromise the security of the Critical Cyber Assets that control the Bulk Power System (BPS). This unauthorized physical access could be exploited to cause damage to equipment. However, WECC_URE6 had several controls in place to prevent any effect on the BPS. The employee has been continuously employed in good standing at the parent company. The employee in scope had CIP training and a current Personnel Risk Assessment. The employee returned to WECC_URE6 permanently and has been granted physical access to the PSP as per CIP-004 R4. The mock audit team did not find any other issues with the CIP access lists in their review. When the employee was initially acting at WECC_URE6, no logical access was granted to CCAs. The CCAs have controls implemented, including account/password management, security event monitoring, patching, malware prevention, change management, restricted ports/services, incident response procedures, and recovery procedures. Logins are required to access cyber assets within the ESP. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) removed those not requiring access from access lists and ensured its access lists are current; 2) implemented a new notification system for departing employees by creating an email list, which notifies a list of people responsible for enabling/disabling physical and logical access, and requires acknowledgement of access removal; and 3) reviewed the updated process with personnel. WECC has verified the completion of all mitigation activity.
2017-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2017016898 | CIP-004-3a | R3 | WECC_URE7 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R3.2. Specifically, WECC_URE7 reported that Personnel Risk Assessments (PRAs) were not renewed within the required seven-year timeframe for five individuals who had authorized electronic and/or unescorted physical access to Critical Cyber Assets (CCAs). WECC_URE7 discovered this issue while conducting an internal review to compare those who had electronic and/or unescorted physical access to CCAs against those who were authorized to have said access. WECC_URE7 implemented a new automated system to handle access authorizations based on roles. As part of the implementation, WECC_URE7 completed a bulk upload of users into the system; however, WECC_URE7 later discovered that a PRA check control was omitted when implementing the new system. This resulted in a failure to validate PRAs appropriately when bulk uploading users. WECC_URE7 learned that the system would function properly when PRAs were uploaded one-by-one, so it began manually checking PRA dates as they were loaded into the system. During the manual process, which was cumbersome, WECC_URE7 inadvertently missed five individual’s PRA dates when it was reviewing what was in the system. The root cause was a less than adequate process to ensure proper configuration of its automated system to check PRA dates prior to CIP access being provisioned. WECC reviewed the Self-Report and, after further discussions with WECC_URE7, determined that it failed to provide current PRAs for five individuals who had authorized electronic and/or unescorted physical access to CCAs. This issue started when the first PRA should have been renewed for one individual, and ended when the last individual’s PRA was renewed, for a total of 159 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE7 failed to renew PRAs for five individuals who had authorized electronic and/or unescorted physical access to CCAs within the required seven-year timeframe. Such failure could result in WECC_URE7 not being aware of changes to an individual’s background in the past seven years which could potentially increase the risk of a bad actor performing unauthorized changes; thereby potentially affecting the reliability of the Bulk Electric System. However, all five individuals were authorized to have access to CCAs. Prior to employment with WECC_URE7, all five individuals had a full in-depth background investigation including employment history, reference, education, financial, and initial criminal history check. Only one of the four individuals with unescorted physical access used that access during the period of time that the PRA was not renewed. That individual had been employed with WECC_URE7 for over 30 years and was vetted as a trusted employee. Based on this information, WECC determined that the issue had a minimal likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, WECC_URE7: 1) revoked CIP access for two of the individuals in scope whose PRAs had not been renewed by the discovery date of this issue of noncompliance; a) renewed PRAs for three of the individuals in scope prior to the discovery date of this issue of noncompliance; 2) renewed all five PRAs; 3) created a report that compares all individuals who have CIP access against those who have a valid PRA; 4) reconfigured its automated system in included a step for validating PRA dates; and 5) created a report that evaluates the roles of individuals who have CIP access to determine if they need it. WECC has verified the completion of all mitigation activity.
2017-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2017017772 | CIP-004-6 | R4. | On June 22, 2017, FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-6, R4, Part 4.2. FRCC_URE1 did not conduct the quarterly assessment of authorization records for those individuals with active electronic access or unescorted physical access. This noncompliance began when FRCC_URE1 failed to conduct the quarterly assessment and ended two months later, when the assessment was complete. The root cause for this noncompliance was lack of internal controls and administrative oversight. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC_URE1's failure to perform a quarterly assessment of authorization records could have led to unauthorized access to BES Cyber System Information, as well as BES Cyber Assets (BCAs) to go undetected. The undetected unauthorized access could have compromised the BES Cyber Systems and BCAs potentially compromising the reliable operation of the BPS. The risk was increased as lack of following proper protocols for quarterly assessment of access records could have allowed unauthorized access that could have compromised the BPS. The risk was reduced because when the assessment of authorization records was completed FRCC_URE1 found no unauthorized access had been granted. Furthermore, no Cyber Security Incidents occurred during the period of noncompliance. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) performed a detailed root cause analysis, 2) performed a gap assessment to identify full extent of condition back to enforcement date, and 3) performed the assessment of authorization records, bringing FRCC_URE1 back into compliance. To prevent recurrence, FRCC_URE1: 1) developed internal controls, including the tracking system that schedules reviews to be performed each quarter, and 2) trained all applicable employees on policy and procedural changes.
2017-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2017017773 | CIP-004-6 | R5. | On June 22, 2017, FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-6, R5, Part 5.1. FRCC_URE1 failed to remove access within 24 hours of the termination of an individual. The individual had authorized unescorted physical access, but no electronic access. The individual’s authorized unescorted physical access was removed ten (10) days after the effective termination date. This issue started when FRCC_URE1 failed to remove unescorted physical access privileges within the 24-hour timeframe and ended when access privileges were removed. The root cause for this noncompliance was lack of internal controls and administrative oversight. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC_URE1's failure to revoke authorized unescorted physical access within the required timeframe could have allowed for someone to gain access and potentially misuse or compromise the BPS. The risk was increased by the number of days of exposure where someone could have gained unauthorized entry. The risk was reduced because at the time of termination the employee's badge (access card) was collected by the supervisor. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) performed a detailed root cause analysis, 2) performed a gap assessment to identify full extent of condition back to the enforcement date, 3) removed access, which brought FRCC_URE1 back into compliance, 4) developed and implemented internal controls, and 5) trained all applicable employees on policy and procedural changes. To prevent recurrence, FRCC_URE1: 1) contracted with an outside company to oversee its CIP compliance program, 2) implement a compliance tracking tool to provide notificaitons when a change of access is requried, and 3) created an “Access Revocation Form” and added as an attachment to the procedure.
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015633 | CIP-006-3c | R6 | MRO_URE1 reported that MRO_URE1 failed to log an employee's entry into the Physical Security Perimeter (PSP) on three separate occasions within a seven-day period. The employee's security access badge did not allow him to gain access to the PSP. A co-worker with authorized unescorted physical access opened the PSP door for the employee. The employee's access into the PSP was not entered into the manual log. The employee gained access to the PSP in the same manner the following day and again six days later. On the final occasion, the employee informed a supervisor, and that supervisor called MRO_URE1's Security Administrative Office who determined that the employee's security access badge had expired, even though the employee still had physical access privileges to the PSP. The cause of this noncompliance was a software glitch in an internal control. To ensure that only authorized personnel have unescorted and electronic access, MRO_URE1 sets the expiration of the security access badge to coincide with the CIP-004 training requirement. When an employee receives training, the Learning Management System (LMS) sends an automatic update to the Security Administration Office, who then sets a new expiration date for the employee's security access badge. In this case, the employee's training notification was not sent due to a LMS glitch, and the security access badge expiration was not extended. The duration of the noncompliance was approximately one week. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee had approved unescorted access to the PSP, and had up-to-date CIP training. The employee informed management of the issue, which is an indication of a strong compliance culture and that MRO_URE's CIP training is effectively conveyed to staff. Finally, MRO_URE1 performed a comprehensive extent of conditions analysis, that determined that this was an isolated incident. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE1: 1) extended the expiration of the employee's security access badge so that the employee's entry and exit into the PSP would be automatically logged; 2) performed a comprehensive extent of conditions analysis, that determined that this was an isolated incident; 3) updated alarm configurations for the PACS alarms for access control events to be more easily identified; 4) provided training to the Security Control Office staff on the updated PACS configuration; 5) changed the title of the manual PSP log book from "Visitor Log" to "Escort Log."
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2016015554 | CIP-006-3c | R4 | MRO_URE2 stated that an authentication device that failed to restrict access only to authorized individuals. To gain access to the Control Center, an individual had to be granted unescorted physical access to the SCADA Physical Security Perimeter (PSP). The Control Center adjoined a room that housed computers (the computer room), that had its own PSP (the Computer Room PSP), and access through that door was controlled by card readers that were on both sides of the door. The two card readers controlled access to different PSPs and had two different lists of authorized users. For example, to enter the Control Center, and then to enter the computer room, an individual had to be authorized to access the both the SCADA PSP and the Computer Room PSP. But not all individuals who were granted access to the SCADA PSP, were also granted access to the Computer Room PSP, and to leave the computer room to enter the Control Center, an individual need only be authorized in the SCADA PSP. MRO_URE2 reported that its security office received a "wrong door" alarm for an individual who opened that door. A subsequent investigation revealed that sometimes, when an individual presented a card on one side of the door, the card reader on the other side of the door would read the card and grant access. Meaning that an authorized individual in the SCADA PSP, but unauthorized in the Computer Room PSP, could stand in the Control Center, present the access card to card reader on the Control Room side, but the card reader on the computer room side of the door would read the badge and unlock the door, logging the access as if the individual was exiting the Computer Room PSP and entering the SCADA PSP, but having the effect of improperly granting access to the Computer Room PSP. The cause of the noncompliance was an access control system was improperly applied to a physical access point shared between the Computer Room PSP and the SCADA PSP, and an overly sensitive card reader that could read a card presented on the other side of a wall. The duration of the noncompliance was approximately 8 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The noncompliance is limited to improper access of the computer room, by individuals who have been granted unescorted physical access to the Control Center. Individuals who are granted unescorted physical access to the Control Center are unlikely to be adversaries, as they have been screened through a personal risk assessment. Additionally, if an individual with unescorted physical access to the Control Center was an adversary, additional access to the computer room, would not raise the risk to the BPS, as the Control Center contains multiple High Impact BES Cyber Systems, where as, for purposes of CIP protections, the computer room does not contain any BES Cyber Systems, and only contains an EACMS device that ran a single application. Finally, a complete review of all access to the computer room determined that improper access was limited to two individuals who improperly accessed the room on four occasions for a total of nine minutes, had no electronic access to the application, and no malicious activity occurred during those brief entries. No harm is known to have occurred. MRO considered MRO_URE2's CIP-006-3c R4 compliance history in determining the disposition track. MRO_URE2’s relevant prior noncompliance with CIP-006-3c R4 include: NERC Violation ID MRO201010967 (CIP-006-3c R4). The prior issue involves an instance of noncompliance where an employee attempted to tape a door latch shut to allow the employee's re-entry after the employee left his access card at home. MRO determined that MRO_URE2's compliance history should not serve as a basis for applying a penalty as the current issue was not caused by a failure to mitigate the prior issue and the current noncompliance was caused by a condition that was not reasonably foreseeable. | To mitigate this issue, MRO_URE2: 1) replaced the card readers with a less sensitive model; 2) conducted a review to determine if there was improper access; and 3) reviewed all other CIP PSPs for similar configurations.
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017017438 | CIP-003-3 | R6 | MRO_URE2 stated that it did not document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs) within 30 days as required by its process. The noncompliance involved changes to a specific type of Ethernet switch that MRO_URE2 had deployed in multiple substations. The cause of the noncompliance was human performance in the timely completion of the documentation. MRO_URE2 has a manual change management process, and the technicians in these instances were delinquent in completing and submitting the paperwork. The duration of the noncompliance was approximately 7 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The updates were all necessary, and the noncompliance was limited to documentation issues only. Further, the updates occurred during routine computer maintenance activities, such as changing passwords, updating firmware levels, and installing security patches. No harm is known to have occurred. MRO considered MRO_URE2's CIP-003-3 R6 compliance history in determining the disposition track. MRO_URE2’s relevant prior noncompliance with CIP-003-3 R6 includes: NERC Violation ID MRO2013013155 (CIP-003-3 R6). The prior issue involves an instances of noncompliance related to more substantive changes in substation design, including the failure to document an unsecured routable connection. MRO determined that MRO_URE2's compliance history should not serve as a basis for applying a penalty as the current issue was not caused by a failure to mitigate the prior issue, and the difference in the nature of the undocumented changes. | To mitigate this issue, MRO_URE2 updated all of its change control records related to the updates.
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017017439 | CIP-004-6 | R2 | MRO_URE2 stated that a report run as part of a newly implemented access management system, detected that five individuals who had access to an EACMS device were not current on CIP training. The individuals had electronic administrative access to a firewall management device. Prior to the enforcement date, this device was only utilized to manage firewalls in the corporate network environment. But after the enforcement date, the role of this device was changed to manage firewalls in the CIP Substation Environment. MRO_URE2 attempted to conduct an assessment to ensure that all CIP v5 requirements were implemented prior to the enforcement date for this device, but the training requirement was overlooked. The cause was human performance error to consider the need for CIP training for persons with access to the firewall management system when that system's role was changed to an EACMS, due to a lack of sufficient controls around migrating this device from the corporate network environment to the CIP network environment. The duration of the noncompliance was approximately 30 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was brief, and the brief duration was the result of MRO_URE2's effective implementation of detective controls. Additionally, the individuals only had access to an EACMS device and not to a BES Cyber System. Finally, all five individuals were in good standing, and all had a current criminal background check and personnel risk assessment (PRA) on file. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance with CIP-004-6 R2. | To mitigate this issue, MRO_URE2: 1) provided training to the five individuals; and 2) augmented the detective control in its access management system to run automated compliance reports to detect similar instances of noncompliance.
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2017017441 | CIP-007-6 | R2 | MRO_URE2 stated that it had two instances of noncompliance with CIP-007-6 R2. The first instance of noncompliance involved a security patch for a specific model of Ethernet switch, that was not installed within 35 days of evaluation of the patch, nor was a mitigation plan created or revised. This was discovered during a patch assessment that was conducted during MRO_URE2's annual vulnerability assessment. This noncompliance affected eight devices; five devices that were part of Medium Impact BES Cyber Systems and three devices that were PCAs associated with Medium Impact BES Cyber Systems. After the first instance of noncompliance was discovered, MRO_URE2 conducted a review of all Cyber Assets in the substation environment to confirm that all patches were up to date. The second instance of noncompliance was discovered during that review. The second instance of noncompliance involved a security patch for a substation automation device that affected a device that was a part of a Medium Impact BES Cyber System and a PCA that was associated with a Medium Impact BES Cyber System. The cause of the noncompliance was a failure of the entity to follow its process because these security patches were not sufficiently tracked as MRO_URE2 moved from its CIP v.3 security patch policy to its CIP v.5 security patch policy. The duration of the noncompliance was approximately 3 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was detected by a secondary control that reduced the duration of the noncompliance. Additionally, the affected devices were not located in a Control Center. Finally, the affected devices were offered the protections of residing in functioning Physical Security Perimeters and Electronic Security Perimeters. No harm is known to have occurred. MRO considered MRO_URE2's CIP-007-6 R2 compliance history in determining the disposition track. MRO_URE2’s relevant prior noncompliance with CIP-007-6 R2 include: NERC Violation ID MRO2013011986 (CIP-007-1 R3). The prior issue involves security patches that were not assessed within 30 days. MRO determined that MRO_URE2's compliance history should not serve as a basis for applying a penalty as the current issue involved not installing patches that had been assessed, and the current issue was not caused by a failure to mitigate the prior issue. | To mitigate this issue, MRO_URE2: 1) installed security patches on all affected devices; and 2) completed a secondary review to confirm that all necessary patches on substation Cyber Assets have been applied.
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2016016293 | CIP-010-2 | R2 | MRO_URE3 stated that four devices located at the Primary Control Center and the Back-Up Control Center were not monitored every 35 days for changes to the baseline configuration. Two of the devices were Protected Cyber Assets (PCAs) and the other two were Electronic Access Points (EAPs). The cause of the noncompliance was that, upon transitioning to CIP v5, MRO_URE3 did not realize that its process for monitoring for changes at least once every 35 days did not accurately include all applicable devices within the company’s environment. Specifically, these four devices could not be configured into MRO_URE3's automated baseline monitoring software program, and were inadvertently omitted from MRO_URE3's task scheduler to remind staff to conduct such reviews. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was self-detected within approximately a month during its manual baseline check process, that kept the duration of the noncompliance relatively brief, which is a strong indication of functioning detective controls. Additionally, per MRO_URE3, it does not allow Interactive Remote Access (IRA) into either its Primary Control Center or Back-Up Control Center's Electronic Security Perimeter (ESP). This protective measure substantially reduced the risk for all Cyber Assets within the ESPs. This restricted electronic access is a strong and uncommon control for a registered entity of MRO_URE3's size. No harm is known to have occurred. MRO_URE3 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE3: 1) reviewed the baselines of the four devices; and 2) placed reminders in outlook calendars to monitor the baselines of all devices that were not configured in its automated baseline monitoring software program. MRO verified that all mitigating activities were complete.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017147 | CIP-004-6 | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-6 R4. A physical security contractor's access privileges on a Physical Access Control System (PACS), were changed by the system administrator without having documentation of proper authorization. As background, RFC_URE1 was in the process of migrating from one system to another system. The contractor already had read-only access to the current system, and had authorized NERC CIP electronic access to the new system. The contractor was working with field technicians who were testing Physical Security Perimeter (PSP) access points and needed access that would allow him to monitor badge activity at the PSP doors. He was not aware that the change in access privileges for the current system would require additional authorization, so he went directly to a system administrator to request access to the screens that would allow him to view the badge activity. The system administrator was aware that the contractor had full access in the new system, but was not aware that the contractor did not have documented authorization for the same type of access in the current system. During routine system monitoring functions, another system administrator discovered the contractor’s unauthorized electronic access and immediately reset the contractor's role back to the original setting. The root cause was employees not following the documented process for using the system's request process for all changes to access. One of the preventative controls in place at the time of the noncompliance, which is still in use, is limiting the number of people with administrator privileges (only individuals with these privileges can provision access). RFC_URE1 relies on these individuals to follow the documented process. This noncompliance involves the management practice of workforce management, which includes effective training to ensure employees understand and follow documented procedures. The duration of the noncompliance was approximately twelve days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. At the time of the noncompliance, the contractor completed cyber security training, had a valid Personnel Risk Assessment, had authorized read-only access to the current system, and had authorized NERC CIP electronic access to the new system. Accordingly, this reduced the likelihood that this contractor would have used the incorrectly provisioned access in a way that would compromise the BPS. Additionally, RFC_URE1 discovered and promptly self-identified this issue and immediately mitigated it, thus further reducing potential risk to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed the contractor’s unauthorized electronic access to the current system; 2) conducted awareness training for PACS system administrators on the RFC_URE1 NERC CIP Access Management Standard; and 3) renamed the user roles within the PACS systems that require NERC CIP authorization. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017146 | CIP-004-6 | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-6 R4. This noncompliance involves two separate instances. First, RFC_URE2 ran an access reconciliation process with the system used to document access requests and authorizations and discovered that an employee who was authorized to have access only as support personnel for had incorrectly been provisioned administrator access (elevates access) by another employee who had administrator access. RFC_URE2 discovered and removed the elevated access the next day. An after-the-fact review confirmed that the employee did not utilize his elevated status, and instead only used the system to complete his current job responsibilities. Second, a physical security contractor's access privileges on a Physical Access Control System (PACS), were changed by the system administrator without having documentation of proper authorization. As background, RFC_URE2 was in the process of migrating from one system to another system. The contractor already had read-only access to the current system, and had authorized NERC CIP electronic access to the new system. The contractor was working with field technicians who were testing Physical Security Perimeter (PSP) access points and needed access to the current system that would allow him to monitor badge activity at the PSP doors. He was not aware that the change in access privileges would require additional authorization, so he went directly to a system administrator to request access to the screens that would allow him to view the badge activity. The system administrator was aware that the contractor had full access in the new system, but was not aware that the contractor did not have documented authorization for the same type of access in the current system. During routine system monitoring functions, another system administrator discovered the contractor’s unauthorized electronic access in the current system and immediately reset the contractor's role back to the original setting. The root cause was employees not following the documented process for using the request process for all changes to access. One of the preventative controls in place at the time of the noncompliance, which is still in use, is limiting the number of people with administrator privileges (only individuals with these privileges can provision access). RFC_URE2 relies on these individuals to follow the documented process. Regarding the second instance, improved visibility into which roles in the access system were NERC CIP roles could have potentially prevented the noncompliance. This noncompliance involves the management practice of workforce management, which includes effective training to ensure employees understand and follow documented procedures. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Regarding the first instance, the employee that had the elevated access was permitted to have access as a support personnel, and was a trusted employee who completed cyber security training and had a valid Personnel Risk Assessment, thus reducing the likelihood that he would have used the administrator access in a way that would compromise the BPS. Regarding the second instance, at the time of the noncompliance, the contractor completed cyber security training, had a valid Personnel Risk Assessment, had authorized read-only access to the current system, and had authorized NERC CIP electronic access to the new system. Accordingly, this reduced the likelihood that this contractor would have used the incorrectly provisioned access in a way that would compromise the BPS. Additionally, RFC_URE2 discovered and promptly self-identified both instances and immediately mitigated them, thus further reducing potential risk to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed the contractor’s unauthorized electronic access to the current system; 2) conducted awareness training for PACS system administrators on the RFC_URE2 NERC CIP Access Management Standard; and 3) renamed the user roles within the PACS systems that require NERC CIP authorization. Additionally, RFC_URE2 submitted mitigating activities to address the first instance: 1) removed the elevated access; 2) sent an email to administrators reminding that all access requests must be done through the system; and 3) implemented nightly reconciliations through the system. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017965 | CIP-007-6 | R2 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-6 R2. Having completed a thorough compliance investigation, RFC_URE3 determined it had a potential issue involving CIP-007-6 R2 by not documenting a custom software application and its authoritative patch source in the tracking portion of the Patch Management Program. While the custom application and its patch source were not documented as part of the CIP Patch Management Program, RFC_URE3 did have controls in place to ensure relevant patches were assessed and appropriate actions were performed. Of the various clarifications and enhancements implemented in V5/V6 of the CIP Standards, CIP-010-2 R1 Part 1.1 specifically requires the development of a baseline configuration to include custom software. Prior to CIP-010-2, CIP-003 generally set forth the configuration management requirements with no mention of custom software. Accordingly, when the custom application at issue was first configured for and installed in the RFC_URE3 environment, the software was not formally included in the RFC_URE3 configuration baseline with other commercially available or open-source application software traditionally tracked for configuration and patch management purposes. That said, with the configuration baseline serving as the starting point for patch management tracking, the custom software was also not formally included in the CIP Patch Management Program in place at that time. Nonetheless, despite the fact that the application was not tracked as part of the CIP Patch Management Program, RFC_URE3 did have controls in place to ensure applicable patches were assessed and implemented as appropriate. Specifically, the vendor of the application works directly with RFC_URE3 resources in the normal course of business and has sent and continues to send email notifications to multiple identified recipients within RFC_URE3 in the form of technical service bulletins (TSBs). Since the installation of the application in the RFC_URE3 environment, these TSBs have always been non-security related bug-fixes or enhancements. Although the recipients would review the TSB upon receipt and in all cases update the application following the change control process, receipt, assessment, and installation of the patch was not documented in the CIP Patch Management Program. On average, less than two TSBs are issued per year. RFC_URE3 received the first security-related TSB from the application vendor. Discussions surrounding the applications in the environment and the issuance of the TSB prompted a review of the configuration baseline and patch management documentation. That review confirmed the application was included in the baseline, but was not being tracked in the Patch Management Program. This discovery triggered an investigation and subsequent remediation actions. The application was added to the authoritative patch source list the following day, and formally assessed. The patch underwent testing within the change control process, but it was determined to have compiling issues and therefore deemed un-installable for RFC_URE3’s customized version of the application. The vendor was contacted regarding the patch compiling issue. The vendor subsequently released an updated version of the security patch for RFC_URE3’s customized version of the application, which was tracked within RFC_URE3’s Patch Management Program and change management initiated for testing and installation. This noncompliance involves the management practice of asset and configuration management because RFC_URE3 did not include the custom software at issue and its patches in RFC_URE3's Patch Management Program. This failure to include and track the software and its patches in RFC_URE3's Patch Management Program is a root cause of this noncompliance. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE3’s risk-harm assessment determined this issue to be of minimal impact to the BPS. Although the patches received via the TSBs were not assessed and documented within the CIP Patch Management Program, they were nonetheless assessed and installed following the change control process within an appropriate timeframe. Additionally, all TSB notifications are directly sent to specifically identified RFC_URE3 contacts as they are issued, thus reducing the risk of not identifying an applicable patch by failing to review a source location on a set interval. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) added the custom application and its patch source to the Patch Management Program; and 2) reviewed the program to ensure that no other custom software installations have been inadvertently excluded from the current Patch Management Program.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017969 | CIP-004-6 | R5 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-004-6 R5. RFC_URE3 identified a possible issue of CIP-004-6 R5 for not completing the removal of unescorted physical access within 24 hours of termination. The facts of this case were complicated by negotiations to retain an employee, who is in good standing with RFC_URE3. RFC_URE3 management began the process of preparing for the voluntary termination of an employee by submitting a Termination & Retirement Notification (TRN) form. This form is routed for approval and notifications are distributed to key individuals within RFC_URE3 who are required to take action on a termination. However, after discussions with Human Resources (HR) for options to retain the employee, an offer was made to the employee to retain his services. At that time, the termination process was temporarily paused until a time in which the employee would accept or reject the offer to stay with RFC_URE3. The following day, the employee’s shift supervisor submitted a second TRN form without knowledge of the initial TRN being submitted and temporarily paused by management on the previous day. That second TRN form was subsequently rejected by management since it was a duplicate of the initial TRN form. As a result, a rejection notification was sent to all form recipients with instructions to stop all actions in the termination process. As discussed below, this action led to confusion amongst responsible personnel thinking that the entire termination process had been cancelled, when in fact the initial TRN was still active and the second TRN had only been rejected as duplicative. After several days of negotiation, RFC_URE3 management was notified by the employee that he would not be returning to work and that he would not be accepting the retention offer. Management notified HR of the employee’s final decision to terminate, at which time HR initiated a termination form which routes to the IT group for electronic access removal and Corporate Security for physical access removal. IT removed all electronic access rights that same day and closed the form. However, the Corporate Security personnel who received the form did not take immediate action due in part to having previously received a TRN rejection notice for this particular employee and the timing of the submission of the termination form. In conjunction with HR’s termination form, RFC_URE3 also employs a “stop gap” NERC Physical Access Form. As per internal processes, this form was also initiated by management. However, in this case, the physical access form was routed to a manager who was unavailable, and as a result, the form was not processed by Corporate Security until five days later. The root cause of this issue (i.e., untimely removal of unescorted Physical Security Perimeter access rights) stems from a failure in both the primary and stop-gap processes for physical access removal. With regard to the primary process, the creation and rejection of the duplicative TRN caused confusion, which ultimately resulted in personnel disregarding the termination form received through HR. With regard to the stop-gap process, the NERC Physical Access Form was initiated, but routed to an individual for approval who was unavailable to approve the form. This noncompliance involves the management practice of workforce management through ineffective training. The duration of the noncompliance was approximately four days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Risk-Harm assessment determined that the risk to the BPS was minimal. Electronic access was revoked immediately, and physical access was revoked within 5 days of notification. The employee separated his employment voluntarily, and was provided an offer to retain his employment due to his good standing with the company. Moreover, the employee has not returned to any of the RFC_URE3 facilities following his voluntary departure. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) provided additional awareness to hiring managers on the steps for employee terminations; and 2) evaluated the termination and notification process and make adjustments as necessary to address any identified gaps.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017966 | CIP-007-6 | R2 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-6 R2. Having completed a thorough compliance investigation, RFC_URE4 determined it had a potential issue involving CIP-007-6 R2 by not documenting a custom software application and its authoritative patch source in the tracking portion of the Patch Management Program. While the custom application and its patch source were not documented as part of the CIP Patch Management Program, RFC_URE4 did have controls in place to ensure relevant patches were assessed and appropriate actions were performed. Of the various clarifications and enhancements implemented in V5/V6 of the CIP Standards, CIP-010-2 R1 Part 1.1 specifically requires the development of a baseline configuration to include custom software. Prior to CIP-010-2, CIP-003 generally set forth the configuration management requirements with no mention of custom software. Accordingly, when the custom application at issue was first configured for and installed in the RFC_URE4 environment, the software was not formally included in the RFC_URE4 configuration baseline with other commercially available or open-source application software traditionally tracked for configuration and patch management purposes. That said, with the configuration baseline serving as the starting point for patch management tracking, the custom software was also not formally included in the CIP Patch Management Program in place at that time. Nonetheless, despite the fact that the application was not tracked as part of the CIP Patch Management Program, RFC_URE4 did have controls in place to ensure applicable patches were assessed and implemented as appropriate. Specifically, the vendor of the application works directly with RFC_URE4 resources in the normal course of business and has sent and continues to send email notifications to multiple identified recipients within RFC_URE4 in the form of technical service bulletins (TSBs). Since the installation of the application in the RFC_URE4 environment, these TSBs have always been non-security related bug-fixes or enhancements. Although the recipients would review the TSB upon receipt and in all cases update the application following the change control process, receipt, assessment, and installation of the patch was not documented in the CIP Patch Management Program. On average, less than two TSBs are issued per year. RFC_URE4 received the first security-related TSB from the application vendor. Discussions surrounding the applications in the environment and the issuance of the TSB prompted a review of the configuration baseline and patch management documentation. That review confirmed the application was included in the baseline, but was not being tracked in the Patch Management Program. This discovery triggered an investigation and subsequent remediation actions. The application was added to the authoritative patch source list the following day, and formally assessed. The patch underwent testing within the change control process, but it was determined to have compiling issues and therefore deemed un-installable for RFC_URE4’s customized version of the application. The vendor was contacted regarding the patch compiling issue. The vendor subsequently released an updated version of the security patch for RFC_URE4’s customized version of the application, which was tracked within RFC_URE4’s Patch Management Program and change management initiated for testing and installation. This noncompliance involves the management practice of asset and configuration management because RFC_URE4 did not include the custom software at issue and its patches in RFC_URE4's Patch Management Program. This failure to include and track the software and its patches in RFC_URE4's Patch Management Program is a root cause of this noncompliance. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE4’s risk-harm assessment determined this issue to be of minimal impact to the BPS. Although the patches received via the TSBs were not assessed and documented within the CIP Patch Management Program, they were nonetheless assessed and installed following the change control process within an appropriate timeframe. Additionally, all TSB notifications are directly sent to specifically identified RFC_URE4 contacts as they are issued, thus reducing the risk of not identifying an applicable patch by failing to review a source location on a set interval. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) added the custom application and its patch source to the Patch Management Program; and 2) reviewed the program to ensure that no other custom software installations have been inadvertently excluded from the current Patch Management Program.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017017970 | CIP-004-6 | R5 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-004-6 R5. RFC_URE4 identified a possible issue of CIP-004-6 R5 for not completing the removal of unescorted physical access within 24 hours of termination. The facts of this case were complicated by negotiations to retain an employee, who is in good standing with RFC_URE4. RFC_URE4 management began the process of preparing for the voluntary termination of an employee by submitting a Termination & Retirement Notification (TRN) form. This form is routed for approval and notifications are distributed to key individuals within RFC_URE4 who are required to take action on a termination. However, after discussions with Human Resources (HR) for options to retain the employee, an offer was made to the employee to retain his services. At that time, the termination process was temporarily paused until a time in which the employee would accept or reject the offer to stay with RFC_URE4. The following day, the employee’s shift supervisor submitted a second TRN form without knowledge of the initial TRN being submitted and temporarily paused by management on the previous day. That second TRN form was subsequently rejected by management since it was a duplicate of the initial TRN form. As a result, a rejection notification was sent to all form recipients with instructions to stop all actions in the termination process. As discussed below, this action led to confusion amongst responsible personnel thinking that the entire termination process had been cancelled, when in fact the initial TRN was still active and the second TRN had only been rejected as duplicative. After several days of negotiation, RFC_URE4 management was notified by the employee that he would not be returning to work and that he would not be accepting the retention offer. Management notified HR of the employee’s final decision to terminate, at which time HR initiated a termination form which routes to the IT group for electronic access removal and Corporate Security for physical access removal. IT removed all electronic access rights that same day and closed the form. However, the Corporate Security personnel who received the form did not take immediate action due in part to having previously received a TRN rejection notice for this particular employee and the timing of the submission of the termination form. In conjunction with HR’s termination form, RFC_URE4 also employs a “stop gap” NERC Physical Access Form. As per internal processes, this form was also initiated by management. However, in this case, the physical access form was routed to a manager who was unavailable, and as a result, the form was not processed by Corporate Security until five days later. The root cause of this issue (i.e., untimely removal of unescorted Physical Security Perimeter access rights) stems from a failure in both the primary and stop-gap processes for physical access removal. With regard to the primary process, the creation and rejection of the duplicative TRN caused confusion, which ultimately resulted in personnel disregarding the termination form received through HR. With regard to the stop-gap process, the NERC Physical Access Form was initiated, but routed to an individual for approval who was unavailable to approve the form. This noncompliance involves the management practice of workforce management through ineffective training. The duration of the noncompliance was approximately four days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Risk-Harm assessment determined that the risk to the BPS was minimal. Electronic access was revoked immediately, and physical access was revoked within 5 days of notification. The employee separated his employment voluntarily, and was provided an offer to retain his employment due to his good standing with the company. Moreover, the employee has not returned to any of the RFC_URE4 facilities following his voluntary departure. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) provided additional awareness to hiring managers on the steps for employee terminations; and 2) evaluated the termination and notification process and made adjustments as necessary to address any identified gaps.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017963 | CIP-007-3a | R5 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R5. Following a thorough investigation RFC_URE5 determined that it had a potential issue involving CIP-007-3a R5 regarding the annual change of an account password. Specifically, engineers were performing annual password changes on in-scope NERC devices at a particular substation. While performing the password changes, 1 protection system relay was temporarily out of service, and as a result, the engineers performing the password changes were instructed not to disturb the device by attempting to perform a password reset. Accordingly, the engineers excluded the device from their password change activities, and in the process of doing so, inadvertently failed to record the device on the password change tracking list for that substation. Subsequently, the device was placed back in service, but since the device had not been captured within the password change list, resetting the password for that device was overlooked and the password was not reset. The potential issue was identified while the business area was performing an analysis of password reset dates recently added to the RFC_URE5’s CIP Cyber Asset Database. This database is being expanded to centralize and capture required device data in lieu of multiple methods of tracking data thus reducing risk of administrator errors. This noncompliance involves the management practice of asset and configuration management because RFC_URE5 did not successfully track that this device needed to have its password changed. Failing to put the device on the password change tracking list for that substation is a root cause of this noncompliance. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk harm assessment determined this issue to be of minimal impact to the BPS. The account involved was subject to several layers of protections commensurate with such accounts on devices located within a CIP-protected environment. Specifically, the relay resides within an Electronic Security Perimeter that is physically protected by a control house Physical Security Perimeter located within a gated, fenced yard. The account involved had its default password changed upon commissioning and has documented subsequent annual password resets. Additionally, implemented controls in place at the time of the occurrence detected and corrected the issue immediately upon identification. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) performed a password reset on the one relay device; 2) completed the centralization of password data in the RFC_URE5 CIP Cyber Asset Database to accurately track password reset dates; and 3) created a quarterly control to ensure devices requiring password changes are performed within the required timeframe.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017964 | CIP-006-6 | R2 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-006-6 R2. After concluding a thorough investigation of the incident, RFC_URE5 determined that an employee entered a substation Physical Security Perimeter (PSP) without the appropriate authorizations for unescorted physical access and without an authorized escort as required under the Visitor Control Program for CIP-006-6 R2. Specifically, two RFC_URE5 Electric Maintenance personnel - a Sr. Substation Technician (Technician) and a Technician Trainee (Trainee) - arrived at a RFC_URE5 substation to perform a routine substation inspection. Upon arriving at the control house PSP, the Technician correctly swiped his access card on the door card reader and the door unlocked; the Technician then opened the door and entered. The Technician was immediately followed by the Trainee who also swiped his card, proceeding through the still open substation door into the PSP; however, both employees were unaware that the Trainee’s card swipe was rejected. Although the Trainee was under constant visual contact while the inspection was performed, the Technician believed the Trainee was authorized for unescorted access, and therefore the Technician did not log the Trainee into the visitors log book while in the control house PSP. Shortly thereafter, both employees exited the control house PSP, but the Trainee returned to retrieve his clipboard that he had forgotten inside. The Trainee swiped his card on the card reader, but the door did not unlock. After 4 failed card swipes, the Technician then swiped his card, unlocking the door and allowing the Trainee to enter the control house unescorted to retrieve his clipboard. The Trainee entered and exited the PSP approximately 15 seconds later. As the above incident was occurring, RFC_URE5's Security Console personnel received the system generated rejected card alarms. An immediate review of video footage and security system records indicated an unauthorized individual was allowed to enter the substation PSP without an authorized escort. Contact was made with the Technician at the substation; he was interviewed and informed of the Trainee’s failed card swipes and lack of authorized physical access to the substation. After speaking with the Technician and ensuring the PSP was secure, RFC_URE5 Security Console personnel contacted the on-call security supervisor to inform them of the incident. Although the Trainee was new to the company, he had a valid personnel risk assessment (PRA) on file and had taken the requisite training required for unescorted physical access. Both the Trainee and Technician believed that the request for unescorted physical access was submitted and approved. It was later determined a delay in submitting the access request form contributed to access not being granted before the Trainee began working at the substation. This noncompliance involves the management practice of workforce management because the Trainee was not properly trained on what to do in the event of a failed card swipe. Ineffective training is a root cause of this noncompliance. The duration of the noncompliance was approximately one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk harm assessment determined this issue to be of minimal impact to the BPS. RFC_URE5’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP‐006‐6 requirements. In fact, this issue was identified as a result of these effective controls. Automated alarming mechanisms worked as intended, enabling Security to quickly respond to the issue. Further impacting the assessment, the Trainee was a RFC_URE5 employee with valid PRAs and requisite training on file. Following the incident, the Trainee’s request for access was submitted and approved, granting unescorted physical access to RFC_URE5 substation PSPs. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) followed disciplinary action protocol with the two employees involved in the incident; and 2) provided targeted reinforcement of access requirements to its substation personnel.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017967 | CIP-007-6 | R2 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-6 R2. Having completed a thorough compliance investigation, RFC_URE5 determined it had a potential issue involving CIP-007-6 R2 by not documenting a custom software application and its authoritative patch source in the tracking portion of the Patch Management Program. While the custom application and its patch source were not documented as part of the CIP Patch Management Program, RFC_URE5 did have controls in place to ensure relevant patches were assessed and appropriate actions were performed. Of the various clarifications and enhancements implemented in V5/V6 of the CIP Standards, CIP-010-2 R1 Part 1.1 specifically requires the development of a baseline configuration to include custom software. Prior to CIP-010-2, CIP-003 generally set forth the configuration management requirements with no mention of custom software. Accordingly, when the custom application at issue was first configured for and installed in the RFC_URE5 environment, the software was not formally included in the RFC_URE5 configuration baseline with other commercially available or open-source application software traditionally tracked for configuration and patch management purposes. That said, with the configuration baseline serving as the starting point for patch management tracking, the custom software was also not formally included in the CIP Patch Management Program in place at that time. Nonetheless, despite the fact that the application was not tracked as part of the CIP Patch Management Program, RFC_URE5 did have controls in place to ensure applicable patches were assessed and implemented as appropriate. Specifically, the vendor of the application works directly with RFC_URE5 resources in the normal course of business and has sent and continues to send email notifications to multiple identified recipients within RFC_URE5 in the form of technical service bulletins (TSBs). Since the installation of the application in the RFC_URE5 environment, these TSBs have always been non-security related bug-fixes or enhancements. Although the recipients would review the TSB upon receipt and in all cases update the application following the change control process, receipt, assessment, and installation of the patch was not documented in the CIP Patch Management Program. On average, less than two TSBs are issued per year. RFC_URE5 received the first security-related TSB from the application vendor. Discussions surrounding the applications in the environment and the issuance of the TSB prompted a review of the configuration baseline and patch management documentation. That review confirmed the application was included in the baseline, but was not being tracked in the Patch Management Program. This discovery triggered an investigation and subsequent remediation actions. The application was added to the authoritative patch source list the following day, and formally assessed. The patch underwent testing within the change control process, but it was determined to have compiling issues and therefore deemed un-installable for RFC_URE5’s customized version of the application. The vendor was contacted regarding the patch compiling issue. The vendor subsequently released an updated version of the security patch for RFC_URE5’s customized version of the application, which was tracked within RFC_URE5’s Patch Management Program and change management initiated for testing and installation. This noncompliance involves the management practice of asset and configuration management because RFC_URE5 did not include the custom software at issue and its patches in RFC_URE5's Patch Management Program. This failure to include and track the software and its patches in RFC_URE5's Patch Management Program is a root cause of this noncompliance. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE5’s risk-harm assessment determined this issue to be of minimal impact to the BPS. Although the patches received via the TSBs were not assessed and documented within the CIP Patch Management Program, they were nonetheless assessed and installed following the change control process within an appropriate timeframe. Additionally, all TSB notifications are directly sent to specifically identified RFC_URE5 contacts as they are issued, thus reducing the risk of not identifying an applicable patch by failing to review a source location on a set interval. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) added the custom application and its patch source to the Patch Management Program; and 2) reviewed the program to ensure that no other custom software installations have been inadvertently excluded from the current Patch Management Program.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017968 | CIP-002-5.1 | R1 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-002-5.1 R1. Following a thorough investigation, RFC_URE5 determined that it had a potential issue involving CIP-002-5.1 R1 regarding the proper documentation of certain cyber assets. Specifically, RFC_URE5 identified several substation devices that did not have their classification changed from a designation of “Future” in-scope Bulk Electric System (BES) Cyber Asset (FBCA) to an in-scope BES Cyber Asset (BCA) upon implementation of the CIP v5/v6 Standards. RFC_URE5 tracks all of its in-scope NERC devices in a CIP Cyber Asset Database (CCAD). RFC_URE5 utilizes a classification of FBCA to designate devices that are planned to be commissioned in the future as a way to ensure, among other things, that the devices are tracked and compliant upon commissioning. All of the devices identified were added to CCAD as FBCAs in preparation for the implementation date, and all applicable device protections were applied to the devices prior to that date in accordance with the CIP Reliability Standards. Although all CIP protections were appropriately applied, the classification for each device in CCAD was not changed from FBCA to BCA until a later date. The issue is believed to be the result of an administrative oversight associated with numerous programmatic changes that all went into effect with the CIP v5/v6 implementation. Nonetheless, the issue was identified through effective internal controls, and immediately corrected. This noncompliance involves the management practice of verification because RFC_URE5 did not verify that the classification for each device in CCAD was timely changed from FBCA to BCA. This failure to verify that these changes occurred is a root cause of this noncompliance. The duration of the noncompliance was approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk-harm assessment determined this issue to be of minimal impact to the BPS. While the BCA classification was not updated in a timely manner, all required cyber security protections were appropriately in place for each device. Identification of the issue within CCAD was identified by internal controls and remediated immediately upon verification of the status of each device. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) changed the designation for all devices in question from FBCA to BCA; 2) reviewed CCAD to ensure that there are no additional FBCA designations that have not been transitioned to BCA; and 3) reviewed the change/configuration process to ensure controls are in place to remove the Future designation when a device is brought into scope, including additional descriptions and awareness of the relevant CCAD fields for those with CCAD modification rights.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017971 | CIP-004-6 | R5 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-004-6 R5. RFC_URE5 identified a possible issue of CIP-004-6 R5 for not completing the removal of unescorted physical access within 24 hours of termination. The facts of this case were complicated by negotiations to retain an employee, who is in good standing with RFC_URE5. RFC_URE5 management began the process of preparing for the voluntary termination of an employee by submitting a Termination & Retirement Notification (TRN) form. This form is routed for approval and notifications are distributed to key individuals within RFC_URE5 who are required to take action on a termination. However, after discussions with Human Resources (HR) for options to retain the employee, an offer was made to the employee to retain his services. At that time, the termination process was temporarily paused until a time in which the employee would accept or reject the offer to stay with RFC_URE5. The following day, the employee’s shift supervisor submitted a second TRN form without knowledge of the initial TRN being submitted and temporarily paused by management on the previous day. That second TRN form was subsequently rejected by management since it was a duplicate of the initial TRN form. As a result, a rejection notification was sent to all form recipients with instructions to stop all actions in the termination process. As discussed below, this action led to confusion amongst responsible personnel thinking that the entire termination process had been cancelled, when in fact the initial TRN was still active and the second TRN had only been rejected as duplicative. After several days of negotiation, RFC_URE5 management was notified by the employee that he would not be returning to work and that he would not be accepting the retention offer. Management notified HR of the employee’s final decision to terminate, at which time HR initiated a termination form which routes to the IT group for electronic access removal and Corporate Security for physical access removal. IT removed all electronic access rights that same day and closed the form. However, the Corporate Security personnel who received the form did not take immediate action due in part to having previously received a TRN rejection notice for this particular employee and the timing of the submission of the termination form. In conjunction with HR’s termination form, RFC_URE5 also employs a “stop gap” NERC Physical Access Form. As per internal processes, this form was also initiated by management. However, in this case, the physical access form was routed to a manager who was unavailable, and as a result, the form was not processed by Corporate Security until five days later. The root cause of this issue (i.e., untimely removal of unescorted Physical Security Perimeter access rights) stems from a failure in both the primary and stop-gap processes for physical access removal. With regard to the primary process, the creation and rejection of the duplicative TRN caused confusion, which ultimately resulted in personnel disregarding the termination form received through HR. With regard to the stop-gap process, the NERC Physical Access Form was initiated, but routed to an individual for approval who was unavailable to approve the form. This noncompliance involves the management practice of workforce management through ineffective training. The duration of the noncompliance was approximately four days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Risk-Harm assessment determined that the risk to the BPS was minimal. Electronic access was revoked immediately, and physical access was revoked within 5 days of notification. The employee separated his employment voluntarily, and was provided an offer to retain his employment due to his good standing with the company. Moreover, the employee has not returned to any of the RFC_URE5 facilities following his voluntary departure. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) provided additional awareness to hiring managers on the steps for employee terminations; and 2) evaluated the termination and notification process and make adjustments as necessary to address any identified gaps.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017018197 | CIP-004-6 | R2 R2.2 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-004-6 R2.2. RFC_URE6’s Security Command Center (SCC), which has responsibility for monitoring Physical Access Control Systems (PACS), is staffed 24/7 by contractor personnel. All operators are employees of the contract security provider (the contractor). Roles and responsibilities for each position are spelled out in the agreement between RFC_URE6 and the contractor. Pursuant to RFC_URE6’s policies which are designed to be compliant with NERC Standards, new operators are permitted to observe operations, but are not permitted to interact with the systems until individual operator accounts are established. New operators do not receive individual accounts until they complete the required NERC training. SCC personnel began onboarding a new operator. When the onboarding began, the operator had not completed the required NERC training and was signed in on the visitor log and escorted while inside the Physical Security Perimeter (PSP). For the duration of this noncompliance, the new operator was signed in on the visitor log and escorted while inside the PSP. This is permitted under RFC_URE6’s policies. That same day, a senior operator logged onto a NERC workstation with the senior operator’s credentials and then turned the system over to the new operator who monitored and responded to live alarms from 5:15 PM to 11:00 PM. The new operator only had access to the PACS. While the new operator was monitoring and responding to live alarms, a senior operator or another experienced operator was present and monitoring the new operator for the entire time period. Pursuant to RFC_URE6’s policies, the new operator should not have been permitted to interact with the system until his individual account was established. The new operator’s interaction with the system through a NERC workstation is not permitted under RFC_URE6’s policies. The next day, another senior operator logged onto a NERC workstation with the senior operator’s credentials and then turned the system over to the new operator who again monitored and responded to live alarms from 3:00 PM to 8:45 PM. The new operator had access only to the PACS. While the new operator was monitoring and responding to live alarms, a senior operator or another experienced operator was present and monitoring the new operator for the entire time period. Pursuant to RFC_URE6’s policies, the new operator should not have been permitted to interact with the system until his individual account was established. The new operator’s interaction with the system through a NERC workstation is not permitted under RFC_URE6’s policies. After the shift, the lead operator (the shift worker that supervises the activities of a given shift and someone that had not been involved beforehand) discovered that RFC_URE6 had not followed its onboarding process in regards to the new operator and notified RFC_URE6 accordingly. RFC_URE6 did not follow its onboarding process because the senior operator allowed a new operator to log into a NERC workstation and interact with the system before the new operator had an individual account established. The new operator should not have been permitted to interact with the system until his individual account was established. The new operator did not have an individual account yet because the new operator had not yet completed the required NERC training. The new operator’s interaction with the system through a NERC workstation is not permitted under RFC_URE6’s policies. After receiving this notification, RFC_URE6 took immediate action to remove the new operator and investigate the issue. RFC_URE6’s investigation determined that the manager for the contractors at RFC_URE6’s SCC failed to provide adequate instructions and information as to the new operator’s status to the lead and senior operators. The issue was that the new operator should not have been logged into a NERC workstation because he had not completed the required NERC training yet and did not have an individual account. At the time of the noncompliance RFC_URE6 had processes in place for onboarding and training of personnel. The manager for the contractors at RFC_URE6’s SCC was trained and made specifically aware of these processes, but failed to ensure the established processes were adhered to and no longer serves RFC_URE6. Following his removal and this incident, RFC_URE6’s process for onboarding new operators has been reinforced with the new manager for the contractors at RFC_URE6’s SCC and all relevant staff supporting the SCC. This noncompliance involves the management practice of verification because the lead operators did not verify that the new operator had completed his required NERC training before allowing him to log into a NERC workstation. That lack of verification is a root cause of this noncompliance. The duration of the noncompliance was approximately one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Under the Operator login, the user does not have the ability to grant unescorted access, modify access control lists, and modify configurations or settings for access control devises or other similar functions. Access to the PACs permits an operator to temporarily release a door and respond to alarms. Because the Operator only had limited access to the PACS, the risk to the BPS was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) denied the onboarding Operator access to the PACS until NERC training was completed; 2) removed the contractor manager who failed to adequately communicate new operator status. The contractor manager no longer serves RFC_URE6; and 3) performed reinforcement training with SCC management. This includes review of onboarding process including NERC training and personnel risk assessment requirements.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017016774 | CIP-006-6 | R2; R2.2 | SPPRE_URE1 submitted a Self-Log stating that it had an issue of noncompliance with CIP-006-6 R2.2. SPPRE_URE1 identified two instances of noncompliance with CIP-006-6 R2.2 where SPPRE_URE1 employees did not follow its documented visitor control program. Instance #1: Eight SPPRE_URE1 employees who did not have authorized access into the Physical Security Perimeter (PSP) were escorted into the Primary Control Center (PCC) for a tour. All eight SPPRE_URE1 employees were issued PSP visitor badges that were required to be scanned upon entry and exit of the PSP. Scanning the badge creates a log entry in the SPPRE_URE1 Physical Access Control System (PACS) that includes the date and time of each visitor’s entry and exit. Seven of the eight SPPRE_URE1 employees scanned their visitor badges upon entry to the PCC. Fourteen minutes after entering the PSP, the eight SPPRE_URE1 employees scanned their badges to exit the PCC, followed by their PCC authorized escort. The following morning, the SPPRE_URE1 Security Operations Specialist notified the PCC authorized escort that seven visitor badges were scanned upon entry and eight visitor badges were scanned upon exit. Because one of the visitors did not follow the entry process in the visitor control program, a log of the visitor’s entry was not created. Instance #2: Three SPPRE_URE1 employees, who did not have authorized unescorted physical access into a PSP, were escorted by an authorized SPPRE_URE1 employee (AE#1) into the PCC for a luncheon. Twelve minutes after the three escorted employees entered the PSP, another authorized SPPRE_URE1 employee (AE #2) was attempting to enter the PCC, but triggered an invalid badge alarm. AE #1 exited the PCC to silence the alarm. AE #1 re-entered and then immediately exited the PCC to assist AE #2 with checking out a temporary badge, leaving the three employees inside the PSP and not within AE#1’s eyesight. SPPRE_URE1’s visitor control program requires that visitor(s) must be continuously escorted within the PSP by an individual with authorized unescorted physical access to the PSP, and the escort ensures that each visitor remains within eyesight at all times inside the PSP. If the escort needs to be relieved by another escort, then the visitor(s) is escorted out of the PSP until another escort can be located. Because the three SPPRE_URE1 employees AE #1 was responsible for escorting within the PCC were not within his eyesight for approximately five minutes and he did not follow the relief process as required by SPPRE_URE1’s visitor control program, AE#1 did not follow SPPRE_URE1’s documented visitor control program. The duration of this instance of noncompliance was nine days, from the date the first instance of noncompliance occurred, through the day after the last instance of noncompliant entry to the PSP. The root cause of these instances of noncompliance was human error. SPPRE_URE1 employees failed to follow SPPRE_URE1’s visitor control program for visitor entry and escort of unauthorized individuals within the PSP. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to follow SPPRE_URE1’s visitor control program has the potential to affect the reliability of the BPS by providing the opportunity for visitors with malicious intent to access Cyber Assets within the PSP, which could compromise bulk electric system (BES) Cyber Systems. Notwithstanding, all PSP visitors were SPPRE_URE1 employees with Personal Risk Assessments and current CIP training on file and were continuously escorted by authorized SPPRE_URE1 personnel, although not the assigned authorized escort, while inside the PCC. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) reinforced the visitor control program in a security awareness communication to all individuals with authorized unescorted physical access to BES Cyber systems; and, 2) conducted training for individuals who require authorized unescorted physical access to a PSP. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2017017394 | CIP-006-6 | R2; R2.2 | SPPRE_URE1 submitted a Self-Log stating that it was in violation of CIP-006-6 R2.2. SPPRE_URE1’s Visitor Control Program requires a SPPRE_URE1 authorized escort to take visitors who are not SPPRE_URE1 employees to the Security Control Center (SCC) to obtain a Physical Security Perimeter (PSP) visitor badge. The process is necessary to ensure the identity of the visitor is properly logged within the Physical Access Control System (PACS) upon entry and exit of a PSP. A contract service technician (technician) was on site to work in SPPRE_URE1’s Primary Control Center (PCC) PSP. The technician was issued a visitor badge for common areas but was not issued a PSP visitor badge in accordance with SPPRE_URE1’s Visitor Control Program. The SPPRE_URE1 authorized escort, who had authorized unescorted physical access to the PSP, escorted a SPPRE_URE1 employee, who did not have authorized access to the PSP, and the technician into the PSP without verifying the technician had a PSP visitor badge. After escorting the visitors into the PSP, the SPPRE_URE1 authorized escort was notified by the SCC that the technician needed a PSP visitor badge because he was not a SPPRE_URE1 employee, in accordance with Visitor Control Program. The SPPRE_URE1 authorized escort took the SPPRE_URE1 employee and technician to the SCC to be issued PSP visitor badges. The duration of this instance of noncompliance was two minutes, from the time the SPPRE_URE1 authorized escort allowed the technician into the PSP without a PSP Visitor Badge, through the time the technician was issued a PSP Visitor Badge. The root cause of this instance of noncompliance was human error. The SPPRE_URE1 authorized escort did not follow the Visitor Control Program, therefore he did not ensure the identity of the visitor was properly logged within the PACS upon entry and exit of the PSP. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to follow the documented Visitor Control Program has the potential to affect the reliability of the BPS because if a security event had occurred impacting the bulk electric system (BES) Cyber Systems within the PSP, SPPRE_URE1 would not have important visitor information recorded in its PACS to adequately analyze the event. Notwithstanding, the PSP visitor’s identity was known by SPPRE_URE1 employees and the visitor was continuously escorted within the PSP. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) emailed and reminded individuals with authorized unescorted physical access to a PSP that each visitor who is not a SPPRE_URE1 employee must use a designated PSP visitor badge to access a PSP; 2) created a tip sheet that summarizes the SPPRE_URE1 visitor control program and posted it at each PSP access point; and, 3) conducted training for individuals who require authorized unescorted physical access to a PSP. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2016016106 | CIP-002-3 | R3; R3.1 | During a Compliance Spot Check, SPP RE determined that SPPRE_URE2 had an issue of noncompliance with CIP-002-3 R3.1. SPPRE_URE2 did not identify two switches, which were used to communicate with its substation and generation facility remote terminal units (RTUs), as Critical Cyber Assets (CCAs). Instead, the switches were identified on the CCA list as non-CCAs within an Electronic Security Perimeter (ESP). The duration of this instance of noncompliance was approximately 45.5 months, from the day following the previous Compliance Audit, through the date the two switches were identified as High Impact Bulk Electric System (BES) Cyber Systems ( a CCA classification under Version 3 is equivalent to a High Impact BES Cyber System under Version 5). The root cause of this instance of noncompliance was human error, i.e., a misinterpretation of the technical guidance associated with communications equipment classifications as CCA’s, which was included in SPPRE_URE2’s CCA Identification Process. SPPRE_URE2 did not correctly consider that the switches performed communications transport between the SCADA system switches and the firewall within the respective ESPs, which changed the nature of how the switches should have been analyzed and categorized. Because of this nuance, SPPRE_URE2 incorrectly applied the Version 3 communications transport exclusion (which was intended to be limited to communications transport equipment between ESPs) to these switches that performed communications transport within the ESP. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to identify CCAs has the potential to affect the reliability of the BPS by presenting a risk that unidentified CCAs will not be protected, which could compromise such assets and lead to the potential loss of CCA functionality or a complete system failure. Notwithstanding, although the switches were not identified as CCAs, they were protected as CCAs because they were on the CCA list and reside inside an ESP and PSP. Therefore, this was merely a documentation deficiency. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) provided additional training to, and interactive discussion with, the applicable personnel regarding how to apply the process to identify BES cyber systems and the CIP-002-5 bright-line criteria to switches inside the ESP; and 2) correctly identified the two switches as High Impact BES Cyber Systems (SPPRE_URE2 was required to mitigate to Version 5 of CIP-002; the equivalent of a CCA classification under Version 3 is High Impact BES Cyber System under Version 5). SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2016016160 | CIP-010-2 | R1; R1.1.3, R1.1.4 | During a Compliance Audit, SPP RE determined that SPPRE_URE3 had an issue of noncompliance with CIP-10-2 R1.1.3 and R1.1.4. SPPRE_URE3 did not include its custom SCADA/EMS software in its configuration baseline for any of the Cyber Assets on which the software had been installed (R1.1.3). SPPRE_URE3 also failed to identify in its configuration baseline two logical network accessible ports for a server (R1.1.4). The duration of this instance of noncompliance was 38 days, from the effective date of the standard through the date the configuration baseline was updated to include the custom SCADA/EMS software and the two logical network accessible ports. The root cause of the instance of noncompliance with CIP-010-2 R1.1.3 was a combination of human error, i.e., personnel oversight of not manually recording the two ports, and a procedural gap, i.e., procedure not requiring the server to be operating in a primary state when capturing the configuration baseline. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to maintain a complete configuration baseline has the potential to affect the reliability of the BPS by providing an opportunity for unauthorized and undetected modifications to be made to applicable Bulk Electric System (BES) Cyber Systems, which could introduce system instability or affect the functionality of such systems. Notwithstanding, regarding R1.1.3, SPPRE_URE3 personnel had documented the installed custom SCADA/EMS software as required by other applicable CIP standards, e.g., CIP-007-6 R1 and R2. Thus, security patches associated with the software were tracked, evaluated, and up-to-date. SPPRE_URE3 was aware of the installed custom software but simply failed to document the software on its configuration baseline. Regarding R1.1.4, the two unidentified ports are required to run the custom SCADA/EMS software. SPPRE_URE3 had identified all logical network ports used to run the applications associated with the custom software but simply failed to manually record the two ports for the secondary server. SPPRE_URE3’s High and Medium Impact BES Cyber Systems and their associated Cyber Assets are continuously monitored and protected by an intrusion prevention/detection system, which provides real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the Electronic Security Perimeter. SPPRE_URE3 retained the logged events and routinely performed security event analysis for the purpose of identifying hidden security issues. Therefore, any malicious software utilizing these two ports would most likely have been immediately detected. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) updated its baseline to include the SCADA/EMS custom software (R1.1.3); 2) updated its baseline to include the two logical network accessible ports (R1.1.4); and 3) revised its configuration process to require all servers to be operating in a primary state when creating baselines to ensure that all applications on the servers are enabled (R1.1.3). SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2017017043 | CIP-004-3a | R4; R4.2 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-3a R4.2. During SPPRE_URE4’s CIP-004 quarterly access audit, SPPRE_URE4 identified three employees where it had not revoked unescorted physical access to SPPRE_URE4’s Critical Cyber Assets within seven calendar days from the date they no longer required such access. SPPRE_URE4 had two Physical Access Control System (PACS) access lists for its Primary Control Center (PCC) Physical Security Perimeter (PSP) and for its Alternate Control Center (ACC) PSP, i.e. the PCC or ACC authorized access list and a 24/7 Group access list. When the ACC card reader was installed, the 24/7 Group access list, originally used to control access solely to the PCC, was assigned to the ACC controller granting authorized unescorted access to the ACC. Each access list had a different ruleset; therefore, if a name was removed from the PCC or ACC authorized access list, it was not automatically removed from the 24/7 Group access list. Instance #1: During SPPRE_URE4’s review of access rights during the transition from CIP Version 3 standards to Version 6 standards, it was determined that Employee A no longer needed authorized unescorted access to SPPRE_URE4’s ACC PSP. When updating the PACS access list with the change, the PACS administrator removed Employee A’s name from the ACC access list but did not realize that Employee A’s name remained on the 24/7 Group access list. Therefore, SPPRE_URE4 did not revoke Employee A’s authorized unescorted access to the ACC PSP. The duration of this instance of noncompliance was 127 days, beginning the date SPPRE_URE4 installed the ACC card reader and granted the employee authorized unescorted access to the ACC PSP, and ending the date SPPRE_URE4 revoked Employee A’s access to the ACC PSP. Instance #2: While reviewing the scope of Instance #1, SPPRE_URE4 discovered that another employee (Employee B), was also listed on the 24/7 Group access list; therefore, Employee B had unauthorized unescorted access to the ACC. Employee B was authorized unescorted access to the PCC PSP, however, SPPRE_URE4 did not revoke Employee B’s unescorted access to the ACC PSP. The duration of this instance of noncompliance was 92 days, beginning the date SPPRE_URE4 installed the ACC card reader that granted authorized unescorted access to the ACC PSP, and ending the date SPPRE_URE4 revoked Employee B’s access to the ACC PSP. Instance #3: While enabling physical access to the PCC PSP in the PACS for another SPPRE_URE4 employee (Employee C), the PACS administrator placed Employee C on the 24/7 Group access list, thereby granting Employee C unauthorized unescorted access to the ACC. Employee C should not have had unescorted access to the ACC. Therefore, SPPRE_URE4 did not revoke Employee C’s unescorted access to the ACC PSP. The duration of this instance of noncompliance was 16 days, beginning the date Employee C was granted unauthorized unescorted access to the ACC, and ending the date SPPRE_URE4 revoked Employee C’s access to the ACC PSP. The root cause of these instances of noncompliance was lack of a documented process for SPPRE_URE4 personnel to follow when creating, adding, or removing physical access rights in the SPPRE_URE4 PACS, i.e. process to ensure employees were removed from both the ACC access list and the 24/7 Group access list when access rights were changed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly remove physical access to a PSP has the potential to affect the reliability of the BPS by allowing unauthorized physical access to Critical Cyber Assets, potentially allowing a person with malicious intent access to these assets. Notwithstanding, the potential risk to the BPS was mitigated by several factors. The three employees that continued to have access to the ACC PSP were long-time employees of SPPRE_URE4 and had authorized unescorted physical access to SPPRE_URE4’s PCC PSP. Additionally, the SPPRE_URE4 ACC PSP is completely within a building that has additional layers of security and access control. The three SPPRE_URE4 employees in question did not attempt to access the ACC PSP during the violation timeframe, and had current CIP-004 Cyber Security training and Personnel Risk Assessments on file. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE4: 1) revoked access to the ACC PSP for the three SPPRE_URE4 employees in question; 2) removed the 24/7 Group access list ruleset to prevent granting unauthorized access to the ACC PSP; and, 3) revised and distributed its Access Control Process to include a step to audit an employee’s access when changed to confirmed access privileges are correct. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017016870 | CIP-006-6 | R1; P1.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-006-6 R1. In particular, Texas RE determined that TRE_URE1 did not utilize two or more different Physical Access Control Systems (PACS) on one Physical Security Perimeter (PSP) as required by CIP-006-6 R1, Part 1.3. TRE_URE1 established a PSP for two Protected Cyber Assets (PCAs) associated with High Impact BES Cyber Systems. Subsequently, TRE_URE1 discovered that the PSP in question only had one physical access control in place instead of the two required for High Impact BES Cyber Systems and their associated devices. Accordingly, TRE_URE1 implemented the required two physical access controls for the PSP, ending the issue. The root cause of TRE_URE1’s noncompliance was an inadequate process to ensure that TRE_URE1 implemented all necessary physical access controls for PSPs containing High Impact BES Cyber Systems and their associated devices. In particular, TRE_URE1’s process for classifying BES Cyber Systems and their associated devices and then installing appropriate physical access controls for those devices required coordination between various departments. Within this framework, TRE_URE1 lacked a process to ensure effective communication between these groups, as well as a process to periodically review their respective activities to ensure all required physical access controls were implemented. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) based on the following five factors. First, the single PSP at issue had a physical access control in place that operated to restrict physical access for the issue duration. Second, the PSP at issue was alarmed to notify TRE_URE1 if there was an unauthorized entry, and TRE_URE1 personnel continuously monitored the PSP for unauthorized access alarms. Third, there were no unauthorized physical access attempts to the PSP during the noncompliance period. Fourth, TRE_URE1 logged visitors into the PSP as required throughout the issue duration. Finally, TRE_URE1 had redundant devices at other physical locations possessing all required physical access controls that could have operated in the event the PCAs at issue were compromised. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) implemented two physical access controls to the PSP as required; 2) performed an extent of condition review confirming that the appropriate physical access controls were in place at all other High Impact BES Cyber Systems locations; 3) implemented a new process to communicate the actual PSP impact ratings with the group responsible for installing all required physical access controls; 4) updated the Physical Security Plan to include the new process of communicating PSP impact ratings to the group responsible for installing all required physical access controls; and 5) implemented a detective control to periodically validate the PSP impact ratings by requiring quarterly recertification of all impact ratings by each responsible business unit. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017017381 | CIP-007-3a | R2; R2.3 | During a Compliance Audit, Texas RE determined that TRE_URE2, had an issue with CIP-007-6 R1, Part 1.1. In particular, TRE_URE2 failed to ensure that a single enabled logical port was required for normal and emergency operations. Texas RE determined that TRE_URE2 initially had an issue with CIP-007-3a R2.3, and subsequently had an issue with CIP-007-6 R1, Part 1.1. Texas RE further determined that, for purposes of this issue, there was no substantive change in TRE_URE2's compliance obligations under the NERC Reliability Standards at issue. TRE_URE2 enabled a single port on four switches. At the time of the installation, TRE_URE2 relied on cyber vulnerability penetration scans from outside of its firewalls to detect any newly enabled ports. In the current circumstance, however, the port at issue was on a non-Windows device located behind a firewall. As a result, the vulnerability scan did not detect it. TRE_URE2 then updated its vulnerability scanning process to perform additional, direct scans of ports on all non-Windows devices on its system and detected the single enabled port at issue. Upon discovering the enabled port in question, TRE_URE2 assigned an Information Technology (IT) technician to disable the port. However, the technician failed to fully disable the port associated with two of the switches. Subsequently, TRE_URE2 performed a review of its system baselines and determined that the port remained enabled. TRE_URE2 completed its analysis of the port at issue, determined it was a necessary port, and added it to its list of logical network accessible ports, ending the issue. The root cause for this issue was an insufficient process for identifying open ports and services. Specifically, TRE_URE2’s process for ensuring only necessary ports were enabled relied solely on vulnerability assessments that did not scan for non-Windows devices located behind a firewall and, therefore, potentially resulting in the failure to identify all enabled ports on its system. In addition, TRE_URE2’s existing procedures lacked sufficient detail to ensure that all TRE_URE2 personnel performed all necessary port identification and documentation activities as required. The duration of the noncompliance was approximately five years and five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following four reasons. First, the enabled port and associated switches are located within a Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP), and are isolated from TRE_URE2’s corporate network and internet behind multiple firewall layers. Second, electronic access to the two switches through the enabled port was itself blocked by a firewall. Third, TRE_URE2 deploys network based intrusion prevention and/or detection devices, which would have alerted TRE_URE2 personnel if any unauthorized electric access attempts were made. Finally, TRE_URE2 determined that the single enabled port was necessary for its normal and emergency operations. No harm is known to have occurred. | To mitigate this issue, TRE_URE2: 1) updated its applicable spreadsheet to include the enabled port at issue as a necessary port for normal and emergency operations; 2) implemented a new process to provide more specific guidance to staff or third-party vendors in performing vulnerability assessments and reviews; 3) modified its cyber vulnerability scanning process to perform additional, direct scans of its system for open ports; 4) implemented its Baseline Management Plan to address baseline procedures in compliance with CIP-010-2; 5) added a new entry in its periodic tasks spreadsheet that stipulates that TRE_URE2 must perform a monthly audit of Baseline Configurations; and 6) counseled the TRE_URE2 technician regarding the need to verify and document completion of assigned tasks, including activities related to disabling or analyzing ports. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017017083 | CIP-004-3a | R4; R4.1 | TRE_URE3 submitted a Self-Report stating that it had two issues with CIP-004-3a R4.1. In particular, TRE_URE3 failed to update its Access Authorization List (AAL) within seven calendar days of granting authorized unescorted physical access to Critical Cyber Assets (CCAs) on two occasions. First, TRE_URE3 restored an employee's authorized unescorted physical access rights to CCAs. As such, TRE_URE3 should have updated its AAL to reflect this change in physical access rights within seven days of making the change, but did not do so. Then, TRE_URE3 granted authorized unescorted physical access rights to a single third-party contractor. As such, TRE_URE3 should have again updated its AAL to reflect this change in physical access rights within seven calendar days, but again failed to do so. TRE_URE3 subsequently discovered during its quarterly CIP Access Review that it had not updated its AAL to reflect these two physical access rights changes. Following this discovery, TRE_URE3 updated its AAL to reflect the changes in the authorized unescorted physical access rights for both individuals, ending the issue. The root cause of these instances of noncompliance was that TRE_URE3 lacked an adequate process to ensure it updated its AAL in a timely manner. In particular, TRE_URE3 did not possess a sufficient process to timely review and compare its AAL with its actual unescorted physical access authorizations. The duration of the noncompliance was approximately 36 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this noncompliance related solely to TRE_URE3’s unescorted physical access documentation. In particular, the two individuals at issue had the appropriate authorized unescorted physical access rights to TRE_URE3 CCAs, and both individuals had completed CIP Cyber Security awareness training and possessed valid Personnel Risk Assessments (PRAs). Second, the issue duration of the noncompliance was short, lasting only 36 days. No harm is known to have occurred. | To mitigate this issue, TRE_URE3: 1) revised the AAL to include the omitted employee and contractor; 2) implemented a process that compares the access authorization list and physical access authorizations twice a day; and 3) updated its access authorization procedure to comply with Version 5 for CIP, including requiring quarterly verifications that individuals with authorized unescorted physical access possess authorization records. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017214 | CIP-007-3a | R3 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R3.1. Specifically, WECC_URE1 reported that it failed to assess for applicability nine security patches or security upgrades, within the required timeframe, for its Medium Impact Bulk Electric System (BES) Cyber Systems (MIBCS) located at its Control Center. The security patch or security upgrade assessment for four patches should have been assessed within 30 calendar days pursuant to CIP-007-3a R3.1, and for five patches should have been evaluated within 35 calendar days pursuant to CIP-007-6 R2 Part 2.1. The root cause was a less than adequate procedure that did not include a review to verify that the assessment of security patches for applicability was performed. WECC reviewed the Self-Report and after further discussions with WECC_URE1 and analysis of data request responses, determined that the WECC_URE1 failed, on nine separate occasions, to assess security patches for applicability within the required timeframe. This issue started after the earliest of the nine security patches was released, and ended when the patch was assessed for applicability, for a total of 260 days of noncompliance. The other eight security patches that were not assessed for applicability within the required timeframe started and ended within those 260 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to assess security patches and security upgrades for applicability within the required timeframe. Such failure could have left WECC_URE1 at risk of possible exploits of vulnerabilities on its Cyber Assets which could result in an attacker gaining access and modifying permissions associated with WECC_URE1’s MIBCS; thereby potentially affecting the reliability of the BES. However, the devices are located in the SCADA systems which is within the Physical Security Perimeter (PSP). There is no access available to the SCADA systems outside the PSP. Additionally, all Cyber Assets are separated by firewalls from WECC_URE1’s corporate networks. WECC_URE1 also uses a system with technology that can detect new and unknown attacks, even for threats for which no vendor patch exists. Based on this, WECC determined that the issue had a minimal likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) reviewed patches for applicability; 2) created a master list (spreadsheet), that is reviewed weekly in its NERC-CIP team meeting, to track applications and software that need to be manually checked for security patches every 35 days; 3) added a peer review column to the spreadsheet in order to note that a peer review was performed and all tasks have been completed; 4) holds a weekly NERC-CIP team meeting to review the spreadsheet, complete peer reviews, and reviews tasks to be sure that if there is staff turnover or someone is out of the office for an extended period of time their tasks get picked up; 5) conducted a training for all Subject Matter Experts involved with patch management to update them on the process; and 6) created a roles and responsibilities matrix to identify staff responsible for CIP documentation and implementation. WECC has verified the completion of all mitigation activity.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016713 | CIP-010-2 | R2 | WECC_URE2 submitted a Self-Report stating it had an issue with CIP-010-2 R2 Part 2.1. Specifically, WECC_URE2 reported that on two separate instances it did not monitor at least once every 35 calendar days for changes to the baseline configuration. The first instance involved a Protected Cyber Asset (PCA) in the High Impact Bulk Electric System (BES) Cyber System (HIBCS). The second instance involved a BES Cyber Asset (BCA) also in the HIBCS. The first instance was discovered while WECC_URE2 was performing a review of its CIP-010 R2 task documentation. WECC_URE2 utilized a manual process to monitor for changes to the baseline configuration for these two devices since the Tripwire agent, which is its automated monitoring process, was not installed on these two devices. The root cause of both instances was less than adequate process for identifying when the performance of a task should occur. WECC reviewed the Self-Report and, after further discussions with WECC_URE2, and analysis of data request responses, determined that the WECC_URE2 on two separate instances failed to monitor at least once every 35 calendar days for changes to the baseline configuration. WECC determined that the first instance began WECC_URE2 failed to monitor at least once every 35 calendar days for changes to the baseline configuration and ended when WECC_URE2 completed its monitoring of the baseline configuration, for a total of seven days of noncompliance. WECC determined that the second instance began when WECC_URE2 failed to monitor at least once every 35 calendars days for changes to the baseline configuration and ended when WECC_URE2 completed its monitoring of the baseline configuration, for a total of nine days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to monitor at least once every 35 calendar days for changes to the baseline configuration on one PCA and one BCA. Such failure could result in an inability to identify intended or unintended modifications to BES Cyber Systems which may affect stability of those systems; thereby potentially affect controlling output of multiple generators at different power plants. However, the likelihood of the harm occurring was reduced by the controls that WECC_URE2 implemented. WECC_URE2 implemented a configuration monitoring process that describes a manual procedure for monitoring changes to the baseline configuration for devices that are not automatically monitored with Tripwire. BES Cyber Assets were protected with two physical access controls for unescorted physical access, and required authentication for interactive remote access. Additionally, the PCA and BCA in scope support operation of a backup automatic generation control system. Should the backup automatic generation control system be lost, backup capability would also be provided by the Emergency Dispatch Center. No harm is known to have occurred. | To mitigate this issue, WECC_URE2 will: 1) complete a manual review of the baseline configuration on both the PCA and BCA in scope; 2) create a monthly standing task for monitoring at least once every 35 calendar days for changes to the baseline configuration; 3) investigate the possibility of automating monitoring of the PCA and BCA in scope; 4) train personnel to monitor for performance using revised tracking, reporting, and alerting processes; 5) identify and document any other controls that resolve the root cause and update applicable procedures where needed; 6) complete automation of monitoring for the devices in scope and implement any new controls; 7) train personnel to use any new controls identified and on updates made to applicable procedures; and 8) after mitigation is complete, perform a monthly review, for the next three months, to verify that the controls have been implemented correctly.
2017-08-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016016292 | CIP-006-3c | R4 | MRO_URE1 stated that a mechanical control component on a Physical Security Perimeter (PSP) door operated improperly, allowing the inactive door leaf of the double door to close ahead of the active door leaf, causing the door to be ajar and unsecured. The door was ajar and unsecured from 5:33 p.m. until 6:40 p.m., and then again from 7:02 p.m. until 9:55 p.m. The issue was discovered during a routine security check performed by system operators. The cause of the noncompliance was the mechanical failure of a door component. This issue started when a mechanical failure caused a PSP door to be left ajar, and ended later that day, when MRO_URE1 discovered the issue, secured the door, and adjusted the door so that it would close properly until it could be replaced. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The unsecured PSP door was protected by additional controls that are not required by the NERC CIP Reliability Standards. Specifically, under MRO_URE1's physical security plan, the building is not open to the general public, and physical access to the building is controlled by a conventional locking system, card entry, and a visitor escort program. This means that an adversary would have to successfully infiltrate a secured point of entry before the adversary could gain access to the unsecured PSP door. Further, the PSP is monitored by CCTV on a 24/7 basis (although human observation is not continuous). Additionally, the duration of the noncompliance was brief, which is attributable to MRO_URE1's scheduled security checks, which is another additional control. Finally, MRO_URE1 reviewed video footage to confirm that there was no unauthorized access to the PSP during the period of noncompliance. No harm is known to have occurred. MRO considered MRO_URE1's CIP-006-3c R4 compliance history in determining the disposition track. MRO_URE1’s relevant prior noncompliance with CIP-006-3c R4 includes: NERC Violation ID MRO2013012572 (CIP-006-1 R3). The prior noncompliance involved a PSP door that did not have alarming enabled on the door. The alarming of the door was apparently overlooked because the door could not be opened from the non-PSP side. MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The current issue was not caused by a failure to mitigate the prior issue, as the current issue was caused by the mechanical failure of a door component that could not be reasonably avoided. | To mitigate this issue, MRO_URE1: 1) manually closed and adjusted the PSP door to enable closing; and 2) replaced the PSP door. MRO_URE1 stated that mitigating activities were complete.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016016553 | CIP-007-6 | R4. | NPCC_URE1 submitted a self-report stating that it had an issue of CIP-007-6 R4. An internal review of BES Cyber Asset capabilities at two medium impact facilities found that 12 of 60 devices did not have logging of cyber security incidents enabled. The 12 devices were originally thought to have both security event logging and detection enabled by default but through the review, it was determined that only detection was enabled. The cause for the noncompliance was an incorrect interpretation of the associated instruction manual. While the devices were capable of performing internal logging of password access attempts, a further configuration step was needed to actually produce the successful/unsuccessful attempts in the sequence of event log. The noncompliance began when the standard became effective and ended when detection and logging were enabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices are BES Cyber Assets associated with Medium Impact Facilities. The capability to detect and prevent failed access attempts was enabled at all times and only the logging of these events for identification of, and after-the -fact investigations of, Cyber Security Incidents was disabled. There were no cyber security incidents detected during the timeframe that logging was not enabled. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1 1) enabled the detection and logging function of the 12 devices to their capability 2) provided additional training to the SME and his designees to review the “lessons learned” and to require review of latest Operating and Instruction Manual associated with each BES Cyber Asset and its current firmware version 3) modified an internal procedure to require vendor verification of the initial review of device capabilities and that the Operating and Instruction Manuals being used correspond to the installed devices firmware version 4) modified an internal procedure to require verification testing once the event logging is configured. This would require relay technicians to enter correct passwords and incorrect passwords, and then provide a copy of the event log for evidence – per asset capability
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016016361 | CIP-004-3a | R4. | NPCC_URE2 submitted a self-report stating that it had an issue of CIP-004-3a R4. NPCC_URE2 failed to remove physical access within seven calendar days of an employee that no longer required access. He had unescorted physical access to NPCC_URE2's control center. Unescorted physical access to the control center was not revoked in the access management system or the badging system. The employee had retired at the end of the year. The cause of the incident was the managers and supervisors in the department having the direct responsibility to revoke access. This lead to an over reliance on a single point of failure to remove access. The combination of competing responsibilities resulted in the revocation task not being completed. The issue started when the employee's access rights should have been removed and ended when access was removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There is dual-factor authentication; an active badge and a PIN, to gain access to the control center. The control center is located in a manned facility that requires corporate access and the PSP is manned 24/7. The individual retired at the end of the year, at which point the badge was collected. No harm is known to have occurred. | To mitigate the issue, NPCC_URE2: 1) revoked unescorted physical access; 2) disciplined the manager for not completing the revocation task; 3) moved the access revocation process to the compliance group. Managers are now only responsible for initial notification of departure. The compliance group facilitates the revocation action. The compliance group has the authorization rights to perform the necessary and timely access revocations in their various systems; 4) assigned an analyst to maintain the department's personnel tracker. The tracker is used to maintain all employees and contractors by functional area and managing supervisor. The tracker will also include pertinent CIP related credentials such as background check dates, personnel risk assessments, training dates, etc.; 5) created a checklist for access revocation;
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2016016362 | CIP-004-3a | R4. | NPCC_URE3 submitted a self-report stating that it had an issue of CIP-004-3a R4. NPCC_URE3 failed to remove physical access within seven calendar days of an employee that no longer required access. He had unescorted physical access to NPCC_URE3's control center. Unescorted physical access to the control center was not revoked in the access management system or the badging system. The employee had retired at the end of the year. The cause of the incident was due to the managers and supervisors in the department having the direct responsibility to revoke access. This lead to an over reliance on a single point of failure to remove access. The combination of competing responsibilities resulted in the revocation task not being completed. The issue started when the employee's access rights should have been removed and ended when access was removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There is dual factor authentication; an active badge and a PIN, to gain access to the control center. The control center is located in a manned facility that requires corporate access and the PSP is manned 24/7. The individual retired at the end of the year, at which point the badge was collected. No harm is known to have occurred. | To mitigate the issue, NPCC_URE3: 1) revoked unescorted physical access; 2) disciplined the manager for not completing the revocation task; 3) moved the access revocation process to the compliance group. Managers are now only responsible for initial notification of departure. The compliance group facilitates the revocation action. The compliance group has the authorization rights to perform the necessary and timely access revocations in their various systems; 4) assigned an analyst to maintain the department's personnel tracker. The tracker is used to maintain all employees and contractors by functional area and managing supervisor. The tracker will also include pertinent CIP related credentials such as background check dates, personal risk assessments, training dates, etc.; 5) created a checklist for access revocation;
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2016015817 | CIP-007-3a | R5; R5.3 | NPCC_URE4 submitted a self-report stating that it had an issue of CIP-007-3a, R5.3. NPCC_URE4 had two instances where passwords were not changed on cyber assets. The SCADA (Supervisory Control and Data Acquisition) devices at NPCC_URE4's substations had password changes performed and documented in NPCC_URE4's password spreadsheet. One of NPCC_URE4's SCADA Admins attempted to log into a CCA at a substation with the new password and failed. The Admin attempted to login a second time with the old password and was successful. Upon further investigation, it was confirmed that two additional devices (3 total) did not have their passwords changed properly, while the remaining CCAs had the passwords changed properly. The duration of this instance is when the previous password change exceeded NPCC_URE4's required time frame to when the passwords on the three CCAs were properly changed. The cause of this instance was a process issue. NPCC_URE4 was unsure whether the passwords were changed to the old password, or whether the devices were overlooked when other devices were having passwords changed, but the process did not ensure that the passwords were changed properly. In the second instance, the NPCC_URE4 Manager of security services and a NPCC_URE4 vender conducted a computer audit report on a Physical Access Control System (PACS) device to check that accounts on the device had passwords changed within 15 months. The report indicated that some local accounts were overdue, and the decision was made to conduct a computer audit report on all workstations and servers using that vendor. The report revealed that 6 local account passwords over 5 PACS devices were overdue for password changes. The accounts consisted of two local admin accounts on primary and backup PCs and servers, and the security account on one PC. The duration of this instance is the time period from the creation of the accounts passed the password change requirement of 15 months to when the identified accounts were either disabled or had their passwords changed. The cause of this instance was a failure to add these accounts to the Security Services password tracking spreadsheet during a PACS servers and workstations refresh. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In the first instance, the number of affected devices was limited, as only 3 of 23 CCAs had not had the password changed properly. The devices were located within a PSP to which 238 NPCC_URE4 employees had access, however only 9 of those employees were part of the SCADA department, and were authorized and had access to the device passwords. All of the affected SCADA devices had physical input port blockers installed, and the devices are located within an ESP which only allowed permitted network traffic. In the second instance, the 5 PACS devices were located behind a firewall with limited remote access capabilities via SSL VPN. The only personnel with remote access were support personnel and user accounts already authorized to access the PACS. The devices themselves are located within a PSP, inside buildings with restricted access and security guards. All 5 devices are monitored for failed and successful login attempts that are reviewed by Security Services personnel. No harm is known to have occurred. | To mitigate this issue NPCC_URE4: 1) Changed the passwords on the 3 affected SCADA devices; 2) Added an additional process for password changes that requires a secondary SCADA employee to validate successful password modification and sign off on the change; 3) Modified the SCADA password spreadsheet to reflect the new process, as well as update the dates for the password changes on the 3 devices; 4) Changed the passwords for the 6 accounts on the 5 PACS devices; 5) Updated the Security Services password spreadsheet to include these 6 accounts; 6) Will perform quarterly computer audit reports on the PACS devices to ensure password compliance; and 7) Created a detailed procedure checklist for refreshing PACS equipment. NPCC has verified completion of all mitigation activities.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2016016368 | CIP-007-6 | R4. | NPCC_URE4 submitted a self-log stating that it had an issue of CIP-007-6 R4. NPCC_URE4's compliance investigation team discovered one review beyond the fifteen (15) day review period. The cause was human error. NPCC_URE4 has two systems that collect and generate log reviews. Both systems were being used to meet the 15 day log review requirement. Two SMEs in different departments were reviewing the logs. One SME was consistently reviewing logs but did not have visibility to the switches and firewalls. The second SME did not consistently perform their review of the logs which resulted in a delayed review of two days. Further investigation determined that the log report was created Friday at midnight and was not reviewed until after the weekend ended. The review of the three (3) switches and five (5) firewalls were out of compliance for two (2) days during one fifteen (15) day review cycle. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance had a delayed review of two days. NPCC_URE4 did not detect any Cyber Security Incidents during the duration the logs were not reviewed. NPCC_URE4 deploys Firewalls to restrict communication to NPCC_URE4's SCADA Environment, an IDS to monitor network traffic for anomalies, and uses software to record events, submit event alerts, and generate event reports. The ability to access the three (3) switches and five (5) firewalls are limited to six (6) individuals that consist of four (4) employees and two (2) contractors. All listed devices are not able to interact with the public internet. No harm is known to have occurred | To mitigate this issue, NPCC_URE4: 1) retrained the individual on their compliance responsibilities; 2) investigated an automated workflow to assign and track compliance tasks; 3) created a calendar to track time bound tasks; 4) reviewed logging for both systems on a weekly basis; 5) reviewed an additional summary report on a weekly basis; 6) reviewed a sampling report on a weekly basis; and 7) assigned resources to review the CIP asset log review on a weekly basis and report to the Manager on status.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2016016369 | CIP-007-6 | R2. | NPCC_URE4 submitted a self-log stating that as it had an issue of CIP-007-6 R2. NPCC_URE4's Compliance Department conducted a review of CIP time based tasks and discovered that the seven (7) patches were not assessed in the 35 calendar day time frame required by the standard. The patches were assessed in 52 days. The cause was due to human error while using the patch assessment application filtering options. The reviewer did not see the patch notifications due to how the patch review application was filtered to display patches. A reviewer has the ability to view patches oldest to newest, newest to oldest, affected asset, criticality, assigned user group, or other fields. The reviewer generally filters from newest to oldest and these tickets would have been on the bottom of the sort list. The reviewer could have reviewed these tickets and not classify them, but the reviewer could not recall reviewing these tickets since they were not classified in patch assessment application. These patches were then determined to be in a un-reviewed state. The noncompliance began on the 36th calendar day and ended when patches were assessed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. On subsequent review, the 7 missed patches were determined to be irrelevant to the applicable NPCC_URE4 SCADA devices. These patches may not have been assessed as Security relevant to the NPCC_URE4 system, but they were deployed within the 70 days per the NPCC_URE4 Change Management Process. All devices reside in a defined ESP that prevents network traffic that isn't explicitly allowed to communicate with identified CIP devices. No harm is known to have occurred | To mitigate this issue, NPCC_URE4: 1) retrained the individual on their compliance responsibilities; 2) investigated an automated workflow to assign and track compliance tasks; 3) review patching notifications on the last week of every month by IT/OT Personnel 4) review patches by the IT Compliance Analyst on a weekly basis as defined by the IT/OT Calendar
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2016016393 | CIP-004-6 | R5. | NPCC_URE4 submitted a self-log stating that it had an issue of CIP-004-6 R5. An employee of NPCC_URE4 retired. The responsible manager and HR Generalist did not perform the required revocation procedures as defined in the NPCC_URE4 access process and procedures or the corporate termination/position transfer check list. Due to the responsible manager and HR Generalist not performing the proper revocation steps, the departments responsible for removing access were not notified to remove access. The employee returned his badge to NPCC_URE's administrator after his retirement. The administrator gave the NERC CIP access credentials to Security Services. At that time Security Service Physical Security Specialist realized the error and notified the appropriate individuals and revoked access. The IT Compliance Analyst investigated the incident and verified that the physical access was revoked 5 days after the employee's retirement in the physical security system and the revocation ticket was closed out 6 days after. NPCC_URE4 Corporate revocation process was completed 6 days after the employee's retirement by the NPCC_URE4 HR Generalist. The cause is the responsible manager was not aware of NPCC_URE4 Corporate or CIP Procedures or had the technical ability to submit the required revocation forms. In addition, no HR Generalist was assigned or was brought in to consult on the employee's retirement process. The noncompliance began the first day after the employee's retirement and ended when access revocation was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access credentials could have been used for malicious actions that could have affected the BES. However, other security methods would have to be circumvented to enable any malicious actions. This would include breaching substation fences/gates where control houses are not accessible from the street or breaching the NPCC_URE4 corporate offices where NPCC_URE4 control rooms are occupied 24/7. Security officers are monitoring NPCC_URE4 substation, offices, and control rooms 24/7 and suspicious activity would have been detected by the NPCC_URE4 physical security system. A company wide memo was sent out, notifying all NPCC_URE4 employees of the retirement and his presence at a NPCC_URE4 facility would be considered suspicious. The employee retired in good standing and retained control of the credentials during the compliance event. The employee did not attempt to access any devices during the timeframe in noncompliance. No harm is known to have occurred. | To mitigate this issue, NPCC_URE4 1) reviewed NPCC_URE4 revocation procedures 2) retrained HR Generalist on revocation procedure 3) verified HR Generalist was assigned for employee terminations 4) revoked NPCC_URE4 CIP Access Credentials 5) verified if the employee was issued a B-Key 6) revoked corporate access.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017817 | CIP-006-6 | R1 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-006-6 R1. RFC_URE1 dispatched a contractor to a substation to perform a walk-down in preparation for a construction project. Upon arriving at the substation yard gate, the contractor correctly used his assigned key to unlock the padlock and swiped his access card on the gate card reader to gain access to the substation yard. Having appropriately gained access to the yard, the contractor then proceeded to the substation control house. Upon reaching the control house doorway (the only access point to the control house Physical Security Perimeter (PSP)), the contractor swiped his access card on the card reader, pulled open the door and entered the control house. At this time, RFC_URE1’s Security Console received a forced door alarm. Security responded to the alarm by calling the substation and speaking with the contractor who entered the control house. The contractor indicated to security that he had swiped his badge on the door card reader, opened the door and entered the control house. The contractor also indicated he was alone and not under escort. Security informed him that he was not authorized for unescorted physical access to that control house and instructed him to exit immediately. The contractor followed instructions and left the control house, closing the door behind him. Thereafter, a security team member was immediately dispatched to the substation to inspect the door and its locking mechanism. Upon inspection, it was discovered that doors’ locking mechanism was not working properly. As a result, the construction contractor was able to pull open the door despite the card reader’s accurate denial of access. RFC_URE1’s security vendor was subsequently contacted to repair the locking mechanism. The vendor arrived within a few hours of the incident. The vendor’s inspection determined that the door's electronic strike was not securing the door each time the door was closed. The electronic strike was demounted and remounted by the vendor, tested and found to be working properly again. Note: Prior to the repair work, the locking mechanism had been previously tested approximately six months earlier as part of RFC_URE1’s CIP-006-6 R3 maintenance and testing program. The lock was found to be working properly at that time. This first issue involves the management practice of external interdependencies because the vendor that installed the door failed to ensure that the door's electronic strike to secure the door functioned every time. Ineffective vendor management is a root cause. ------------ An employee arrived to work at RFC_URE1’s Control Room facility. On that particular morning, the employee had forgotten his access card. Although the employee was authorized for unescorted physical access to the Control Room PSP and had current training and personnel risk assessment (PRA) on file, RFC_URE1’s physical access program requires personnel who do not have their access card in their possession to be escorted as prescribed under the visitor control program. Accordingly, the employee was assigned an authorized escort for the day and, with the exception of the below incident, was continuously escorted for the duration of his shift. Later that afternoon, without his escort’s knowledge, the employee walked off the Control Room floor, proceeded up to the second level and exited the PSP through an access point door leading to a rear stairwell. Against physical security protocols, the employee further propped open the access point door to allow himself unobstructed access upon his return to the PSP area. The employee subsequently proceeded down to the first level and exited the facility. The employee was outside for approximately 2 minutes before re-entering the facility and returning to the PSP area, at which time he re-secured the access point door. During this time, RFC_URE1’s Security Console received a door held open alarm. Security immediately responded to the alarm, and logged an investigation report, identifying the employee and his escort. Further investigation determined that the employee failed to follow physical security protocols by (i) exiting and re-entering the PSP unescorted and (ii) propping open the PSP rear door. Video and event logs determined that the door was left unsecure for less than 3 minutes. This second issue involves the management practice of workforce management because the employee was ineffectively trained on how to follow RFC_URE1's physical security protocols. Ineffective training is a root cause. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk harm assessment determined the above issues to be of minimal impact to the BPS. RFC_URE1’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP‐006‐6 requirements. In fact, these issues were identified as a result of these effective controls. In both cases, automated alarming mechanisms worked as intended, enabling Security to quickly respond to the issues. Further impacting the assessment, the contractor in the first instance was a former RFC_URE1 employee with valid PRAs and requisite training on file dating back approximately seven years. Following the incident, the contractor was subsequently granted unescorted Substation PSP access upon completion of the current physical access training. With regard to the second incident, the employee was in fact authorized for unescorted access, with valid PRAs and training on file. Video review confirmed that there was no incident of unauthorized access within the 2-3 minute timeframe during which the access point was left unsecured. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: Issue 1 1) responded to the forced door alarm, identified the individual at the substation, and instructed him to leave the premises. The door was inspected and a security vendor was contacted to perform repairs on the door's locking mechanism; 2) reviewed its CIP-006 R3 maintenance and testing checklist and updated as necessary to ensure there are no gaps in the inspection process; 3) re-inspected the substation PSP door; 4) engaged independent assessors to evaluate the doors and the corresponding control mechanisms at a sample set of PSPs to evaluate alarm contact placement, control hardware, locking mechanism, and other controls as appropriate. Issue 2 1) responded to the alarm, contacting personnel ensuring the doors were secured and recurrence halted. Additionally, the employee was referred to Human Resources and disciplinary action was taken; and 2) provided internal coaching to the escort involved in the incident.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017820 | CIP-007-6 | R2 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-007-6 R2. RFC_URE1 performed a scheduled monthly review of RFC_URE1’s energy management system (EMS) Deferred Patch Plan (DPP) log. During the review, it was discovered that 2 patch mitigation plans (MP) captured on the DPP log had not been updated to reflect the operational need to extend their installation. Upon investigation of the issue, the following facts were collected and causal factors identified. A vendor released security patches applicable to certain Windows device types within RFC_URE1’s EMS environment. The patches were correctly assessed within 35 days of their respective release and found to be applicable, but their installations needed to be deferred beyond the required 35 day installation timeframe. Accordingly, MPs for the patches were created and appropriately added to the DPP log with a proposed completion date. The DPP log for both MPs was approved within 35 days of their respective assessments. Subsequently, at a recurring EMS patch management meeting, a determination was made that all patch installations in the EMS environment would be further delayed by operational order due to current and forecasted excessive temperatures in the RFC_URE1 region. As a result, it was discussed that the proposed completion dates for the two MPs noted-above would need to be extended. At that time, the individual responsible for EMS patch installations believed that the discussion regarding the extension of the proposed completion dates was sufficient notification to the individual responsible for managing the DPP log. However, the individual responsible for managing the DPP log expected to receive written confirmation after the meeting, which they subsequently did not receive. As a result of this miscommunication, the proposed completion dates for the two MPs were not extended in a timely manner. RFC_URE1’s CIP Patch Management Program assigns specific roles and responsibilities to personnel involved in the patch process. In particular, the Patch Program Coordinator is responsible for managing the patch source list, identifying and assessing patches, maintaining a patch inventory log, and managing the DPP log. In the EMS functional area, this role was divided amongst two individuals, where one individual managed the patch identifications, assessments, installations, and provided the relevant DPP information to the other individual responsible for creating, updating and monitoring the DPP log based on the information provided. While the process within the program was followed, bifurcating the Patch Program Coordinator role resulted in a communication gap that led to the error reported herein. This noncompliance involves the management practice of workforce management because the individual responsible for EMS patch installations believed that the discussion surrounding the extension of proposed completion dates for the two patch mitigation plans was sufficient. Ineffective training is a root cause. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE1’s risk-harm assessment determined the above issue to be administrative in nature and of minimal impact to the BPS. The patches were timely identified, assessed and correctly recorded on the DPP log. As required for all deferred patches, mitigating measures were appropriately in place and remained in place during the potential noncompliance period. Internal program controls effectively detected and ensured correction of the issue within one day of identification. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) updated RFC_URE1's DPP log to extend the proposed installation dates for the two MPs. The DPP log was approved by the CIP Senior Manager delegate; 2) assigned only one individual to the Patch Program Coordinator role; and 3) reviewed its CIP-007-6 patch management process to ensure there are no additional gaps with creating, revising, or obtaining approval of the MPs within the DPP.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017818 | CIP-006-6 | R1 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-006-6 R1. RFC_URE2 dispatched a contractor to a substation to perform a walk-down in preparation for a construction project. Upon arriving at the substation yard gate, the contractor correctly used his assigned key to unlock the padlock and swiped his access card on the gate card reader to gain access to the substation yard. Having appropriately gained access to the yard, the contractor then proceeded to the substation control house. Upon reaching the control house doorway (the only access point to the control house Physical Security Perimeter (PSP)), the contractor swiped his access card on the card reader, pulled open the door and entered the control house. At this time, RFC_URE2’s Security Console received a forced door alarm. Security responded to the alarm by calling the substation and speaking with the contractor who entered the control house. The contractor indicated to security that he had swiped his badge on the door card reader, opened the door and entered the control house. The contractor also indicated he was alone and not under escort. Security informed him that he was not authorized for unescorted physical access to that control house and instructed him to exit immediately. The contractor followed instructions and left the control house, closing the door behind him. Thereafter, a security team member was immediately dispatched to the substation to inspect the door and its locking mechanism. Upon inspection, it was discovered that doors’ locking mechanism was not working properly. As a result, the construction contractor was able to pull open the door despite the card reader’s accurate denial of access. RFC_URE2’s security vendor was subsequently contacted to repair the locking mechanism. The vendor arrived within a few hours of the incident. The vendor’s inspection determined that the door's electronic strike was not securing the door each time the door was closed. The electronic strike was demounted and remounted by the vendor, tested and found to be working properly again. Note: Prior to the repair work, the locking mechanism had been previously tested approximately six months earlier as part of RFC_URE2’s CIP-006-6 R3 maintenance and testing program. The lock was found to be working properly at that time. This first issue involves the management practice of external interdependencies because the vendor that installed the door failed to ensure that the door's electronic strike to secure the door functioned every time. Ineffective vendor management is a root cause. ------------ An employee arrived to work at RFC_URE2’s Control Room facility. On that particular morning, the employee had forgotten his access card. Although the employee was authorized for unescorted physical access to the Control Room PSP and had current training and personnel risk assessment (PRA) on file, RFC_URE2’s physical access program requires personnel who do not have their access card in their possession to be escorted as prescribed under the visitor control program. Accordingly, the employee was assigned an authorized escort for the day and, with the exception of the below incident, was continuously escorted for the duration of his shift. Later that afternoon, without his escort’s knowledge, the employee walked off the Control Room floor, proceeded up to the second level and exited the PSP through an access point door leading to a rear stairwell. Against physical security protocols, the employee further propped open the access point door to allow himself unobstructed access upon his return to the PSP area. The employee subsequently proceeded down to the first level and exited the facility. The employee was outside for approximately 2 minutes before re-entering the facility and returning to the PSP area, at which time he re-secured the access point door. During this time, RFC_URE2’s Security Console received a door held open alarm. Security immediately responded to the alarm, and logged an investigation report, identifying the employee and his escort. Further investigation determined that the employee failed to follow physical security protocols by (i) exiting and re-entering the PSP unescorted and (ii) propping open the PSP rear door. Video and event logs determined that the door was left unsecure for less than 3 minutes. This second issue involves the management practice of workforce management because the employee was ineffectively trained on how to follow RFC_URE2's physical security protocols. Ineffective training is a root cause. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk harm assessment determined the above issues to be of minimal impact to the BPS. RFC_URE2’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP‐006‐6 requirements. In fact, these issues were identified as a result of these effective controls. In both cases, automated alarming mechanisms worked as intended, enabling Security to quickly respond to the issues. Further impacting the assessment, the contractor in the first instance was a former RFC_URE2 employee with valid PRAs and requisite training on file dating back approximately seven years. Following the incident, the contractor was subsequently granted unescorted Substation PSP access upon completion of the current physical access training. With regard to the second incident, the employee was in fact authorized for unescorted access, with valid PRAs and training on file. Video review confirmed that there was no incident of unauthorized access within the 2-3 minute timeframe during which the access point was left unsecured. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: Issue 1 1) responded to the forced door alarm, identified the individual at the substation, and instructed him to leave the premises. The door was inspected and a security vendor was contacted to perform repairs on the door's locking mechanism; 2) reviewed its CIP-006 R3 maintenance and testing checklist and updated as necessary to ensure there are no gaps in the inspection process; 3) re-inspected the substation PSP door; 4) engaged independent assessors to evaluate the doors and the corresponding control mechanisms at a sample set of PSPs to evaluate alarm contact placement, control hardware, locking mechanism, and other controls as appropriate. Issue 2 1) responded to the alarm, contacting personnel ensuring the doors were secured and recurrence halted. Additionally, the employee was referred to Human Resources and disciplinary action was taken; and 2) provided internal coaching to the escort involved in the incident.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017017821 | CIP-007-6 | R2 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-007-6 R2. RFC_URE2 performed a scheduled monthly review of RFC_URE2’s energy management system (EMS) Deferred Patch Plan (DPP) log. During the review, it was discovered that 2 patch mitigation plans (MP) captured on the DPP log had not been updated to reflect the operational need to extend their installation. Upon investigation of the issue, the following facts were collected and causal factors identified. A vendor released security patches applicable to certain Windows device types within RFC_URE2’s EMS environment. The patches were correctly assessed within 35 days of their respective release and found to be applicable, but their installations needed to be deferred beyond the required 35 day installation timeframe. Accordingly, MPs for the patches were created and appropriately added to the DPP log with a proposed completion date. The DPP log for both MPs was approved within 35 days of their respective assessments. Subsequently, at a recurring EMS patch management meeting, a determination was made that all patch installations in the EMS environment would be further delayed by operational order due to current and forecasted excessive temperatures in the RFC_URE2 region. As a result, it was discussed that the proposed completion dates for the two MPs noted-above would need to be extended. At that time, the individual responsible for EMS patch installations believed that the discussion regarding the extension of the proposed completion dates was sufficient notification to the individual responsible for managing the DPP log. However, the individual responsible for managing the DPP log expected to receive written confirmation after the meeting, which they subsequently did not receive. As a result of this miscommunication, the proposed completion dates for the two MPs were not extended in a timely manner. RFC_URE2’s CIP Patch Management Program assigns specific roles and responsibilities to personnel involved in the patch process. In particular, the Patch Program Coordinator is responsible for managing the patch source list, identifying and assessing patches, maintaining a patch inventory log, and managing the DPP log. In the EMS functional area, this role was divided amongst two individuals, where one individual managed the patch identifications, assessments, installations, and provided the relevant DPP information to the other individual responsible for creating, updating and monitoring the DPP log based on the information provided. While the process within the program was followed, bifurcating the Patch Program Coordinator role resulted in a communication gap that led to the error reported herein. This noncompliance involves the management practice of workforce management because the individual responsible for EMS patch installations believed that the discussion surrounding the extension of proposed completion dates for the two patch mitigation plans was sufficient. Ineffective training is a root cause. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE2’s risk-harm assessment determined the above issue to be administrative in nature and of minimal impact to the BPS. The patches were timely identified, assessed and correctly recorded on the DPP log. As required for all deferred patches, mitigating measures were appropriately in place and remained in place during the potential noncompliance period. Internal program controls effectively detected and ensured correction of the issue within one day of identification. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) updated RFC_URE2's DPP log to extend the proposed installation dates for the two MPs. The DPP log was approved by the CIP Senior Manager delegate; 2) assigned only one individual to the Patch Program Coordinator role; and 3) reviewed its CIP-007-6 patch management process to ensure there are no additional gaps with creating, revising, or obtaining approval of the MPs within the DPP.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016479 | CIP-011-2 | R1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-011-2 R1. During a project meeting, RFC_URE3 staff discovered Bulk Electric System Cyber System Information (BCSI) stored on a RFC_URE3 shared site which was not the dedicated CIP Information Repository (CIR) for the project. There were two shared sites created for the project - one was dedicated as a CIR for BCSI storage and one was designated for non-BCSI information. RFC_URE3's NERC CIP Information Protection Program requires BCSI to be stored in a CIR operated by the appropriate business unit. Further investigation identified that the documents were copied to the shared site. The root cause of this noncompliance was the fact that a contractor inadvertently copied files to the incorrect project folder. This major contributing factor involves the management practices of information management, which includes protecting information items, and external interdependencies, which includes managing risk due to external interdependencies. While RFC_URE3 was mitigating this issue, it identified the following three additional instances regarding the placement and handling of BCSI in a manner that is contrary to RFC_URE3 procedures for information protection: (a) attaching BSCI to a ticket in RFC_URE3’s system used to communicate Supervisory Control and Data Acquisition (SCADA) point changes to RFC_URE3 Emergency Management System; (b) BCSI that was transmitted via the corporate email system externally to a RFC_URE3 vendor; and, (c) BCSI that was inadvertently stored on a RFC_URE3 network share folder that was not a CIR. In regard to the system issue, a testing engineer accessed the ticket system and discovered that he had uploaded a partial SCADA point identities list drawing containing BCSI to the system. This drawing is used to communicate SCADA point changes to Energy Management System and Distribution Management System to track the SCADA communication updates to the Real-Time IT group. The system is not a designated CIR. Immediately upon discovery, the Real-Time IT group was contacted to remove the BCSI from the system ticket. The Real-Time IT group confirmed the drawing was immediately removed and that no known physical copies of the document existed. The root cause of this instance of noncompliance was a lack of attention to detail on the part of the responsible employee, who had been working extended hours for multiple days prior to the issue occurring. In the days leading up to the event, there were multiple transmission operational events requiring support from this individual. As a result, this individual had been working extended hours for three days prior to this event. This major contributing factor involves the management practice of workforce management, which includes managing staff performance. In regard to the external transmission of BCSI via email, a RFC_URE3 project engineering contractor attached BCSI engineering drawings on two separate occasions to emails that were sent to an external engineering design firm acting as a contract vendor with RFC_URE3. Both the RFC_URE3 contractor and the external engineering design firm are regular entities that perform design and project management work for RFC_URE3. The root cause of this instance of noncompliance was the contractor’s lack of awareness that he was violating RFC_URE3 policies because the entity to which the information was being sent is well-known and trusted. Furthermore, the contractor also failed to properly screen attachments to emails for BCSI before forwarding them to the external entity. This major contributing factor involves the management practices of information management, which includes protecting information items, and external interdependencies, which includes managing risk due to external interdependencies. In regard to the storing of BCSI on a network share folder, a RFC_URE3 engineer identified that certain configuration files for a remote terminal unit (RTU) classified as BCSI were left in a storage location that is not designated as a CIR. The RTU configuration files contain information that is classified as BCSI. The storage location is a restricted access network shared folder and served as the operational location of record for RTU configurations until the deployment of a new CIR. All of the medium impact RTUs were migrated at the time of deployment to the CIR. However, certain files needed to remain in the storage location for scheduled CIP configuration update work occurring one month later. These configuration files should have been deleted after they were updated. However, in this case, the responsible engineer did not delete the files after transitioning them to the new CIR. The root cause of this instance of noncompliance was the employee’s failure to follow established policies and procedures for protection of BCSI. This major contributing factor involves the management practices of workforce management, which includes providing training, education, and awareness to employees, and information management, which includes protecting information items. The duration of the noncompliance was approximately nine months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors: a. First, with respect to the storage of BCSI on a shared site which was not a CIR, the shared site in question was access-controlled and accessible to trusted and approved RFC_URE3 employees and contractors with a valid business need for access. In this particular case, the site was restricted to seven individuals, all of whom had a valid business need for access and were assigned to the project. Furthermore, all but one of those individuals had current CIP training, current Personnel Risk Assessments, and held valid access to protected BCSI. The seventh individual was in the process of obtaining CIP clearance. b. Second, with respect to the system issue, the system itself and the documents within it are only accessible from the corporate data network requiring current employee credentials. Furthermore, the RTUs at issue have point-to-point serial based connectivity and do not have external routable connectivity. Therefore, in order to impact the RFC_URE3 system, a person with the protected information would still need physical access to specific protected locations in order to utilize the information maliciously. Finally, the employee who made the mistake identified it quickly and corrected it immediately. c. Third, with respect to transmission of CIP information externally, the emails were sent to a known and trusted RFC_URE3 contract vendor that has a signed Non-Disclosure Agreement with RFC_URE3. Even if a third-party had intercepted one of the emails, the third-party would still have to penetrate other layers of defense to access the system, including an intermediate jump server that requires two factor authentication. d. Fourth, with respect to the storing of BCSI on a network share folder, the storage location is a network shared folder protected within the corporate data network. Access to the network shared folder is restricted to RFC_URE3 transmission and substation employees with a current account and is available only to selected, trusted employees with a business need. Furthermore, RFC_URE3 quickly removed the BCSI in question from the location following discovery. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) limited access to the shared site; 2) removed CIP protected information from the ticket; 3) reviewed procedure for proper handling of CIP protected information in the system. Modified procedure to specify inclusion of link to RTU points lists for all submittals and not just medium impact stations; 4) performed mandatory compliance stand downs on handling NERC CIP drawings; 5) provided interim direction that NERC CIP drawings should not be transmitted by email both internally and externally to the RFC_URE3 system or externally to RFC_URE3 contract vendors; 6) removed CIP protected information from the non-CIP Protected Network Share folder; 7) provided awareness to RTU Engineers on handling of RTU configuration files for Medium Impact RTUs; 8) ensured individuals affected by this event are aware of and understand the three relevant procedures; 9) reviewed the system for accounting of all tickets which contain information which could be classified as CIP protected information. Archived in a CIR all attachments which could contain CIP Protected information and included the CIR link in the ticket; and 10) deleted or purged attachments from all tickets on the System identified related to medium impact substations with attachments that would now be classified as CIP protected information. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017016811 | CIP-011-2 | R1 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-011-2 R1. An employee in RFC_URE4’s group responsible for transmission and substations scanned nine design drawings classified as Bulk Electric System (BES) Cyber System Information (BCSI) on a plotter located at a RFC_URE4 facility. Upon completing the scans the employee questioned the programming and connections of the plotter. RFC_URE4 then reviewed the plotter and discovered that it was configured to send the scanned images to a non-CIR folder on a shared drive. Permissions for the aforementioned folder are granted to most employees and supporting contractors for the RFC_URE4 transmission and substation group, not all of whom meet requirements for BCSI. The destination network drive folder where the plotter was sending the scanned documents, at the time the issue occurred, was managed by subject matter experts, who performed a removal of the scanned files every 30 days, as part of periodic data management. Thus, the scans in question were purged and a new plotter was installed. The root cause of this noncompliance was the misconfiguration of the plotter. This noncompliance involves the management practices of information management and asset and configuration management. Information management is involved because RFC_URE4 failed to ensure the confidentiality of information important to protecting the BES. Asset and configuration management is involved because the plotter was installed with incorrect configuration baselines and controls. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that BCSI documents could be accessed by bad actors and utilized to adversely impact the BPS. The risk is minimized because the documents were stored in a secured building so only trusted employees would have access to the information. Further, the employee that performed the scan is a trusted employee with valid NERC credentials. Finally, the individuals with access to where the files are located are trusted employees and contractors. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) met with key stakeholders and advised them to instruct their teams not to scan unless authorization is obtained; 2) communicated verbally to relay and protection personnel at a weekly departmental Safety Meeting awareness of “CIP Protected Information” handling expectations; 3) reviewed with key stakeholders a presentation on CIP Information Protection that addresses the plotters issue and signage; 4) placed signage at the plotters which states that documents with a “CIP Protected Information” label are prohibited from being scanned; and, to obtain a printed copy, individuals must contact the department drawing administrator via email; 5) configured the ninth floor plotter to scan images that may contain BCSI to a designated CIR, available only to authorized users; 6) shared lessons learned; 7) discussed RFC_URE4’s investigation and results on the issue of BCSI inadvertently stored on a non-CIR; 8) developed guidance on scanning and printing BCSI and distribute the guidance amongst RFC_URE4 stakeholders; and 9) included guidance content as part of the onboarding RFC_URE4 training content for the new hires. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017016889 | CIP-004-6 | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-004-6 R5. This noncompliance stems from an internal transfer of a trusted long-term employee at RFC_URE5. The employee’s supervisor requested that the employee retain electronic and physical access to High Impact Bulk Electric System (BES) Cyber Systems until the end of the year to ensure a smooth transition. When the supervisor returned to the office after the first of the year, the supervisor was contacted to see if it was now appropriate to remove the employee’s access. The supervisor stated that the employee no longer needed System Control Read Only electronic access for her new role and for NERC training. The supervisor also stated the Training Department will provide login credentials for Supervisory Control and Data Acquisition as needed. The employee retained unescorted physical access to Physical Security Perimeters for NERC training and storm duty appropriate for the employee’s new position. Based on the supervisor’s response, RFC_URE5 subsequently created and approved an access request system ticket which moved the employee’s account to the disabled queue. Additionally, a screenshot of the final step to remove access from the appropriate Active Directory Domain Account was taken for evidence purposes. Although all of these appropriate actions were taken, the “apply” radio button was not selected and RFC_URE5 did not complete the access removal action. Therefore, the employee retained unnecessary and unauthorized access after the employee’s transfer. RFC_URE5 discovered this issue during a periodic review of disabled users. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the RFC_URE5 employee was not effectively trained to hit the apply button to complete the removal of access. This ineffective training is a root cause of the noncompliance. Verification is involved because RFC_URE5 did not have an effective check in place to verify that access was completely removed. The duration of the noncompliance was approximately nine days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance comes from allowing an individual to access BES Cyber Systems when that individual is not authorized to have such access. The risk is minimized here because the individual in question was a long term trusted employee undergoing an internal transfer. The unauthorized access the employee retained was “read only” access which further minimizes the risk because the employee could not make any unauthorized changes to any of the information the employee had unauthorized access to for ten days. Additionally, RFC_URE5 discovered, through an internal control (a periodic review of disabled users), and remediated this noncompliance quickly which reduces the risk of harm. The quick discovery and resolution of this noncompliance minimized the risk of actual harm to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) removed the employee’s electronic access when it discovered the user account was still enabled; 2) performed Operational Technology (OT) awareness training of the existing procedure for electronic access removal to all relevant personnel; 3) conducted research and, where practical, automated the existing OT process to capture evidence of disabled and/or removed user accounts from appropriate Active Directory groups; 4) tested and finalized automated scripts to capture evidence of disabled and/or removed user accounts from appropriate Active Directory groups; 5) enhanced/replaced existing OT desktop procedure to include the automated script to capture evidence of disabled and/or removed user accounts from appropriate Active Directory groups; and 6) notified and trained the OT organization on changes made to the OT desktop procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016484 | CIP-007-6 | R2 P2.3 | ReliabilityFirst determined that RFC_URE5 had an issue of CIP-007-6 R2 P2.3 identified during a Compliance Audit. During evidence collection for a ReliabilityFirst Audit, RFC_URE5 discovered that five devices running a specific operating system did not have security patches implemented within the 35 calendar day requirement following the completion of the evaluation of the patches’ applicability. The monitoring and tracking of security patches for these five devices was not part of RFC_URE5's formal CIP compliance program. Patches for these five devices were timely assessed, within 35 calendar days of the release of the patches, but most patches for these five devices were not timely implemented within 35 calendar days of the patches’ assessment. Specifically, two security patches were not timely implemented. The patches for these five devices were not timely implemented because RFC_URE5 did not include the tracking and monitoring of security patches for these five devices within its formal CIP compliance program due to a manual oversight. This noncompliance involves the management practices of asset and configuration management and verification. Asset and configuration management is involved because RFC_URE5 did not include the tracking and monitoring of security patches for these five devices within its formal CIP compliance program. RFC_URE5 did not include these five devices due to a manual review oversight. Due to this oversight, the patches for these five devices were tracked separately and manually. Verification is involved because RFC_URE5 did not have a process in place to verify that all applicable devices were included in its formal CIP compliance program to ensure that security patches for all applicable devices were timely assessed and implemented. This lack of an effective process and failure to verify is a root cause of this noncompliance. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is the opportunity for infiltration of unauthorized network traffic into the Electronic Security Perimeter (ESP) when security patches and upgrades are not installed on Cyber Assets within the ESP. The risk is minimized here because RFC_URE5's Supervisory Control and Data Acquisition systems are not affected. The patches for these specific devices were being manually monitored outside of the CIP compliance program which reduces the risk posed by the vulnerabilities identified by the patches because the patches at issue were timely assessed. Additionally, the five devices at issue are security devices that have other protections in place to deter attackers or other risks such as layered firewalls. Network traffic within the ESP is actively monitored by Intrusion Detection Systems that monitor for malware and virus propagation attempts. Further, if the devices were lost, operations would still occur within the control networks without issue and interruption. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) completed the implementation of the patches on all applicable devices; 2) added a specific software to the patch source list; and 3) modified the change control process and related monitoring to ensure that IT Security staff responsible for monitoring patch sources are aware when new software or a new hardware type is introduced into the production CIP environment. This action will help prevent recurrence because it will ensure that the assessment and implementation of security patches for these devices are included in RFC_URE5's formal CIP compliance program and this will help prevent patches from being missed and not timely implemented. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016672 | CIP-007-3a | R3 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-007-3a R3. RFC_URE5 transferred the responsibility for patch monitoring and assessment from one employee to another. The new employee in charge of patch monitoring and assessment conducted a thorough review of all devices to ensure that all were patched to the correct version. During the review, the RFC_URE5 employee discovered 12 routers that had security vulnerabilities and were not patched to the current security patch version. After this discovery, RFC_URE5 performed a comprehensive investigation and that investigation revealed that four security patches applicable to the 12 routers had been released and not been identified or assessed. The patch source RFC_URE5 relied upon for patch notifications had released notifications for these four patches and RFC_URE5 received notifications for these four patches. The RFC_URE5 employee previously responsible for monitoring patch sources, however, overlooked these four notifications because the employee had configured the patch notifications alerts to be sent to their personal email address and the notifications were never properly evaluated. The noncompliance involves the management practice of workforce management. The employee responsible for receiving patch notifications improperly had the patch notifications sent to their personal email. A root cause of this noncompliance is ineffective training because the employee did not understand that patch notifications should be sent to his work email and not to his personal email. RFC_URE5 also had an ineffective process that allowed the employee to have the notifications sent to their personal email. The duration of the noncompliance was approximately thirteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is the opportunity for infiltration of unauthorized network traffic into the Electronic Security Perimeter (ESP) when security patches and upgrades are not installed on Cyber Assets within the ESP. The risk is minimized here because RFC_URE5's Supervisory Control and Data Acquisition systems are not affected. Additionally, the five devices at issue are security devices that have other protections in place to deter attackers or other risks such as layered firewalls. Network traffic within the ESP is actively monitored by Intrusion Detection Systems (IDS) that monitor for malware and virus propagation attempts. Access lists and firewall rules prevent access to the routers deployed in support of the energy management system infrastructure unless originating from the Zone A (ICS network). In order to remotely administrate the routers, the traffic must originate from Zone A management systems or administrators workstations. This setup makes it more difficult for anyone to access and compromise the routers. This traffic would also be inspected by IDS. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) assessed the missed patches (the four router patches); 2) implemented or otherwise mitigated the vulnerabilities related to the security patches; 3) ensured that a dedicated central PO Box exists for all patch source emails; 4) updated RFC_URE5's Procedure to ensure that a review is periodically conducted to ensure that emails have been reviewed by the Vulnerability Assessments Coordinator; and 5) updated RFC_URE5's Procedure to ensure that all patch sources utilizing email are configured to send to the centralized monitoring PO Box. This will help prevent recurrence because it creates one location to receive and monitor all patch source notification emails. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016485 | CIP-007-6 | R4 P4.2 | ReliabilityFirst determined that RFC_URE5 had an issue of CIP-007-6 R4 P4.2 identified during a Compliance Audit. During RFC_URE5 evidence collection process for the ReliabilityFirst-led Compliance Audit, RFC_URE5 discovered that it had two devices with logging gaps that should not have existed. (RFC_URE5 performed an extent of condition and discovered that all other in-scope devices capable of sending logs were found to be properly reporting during the period of the noncompliance.) RFC_URE5 had been unaware that a system it relied upon to collect and correlate logs, and to send security alerts if needed, had not been receiving logs from all necessary devices. These gaps represent a failure to detect when system logging required from necessary devices has stopped working. This noncompliance involves the management practice of asset and configuration management and verification. Asset and configuration management is involved because RFC_URE5 did not properly identify and configure two devices which should have been providing logs in order to evaluate system security. This failure is partially caused by RFC_URE5's inefficient process for the manual review of logs that cannot be included in their automated system and that is a root cause of this noncompliance. RFC_URE5 failed to establish inventory and configuration control systems which would have rectified this instance of noncompliance. (RFC_URE5 determined the initial root cause to be human error, due to the support personnel not adding the device to the appropriate rule to generate the alert associated with a logging failure. Further root cause analysis determined the issue was due to support evidence that was not required in the change ticket to substantiate the affirmative answer of connection upon change implementation.) RFC_URE5 also failed to verify that the system was working as expected and designed. The duration of the noncompliance was approximately eighteen days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is the opportunity for infiltration of unauthorized network traffic into the Electronic Security Perimeter (ESP) when security patches and upgrades are not installed on Cyber Assets within the ESP. The risk is minimized because despite not being configured for automatic alerting and monitoring, manual monitoring processes and review procedures would assist in identifying possible security risks. All other in-scope devices capable of sending logs were found to be properly reporting during the noncompliance. The instant noncompliance also has a short duration of fewer than 30 days that helps minimize the risk. Additionally, network traffic within the ESP is actively monitored by Intrusion Detection Systems (IDS) that monitor for malware/virus propagation attempts which help minimize the risk caused by the gaps between these two devices because IDS is looking for threats that would exploit the gaps. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) added a daily report which shows log sources that are new and have not been assigned to the appropriate group yet; 2) utilized a new feature to associate the rule that generates the alerts related to logging failures with log source groups instead of individual sources. This simplifies the setup and makes it more transparent when a device is not properly configured; 3) added a policy to prevent local log files from being overwritten. When a local log file on an in-scope device reaches a certain size, the file will be closed and a new file will be opened for continuous log recording. The local log files will be captured in the daily and monthly server backups by Operational Technology (OT); 4) generated alert tickets to OT support for devices that have stopped sending logs; 5) modified the mailbox where alerts are sent to make it easier to review and act on the alerts; 6) reviewed reports on devices that have stopped sending logs. RFC_URE5 will review these reports weekly; and 7) created a task within the change control process to require evidence when the logging and alerting tool has been updated to reflect the change. A nightly report is being developed and the report data will be incorporated into the security controls review to validate that device logs are being sent both before and after the change. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016481 | CIP-010-2 | R1 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-010-2 R1. First, RFC_URE5 rolled out software to all Windows devices across both the CIP and non-CIP domains (RT domains). A ticket (“ticket 1”) was created for non-CIP servers in the RT domain and a second ticket (ticket 2) was created for CIP workstations in the CIP domain. RFC_URE5 performed testing on both tickets. RFC_URE5 used an Active Directory group to deploy the software for the non-CIP servers. RFC_URE5 had previously warned employees about the risks of accidental deployment on two Windows Electronic Access Control or Monitoring Systems (EACMs) servers in the predominantly non-CIP domain. The person responsible for deployment did not heed the aforementioned warning and accidentally included two terminal servers (EACMS) in the Active Directory group used for the non-CIP server deployment. Following this incorrect deployment, the terminal servers in the primarily non-CIP domains received the software update prior to the intended implementation. RFC_URE5's management had approved the software for deployment across all windows devices but RFC_URE5 personnel did not follow the proper procedures in order to receive proper authorization for the deployment of the two EACMS servers. The change ticket did not specifically include these two devices, therefore the change was not approved for these two devices. Although testing had been performed on the terminal servers, not all security controls were individually tested on the test terminal servers prior to the change being implemented on the production terminal servers. The security controls were individually tested on the test Windows workstations prior to deployment on the production terminal servers. RFC_URE5 discovered this issue during its review for unauthorized changes the next day. This noncompliance involves the management practice of workforce management and asset and configuration management. Workforce management is involved because the individual responsible for deploying software to non-CIP devices was ineffective. He was ineffective because he was ineffectively trained and that ineffective training is a root cause of this noncompliance. RFC_URE5 also did not have a check in place to ensure that all software was properly and timely deployed and that involves asset and configuration management. The duration of the noncompliance was approximately eight days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is the temporary loss of access to the terminal servers making it more difficult to troubleshoot CIP assets if an unrelated incident occurred immediately following the upgrade. The risk is minimized since the changes at issue on the two terminal servers had been tested on terminal servers and deemed safe and necessary prior to its implementation. The changes had been approved by management for deployment across all Windows devices. This is primarily a documentation issue as the two changes on the devices were managed appropriately with proper testing and approvals, but the two specific devices were overlooked within the document and had not been identified or listed in the change record. The changes were only missing the final documentation approval for deployment. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) updated the baselines for the two terminal servers to include the software; 2) developed a training plan for all personnel working on CIP devices that are not located in the main CIP domain (to address all devices outside of the primary CIP environment); 3) conducted refresher training for all personnel working on CIP devices that are not located in the main CIP domain (to address all devices outside of the primary CIP environment); 4) updated procedures to include validation of Active Directory groups against the assets listed on the Request for Change ticket; 5) trained personnel on the updated procedures; and 6) moved the two terminal servers out of the RT domain and into the CIP domain (to address these specific devices). Upon the successful completion of the Mitigation Plan, the associated personnel will have been better trained on handling CIP devices that are located outside of the primary CIP environment. In addition, by moving the two terminal servers out of the RT domain and into the CIP domain, a similar issue on the terminal servers is unlikely to happen again in the future. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016483 | CIP-010-2 | R1 P1.1 P1.3 | ReliabilityFirst determined that RFC_URE5 had an issue of CIP-010-2 R1 P1.1 and P1.3 identified during a Compliance Audit. This noncompliance contains two separate issues. First, during preparation for a ReliabilityFirst led Compliance Audit, RFC_URE5 staff discovered that a group of devices running a specific Operating System were not being monitored and tracked as part of RFC_URE5's CIP compliance program. Specifically, RFC_URE5's inventory of custom software requiring baselines was missing two different pieces of custom software. Second, RFC_URE5 tracked approximately 99% of the data on its baseline listings automatically. RFC_URE5 tracked approximately 1% of that data manually because the devices on which that data resided could not be updated automatically. RFC_URE5 found five updates that occurred where baselines were not updated within 30 days of the change. Of that five, one was an upgrade to Firmware/Security Patches and four were custom software changes. This noncompliance involves the management practices of asset and configuration management. Asset and configuration management is involved because RFC_URE5 did not ensure that two custom applications were included in their baseline development and monitoring process. A root cause was RFC_URE5 failing to include two custom applications in their baseline development and monitoring process. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that the entity’s recovery procedures may have been outdated due to changes on devices or not knowing the exact custom software to reload on the system, potentially causing delays in restoration to full functionality. The risk is minimized because the main software was documented and the devices where patching was not properly documented were still being maintained outside of the normal patching process. The risk is also minimized because it only affected a custom application, some software, and was primarily a documentation issue. Additionally, network traffic within the Electronic Security Perimeter is actively monitored by Intrusion Detection Systems (IDS) that monitor for malware/virus propagation attempts which help minimize the risk caused by the gaps between these two devices because IDS is looking for threats that would exploit the gaps. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) updated the baselines for the missed items. RFC_URE5 incorporated the custom software list into the existing automated scanning process and this will significantly reduce the human error associated with manual data collection and ensure that data is collected and reviewed within the compliance timeframes; 2) created a report to track the number of days since the last review for each baseline type (both automated and manual). This reduces the risk that a review deadline will be missed; 3) incorporated the custom software list into the existing automated scanning process; and 4) developed a checklist to be utilized prior to enforcement of any new standards. This checklist will reduce the risk that either automated or manual aspects of future requirements are missed. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016482 | CIP-010-2 | R2 | ReliabilityFirst determined that RFC_URE5 had an issue of CIP-010-2 R2 identified during a Compliance Audit. During preparation of evidence for a ReliabilityFirst Compliance Audit, RFC_URE5 discovered a gap in baseline monitoring and reviews for approximately 1% of their Cyber Assets. Through an asset management oversight, RFC_URE5 had not conducted baseline configuration reviews at least once every 35 calendar days for approximately 1% of its Cyber Assets. RFC_URE5 identified five different baseline types, involving five different device types where monitoring and reviews had not occurred. For the devices at issue, RFC_URE5 cannot enable automated monitoring and reviews of baselines. RFC_URE5 had a manual review process in place for these devices, but that manual review process was ineffective as RFC_URE5 had not conducted baseline configuration reviews at least once every 35 calendar days for approximately 1% of its Cyber Assets. This noncompliance involves the management practices of asset and configuration management. Asset and configuration management is involved because RFC_URE5 did not ensure that required baseline configuration reviews were conducted once every 35 days for approximately 1% of their Cyber Assets. This failure to have an effective process in place to ensure that all baseline configuration reviews were timely reviewed is a root cause of this noncompliance. RFC_URE5's controls for monitoring baseline configuration reviews were insufficient to prevent this noncompliance. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that without proper monitoring and review of baseline configurations, and detection for deviations and unauthorized changes, a delay in possible back-up and recovery due to baselines that were not reviewed and updated appropriately is possible. Bulk Electric System Cyber Assets could be open to exploitation based on unknown potential vulnerabilities. The risk would manifest itself in a delay of possible backup and recovery due to baselines which were improperly reviewed. The risk is minimized because RFC_URE5 identified the noncompliance and swiftly reported the issue which reflects an existing program that enables RFC_URE5 to discover these types of issues quickly. Additionally, this gap in baseline monitoring and reviews applied to only approximately 1% of RFC_URE5's Cyber Assets. The manual baseline review process is rarely used. Compliance is met for automatically scripted baseline data (99.6% of baseline data) by using the existing baseline review process at least every 35 days. Additionally, network traffic within the Electronic Security Perimeter is actively monitored by Intrusion Detection Systems (IDS) that monitor for malware/virus propagation attempts which help minimize the risk caused by the gaps between these two devices because IDS is looking for threats that would exploit the gaps. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) initiated and completed a manual baseline review. This is a manual baseline review to be performed to mitigate the 35 day requirement being exceeded for manual baseline reviews being performed. A Baseline Change Log entry will be made to document the performance of the manual baseline review; 2) added “Manual Baseline Notes” field to the existing baseline review library to facilitate manual baseline reviews. This is an enhancement to an existing process to better facilitate manual baseline reviews by adding a field to document the occurrence of each manual baseline review. 3) created a report to track the number of days since last review for each baseline type (both automated and manual) process. This is an enhancement to the report used in the existing process by personnel responsible for manual baseline reviews to include the same "days remaining" calculation for manual baselines as used for automatic baseline reviews to ensure reviews are completed within 35 days; 4) created MS Outlook Calendar event tasks to review manual baseline data on a bi-weekly frequency. This reduces the risk of personnel missing the compliance requirement to review manual baselines within 35 days; and 5) developed a checklist to be utilized prior to enforcement of any new standards. This new checklist will assist in identification of measures to be implemented by RFC_URE5 to ensure 100% compliance with new standards. RFC_URE5 is also performing a review of remaining in-scope manual baselines (approximately 1% of total baselines) to determine and automate or remove manual baselines where possible to minimize the future need of manual baseline reviews and to reduce risks resulting from any future missed manual baseline reviews. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017016969 | CIP-006-6 | R1 | RFC_URE6 submitted a Self-Report stating that it had an issue of CIP-006-6 R1. RFC_URE6 experienced a Physical Access Control System (PACS) failure at an operations center. Following a loss in power, a single device, which controls 6 doors to the Physical Security Perimeter (PSP), failed when the back-up to flash memory reverted to an old configuration that required only one type of authentication. This allowed anyone with a RFC_URE6 access card to gain entry into the PSP by swiping their access card without having to also enter a unique PIN. Approximately four hours later, a RFC_URE6 employee gained access by only swiping his card and promptly notified security that he was not also required to enter his unique PIN. Security immediately began manning the doors to verify employees’ identification and working to resolve the issue. One hour later, Security identified the root cause and was able to re-enable the dual authentication function at all doors controlled by the device. Within minutes, the PACS were fully restored. An after action review revealed that six individuals were able to gain access to the PSP during the noncompliance without having to enter a unique PIN after swiping their respective access cards. The review also revealed that those six individuals had authorized unescorted access to that PSP. There were two root causes to the device failure. First, after the power outage, the backup battery was completely drained, which caused the door’s configuration to revert to the old configuration from prior to the enactment of CIP Version 5. Since only one form of authentication was required under that configuration, the system stopped enforcing dual authentication. Second, the programming for the system’s back-up to flash memory was miscoded and thus failed to pick up the device configuration provided daily by the PACS. This noncompliance involves the management practice of validation, which confirms that changes to systems, such as new configurations, function as designed in the intended environment. The duration of the noncompliance was approximately six hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. RFC_URE6 immediately identified the noncompliance and began promptly working to restore dual authentication to ensure that only individuals with authorized unescorted access were permitted into the PSPs. This reduced the time that there was an opportunity for unauthorized individuals to enter the PSP. Additionally, a RFC_URE6-issued access card was still required to enter the PSP during the period of noncompliance. This further reduced the likelihood that an intruder could have gained access to the PSP. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) investigated the cause of the flash memory not being updated with the current version of the configuration. Upon completion of this investigation, RFC_URE6 determined which parts of the device required repair or replacement; 2) updated the current device to validate, in the future, that flash memory is updated on all impacted devices after the configuration is updated; 3) replaced the backup battery; and 4) performed an analysis on the extent of the condition and determined that there were no other device devices that had the same misconfiguration issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2016016217 | CIP-010-2 | R2 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-010-2 R2. RFC_URE7’s Control Center became compliant with CIP version 5 Standards and Requirements as a High Impact BES Cyber location. (Prior to this date, RFC_URE7 did not have any Critical Assets nor Critical Cyber Assets identified under CIP version 3.) The firewall for the Control Center network was enabled, meaning that the default settings were changed to block all traffic except what was explicitly allowed by the firewall rules. The blocked traffic was associated with the vulnerability scanning being conducted inside of the high impact BES Cyber System located inside the Control Center. A process was in place that allowed scanning to continue to be performed inside of the network, while the firewall blocked communication to other external networks. As part of its internal control program, RFC_URE7 conducts weekly comparisons for changes in the baseline configuration. A change was made to the firewall rules to allow traffic between the vulnerability scanners inside the Control Center network and the vulnerability scanning server on the administrative network. The daily automated comparison report was run for baseline changes. The next day, an IT compliance analyst noted new entries in the open ports reports and the software/patch inventory by the host report. The deviations that were discovered were discussed during the weekly change control meeting held by applicable IT personnel. During the investigation of these discrepancies, RFC_URE7 determined that the vulnerability scanning was not occurring inside of the Control Center network. Prior weekly comparison for changes in the baseline was determined to be based on data prior to the firewall being enabled. As a result, the total time between scanning for changes in the baseline configuration was 40 days, while CIP-010-1, Part 2.1 requires that it occur at least once every 35 days. The root cause of this noncompliance was a communication breakdown during CIP v5 implementation regarding what traffic would initially be allowed through the firewall. As a result of this miscommunication, incorrect data was being reported to IT security for its weekly comparison scans for changes in baseline configuration. This major contributing factor involves the management practices of implementation, which includes ensuring requirements from operations and maintenance have been communicated and implemented, and asset and configuration management, which includes establishing inventory and configuration baselines, as well as controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately five days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although the failure to monitor for changes to the baseline configuration could allow for changes to go undetected, RFC_URE7 completed its monitoring activities only 5 days late, which minimizes the amount of time that an unauthorized change could have gone undetected. RFC_URE7 also performs daily scans on all endpoints in the environment, which it rolls up into weekly comparisons of ports and system status changes. These additional security functions provide additional detection opportunities in the event the firewall had been compromised. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) verified that the firewall changes made in regard to the scanning traffic was accurate; 2) changed to a different firewall product in order to allow traffic between the vulnerability scanners inside the Control Center network and the vulnerability scanning server on the admin network; 3) verified manually that the weekly scans ran successfully in order to validate the accuracy of the generated reports; and 4) provided management direction to perform a manual verification to confirm that scans are actually successful and specifically address this issue at each weekly meeting of relevant subject matter experts. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017016967 | CIP-004-6 | R5 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-004-6 R5. RFC_URE7’s Human Resources personnel received an access revocation form from RFC_URE7’s Control Center supervisor identifying an employee with approved electronic and unescorted physical access to the Control Center who was to be terminated. A service desk ticket was created to track removal of the employee from both electronic and physical access to the generation management system (GMS) within 24 hours. The employee’s electronic access included two shared accounts comprising the (a) GMS application and (b) the two network Active Directory accounts. RFC_URE7 changed the password to the GMS application within 48 hours. However, the passwords to the two network Active Directory accounts were not changed for 34 days, or 4 days beyond the requirement. The root cause of this noncompliance was an insufficient workflow which resulted in the team responsible for Active Directory accounts not receiving notification from the IT group to change the passwords. This major contributing factor involves the management practices of information management, which includes controlling access to information items, and workforce management, which includes managing employee permissions and access to assets. The duration of the noncompliance was approximately three days. | This issue posed a minimal risk to the reliability of the bulk power system based on the following factors. First, the employee’s electronic access and unescorted physical access to the GMS system was properly terminated within 24 hours. As such, the employee had no access to applicable workstations to use either of the shared accounts at issue. Second, access to the GMS system requires both the network Active Directory password for the workstation and then the GMS application password to access GMS information. Because the GMS application password was changed within 48 hours, the employee could not have accessed any GMS information even with knowledge of the network Active Directory passwords. Third, the noncompliance was discovered and corrected only 4 days outside of the requirement, minimizing the likelihood of any harm being realized. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) changed the Network AD shared account passwords; 2) added the GMS Team to the list of recipients whom will receive a ticket in their queue for all RFC_URE7 account terminations. This means that the team will be required to address all termination tickets and take action on any of the NERC Shared account tickets; and, 3) instituted an additional process of weekly monitoring for the GMS owners shared password ticket until completed.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017016968 | CIP-006-6 | R2 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-006-6 R2. When conducting a quarterly review of visitor logs, RFC_URE7 documented several incomplete entries in the visitor logs. Notably, all visitors were identified and logged. However, certain pieces of information were missing. For instance, the date and purpose were omitted from some entries as well as the time in and time out. The root cause of this noncompliance was a failure to follow established procedure for completing the visitor logs and insufficient emphasis placed on the importance of completing these logs fully. This major contributing factor involves the management practice of information management, which includes controlling access to information items. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the Control Center has several security measures in place to protect the PSP. The Control Center is staffed 24 hours per day, seven days per week with a minimum of 3 employees. Furthermore, an individual must first pass through a card reader and enter a specific four digit pin to gain access to the Control Center. Second, this noncompliance primarily concerns incomplete documentation because the visitors were all identified, logged, and continuously escorted the entire time while in the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) reemphasized Visitor Control Program importance to all Control Center personnel with an email from Control Center Management; 2) increased awareness on visitor logging with adding new signage at the perimeter of the PSP of the Control Center for all visitors; 3) revised annual cyber training to include more emphasis on the Visitor Control Program and what needs to be documented upon a visitors exit out of the PSP; 4) conducted a refresher training with all Control Center personnel on RFC_URE7’s Visitor Control Program procedure; and, 5) self-assessed Control Center personnel to ensure the emphasis and refresher training on the Visitor Control Program is effective. RFC_URE7 also conducted weekly spot checks for one month to review the Visitor Log for completeness and documents by signing bottom of Visitor Log Page.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016015931 | CIP-011-2 | R1 | RFC_URE8 submitted a Self-Report stating that it had an issue of CIP-011-2 R1. While updating its procedures in preparation for CIP v5, RFC_URE8 updated its procedure for information protection. As part of this procedure, RFC_URE8 applies a greater level of granularity to identify protected information. While performing this update, RFC_URE8 reviewed its trouble ticket system to confirm that no tickets met the more granular threshold for “CIP Protected” information. One ticket was identified as containing information that, under CIP-011-2 R1, met the “CIP Protected” threshold in RFC_URE8’s program document. However, the information did not meet the criteria for protection under CIP v3. The root cause of this noncompliance was RFC_URE8’s lack of awareness while implementing this new procedure that it needed to reevaluate the tickets in the trouble ticket system to identify any tickets that contained information that should be protected under CIP v5, prior to the CIP v5 enforceable date. This lack of awareness was due to the fact that the trouble ticket system generally does not contain any CIP protected information. This major contributing factor involves the management practices of implementation and information management. Implementation is involved because RFC_URE8 implemented a new procedure without first identifying all potential changes that would need to take place as a result. Information management is involved because RFC_URE8 failed to protect CIP Protected information. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the information contained in the ticket at issue provided only the name of an administrative account. More specific knowledge regarding the Bulk Electric System (BES) Cyber System at issue would be needed before this information could pose a risk to the BES. Second, RFC_URE8 has already taken action to remove the CIP Protected information in the ticket at issue and has performed additional reviews of service manager tickets as part of its internal review without identifying an additional instance. Third, the server at issue is also protected from attacks by defense in depth systems including firewalls, protected networks, two factor authentication, monitoring and alerting systems, and physical security systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) removed the CIP Protected Information from the impacted ticket; 2) searched the past three years of trouble tickets to identify possible additional tickets with CIP Protected Information; 3) sent an email to associates with access to service manager reminding them to follow the CIP Information Protection expectations and to ask compliance teams for additional guidance if there is uncertainty; 4) developed a methodology to determine what action to take for tickets containing Protected Information; 5) applied methodology developed and completed removal of CIP Protected Information in trouble tickets from past three years; and 6) reviewed existing procedures for alignment. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2017017819 | CIP-006-6 | R1 | RFC_URE9 submitted a self-log stating that it had an issue of CIP-006-6 R1. RFC_URE9 dispatched a contractor to a substation to perform a walk-down in preparation for a construction project. Upon arriving at the substation yard gate, the contractor correctly used his assigned key to unlock the padlock and swiped his access card on the gate card reader to gain access to the substation yard. Having appropriately gained access to the yard, the contractor then proceeded to the substation control house. Upon reaching the control house doorway (the only access point to the control house Physical Security Perimeter (PSP)), the contractor swiped his access card on the card reader, pulled open the door and entered the control house. At this time, RFC_URE9’s Security Console received a forced door alarm. Security responded to the alarm by calling the substation and speaking with the contractor who entered the control house. The contractor indicated to security that he had swiped his badge on the door card reader, opened the door and entered the control house. The contractor also indicated he was alone and not under escort. Security informed him that he was not authorized for unescorted physical access to that control house and instructed him to exit immediately. The contractor followed instructions and left the control house, closing the door behind him. Thereafter, a security team member was immediately dispatched to the substation to inspect the door and its locking mechanism. Upon inspection, it was discovered that doors’ locking mechanism was not working properly. As a result, the construction contractor was able to pull open the door despite the card reader’s accurate denial of access. RFC_URE9’s security vendor was subsequently contacted to repair the locking mechanism. The vendor arrived within a few hours of the incident. The vendor’s inspection determined that the door's electronic strike was not securing the door each time the door was closed. The electronic strike was demounted and remounted by the vendor, tested and found to be working properly again. Note: Prior to the repair work, the locking mechanism had been previously tested approximately six months earlier as part of RFC_URE9’s CIP-006-6 R3 maintenance and testing program. The lock was found to be working properly at that time. This first issue involves the management practice of external interdependencies because the vendor that installed the door failed to ensure that the door's electronic strike to secure the door functioned every time. Ineffective vendor management is a root cause. ------------ An employee arrived to work at RFC_URE9’s Control Room facility. On that particular morning, the employee had forgotten his access card. Although the employee was authorized for unescorted physical access to the Control Room PSP and had current training and personnel risk assessment (PRA) on file, RFC_URE9’s physical access program requires personnel who do not have their access card in their possession to be escorted as prescribed under the visitor control program. Accordingly, the employee was assigned an authorized escort for the day and, with the exception of the below incident, was continuously escorted for the duration of his shift. Later that afternoon, without his escort’s knowledge, the employee walked off the Control Room floor, proceeded up to the second level and exited the PSP through an access point door leading to a rear stairwell. Against physical security protocols, the employee further propped open the access point door to allow himself unobstructed access upon his return to the PSP area. The employee subsequently proceeded down to the first level and exited the facility. The employee was outside for approximately 2 minutes before re-entering the facility and returning to the PSP area, at which time he re-secured the access point door. During this time, RFC_URE9’s Security Console received a door held open alarm. Security immediately responded to the alarm, and logged an investigation report, identifying the employee and his escort. Further investigation determined that the employee failed to follow physical security protocols by (i) exiting and re-entering the PSP unescorted and (ii) propping open the PSP rear door. Video and event logs determined that the door was left unsecure for less than 3 minutes. This second issue involves the management practice of workforce management because the employee was ineffectively trained on how to follow RFC_URE9's physical security protocols. Ineffective training is a root cause. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A risk harm assessment determined the above issues to be of minimal impact to the BPS. RFC_URE9’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP‐006‐6 requirements. In fact, these issues were identified as a result of these effective controls. In both cases, automated alarming mechanisms worked as intended, enabling Security to quickly respond to the issues. Further impacting the assessment, the contractor in the first instance was a former RFC_URE9 employee with valid PRAs and requisite training on file dating back approximately seven years. Following the incident, the contractor was subsequently granted unescorted Substation PSP access upon completion of the current physical access training. With regard to the second incident, the employee was in fact authorized for unescorted access, with valid PRAs and training on file. Video review confirmed that there was no incident of unauthorized access within the 2-3 minute timeframe during which the access point was left unsecured. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: Issue 1 1) responded to the forced door alarm, identified the individual at the substation, and instructed him to leave the premises. The door was inspected and a security vendor was contacted to perform repairs on the door's locking mechanism; 2) reviewed its CIP-006 R3 maintenance and testing checklist and updated as necessary to ensure there are no gaps in the inspection process; 3) re-inspected the substation PSP door; 4) engaged independent assessors to evaluate the doors and the corresponding control mechanisms at a sample set of PSPs to evaluate alarm contact placement, control hardware, locking mechanism, and other controls as appropriate. Issue 2 1) responded to the alarm, contacting System Operations personnel ensuring the doors were secured and recurrence halted. Additionally, the employee was referred to Human Resources and disciplinary action was taken; and 2) provided internal coaching to the escort involved in the incident.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2017017822 | CIP-007-6 | R2 | RFC_URE9 submitted a self-log stating that it had an issue of CIP-007-6 R2. RFC_URE9 performed a scheduled monthly review of RFC_URE9’s energy management system (EMS) Deferred Patch Plan (DPP) log. During the review, it was discovered that 2 patch mitigation plans (MP) captured on the DPP log had not been updated to reflect the operational need to extend their installation. Upon investigation of the issue, the following facts were collected and causal factors identified. A vendor released security patches applicable to certain device types within RFC_URE9’s EMS environment. The patches were correctly assessed within 35 days of their respective release and found to be applicable, but their installations needed to be deferred beyond the required 35 day installation timeframe. Accordingly, MPs for the patches were created and appropriately added to the DPP log with a proposed completion date. The DPP log for both MPs was approved within 35 days of their respective assessments. Subsequently, at a recurring EMS patch management meeting, a determination was made that all patch installations in the EMS environment would be further delayed by operational order due to current and forecasted excessive temperatures in the RFC_URE9 region. As a result, it was discussed that the proposed completion dates for the two MPs noted-above would need to be extended. At that time, the individual responsible for EMS patch installations believed that the discussion regarding the extension of the proposed completion dates was sufficient notification to the individual responsible for managing the DPP log. However, the individual responsible for managing the DPP log expected to receive written confirmation after the meeting, which they subsequently did not receive. As a result of this miscommunication, the proposed completion dates for the two MPs were not extended in a timely manner. RFC_URE9’s CIP Patch Management Program assigns specific roles and responsibilities to personnel involved in the patch process. In particular, the Patch Program Coordinator is responsible for managing the patch source list, identifying and assessing patches, maintaining a patch inventory log, and managing the DPP log. In the EMS functional area, this role was divided amongst two individuals, where one individual managed the patch identifications, assessments, installations, and provided the relevant DPP information to the other individual responsible for creating, updating and monitoring the DPP log based on the information provided. While the process within the program was followed, bifurcating the Patch Program Coordinator role resulted in a communication gap that led to the error reported herein. This noncompliance involves the management practice of workforce management because the individual responsible for EMS patch installations believed that the discussion surrounding the extension of proposed completion dates for the two patch mitigation plans was sufficient. Ineffective training is a root cause. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE9’s risk-harm assessment determined the above issue to be administrative in nature and of minimal impact to the BPS. The patches were timely identified, assessed and correctly recorded on the DPP log. As required for all deferred patches, mitigating measures were appropriately in place and remained in place during the potential noncompliance period. Internal program controls effectively detected and ensured correction of the issue within one day of identification. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) updated RFC_URE9's DPP log to extend the proposed installation dates for the two MPs. The DPP log was approved by the CIP Senior Manager delegate; 2) assigned only one individual to the Patch Program Coordinator role; and 3) reviewed its CIP-007-6 patch management process to ensure there are no additional gaps with creating, revising, or obtaining approval of the MPs within the DPP.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2017017823 | CIP-010-2 | R1 | RFC_URE9 submitted a self-log stating that it had an issue of CIP-010-2 R1. Having completed a thorough compliance investigation of a configuration change captured in its security and threat detection program, RFC_URE9 determined it had a potential issue involving CIP-010-2, Part 1.2, regarding authorization for Bulk Electric System (BES) Cyber Asset (BCA) baseline changes in production. Specifically, a change management request form (CRF) was opened to test and install Device Manager software on three RFC_URE9 programmer workstation BCAs. The CRF included all requisite information, and was appropriately approved to proceed to the testing phase. While the CRF was still in its testing phase, however, a scheduled review of the security and threat detection logs discovered a baseline configuration change on one of the target programmer workstation BCAs in production. An investigation determined the person responsible for testing had installed the Device Manager software on the BCA, in order to perform more in-depth functional testing that could only be performed in the production environment. However, RFC_URE9’s Configuration Change Management Program requires management approval before testing can be moved and associated configuration changes can be made in the production environment. In this case, the CRF had not been approved for testing in production. Accordingly, the configuration changes made to the BCA for testing purposes had not been approved in accordance with RFC_URE9’s configuration change management procedures. On interview, the responsible employee was unaware that she had not followed procedures requiring approval before moving testing activities into the production environment. The CRF was later canceled and the software uninstalled, upon subsequent determination that the software would not be needed in the energy management system (EMS) environment. This noncompliance involves the management practice of workforce management because the employee performing the testing did not follow procedures that require approval before moving testing activities into the production environment. Ineffective training is a root cause. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE9’s risk-harm assessment determined this issue to be of minimal impact to the BPS. The BCA was appropriately protected from unauthorized access within the Electronic Security Perimeter and enclosed in a Physical Security Perimeter, and installation of the software on to the BCA did not introduce any negative impacts (e.g., malware, unnecessary open ports and services, etc.) to the EMS environment. Moreover, the issue was identified as a result of effective controls in place to detect such configuration changes and ensure timely resolution of unintended errors. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) removed the Device Manager software from the programmer workstation BCA; 2) provided additional training to EMS management personnel to reiterate RFC_URE9’s configuration change management process and procedures; and 3) provided awareness of all in-scope assets to the personnel in the testing team.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016419 | CIP-007-6 | R.2; R2.2 | SPPRE_URE1 submitted a Self-Log stating that it had an issue of noncompliance with CIP-007-6 R2.2 because SPPRE_URE1 did not properly evaluate a security patch for applicability within 35 calendar days after it was released. While performing monthly patch evaluations, SPPRE_URE1 discovered that a patch evaluated the previous month had not been properly evaluated for applicability. During the previous evaluation, SPPRE_URE1 had misinterpreted the information released by the vendor and assessed the security patch as a version upgrade that had already been applied to SPPRE_URE1 Cyber Assets instead of assessing it as a security patch. The security patch was re-evaluated 43 days after its release, and SPPRE_URE1 determined that the security patch should be applied to two Cyber Assets. The root cause of this instance of noncompliance was human error. The duration of this instance of noncompliance was eight days, beginning the day after the security patch should have been evaluated for applicability and continuing through the date the security patch was evaluated for applicability. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly evaluate a security patch for applicability has the potential to affect the reliability of the BPS because all known vulnerabilities may not be mitigated in a timely manner and could leave Cyber Assets vulnerable to a cyber-attack. Notwithstanding, the security patch that should have been evaluated was to address a known vulnerability associated with connections to external networks. However, the two Cyber Assets involved did not have direct access to external networks. Additionally, the security patch was evaluated immediately upon discovery and implemented 13 days following the evaluation, within the maximum time allowed for patch application in CIP-007-6 R2. The issue of noncompliance was short in duration (7 days). No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) evaluated and applied the security patch; 2) utilized a different support document URL for the vendor's website that more clearly represents the versions affected by identified vulnerabilities and the resulting patches; and, 3) provided guidance and coaching to the employee about the importance of attention to detail and verification of work before completion. SPP RE has verified the completion of all mitigation activity.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2017016766 | CIP-006-6 | R1; R1.2, R1.8 | SPPRE_URE2 submitted a Self-Log stating that it had an issue of noncompliance with CIP-006-6 R1.2 and R1.8. SPPRE_URE2 identified three instances of noncompliance where employees with authorized unescorted physical access to a Physical Security Perimeter (PSP) did not properly utilize the operational and procedural controls implemented to restrict physical access (R1.2), and entry into the PSP by such employees with authorized unescorted physical access had not been logged (R1.8) as defined in SPPRE_URE2’s CIP physical security plan. Instance #1: an SPPRE_URE2 employee (Employee #1) who has authorized unescorted access to the Primary Control Center (PCC) PSP was issued a temporary PSP badge. While attempting to access the PSP, Employee #1 properly scanned the temporary badge, but entered the incorrect PIN number associated with the badge, generating a door alarm and a siren from the Physical Access Control System (PACS). The on-duty SPPRE_URE2 employee (Employee #2) exited the PSP and re-entered providing Employee #1 access to the PCC without Employee #1 using his temporary PSP badge. Also, Employee #2 did not contact the Security Control Center (SCC) to ask why the temporary badge was not working as required by SPPRE_URE2’s CIP physical security plan. Instance #2: the SPPRE_URE2 lead custodian (SPPRE_URE2 LC) scanned her replacement badge triggering an invalid badge alarm. The SPPRE_URE2 Energy Management System employee immediately scanned his badge to clear the alarm and let the SPPRE_URE2 LC into the PSP. Twenty-two minutes after entering the PSP, the SPPRE_URE2 LC scanned her replacement badge to exit the PSP, triggering another invalid badge alarm. Again, the SPPRE_URE2 Energy Management System employee scanned his badge to clear the alarm and allowed the SPPRE_URE2 LC to exit from the PSP; however, he did not contact the SCC to find out why the replacement badge did not work, per SPPRE_URE2's CIP physical security plan. Instance #3: Employee #3 was issued a temporary PSP badge. Employee #3 scanned the temporary badge to enter the Backup Control Center (BCC) PSP and triggered an invalid badge alarm. Another SPPRE_URE2 employee scanned his badge and entered his PIN to silence the alarm and allowed Employee #3 to enter the PSP without scanning the temporary badge. Employee #3 did not call the SCC to find out why the temporary badge did not work per the CIP physical security plan. The duration of these instances of noncompliance was 158 days, beginning the date of the first instance where SPPRE_URE2 did not follow its CIP physical security plan and continuing through the date of the last instance where SPPRE_URE2 did not follow its CIP physical security plan. The root cause of these instances of noncompliance was a combination of human error and awareness because SPPRE_URE2 employees failed to follow the SPPRE_URE2 CIP physical security plan. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-006-6 R1 has the potential to affect the reliability of the BPS by presenting a risk of unauthorized access to SPPRE_URE2’s PSP, which if undetected, could compromise BES Cyber Systems located within the PSP. Notwithstanding, the SPPRE_URE2 employees who entered the PSPs without use of their badges and PIN had authorized unescorted physical access to the PSPs, therefore, there was no actual risk to the PSPs and BES Cyber Systems. No harm is known to have occurred. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE2: 1) distributed a security awareness communication to all individuals with authorized unescorted physical access to BES Cyber Systems reinforcing the importance and appropriate use of the physical security controls in SPPRE_URE2’s CIP physical security plan; and, 2) identified and allowed remote access for provisioning badges during times when the designated SPPRE_URE2 employees who authorize such provisions are out of the office. SPP RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017017343 | CIP-008-5 | R3, Part R3.1 | TRE_URE1 submitted a Self-Log stating that it had an issue of CIP-008-5 R3, Part 3.1. Specifically, TRE_URE1 failed to notify each person or group with defined roles in the Cyber Security Incident response plan (CSIRP) of updates to the CSIRP within 90 days as required. TRE_URE1 conducted a CSIRP test for Medium and Low BES Cyber Systems. According to CIP-008-5 R3, Part 3.1, TRE_URE1 was required to notify each person or group with a defined role in the CSIRP based on any documented lessons learned within 90 calendar days of the completed CSIRP test. As such, TRE_URE1 should have provided such notice within 90 days following completion of the CSIRP test. However, TRE_URE1 provided the initial notice of CSIRP updates to certain individuals and groups more than 90 days following completion of the CSIRP test. Moreover, this initial notice inadvertently omitted four individuals and two groups with defined roles in the CSIRP. During a subsequent review of its CIP-008-5 compliance information, TRE_URE1 discovered the omissions and distributed the CSIRP updates to all individuals and groups with defined roles in the CSIRP, ending the issue. The root cause of TRE_URE1’s noncompliance was an inadequate process for distributing updated CSIRP information to all individuals and groups with defined roles in the CSIRP. In particular, TRE_URE1 relied solely on an individual manually creating the relevant distribution list to provide updates to all applicable individuals and groups and providing such updates in a timely manner. This issue duration was approximately 35 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following six reasons. First, the period of the initial delay in distributing the required CSIRP updates was short, lasting only two days. Second, TRE_URE1 quickly detected and corrected the overall noncompliance within 35 days of the start of the issue. Third, the updates to the CSIRP were not substantive and did not change the roles or responsibilities for the individuals and groups omitted from the original notification. Fourth, all individuals and groups receiving the CSIRP updates participated in the CSIRP test. Fifth, TRE_URE1 annually trains all individuals and groups receiving the updated CSIRP information on the CSIRP, further reducing any lack of awareness regarding response procedures. Sixth, the updates to the CSIRP were based on a test of the plan and not based on response to an actual Reportable Cyber Security Incident. No harm was known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) sent a copy of the updated CSIRP to all individuals and groups with defined roles in the CSIRP; 2) created an automated distribution list that includes each person or group with a defined role in the CSIRP to be used for future updates to the plan; and 3) ensured that each person or group with a defined role in the CSIRP has ongoing access to the current version of the CSIRP to facilitate continuous access to the CSIRP during the editing process following a CSIRP test. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016016600 | CIP-010-2 | R1, Part 1.3 | During a Compliance Audit Texas RE determined that TRE_URE2 had an issue with CIP-010-2 R1, Part 1.3. In particular, TRE_URE2 did not have one or more documented processes specifying that for changes deviating from the existing baseline configuration, TRE_URE2 personnel will update the baseline configuration within 30 calendar days of completing the change. The root cause of this issue was that TRE_URE2’s documentation did not fully detail all required steps in its baseline configuration change management process. In particular, TRE_URE2’s existing documentation included steps to identify and implement baseline variances, as well as processes to update the baseline configuration to reflect those changes, but did not explicitly state that such actions must be taken within 30 calendar days of the baseline configuration change. The issue was approximately 94 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was limited to a documentation issue. Specifically, TRE_URE2’s existing documents addressed most aspects of the baseline configuration change management process, but did not specify the appropriate timing for completing such actions. Moreover, TRE_URE2 presented evidence that although its existing procedures did not contain a requirement to update its baseline configuration within 30 calendar days of completing a baseline configuration change, TRE_URE2 had in practice implemented a process to complete all baseline configuration updates within the required 30 calendar day time frame. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) modified its baseline configuration change management process documents to include an explicit requirement to update the baseline configuration within 30 calendar days of completing a change that deviates from the existing baseline configuration; 2) demonstrated that the revised process documents were reviewed by the relevant manager; and 3) distributed its new baseline configuration change management process documents to all applicable staff members. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017017086 | CIP-014-2 | R1 | TRE_URE3 submitted a Self-Report stating that it had an issue of CIP-014-2 R1. Specifically, TRE_URE3 failed to include two required substations in its initial CIP-014-2 R1 risk assessment. The root cause of this omission was the lack of controls in TRE_URE3’s Physical Security Study Procedure. Specifically, TRE_URE3 relied on a manual process to identify substations meeting CIP-014’s applicability criteria and the individual performing the substation weight value per line calculations per that process miscalculated the values for the two substations at issue. The issue duration was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, the substations omitted in the initial risk assessment did not constitute substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. Second, the third party reviewing TRE_URE3’s updated risk assessment plan verified the conclusions in TRE_URE3’s updated risk assessment. Finally, the two substations at issue already had physical security protections under TRE_URE3’s existing Physical Security Plan. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) corrected the initial risk assessment; 2) obtained verification from an independent third party regarding the determinations in the revised risk assessment; 3) established an automated process for determining whether substations meet CIP-014’s risk assessment criteria; and 4) updated its Physical Security Study Procedure to include multiple controls to ensure the list of Applicable stations and substations is accurate and complete. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017017524 | CIP-003-6 | R1, Part 1.2 | TRE_URE4 submitted a Self-Report stating that it had an issue of CIP-003-6 R1. Specifically, TRE_URE4 did not develop all required cyber security policies specified in CIP-003-6 R1, Part 1.2 for its assets identified in CIP-002 containing low impact BES Cyber Systems by the NERC Standard enforcement date. The root cause of this issue was insufficient understanding of the specific compliance obligations under the newly applicable CIP Version 5 standards. In particular, TRE_URE4 compliance personnel did not understand the need to develop new cyber security policies to address Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity for a low-impact BES Cyber System. The issue duration was approximately 27 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the duration of the issue was short, lasting only 27 days. Second, TRE_URE4 possessed an existing cyber security policy sufficient to comply with prior CIP requirements, limiting the scope of TRE_URE4’s documentation issues solely to Electronic access controls for LERC and Dial-up Connectivity. Third, no Cyber Security Events occurred during the noncompliance period. Finally, TRE_URE4 is a small generation facility. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE4: 1) executed and implemented the cyber security policies required by CIP-003-6 R1, Part 1.2 for low impact BES Cyber Systems; and 2) hired a third-party contractor to provide compliance services to monitor and address compliance with the new CIP Version 5 Standards applicable to low-impact BES Cyber Systems, as well as provide training to TRE_URE4 personnel regarding their compliance obligations. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2017017525 | CIP-003-6 | R2 | TRE_URE4 submitted a Self-Report stating that it had an issue of CIP-003-6 R2. Specifically, TRE_URE4 reported that it did not implement one or more documented cyber security plans for a low impact BES Cyber Systems that include all required elements set forth in CIP-003-6 R2, Attachment 1, Sections 1 and 4. The root cause of this issue was insufficient understanding of the specific compliance obligations under the newly applicable CIP Version 5 standards. In particular, TRE_URE4 compliance personnel did not understand the need to develop new cyber security policies to address a low-impact BES Cyber System, including the obligation to test their Cyber Security Incident response plan prior to the April 1, 2017 deadline. The issue duration was approximately 32 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the duration of the issue was short, lasting only 32 days. Second, TRE_URE4 possessed an existing cyber security policy sufficient to comply with prior CIP requirements, limiting the scope of TRE_URE4’s documentation issues. Third, no Cyber Security Events occurred during the noncompliance period. Finally, TRE_URE4 is a small generation facility. No harm is known to have occurred. Texas RE considered TRE_URE4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE4: 1) completed the required documentation and demonstrated implementation of the activities required by CIP-003-6 R2 Attachment 1, Sections 1 and 4, including all required testing activities; and 2) hired a third-party contractor to provide compliance services to monitor and address compliance with the new CIP Version 5 Standards applicable to low-impact BES Cyber Systems, as well as provide training to TRE_URE4 personnel regarding their compliance obligations. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017529 | CIP-007-6 | R2 | WECC_URE1 submitted a Self-Log stating that it had a possible issue of noncompliance with CIP-007-6 R2.2. 3. Specifically, WECC_URE1 reported that in two instances, it failed to evaluate security patches for applicability within 35 calendar days of the last assessment for the Bulk Electric System (BES) Cyber Assets. WECC_URE1 uses a software asset management system for its patch management system. However, WECC_URE1 failed to track patches for programming software, because it failed to input the correct version of a programming software into its software asset management system. WECC_URE1 discovered that it failed to review a programming software patch for applicability within 35 calendar days. A second issue of noncompliance occurred when an additional programming software patch was released and WECC_URE1 failed to review the patch for applicability within 35 calendar days. The second issue was discovered and the patch evaluated. WECC_URE1 has servers that were subject to these issues. Some of the assets included the EMS SCADA servers within the High-Impact BES Cyber System (HIBCS) that provide data for high-speed historian playback and have no role in real time operations. Other assets included servers that reside in an intermediate system and access to those servers does not provide access to control networks. The first issue started when the programming software patch was released without WECC_URE1 evaluating the patch, and ended when the programming software patch was discovered and evaluated, for a total of 15 days of noncompliance. WECC determined that the second issue began when the additional programming software patch was released without WECC_URE1 evaluating the patch, and ended when the patch was evaluated, for a total of 32 days of noncompliance. In the first issue of noncompliance, the cause was that WECC_URE1 failed to update its software asset management system with the new branch of programming software. In the second issue of noncompliance, the cause was that WECC_URE1 failed to understand and follow new management policies implemented as a mitigation for the first issue of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In these two instances, WECC_URE1 failed to review programming software patch updates for applicability within the required 35 calendar day timeframe for BES Cyber Assets. Failure to perform security patch assessments in a timely manner could potentially result in an attacker gaining access to WECC_URE1’s HIBCS or intermediate system to cause disruptions to its operation capabilities; thereby, affecting the reliability of the BPS. However, WECC_URE1 implemented controls to reduce the likelihood of these results from occurring. Specifically, WECC_URE1 utilized a vulnerability assessment tool to discover the issues of noncompliance. Additionally, the affected assets have no control capability. The EMS SCADA servers have no real-time operations and the servers in the intermediate system do not provide access to control networks. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) assessed all available security patches for applicability; 2) created a process to update its software asset management system when there are changes to patching sources; 3) created a vulnerability assessment of cyber assets which audits programs against each other to ensure consistency; and 4) provided training for all applicable personnel.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2017017134 | CIP-004-6 | R5 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-6 R5.2. Specifically, WECC_URE2 reported that after an individual changed positions within the company and no longer needed physical access to the Physical Security Perimeter (PSP), WECC_URE2 did not revoke physical access for said individual within the required one calendar day timeframe. The individual transferred positions and WECC_URE2 discovered the individual still had access to the control center PSPs protecting its Medium Impact Bulk Electric System (BES) Cyber System (MIBCS). WECC_URE2 then revoked the individual’s access and conducted an investigation to discover how the individual’s transfer was overlooked. WECC_URE2 determined that its transfer notification process did not clearly identify the appropriate staff that should have received the notification. Additionally, WECC_URE2 discovered that the automated daily report regarding employees who have transferred did not clearly identify the transfer. WECC reviewed the Self-Report, and after further discussions with WECC_URE2 and analysis of data request responses, determined that WECC_URE2 failed to revoke physical access per CIP-004-6 R5 part 5.2, for one individual who no longer required the physical access. This issue started when WECC_URE2 failed to revoke physical access for one individual, and ended when WECC_URE2 revoked the physical access, for a total of 21 days of noncompliance. The cause was a less than adequate process that did not provide specific distribution lists to use for a transfer notification. This caused applicable individuals to not receive the transfer notification, therefore missing the need to revoke physical access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to revoke an individual’s physical access to a MIBCS PSP within one calendar day after WECC_URE2 determined the individual no longer needed physical access. Such failure could present a risk of unauthorized access to WECC_URE2’s MIBCS. Such unauthorized access could be exploited to cause damage or outages within the BES, thereby potentially affecting the reliability of the BPS. However, the likelihood of the risk occurring was reduced by the controls WECC_URE2 had implemented. The individual is still in good standing at WECC_URE2 and did not leave the company, but transferred positions within WECC_URE2. Additionally, the individual only had physical access to the MIBCS PSP in order to perform custodial duties and did not have electronic access to the BES Cyber Assets. WECC_URE2 also confirmed that the individual did not utilize their badge to access the PSP from the time their position changed until the time their access was revoked. No harm is known to have occurred. | To mitigate this issue, WECC_URE2: 1) revoked the individual’s physical access; 2) conducted daily phone calls to ensure transfers were processed correctly until the implementation of mitigating activities was complete; 3) verified that there were no other individuals who had unauthorized physical access to the MIBCS PSP; 4) updated process documents to properly address revocation timeframes; 5) created an email distribution list to properly notify applicable individuals involved in providing physical access to the PSP; and 6) modified its system of record to provide an automated notification for transfers of employees with BCS access.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016514 | CIP-006-6 | R1 | WECC_URE3 submitted a Self-Report stating that it had an issue with CIP-006-6 R1 Part 1.10. This noncompliance was also an area of concern as identified by WECC auditors during WECC_URE3’s CIP Version 3 to CIP Version 5 transition audit. For CIP-006-6 R1 Part 1.10, WECC_URE3 reported that although its physical security infrastructure had been designed and created so that all applicable cabling and communication equipment resided within a PSP, WECC_URE3 did not update its physical security plan documentation stating such. WECC_URE3 was in violation of Part 1.10 when it did not document how it restricted physical access to cabling and other nonprogrammable communications components located outside of a PSP. The cause was due to the unexpected retirement of its CIP-006 Subject Matter Expert which left compliance with this Standard and Requirement to personnel who were less familiar with CIP-006 and had little time for training or preparation due to the impending WECC audit and CIP Version 5 transition. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE3, and ended when WECC_URE3 updated its physical security plan to include Part 1.10, for a total of 70 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE3 failed to document how it restricted physical access to cabling or other nonprogrammable communications components located outside of a PSP per Part 1.10. Such failure could result in cables being tampered with in order to access communications and modify information; thereby potentially affecting the BES. However, the likelihood of this risk occurring was reduced by the fact that WECC_URE3’s physical security infrastructure had been designed and created so that all applicable cabling and communication equipment reside within a PSP. This was a documentation issue only. No harm is known to have occurred. WECC_URE3 has no previous compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE3 updated its physical security plan to include Part 1.10 of CIP-006-6 R1.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2017016890 | CIP-003-3 | R5 | WECC_URE4 submitted a Self-Report stating that it had an issue with CIP-003-3 R5. Specifically, WECC_URE4 reported that IT security personnel were reviewing the electronic access to its CIP Version 5 directory and discovered that personnel had electronic access to CIP-protected information that were not authorized to have said access. One of WECC_URE4’s domain user groups was given ‘read’ access to all ‘shared’ folders without consideration to the restrictions required for access to CIP protected information. IT security had a process in place for provisioning access to ‘private’ or ‘shared’ folders which had been updated prior to discovery of the potential noncompliance. The intent of the update was to allow traversal to subfolders, but inadvertently, read access was given to all shared directories to anyone in the company with a network login, including the CIP Version 5 restricted directory. The information in the CIP Version 5 directory originally contained mostly draft CIP Version 5 documentation. WECC_URE4 started saving CIP Version 5 change control evidence that had specific device information; lists of Critical Assets; and Bulk Electric System (BES) Asset information, information that WECC_URE4 had classified as CIP protected information. It should also be noted that physical and electronic access to CIP assets remained protected through access controls pursuant to applicable Reliability Standards. The cause was a less than adequate procedure that did not include all the necessary steps on how to set permission levels when creating directories. WECC reviewed the Self-Report and, after further discussions with WECC_URE4 and analysis of data request responses, determined that WECC_URE4 failed to restrict electronic access to CIP-protected information to unauthorized personnel per its CIP information protection program, as per CIP-003-3 R5. WECC determined that this issue began when CIP-protected information was available to unauthorized personnel, and ended when WECC_URE4 restricted electronic access to the CIP Version 5 directory to only authorized personnel, for a total of 83 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE4 failed to restrict electronic access to CIP protected information per its procedure when it provisioned ‘read’ access to the protected information to all personnel with a network login. Such failure could lead to intentionally or inadvertently sharing of the protected information with bad actors who could use the information to compromise CIP assets on WECC_URE4’s network and potentially disrupting operations; thereby affecting the reliability of the BES. However, the likelihood of the risk occurring was reduced by the controls that WECC_URE4 had implemented. WECC_URE4’s review process detected this issue of noncompliance. Electronic access to CIP-protected information in and of itself does not provide physical or electronic access to any CIP assets. No harm is known to have occurred. WECC_URE4 had no relevant prior noncompliance with this Standard and Requirement. | To mitigate this issue, WECC_URE4: 1) modified directory permissions to restrict access to the CIP Version 5 directory to authorized personnel only; and 2) updated its IT security procedure to include additional steps for setting and validating directory permissions.
2017-07-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016818 | CIP-007-6 | R5 | MRO_URE1 stated that it did not file a timely TFE request for two protocol converter devices (PACS devices) that were unable to feasibly either "limit the number of unsuccessful authentication attempts" or "generate alerts after a threshold of unsuccessful authentication attempts." The cause of this noncompliance was MRO_URE1's failure to timely realize that these devices were unable to feasibly comply with CIP-007-6 R5 Part 5.7. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The TFE was subsequently granted, and the noncompliance can be accurately categorized as an administrative issue as opposed to an issue that threatens the reliability of the BPS. Further, if an adversary did gain access to these devices, the adversary could not utilize these devices alone to grant access rights to users, but only disable MRO_URE1's ability to make additions or subtractions to the list of authorized users. Finally, the duration of the noncompliance was relatively short. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-007-6. | To mitigate this issue, MRO_URE1 submitted a TFE that was subsequently approved. MRO verified that mitigating activities were complete.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016636 | CIP-009-6 | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-009-6 R1. RFC_URE1 experienced issues with two tools: (1) a server which is used for two factor authentication in remote access; and, (2) its tool for monitoring, alerting, and logging. In the first issue related to the server, RFC_URE1 conducted an annual Disaster Recovery Plan drill, during which they discovered that: (a) insufficient evidence was available to show that backup reviews had been conducted; and, (b) their offline, backup file was not effectively captured for approximately three months. (The server system has two methods of preserving the user database. First, a replication of the database is distributed in real-time to the secondary servers. Second, a backup file is used if the database running on the primary and secondary servers becomes corrupt.) According to the Restoration Plan, backup reviews should have been conducted weekly. In the second issue, during the same Disaster Recovery Plan drill, RFC_URE1 discovered that the system used for backups for the system became corrupt. As a result, alerts of failed backups were not issued. Because no alerts were generated, no action was taken to address the failed backups for approximately two months. The root cause of this noncompliance includes: (1) insufficient procedures for backups, specifically that the procedures failed to include all information necessary to properly set them up; (2) the failure to follow procedures requiring weekly review of backups; (3) equipment failure involving backups for the alert system, which prevented alerts from being issued; and, (4) infrequent verification of backups. These major contributing factors involve the management practices of asset and configuration management, verification, and workforce management. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, both systems serve as additional security tools, and neither one has a direct role in the operation of Bulk Electric System assets as long as facilities are manned. Second, the database is backed up to multiple secondary servers in real time. Therefore, if the primary or a secondary device went down, one of the other devices would be promoted to primary. Third, the risk posed by the lack of backups is mitigated by the fact that a restoration of that system could still be performed. However, it would just be a more time-intensive, manual process and only historical data would be lost. Fourth, both systems are protected by a defense in depth strategy including: (1) being completely segmented from the internet and the RFC_URE1 enterprise network by a series of firewalls; and, (2) having multiple layers of login to reach the systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) reconfigured service related to backups for the server and confirmed backups are working as expected; 2) confirmed email message alerts related to failed backups are sent to the appropriate group; 3) implemented weekly manual logging of backups, including what action is taken if backups fail; 4) implemented weekly manual logging of backups including what action is taken if backups fail; 5) updated Disaster Recovery plans to state backup reviews are done manually and sent notice of plan update to responder groups mentions in the plan; 6) updated the Build Guide document to include backup and alerting; 7) conducted a review session to members of the responsible group to review expectations for backups; and 8) began bi-weekly confirmation of weekly backup review. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017016760 | CIP-003-3 | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. While verifying the total number of users with NERC CIP access, RFC_URE1 discovered that some users who lacked adequate training had retained NERC CIP Information Repository (CIR) access. Following discovery, RFC_URE1 pulled a report from their online training center to determine the number of users who had proper NERC CIP training. This list was then compared to a report of all users in the access management system. By comparing these lists, RFC_URE1 determined that four users whose training had expired, retained access to CIP protected Cyber System Information (BCSI) in the form of a CIR. Later that same day, the responsible group completed its review of all items and manually removed all access associated with the four users’ accounts, which consisted of the following: (a) the four users had retained five levels of access; (b) one user had retained RFC_URE1 information access; (c) two users had retained RFC_URE1 CIR access; and, (d) one user had retained access to two separate levels of Shared Services information access. One user was on personal leave for more than 30 days, but the access management system did not automatically remove access as required despite the entering of all appropriate removal tickets. NERC CIP training expired for the other three users. For the user with access to the Shared Services CIRs, the access management system did not automatically remove access to the resource. This user retained access to two Shared Services CIRs that were required in a previous role within RFC_URE1. This user was unaware he had access to these CIRs and did not access them. Two users retained access to RFC_URE1 CIRs. These access levels were retained after the users' training expired. Because the access was outside of a role, the access was not removed. The root cause of this noncompliance was the technical limitation in the access management system tool on how it automatically processes removals. The technical limitation was not discovered during pre-launch testing. Access management system is a tool that distributes access based on access roles. Each role is a combination of entitlements to NERC CIP electronic information and physical access. RFC_URE1 expected the access management system to remove all access that the user had within 24 hours automatically. However, the access management system did not remove access privileges granted through entitlements that were not associated with a "role." This noncompliance involves the management practices of information management, implementation, and verification. Information management is involved because RFC_URE1 failed to limit the access of employees to information which they did not have the training or clearance to access. Implementation is involved because RFC_URE1’s access management system tool was improperly configured to remove NERC CIP access properly for those not associated with a role. Verification is involved because RFC_URE1 failed to verify that the access management system tool was properly configured to their specifications. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by these instances of noncompliance is the provision of access for bad actors to BES Cyber Assets which could adversely impact the reliability of the electric grid. The risk is minimized in this instance because the employees who were incorrectly provided access remain in good standing with the company and the company has no reason to believe that any malicious action caused this occurrence. The risk is further minimized because each user had a current personal risk assessment and prior CIP training. ReliabilityFirst also notes that of the four users with expired credentials, three were unaware that they retained access and the fourth was unable to login as a result of technical controls put in place when the individual went on extended leave. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed NERC CIP Access for the four employees initially identified when preparing and assessing a summary report; 2) identified users with access outside of roles; 3) reviewed the entitlements not in access roles in the access management system and took action as needed; and 4) updated and implemented changes to RFC_URE1 process documents for adding new Active Directory groups into certain locations.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016638 | CIP-009-6 | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-009-6 R1. RFC_URE2 experienced issues with two tools: (1) a server which is used for two factor authentication in remote access; and, (2) its tool for monitoring, alerting, and logging. In the first issue related to the server, RFC_URE2 conducted an annual Disaster Recovery Plan drill, during which they discovered that: (a) insufficient evidence was available to show that backup reviews had been conducted; and, (b) their offline, backup file was not effectively captured for approximately three months. (The server system has two methods of preserving the user database. First, a replication of the database is distributed in real-time to the secondary servers. Second, a backup file is used if the database running on the primary and secondary servers becomes corrupt.) According to the Restoration Plan, backup reviews should have been conducted weekly. In the second issue, during the same Disaster Recovery Plan drill, RFC_URE2 discovered that the system used for backups for the system became corrupt. As a result, alerts of failed backups were not issued. Because no alerts were generated, no action was taken to address the failed backups for approximately two months. The root cause of this noncompliance includes: (1) insufficient procedures for backups, specifically that the procedures failed to include all information necessary to properly set them up; (2) the failure to follow procedures requiring weekly review of backups; (3) equipment failure involving backups for the alert system, which prevented alerts from being issued; and, (4) infrequent verification of backups. These major contributing factors involve the management practices of asset and configuration management, verification, and workforce management. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, both systems serve as additional security tools, and neither one has a direct role in the operation of Bulk Electric System assets as long as facilities are manned. Second, the database is backed up to multiple secondary servers in real time. Therefore, if the primary or a secondary device went down, one of the other devices would be promoted to primary. Third, the risk posed by the lack of backups is mitigated by the fact that a restoration of that system could still be performed. However, it would just be a more time intensive, manual process and only historical data would be lost. Fourth, both systems are protected by a defense in depth strategy including: (1) being completely segmented from the internet and the RFC_URE2 enterprise network by a series of firewalls; and, (2) having multiple layers of login to reach the systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) reconfigured service related to backups for the server and confirmed backups are working as expected; 2) confirmed email message alerts related to failed backups are sent to the appropriate group; 3) implemented weekly manual logging of backups, including what action is taken if backups fail; 4) implemented weekly manual logging of backups including what action is taken if backups fail; 5) updated Disaster Recovery plans to state backup reviews are done manually and sent notice of plan update to responder groups mentions in the plan; 6) updated the Build Guide document to include backup and alerting; 7) conducted a review session to members of the responsible group to review expectations for backups; and 8) began bi-weekly confirmation of weekly backup review. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017016758 | CIP-003-3 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. While verifying the total number of users with NERC CIP access, RFC_URE2 discovered that some users who lacked adequate training had retained NERC CIP Information Repository (CIR) access. Following discovery, RFC_URE2 pulled a report from their online training center to determine the number of users who had proper NERC CIP training. This list was then compared to a report of all users in the access management system. By comparing these lists, RFC_URE2 determined that four users whose training had expired, retained access to CIP protected Cyber System Information (BCSI) in the form of a CIR. Later that same day, the responsible group completed its review of all items and manually removed all access associated with the four users’ accounts, which consisted of the following: (a) the four users had retained five levels of access; (b) one user had retained RFC_URE2 information access; (c) two users had retained RFC_URE2 CIR access; and, (d) one user had retained access to two separate levels of Shared Services information access. One user was on personal leave for more than 30 days, but the access management system did not automatically remove access as required despite the entering of all appropriate removal tickets. NERC CIP training expired for the other three users. For the user with access to the Shared Services CIRs, the access management system did not automatically remove access to the resource. This user retained access to two Shared Services CIRs that were required in a previous role within RFC_URE2. This user was unaware he had access to these CIRs and did not access them. Two users retained access to RFC_URE2 CIRs. These access levels were retained after the users' training expired. Because the access was outside of a role, the access was not removed. The root cause of this noncompliance was the technical limitation in the access management system tool on how it automatically processes removals. The technical limitation was not discovered during pre-launch testing. Access management system is a tool that distributes access based on access roles. Each role is a combination of entitlements to NERC CIP electronic information and physical access. RFC_URE2 expected the access management system to remove all access that the user had within 24 hours automatically. However, the access management system did not remove access privileges granted through entitlements that were not associated with a "role." This noncompliance involves the management practices of information management, implementation, and verification. Information management is involved because RFC_URE2 failed to limit the access of employees to information which they did not have the training or clearance to access. Implementation is involved because RFC_URE2’s access management system tool was improperly configured to remove NERC CIP access properly for those not associated with a role. Verification is involved because RFC_URE2 failed to verify that the access management system tool was properly configured to their specifications. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by these instances of noncompliance is the provision of access for bad actors to BES Cyber Assets which could adversely impact the reliability of the electric grid. The risk is minimized in this instance because the employees who were incorrectly provided access remain in good standing with the company and the company has no reason to believe that any malicious action caused this occurrence. The risk is further minimized because each user had a current personal risk assessment and prior CIP training. ReliabilityFirst also notes that of the four users with expired credentials, three were unaware that they retained access and the fourth was unable to login as a result of technical controls put in place when the individual went on extended leave. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed NERC CIP Access for the four employees initially identified when preparing and assessing a summary report; 2) identified users with access outside of roles; 3) reviewed the entitlements not in access roles in the access management system and took action as needed; and 4) updated and implemented changes to RFC_URE2 process documents for adding new Active Directory groups into certain locations.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016662 | CIP-004-6 | R4 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-6 R4. Two employees had physical access to RFC_URE3’s Physical Security Perimeters (PSPs) at one of its power plants (which was brought into CIP scope as a medium impact site under CIP version 5), but did not have authorization records as required by CIP-004-6 R4. As background, in preparation for CIP Version 5, RFC_URE3 created a list of employees who had physical access to said power plant and current NERC CIP qualifications, including training and Personnel Risk Assessments. RFC_URE3 then used this list to bulk load associated access records into its access system that holds authorization records. RFC_URE3 completed its quarterly review and determined that two employees’ authorization records were missing in the access system. RFC_URE3 determined that, due to several list modifications prior to the bulk load into the access system, two employees’ names were inadvertently excluded from the final load list. Accordingly, two employees had physical access to PSPs in said power plant, but did not have authorization records in RFC_URE3’s access system. The root cause was a process gap in that RFC_URE3 did not require a verification step after initially loading the list into the access system to ensure RFC_URE3 included all necessary employees and corresponding records in the system. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. This was a documentation issue. The employees had appropriate NERC CIP qualifications, including training and Personnel Risk Assessments throughout the duration of the noncompliance, had a business need to access the PSPs, and were authorized to access the PSPs prior to CIP Version 5 enforceable date. RFC_URE3 failed to ensure it carried over the employees’ authorization records once the power plant became a medium impact site under CIP version 5. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) revoked access for both employees until it could obtain the proper authorization records for the employees; 2) documented its previously ad hoc bulk load process to ensure consistency for future use of the process; and 3) communicated the newly developed bulk load process to all Business Units via email and an in-person meeting. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016637 | CIP-009-6 | R1 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-009-6 R1. RFC_URE4 experienced issues with two tools: (1) a server which is used for two factor authentication in remote access; and, (2) its tool for monitoring, alerting, and logging. In the first issue related to the server, RFC_URE4 conducted an annual Disaster Recovery Plan drill, during which they discovered that: (a) insufficient evidence was available to show that backup reviews had been conducted; and, (b) their offline, backup file was not effectively captured for approximately three months. (The server system has two methods of preserving the user database. First, a replication of the database is distributed in real-time to the secondary servers. Second, a backup file is used if the database running on the primary and secondary servers becomes corrupt.) According to the Restoration Plan, backup reviews should have been conducted weekly. In the second issue, during the same Disaster Recovery Plan drill, RFC_URE4 discovered that the system used for backups for the system became corrupt. As a result, alerts of failed backups were not issued. Because no alerts were generated, no action was taken to address the failed backups for approximately two months. The root cause of this noncompliance includes: (1) insufficient procedures for backups, specifically that the procedures failed to include all information necessary to properly set them up; (2) the failure to follow procedures requiring weekly review of backups; (3) equipment failure involving backups for the alert system, which prevented alerts from being issued; and, (4) infrequent verification of backups. These major contributing factors involve the management practices of asset and configuration management, verification, and workforce management. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, both systems serve as additional security tools, and neither one has a direct role in the operation of Bulk Electric System assets as long as facilities are manned. Second, the database is backed up to multiple secondary servers in real time. Therefore, if the primary or a secondary device went down, one of the other devices would be promoted to primary. Third, the risk posed by the lack of backups is mitigated by the fact that a restoration of that system could still be performed. However, it would just be a more time intensive, manual process and only historical data would be lost. Fourth, both systems are protected by a defense in depth strategy including: (1) being completely segmented from the internet and the RFC_URE4 enterprise network by a series of firewalls; and, (2) having multiple layers of login to reach the systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) reconfigured service related to backups for the server and confirmed backups are working as expected; 2) confirmed email message alerts related to failed backups are sent to the appropriate group; 3) implemented weekly manual logging of backups, including what action is taken if backups fail; 4) implemented weekly manual logging of backups including what action is taken if backups fail; 5) updated Disaster Recovery plans to state backup reviews are done manually and sent notice of plan update to responder groups mentions in the plan; 6) updated the Build Guide document to include backup and alerting; 7) conducted a review session to members of the responsible group to review expectations for backups; and 8) began bi-weekly confirmation of weekly backup review. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017016761 | CIP-003-3 | R5 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. While verifying the total number of users with NERC CIP access, RFC_URE4 discovered that some users who lacked adequate training had retained NERC CIP Information Repository (CIR) access. Following discovery, RFC_URE4 pulled a report from their online training center to determine the number of users who had proper NERC CIP training. This list was then compared to a report of all users in the access management system. By comparing these lists, RFC_URE4 determined that four users whose training had expired, retained access to CIP protected Cyber System Information (BCSI) in the form of a CIR. Later that same day, the responsible group completed its review of all items and manually removed all access associated with the four users’ accounts, which consisted of the following: (a) the four users had retained five levels of access; (b) one user had retained RFC_URE4 information access; (c) two users had retained RFC_URE4 CIR access; and, (d) one user had retained access to two separate levels of Shared Services information access. One user was on personal leave for more than 30 days, but the access management system did not automatically remove access as required despite the entering of all appropriate removal tickets. NERC CIP training expired for the other three users. For the user with access to the Shared Services CIRs, the access management system did not automatically remove access to the resource. This user retained access to two Shared Services CIRs that were required in a previous role within RFC_URE4. This user was unaware he had access to these CIRs and did not access them. Two users retained access to RFC_URE4 CIRs. These access levels were retained after the users' training expired. Because the access was outside of a role, the access was not removed. The root cause of this noncompliance was the technical limitation in the access management system tool on how it automatically processes removals. The technical limitation was not discovered during pre-launch testing. Access management system is a tool that distributes access based on access roles. Each role is a combination of entitlements to NERC CIP electronic information and physical access. RFC_URE4 expected the access management system to remove all access that the user had within 24 hours automatically. However, the access management system did not remove access privileges granted through entitlements that were not associated with a "role." This noncompliance involves the management practices of information management, implementation, and verification. Information management is involved because RFC_URE4 failed to limit the access of employees to information which they did not have the training or clearance to access. Implementation is involved because RFC_URE4’s access management system tool was improperly configured to remove NERC CIP access properly for those not associated with a role. Verification is involved because RFC_URE4 failed to verify that the access management system tool was properly configured to their specifications. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by these instances of noncompliance is the provision of access for bad actors to BES Cyber Assets which could adversely impact the reliability of the electric grid. The risk is minimized in this instance because the employees who were incorrectly provided access remain in good standing with the company and the company has no reason to believe that any malicious action caused this occurrence. The risk is further minimized because each user had a current personal risk assessment and prior CIP training. ReliabilityFirst also notes that of the four users with expired credentials, three were unaware that they retained access and the fourth was unable to login as a result of technical controls put in place when the individual went on extended leave. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) removed NERC CIP Access for the four employees initially identified when preparing and assessing a summary report; 2) identified users with access outside of roles; 3) reviewed the entitlements not in access roles in the access management system and took action as needed; and 4) updated and implemented changes to RFC_URE4 process documents for adding new Active Directory groups into certain locations.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016670 | CIP-003-3 | R6 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. A RFC_URE5 Transmission Technician installed, uninstalled and reinstalled a Bulk Import Utility on an IT Server without a change ticket, without proper authorization, and without a documented evaluation of the potential impacts of the change. The server (Note: the server does not control any systems. Additionally, no workstations are attached to this server and this server did not control any facilities.) was configured as a jump host and used to facilitate a secure communication path between a user and remotely located substation equipment. RFC_URE5 discovered this issue through its configuration management tool that tracks unexpected changes to the baseline daily. RFC_URE5 monitors this tool monthly for unexpected changes to the baseline and identified this issue during its review. This noncompliance involves the management practice of workforce management. In this instance, the RFC_URE5 Transmission Technician did not follow RFC_URE5’s established change management procedures for making changes on a CIP Cyber Asset because he did not understand what constituted a CIP Change on this CIP Cyber Asset. The Transmission Technician did not understand this because he was ineffectively trained and this ineffective training is a root cause of this noncompliance. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that by not following RFC_URE5’s IT Change Control Procedures, the opportunity to exploit the CIP Cyber Asset at issue is increased because the change can introduce new vulnerabilities into the CIP Cyber Asset. The risk is minimized here because the IT Server in question that received the unauthorized change does not control any systems, workstations, or facilities. RFC_URE5’s detective controls are also functioning effectively as this unauthorized change was discovered through RFC_URE5’s monitoring of RFC_URE5’s configuration management tool that tracks baseline deviations. Lastly, after detecting the unauthorized change, RFC_URE5 personnel verified that there were no security vulnerabilities introduced as a result of the change and RFC_URE5 removed the administrative access privileges for all Transmission personnel to the IT servers. (RFC_URE5 personnel verified that no unnecessary logical ports were enabled, verified that all applicable security patches were applied, validated that RFC_URE5’s anti-virus service was running and definition files were current, validated that device logging was still operational, validated that security event alerting was still operational, validated that no new accounts were created and that the authentication of interactive access was still being enforced, and that baseline configuration documentation had been updated.) No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) completed the software change initiated by the RFC_URE5 Transmission Technician in accordance with RFC_URE5’s IT Change Control Procedures, including the addition of the associated software change to the Server White List; 2) removed the administrative access privileges for this Transmission Technician and all other Transmission Personnel to this IT Server due to their infrequent use of IT Change Control Procedures. RFC_URE5 determined that RFC_URE5 IT staff could perform these types of changes more effectively; and 3) counseled and retrained the Transmission Technician on the importance of following procedures. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2016016673 | CIP-004-3a | R4 | RFC_URE6 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. During RFC_URE6’s fourth quarter evidence collection process, RFC_URE6 discovered that an employee with access to Physical Security Perimeters (PSPs) had resigned, but RFC_URE6 did not completely revoke his access privileges in the Physical Access Control System (PACS). RFC_URE6 splits its PACS into two parts – one for general corporate access to RFC_URE6 facilities and one that controls access into the designated CIP PSPs. As part of the separation process in this case, the separated employee’s physical badge was collected and destroyed. The employee’s access privileges expired the day he resigned in the general corporate PACS, but remained active in the more limited, CIP PSP PACS. The root cause of this noncompliance was the fact that the responsible infrastructure security analyst overlooked the email notification from human resources. (An additional issue relates to the fact that this issue was not identified during the previous two quarterly reviews of access privileges. The person responsible for reviewing this list was not made aware of the employee’s resignation.) This major contributing factor involves the management practice of workforce management, which includes managing employee access to assets. The duration of the noncompliance was approximately eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the employee’s physical badge was collected and destroyed, preventing him from accessing the CIP PSP PACS. Additionally, the employee would also have had to gain access to the general corporate PACS prior to entering the CIP PSP PACS. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) removed physical unescorted access for the employee in question; 2) performed a review of the activity for the access card assigned to the employee to identify any activity into any designated PSPs after the separation date; 3) determined that there were no access attempts using the corporate access control system to the service center by the employee after the separation date. Without access to the service center the employee would not have had physical access to the areas where Bulk Electric System (BES) Cyber Assets are located; 4) expanded the mailing list for who receives the termination notifications to include all of the RFC_URE6 Infrastructure Security Compliance personnel so there are more people looking at whether individuals who are being separated from the company have physical and/or logical access to BES Cyber Assets and therefore need to have their access revoked. This will prevent a single point of failure for future termination notices; and 5) reduced the number of people reviewed and approved on a quarterly basis by any one area manager to a more manageable level. The approval list has also been divided into job roles so there is a better understanding of who has a business need to be granted access to the PSP. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2016016639 | CIP-009-6 | R1 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-009-6 R1. RFC_URE7 experienced issues with two tools: (1) a server which is used for two factor authentication in remote access; and, (2) its tool for monitoring, alerting, and logging. In the first issue related to the server, RFC_URE7 conducted an annual Disaster Recovery Plan drill, during which they discovered that: (a) insufficient evidence was available to show that backup reviews had been conducted; and, (b) their offline, backup file was not effectively captured for approximately three months. (The server system has two methods of preserving the user database. First, a replication of the database is distributed in real-time to the secondary servers. Second, a backup file is used if the database running on the primary and secondary servers becomes corrupt.) According to the Restoration Plan, backup reviews should have been conducted weekly. In the second issue, during the same Disaster Recovery Plan drill, RFC_URE7 discovered that the system used for backups for the system became corrupt. As a result, alerts of failed backups were not issued. Because no alerts were generated, no action was taken to address the failed backups for approximately two months. The root cause of this noncompliance includes: (1) insufficient procedures for backups, specifically that the procedures failed to include all information necessary to properly set them up; (2) the failure to follow procedures requiring weekly review of backups; (3) equipment failure involving backups for the alert system, which prevented alerts from being issued; and, (4) infrequent verification of backups. These major contributing factors involve the management practices of asset and configuration management, verification, and workforce management. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, both systems serve as additional security tools, and neither one has a direct role in the operation of Bulk Electric System assets as long as facilities are manned. Second, the database is backed up to multiple secondary servers in real time. Therefore, if the primary or a secondary device went down, one of the other devices would be promoted to primary. Third, the risk posed by the lack of backups is mitigated by the fact that a restoration of that system could still be performed. However, it would just be a more time intensive, manual process and only historical data would be lost. Fourth, both systems are protected by a defense in depth strategy including: (1) being completely segmented from the internet and the RFC_URE7 enterprise network by a series of firewalls; and, (2) having multiple layers of login to reach the systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) reconfigured service related to backups for the server and confirmed backups are working as expected; 2) confirmed email message alerts related to failed backups are sent to the appropriate group; 3) implemented weekly manual logging of backups, including what action is taken if backups fail; 4) implemented weekly manual logging of backups including what action is taken if backups fail; 5) updated Disaster Recovery plans to state backup reviews are done manually and sent notice of plan update to responder groups mentions in the plan; 6) updated the Build Guide document to include backup and alerting; 7) conducted a review session to members of the responsible group to review expectations for backups; and 8) began bi-weekly confirmation of weekly backup review. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017016757 | CIP-003-3 | R5 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. While verifying the total number of users with NERC CIP access, RFC_URE7 discovered that some users who lacked adequate training had retained NERC CIP Information Repository (CIR) access. Following discovery, RFC_URE7 pulled a report from their online training center to determine the number of users who had proper NERC CIP training. This list was then compared to a report of all users in the access management system. By comparing these lists, RFC_URE7 determined that four users whose training had expired, retained access to CIP protected Cyber System Information (BCSI) in the form of a CIR. Later that same day, the responsible group completed its review of all items and manually removed all access associated with the four users’ accounts, which consisted of the following: (a) the four users had retained five levels of access; (b) one user had retained RFC_URE7 information access; (c) two users had retained RFC_URE7 CIR access; and, (d) one user had retained access to two separate levels of Shared Services information access. One user was on personal leave for more than 30 days, but the access management system did not automatically remove access as required despite the entering of all appropriate removal tickets. NERC CIP training expired for the other three users. For the user with access to the Shared Services CIRs, the access management system did not automatically remove access to the resource. This user retained access to two Shared Services CIRs that were required in a previous role within RFC_URE7. This user was unaware he had access to these CIRs and did not access them. Two users retained access to RFC_URE7 CIRs. These access levels were retained after the users' training expired. Because the access was outside of a role, the access was not removed. The root cause of this noncompliance was the technical limitation in the access management system tool on how it automatically processes removals. The technical limitation was not discovered during pre-launch testing. Access management system is a tool that distributes access based on access roles. Each role is a combination of entitlements to NERC CIP electronic information and physical access. RFC_URE7 expected the access management system to remove all access that the user had within 24 hours automatically. However, the access management system did not remove access privileges granted through entitlements that were not associated with a "role." This noncompliance involves the management practices of information management, implementation, and verification. Information management is involved because RFC_URE7 failed to limit the access of employees to information which they did not have the training or clearance to access. Implementation is involved because RFC_URE7’s access management system tool was improperly configured to remove NERC CIP access properly for those not associated with a role. Verification is involved because RFC_URE7 failed to verify that the access management system tool was properly configured to their specifications. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by these instances of noncompliance is the provision of access for bad actors to BES Cyber Assets which could adversely impact the reliability of the electric grid. The risk is minimized in this instance because the employees who were incorrectly provided access remain in good standing with the company and the company has no reason to believe that any malicious action caused this occurrence. The risk is further minimized because each user had a current personal risk assessment and prior CIP training. ReliabilityFirst also notes that of the four users with expired credentials, three were unaware that they retained access and the fourth was unable to login as a result of technical controls put in place when the individual went on extended leave. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) removed NERC CIP Access for the four employees initially identified when preparing and assessing a summary report; 2) identified users with access outside of roles; 3) reviewed the entitlements not in access roles in the access management system and took action as needed; and 4) updated and implemented changes to RFC_URE7 process documents for adding new Active Directory groups into certain locations.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016016178 | CIP-007-6 | R2 | RFC_URE8 submitted Self-Reports stating that it had an issue of CIP-007-6 R2. This noncompliance involves two separate instances. First, RFC_URE8 timely identified and evaluated a patch that was released and determined it to be applicable to two CIP assets. Pursuant to CIP 007-5 R2.3, RFC_URE8 created a mitigation plan to allow for workload and, as such, the patches were scheduled to be implemented by CIP Version 5 enforceable date. However, RFC_URE8 failed to apply the patch on time due to a scheduling error. RFC_URE8 identified the late patches during a routine weekly review and applied them a few days later. Second, a patch was released to address Java vulnerabilities. RFC_URE8 reviewed this patch, and, as permitted by CIP 007-6 R2, created a mitigation plan to apply the patches. Due to an oversight, RFC_URE8 did not act upon or extend the mitigation plan by the deadline. RFC_URE8 then identified the missed patch fourteen days later, through its routine weekly review and immediately extended the mitigation plan. For both instances, although the mitigation plans expired, the security controls in the mitigation plans remained in place. The root cause was a lack of defined and documented process to track the mitigation plans. RFC_URE8 had controls in place, including weekly meetings to review patches and mitigation plans, but this process was not documented and allowed for the oversight of these two patches. This cause involves the management practices of asset and configuration management, which includes controlling and documenting changes, such as patches. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, although the mitigation plans expired prior to RFC_URE8 implementing the patches or extending the mitigation plans, the security controls that mitigated the vulnerabilities were still in place, thus reducing the risk that the assets could be compromised. Second, RFC_URE8 self-identified the instances and thereafter immediately mitigated the noncompliance, thus reducing the period of time that the BPS was put at any increased risk as a result of the noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) applied the patch, as required; 2) extended the patch mitigation plan which was approved by the CIP Senior Manager’s designee; 3) amended the Patch Management Rescheduling Process to require the patch implementation team to verbally, as well as via email, inform the Patch Management team when requesting that patching be rescheduled, and to receive a confirmation that this has been understood; 4) documented existing weekly patch mitigation plan review process, in order to promote repeatability, assign responsibility/accountability and prevent future errors; and 5) trained applicable employees on improvements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2016016653 | CIP-004-6 | R4 | RFC_URE9 submitted a Self-Report stating that it had an issue of CIP-004-6 R4. During a quarterly review of physical access privileges to corporate data centers, which are Bulk Electric System Cyber System Information (BCSI) repositories, RFC_URE9’s compliance department discovered that one person was granted access to a single data center without a record of authorization. The data center houses servers containing CIP compliance data, which contain BCSI. Upon discovery, the compliance department immediately contacted the data center owner, who determined that the individual’s access to the data center was appropriate, and provided the supporting documentation and approval. RFC_URE9 investigated and determined that a corporate security specialist had granted the employee access to the data center without looking into an apparent lack of supporting documentation, because the individual had access to other data centers. Based on job responsibilities, that individual should have had access, but the documentation that would have authorized access was not in place when corporate security granted the access. The root cause of this noncompliance was the fact that the corporate security employee did not follow the relevant process for granting access to corporate data centers. RFC_URE9’s current preventative controls include requiring corporate security to contact a data center owner prior to granting access to individuals. In this case, the corporate security employee violated this control by granting access to this individual based on the assumption that he or she was authorized to enter this particular data center because he or she had authorized access to other data centers. This major contributing factor involves the management practice of information management, which includes controlling access to information items. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the data center houses servers with CIP compliance data that contains BCSI, physical access to the servers does not allow for direct access to BCSI. An individual must also have electronic access to the server and a program to open the information. In this instance, the individual did not have electronic access. Second, RFC_URE9 identified the issue through an internal detective control (i.e., the quarterly review of physical access privileges). No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) obtained an authorization record for the individual with appropriate access; 2) retrained the Corporate Security specialist on the process to grant access to corporate data centers; and 3) revised its Corporate Security procedures to clearly identify physical access areas that require additional approvals.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2016016654 | CIP-004-6 | R4 | RFC_URE9 submitted a Self-Report stating that it had an issue of CIP-004-6 R4. During a monthly review of electronic access privileges, which is a detective control used to identify access issues, RFC_URE9’s compliance department discovered that multiple people were granted access to a folder potentially containing Bulk Electric System Cyber System Information (BCSI) who had not been authorized to have that access. Upon discovery, RFC_URE9’s compliance department immediately contacted the IT department to terminate that access. The same day, the compliance department then verified that access was removed through a follow-up review of access privileges. The root cause of this noncompliance was the fact that an IT administrator inadvertently granted access to a BCSI tracked folder while adding a scanning function to the folder. This major factor involves the management practice of information management, which includes controlling access to information items. The duration of the noncompliance was approximately three weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the folder was identified as potentially containing BCSI so that it could be used to house BCSI, the folder actually contained no BCSI materials. Second, RFC_URE9 identified the issue through a regularly occurring internal detective control. ReliabilityFirst also notes that during the time period that the access was open, only one individual accessed two non-BCSI files contained in the folder. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) restricted access to the folder to authorized users; and 2) enhanced its existing controls to ensure that the compliance specialist verifies each requested change to BCSI. Following each change the compliance specialist will verify that a corresponding alert is generated from the system. If an alert was not generated, the compliance specialist will request a user report from IT. The compliance specialist will then verify that the change performed matches the change requested. This verification will ensure that the compliance specialist identifies any erroneous changes and works with IT to correct issues in a timely manner.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016196 | CIP-003-3 | R6 | SPPRE_URE1 submitted a Self-Log stating that it had an issue of noncompliance with CIP-003-3 R6. During an internal review of Change Request tickets, SPPRE_URE1 discovered that baseline configuration documentation was not updated as required by SPPRE_URE1’s process. Specifically, the baseline configuration document was not updated within 30 days after completing a software installation on four Cyber Assets. The duration of this instance of noncompliance was 25 days, beginning 31 days after the software installation occurred and continuing through the date the baseline configuration update documentation was updated to reflect the current version of software installed on the four applicable Cyber Assets. The root cause of this instance of noncompliance was human error in implementing SPPRE_URE1’s process. The SPPRE_URE1 employee who performed the software installation on the four Cyber Assets should have updated the baseline configuration documentation within 30 days. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely update baseline configurations has the potential to affect the reliability of the BPS, by providing the opportunity for SPPRE_URE1 to not address potential vulnerabilities to Critical Cyber Assets that could be caused by changes in the baseline configurations, which could affect the availability of Critical Cyber Assets and/or lead to unauthorized access to Critical Cyber Assets. Notwithstanding, this issue of non-compliance was a documentation error. SPPRE_URE1 performed updates to its Cyber Assets as required, documenting changes on a Change Request ticket, and updating other required documentation within the required timeframes. SPPRE_URE1 identified this issue of non-compliance during an internal review and mitigated the documentation error within two weeks of discovery. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) updated the baseline configuration to reflect the current version of software installed on applicable Cyber Assets; 2) met with the employee responsible for not updating the baseline configuration document and discussed its change control configuration process; and 3) emailed the IT security department and reinforced the necessity to update baseline configuration documentation each time a change is made to applicable Cyber Assets before closing the tracking ticket. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016417 | CIP-003-3 | R4; R4.1 | SPPRE_URE1 submitted a Self-Log stating that it had an issue of noncompliance with CIP-003-3 R4.1 because a SPPRE_URE1 employee did not properly follow the SPPRE_URE1 procedures for protecting and securely storing BES Cyber System Information. A SPPRE_URE1 laptop was stolen from an employee’s vehicle. After further investigation by SPPRE_URE1 information technology (IT) staff, it was determined that files on the latptop could have contained SPPRE_URE1 Bulk Electric System (BES) Cyber System Information. In accordance with SPPRE_URE1’s process, the files on the employee’s laptop should have been properly stored within a secure location defined in SPPRE_URE's process and deleted from the employee’s laptop. The duration of this instance of noncompliance was 363 days, beginning the date the CVA information should have been placed in storage per SPPRE_URE1’s process, and continuing through the date the security awareness notification was disseminated to personnel with access to BES Cyber System Information that directed employees to delete BES Cyber System Information from devices when it is no longer needed. The root cause of this instance of noncompliance was the SPPRE_URE1 employee’s failure to follow SPPRE_URE1’s process and delete the files from the laptop once the files were copied to the designated storage location. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to delete unnecessary BES information from a laptop has the potential to affect the reliability of the BPS by providing the opportunity for a person with malicious intent to access the information and use it to plan a Cyber Attack. Notwithstanding, the stolen laptop was encrypted and the files alone did not contain enough information for a person to successfully exploit any SPPRE_URE1 systems or the BES. Additionally, an individual attempting to access the laptop would need the username\password combination to gain access to the files. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) sent a notice to all SPPRE_URE1 applicable personnel on best practices for creating and storing BES Cyber System Information. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016195 | CIP-003-3 | R5 | SPPRE_URE1 submitted a Self-Log stating that it had an issue of noncompliance with CIP-003-3 R5. During an internal review, SPPRE_URE1 found it had not fully implemented its program for managing access to protected Critical Cyber Asset information. Specifically, eight user accounts were added to two Cyber Assets, which contain protected Critical Cyber Asset information, without completing an access request form as required by SPPRE_URE1’s program. SPPRE_URE1’s access request form contains steps to ensure that; each Cyber Asset user has a current Personnel Risk Assessment (PRA) and training, the access request is reviewed and approved by the appropriate personnel, and documentation of access has occurred before granting access to SPPRE_URE1 Cyber Assets. SPPRE_URE1 used a change request form instead of the access request form; therefore, it did not verify the proper information for each Cyber Asset user prior to granting access to the two Cyber Assets. The duration of this instance of noncompliance was 454 days, beginning the date the eight user accounts were added to the Cyber Assets without the use of the access request form, and continuing through the date SPPRE_URE1 documented the access to the two Cyber Assets using the access request form. The root cause of this instance of noncompliance was lack of training in implementing SPPRE_URE1’s documented process for granting access to Cyber Assets and lack of internal controls to ensure adherence to the process. SPPRE_URE1’s change control program was properly followed in the implementation of the Cyber Assets and the change request form, although the incorrect form, was completed when the new Cyber Assets were installed. However, the access request form was not completed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure for SPPRE_URE1 to follow its information protection process has the potential to affect the reliability of the BPS because employees could be granted access to Cyber Assets without applicable authorization, compliant PRAs, or proper training. Notwithstanding, the issue of noncompliance was a documentation error because the incorrect form was utilized to document the addition of the eight user accounts. The eight SPPRE_URE1 employees who were granted access to the two Cyber Assets were authorized with electronic access to SPPRE_URE1 Electronic Access Control and Monitoring System Cyber Assets, and had current PRAs and current training on file. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) re-trained individuals responsible for managing Cyber Assets on the necessity to process user access requests using the access request form; 2) updated SPPRE_URE1’s Cyber Vulnerability Assessment (CVA) process to include a requirement to use a checklist to validate all assets subject to CIP compliance; and, 3) performed a supplemental CVA on the two Cyber Assets to further validate user accounts present on the system and corrected the user account baseline configuration documentation to reflect the eight new user accounts. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017017576 | CIP-004-6 | R1; P 1.1 | TRE_URE1 submitted a Self-Log stating that it had an issue with CIP-004-6 R1, Part 1.1. In particular, TRE_URE1 did not implement all elements of its documented cyber security awareness procedure. During an internal spot check, TRE_URE1 determined that it failed to comply with all specific requirements listed in its cyber security awareness procedure document. TRE_URE1’s cyber security awareness procedure specifies that TRE_URE1 personnel will distribute posters and issue monthly email newsletters to TRE_URE1 personnel to reinforce cyber security practices. The cyber security awareness procedure further provides that the specific locations of all security awareness posters must be approved by TRE_URE1’s compliance director. In the current circumstances, TRE_URE1 personnel distributed posters and sent monthly newsletters via email to all relevant employees. In doing so, however, the TRE_URE1 personnel at issue failed to also obtain director approval for the location of the security awareness posters. The root cause of this issue is an insufficient process for ensuring compliance with CIP-004-6 R1. Specifically, the TRE_URE1 personnel in question did not clearly understand the requirement to obtain director approval for all cyber security awareness poster locations set forth its security awareness process document. The issue duration was approximately eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was strictly administrative in nature. Specifically, although TRE_URE1 failed to obtain director approval for the locations of its cyber security awareness posters, TRE_URE1 followed its process to place cyber security posters at various work sites and to distribute monthly cyber security newsletters via email, accomplishing the reliability task of ensuring cyber security awareness among its relevant personnel. No harm is known to have occurred. Texas RE considered TRE_URE1's compliance history and determined there were no relevant instances of noncompliance related to CIP-004 R1. | To mitigate this issue, TRE_URE1: 1) obtained the proper approval for the locations of all cyber security awareness posters at issue; 2) discussed the noncompliance issue with the affected employees and stressed the importance of following work group procedures; and 3) removed the requirement from its cyber security procedure to obtain compliance director approval for all cyber security awareness poster locations. Texas RE has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016685 | CIP-010-2 | R1, Part 1.1 | WECC_URE1 submitted a Self-Report stating that, it had an issue with CIP-010-2 R1 Part 1.1. Specifically, for the first instance, while conducting an internal review, WECC_URE1’s internal auditor determined that baseline configurations did not exist for its Physical Access Controls Systems (PACS) controllers. The baseline configurations should have been developed using WECC_URE1’s configuration change management process during its transition to the current Standards and Requirements. The root cause of the first instance was less than adequate communications with the workgroup responsible for CIP assets and that workgroups compliance obligation relating to WECC_URE1’s baseline configuration procedures. During WECC’s review of WECC_URE1’s Self-Report, a second instance of possible noncompliance was identified. While completing a patch deployment process, which involved patching servers, a PACS server was not included in the baseline comparison process, and, therefore, did not have its baseline configuration change updated within 30 calendars days of completing the change pursuant to CIP-010-2 R1 Part 1.3. The root cause of the second instance was a lack of a written procedure or a checklist, which resulted in the step to compare baseline configurations after a change to be missed. WECC determined the first instance began when the Standard and Requirement became mandatory and enforceable to WECC_URE1, and ended when WECC_URE1 documented baseline configurations for the PACS controllers, for a total of 165 days of noncompliance. WECC determined the second instance began when the change that deviated from the baseline configuration on one PACS should have been updated, and ended when the updated baseline configuration was authorized and updated, for a total of 55 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In the first instance, WECC_URE1 failed to develop baseline configurations for 12 PACS controllers. Failure to create a baseline configuration could result in WECC_URE1 not knowing which programs are installed on the PACS and/or which ports and services are required for correct communication and functioning of the PACS. Additionally, incorrect configurations of Access Control Lists or firewalls could prevent the proper functions of the PACS controllers, which could allow or deny personnel physical access to restricted locations that are responsible for system operations, communications, and data repositories; thereby potentially affecting the reliability of the BPS. In the second instance, WECC_URE1 failed to update the baseline configuration for one PACS server, as necessary, within 30 calendar days of completing the change. Failure to document the baseline configuration of its PACS could have permitted unauthorized changes to occur and go undetected, which could potentially affect the reliability of the BPS However, in both instances, WECC_URE1 implemented controls to reduce the likelihood of the risks occurring. WECC_URE1’s internal auditor discovered the first issue of noncompliance. The PACS are all micro-controllers and are not all Internet Protocol enabled. Some of the PACS controllers were serial devices and not capable of remote access. The PACS reside on an isolated network with no connectivity to BES assets. Additionally, PACS reside within secure locations with defense-in-depth controls to prevent access. Previous compliance vulnerability assessments and new asset commissioning documentation confirms that the controllers had no unauthorized changes. No harm is known to have occurred. WECC_URE1 had no relevant prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE1: 1) verified all Cyber Assets, groups, or classes have an authorized baseline file documented in the designated storage location; 2) clarified procedures for PACS controllers are within the CIP Asset Baseline Management by Asset Class Procedure to denote differences between main controllers and terminal controllers and ensured appropriate configuration items were captured for each asset type; 3) scheduled a monthly meeting to discuss CIP topics to encourage collaboration, provide a forum for subject matter experts to ask questions, and discuss challenges, opportunities, etc.; 4) updated its Change Management Plan to: i. clarify that baseline configuration changes are authorized via change control; ii. ensure it references CIP Asset Baseline Plan and Procedure, and the CIP Procedures by Asset; iii. to include a requirement that any Change Initiator, Change Manager or Change Advisory Board member that signs a change control who has not performed a CIP change control within the previous 35 days must obtain peer review for their change control documentation from an appropriate individual who has performed a CIP change control with the previous 35 days; and 5) provided clarification and/or a deeper-dive training to ensure subject matter experts had a clear understanding of CIP processes.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016413 | CIP-006-6 | R1, Part 1.2 | WECC_URE2 submitted a Self-Report stating that it had an issue with CIP-006-6 R1 Part 1.2. Specifically, WECC_URE2 reported that during a new employee CIP training on CIP-006, it discovered that the Physical Security Perimeter (PSP) Access Point (AP) door to a Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) was unlocked. The card reader was active and logging and alerting, but the door was not locked utilizing a brass key; thereby allowing anyone to open the door and gain access to the PSP. WECC_URE2 had all PSP doors with manual brass key locks replaced with a special tumbler and new key set to ensure that only persons with authorized unescorted physical access would be able to obtain a brass key and access the PSPs using a manual entry. During the 1-day tumbler replacement work effort, the tumbler at the MIBCS PSP had installation issues which required the locksmith to rework the tumbler after all other tumblers were in place. The tumbler at the MIBCS PSP was replaced a second time and was assumed locked at the end of the installation. The root cause of this issue was less than adequate process; specifically, for checking that all AP doors to PSPs were appropriately locked during the change control process. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE2, and ended when WECC_URE2 locked the door to the MIBCS, for a total of 47 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to utilize at least one physical access control to allow unescorted physical access to a PSP to only those individuals who have authorized unescorted physical access. Such failure could result in WECC_URE2’s inability to control physical access to its MIBCS, which could result in malicious activity to, or the removal or destruction of Cyber Assets; thereby potentially affecting the reliability of the Bulk Power System (BPS). However, the controls implemented by WECC_URE2 reduced the likelihood of the risk occurring. WECC_URE2’s periodic testing of its Internal Compliance Program detected this issue. All personnel with authorized unescorted physical access have a documented Personnel Risk Assessment and cyber security training. WECC_URE2 utilized user assigned badges that have a unique identifier, and monitored physical access alarms through its Physical Access Control and Monitoring System (PACS). No harm is known to have occurred. WECC_URE2 has no prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE2: 1) locked the AP door to the PSP; 2) performed a security check of all PSP doors to ensure they are closed and locked; and 3) added a process whereby applicable personnel are to check that all PSP doors are closed and locked during daily rounds and to include a log to record door lock verifications.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016660 | CIP-010-2 | R1, Part 1.1.4 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of CIP-010-2 R1 Part 1.1.4. WECC_URE3 failed to properly identify and document all logical network accessible ports. Specifically, WECC_URE3 failed to develop a complete baseline configuration, including all logical network accessible ports for nine devices at its control center WECC determined that this issue began when the Standard and Requirement became enforceable and ended when WECC_URE3 updated its authorized ports and services list, performed the appropriate steps to baseline the nine devices and updated the baseline document in WECC_URE3’s change management data base, for a total of 203 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to develop a complete baseline configuration including all logical network accessible ports for nine devices at its control center, which could result in WECC_URE3 failing to detect malicious applications and/or malicious communications. However, during WECC audit interviews with the WECC_URE3’s subject matter experts (SMEs), WECC_URE3’s SMEs explained that each logical network accessible port was needed for legitimate application or services in the support of the BES or Cyber Assets that support BES functions. This issue is considered administrative in nature because WECC_URE3 did not update and/or maintain its baseline documentation referencing the running ports and services. No harm is known to have occurred. WECC_URE3 had no prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE3: 1) updated its authorized ports and services list and baseline documentation to reference the missing ports/services; 2) enhanced its three individual process checklists used during WECC_URE3’s testing procedure; and 3) conducted training on its new testing verification process with all applicable subject matter experts and system administrators. WECC has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016513 | CIP-006-6 | R2 | WECC_URE4 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-006-6 R2 Part 2.2. WECC_URE4 reported that it did not maintain a complete log of visitor entry and exit from the Physical Security Perimeter (PSP) at its control center. Specifically, WECC_URE4’s visitor log was incomplete on nine separate instances. In two instances, the log was missing the name of the individual point of contact responsible for escorting the visitor and in seven instances the exit time for the visitor was missing. WECC_URE4 discovered the issue of noncompliance during its quarterly review of the log entries. This issue started when the first instance of not maintaining a complete log of visitor entry and exit occurred, and ended when management distributed an email to all applicable personnel to remind them of their obligation to follow documented visitor control procedures, for a total of 110 days of noncompliance. The root cause was WECC_URE4 employees not following documented visitor control procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 had visitor control documented procedures in place and conducted training for personnel with unescorted physical access privileges. WECC_URE4 had authentication and log monitoring controls to alert personnel of failed access attempts. Additionally, WECC_URE4 has installed port blockers, and monitors for unresponsive hosts. No harm is known to have occurred. | To mitigate this issue, WECC_URE4: 1) conducted a comprehensive review of the internal visitor control process; 2) held a corrective action meeting, which included upper management, to discuss its visitor control program; 3) sent an email to all applicable personnel to remind them of their obligation to follow documented visitor control procedures; increased monitoring of the log entries to a weekly occurrence through approximately the end of the next quarter; and 4) established a process to have its management escalate additional deficiencies when discovered as necessary for progressive disciplinary activities to the supervisor of the employee acting as an escort when it is determined that they are in non-performance of the documented procedure. WECC has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2017017079 | CIP-007-6 | R4 | WECC_URE5 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-6 R4.4. Specifically, WECC_URE5 reported that it did not perform a required review of the summarization or sampling of logged events for two High Impact Bulk Electric System (BES) Cyber Systems (HIBCS) and their associated Cyber Assets within the required 15 calendar day timeframe. Only one employee had the ability to perform the review and inclement weather prevented them from completing the review on-site. Technical issues also prevented the employee from completing the review remotely. This issue started when WECC_URE5 failed to review logged events for two HIBCS within the required 15 calendar day timeframe, and ended when the logs for the two devices were reviewed, for a total of two days of noncompliance. The root cause was a lack of allowance for contingences. Reminders were set too close to deadlines and only one employee had the ability to perform the review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 constantly monitors the HIBCS in its Control Center; if any change had occurred, operators would have been able to alert technicians to immediately examine the devices, limiting the amount of time that the HIBCS would be impacted. While they did not prevent the issue in this case, WECC_URE5 used calendar reminders to ensure the 15-day deadline was not forgotten, thereby lessoning the time between reviews. WECC_URE5 reviewed the logs within two days of the noncompliance and the likelihood of an event occurring and causing risk to the BES within those two days is low. No harm is known to have occurred. WECC determined that WECC_URE5’s compliance history should not serve as an aggravating factor. | To mitigate this issue, WECC_URE5: 1) reviewed all logs; 2) gave an additional employee the ability and access to review security logs as a backup; 3) replaced calendar reminders with a task board that is reviewed daily by at least two individuals; and 4) changed the review notifications to occur every 10 calendar days, instead of 15, to provide a buffer for circumstances outside of its control. WECC has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2016016691 | CIP-006-6 | R2 | WECC_URE6 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-006-6 R2 Part 2.1. Specifically a new trainee was left unattended for brief periods of time within WECC_URE6’s dispatch center. The trainee had previously received training for Cyber Security and the required Personnel Risk Assessment (PRA) was completed. However, notification of the completed PRA was delayed and the trainee was not given their access card until later. Prior to receiving their badge, the trainee was allowed into WECC_URE6’s dispatch center as a visitor and should have been escorted at all times. This issue started when the new trainee was first left unattended, and ended when the trainee received their access card, for a total of two days of noncompliance. The root cause was a less than adequate understanding of newly applicable CIP standards, requirements, and visitor control policies in context to its visitor access control program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6’s dispatch personnel identified the visitor left unescorted within the Physical Security Perimeter (PSP) and reported it. Additionally, WECC_URE6 performs in-depth quarterly reviews of physical access. An additional control is that WECC_URE6’s dispatch center is small and staffed with authorized and trained employees who monitor for unauthorized personnel, door alarms, and other anomalies. WECC_URE6 also has policies and training for management and employees with a focus on awareness of policies. The visitor was also a new employee who had already received training in Cyber Security and had the required PRA completed. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) retrained all applicable personnel on its Cyber Security procedures; 2) modified personnel training procedures to instruct that new trainees will not receive training in the dispatch center unless they have an assigned access card; and 3) emailed applicable employees the quarterly update, including a summary of the violation and a reminder that all visitors within the PSP must be escorted at all times. WECC has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2017016849 | CIP-014-2 | R6 | WECC_URE7 submitted a Self-Report stating that it had three issues with CIP-014-2 R6 Part 6.2 and 6.3. For the first instance, WECC_URE7 reported that, due to an internal misunderstanding of the applicability of CIP-014-2, it omitted the control center when conducting its evaluation of potential threats and vulnerabilities of a physical attack; therefore, WECC_URE7 did not create a threat and vulnerability assessment or physical security plan to address its control center. Subsequently, an unaffiliated third-party review was not conducted for the control center per CIP-014-2 R6. WECC determined that, in this instance, WECC_URE7 did not violate CIP-014-2 R6. WECC_URE7 identified its control center, pursuant to CIP-014-2 R1 and R2, but omitted it when they completed CIP-014-2 R4 and R5. WECC_URE7’s security plan did not include its control center, which WECC_URE7 self-reported, but its security plan was reviewed by an unaffiliated third party reviewer pursuant to CIP-014-2 R6. For the second instance, WECC_URE7 reported that it had an unaffiliated third-party review the evaluation of potential threats and vulnerabilities identified, and its security plans developed under CIP-014-2 R4 and R5, respectively. However, that review was performed beyond the 90-day requirement pursuant to CIP-014-2 R6 Part 6.2. WECC_URE7 discovered this issue while performing an internal compliance evaluation. WECC_URE7 determined that when the individual responsible for CIP-014-2 left the company, WECC_URE7 did not have a good understanding of the tasks that needed to be performed and the time frame around performing those tasks. WECC determined the second instance 91 days after the security plan was completed, and ended when the unaffiliated third-party performed the review, for a total of 2 days of noncompliance. For the third instance, WECC_URE7 reported that, after receiving recommendations for its security plan from the unaffiliated third party reviewer, it did not modify its security plan and/or document reasons for not modifying its security plan within 60 days of the completion of the unaffiliated third party review, pursuant to CIP-014-2 R6 Part 6.3. WECC_URE7 discovered this issue while performing an internal compliance evaluation. Although WECC_URE7 reviewed the recommendations and documented whether or not to implement them, it did not date its response, nor did WECC_URE7 update its security plan accordingly. WECC_URE7 determined that when the individual responsible for CIP-014-2 left the company, WECC_URE7 did not have a good understanding of the tasks that needed to be performed and the time frame around performing those tasks. WECC determined the third instance began 61 days after the completion of the unaffiliated third party review and determined this instance is ongoing. The root cause of the two instances was a less than adequate process for transitioning CIP-014 compliance obligations when employees terminate their employment with WECC_URE7 | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, WECC_URE7 failed to ensure that its unaffiliated third party review of its security plan was completed within 90 calendar days, and failed to modify its evaluation of the potential threats and vulnerabilities of a physical attack to its identified facility(ies) or to its security plan, or document the reason(s) for not modifying the evaluation or security plan(s) per the recommendations of its third-party reviewer. Such failure could result in WECC_URE7 having less than adequate mitigating measures in place to prevent a physical attack that could damage and/or render the control center inoperable; thereby potentially affecting the reliability of the Bulk Power System (BPS). However, the likelihood of the risk occurring was reduce by the controls WECC_URE7 had implemented. WECC_URE7 had an internal compliance evaluation that discovered this issue. Additionally, WECC_URE7’s control center had mitigating measures that deter, detect, and defend potential physical security threats; is primarily a brick construction multilevel facility located in a residential area where it is partially concealed behind existing foliage; and has no signage indicating the type or function of the facility. The perimeter is protected with a brick wall, chain link, and rigid fence that is monitored with physical intrusion detection systems. Entry to the fenced perimeter is via two access-controlled gates. The main entry gate is a Class III crash-rated gate. All areas of the perimeter are monitored by cameras that are viewed and controlled locally and can be accessed remotely by corporate security operators. All ground-level windows on the public sides of the building are coated with blast and penetration coating. Intercom systems are used at all entry points. Each entry point has camera coverage to provide a view of the intercom and the entry point overall. WECC_URE7 has 24/7 security monitoring by physical security personnel located at the control center. No harm is known to have occurred. WECC_URE7 had no prior compliance history with this Standard and Requirement. | To mitigate this issue, WECC_URE7: 1) update its potential threat and vulnerability assessment and its security plan with the unaffiliated third party reviewer’s recommendations it agrees with; 2) document its reasons for not modifying its evaluation or security plan(s) as recommended by the unaffiliated third party reviewer; and 3) create automatic task reminders utilizing a Governance Risk Compliance (GRC) tool that will assign all necessary tasks associated with Requirement R6 to both an individual and a group responsible for performing the tasks; thereby ensuring the task is received by more than one individual.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2016016060 | CIP-007-6 | R4, Parts 4.1.1 and 4.1.2 | WECC_URE8 submitted self-reports stating that it had issues of with CIP-007-6 R4 Part 4.1.1 and 4.1.2. Specifically, WECC_URE8 reported that four relays in its Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) without Electronic Routable Connectivity (ERC) were put into service without activating the “Password Access Events” feature, which would have allowed WECC_URE8 to log successful login attempts, failed access attempts, and failed login attempts. WECC_URE8 discovered this oversight for the first three relays while verifying installation work associated with the three relays, and discovered the fourth relay while performing work validation as part of its change management process. The root cause of this issue was an employee not following WECC_URE8’s documented procedures. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE8, and ended when WECC_URE8 configured the last of the four relays to log successful login attempts, and failed access attempts and failed login attempts, for a total of 165 days of noncompliance | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE8 failed to log successful login attempts, failed access attempts, and failed login attempts on four relays in its MIBCS without ERC. Such failure could result in an inability to perform thorough after-the-fact investigations of Cyber Security Incidents. Additionally, unauthorized individuals could gain access to the relays which provide local breaker failure backup protection for circuit breakers. Unauthorized access could result in a malicious actor manipulating settings or taking action on the relays; thereby, potentially affecting the reliability of the BPS. However, the likelihood of the risk occurring was reduced by the controls WECC_URE8 had implemented. The four relays are in a MIBCS with no ERC; the default passwords had been changed prior to placing the relays into production; and physical access is restricted to authorized personnel who have a documented Personnel Risk Assessment and cyber security training. All physical access points to the PSP where the MIBCS is located are equipped with door contacts that alarm and alert for any unauthorized physical access attempts. WECC_URE8 has a post-implementation review process for all new Cyber Assets. The physical security controls designed for this MIBCS were deployed in a manner to provide a defense-in-depth security strategy for protecting assets critical to the operation of the BES. No harm is known to have occurred. WECC_URE8 had no relevant prior noncompliance with this Standard and Requirement. | To mitigate this issue, WECC_URE8: 1) enabled the Password Access Events feature for all four relays; 2) delivered a NERC CIP awareness presentation to field crew supervisors and managers who share the presentation with their field crews; 3) conducted a conference call with test supervisors to discuss NERC CIP related developments and topics. Additional conference calls are scheduled as an on-going monthly calendar item; 4) conducted NERC CIP refresher courses to reinforce concepts and issues, and addressed concerns for all test technicians and their associated supervisors and senior managers; and 5) implemented a process for setting relays to record password access events in the Event Recorder/Sequential Event Recorder when protection engineers design the configuration files to relays
2017-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017656 | CIP-004-6 | R3 | MRO_URE1 submitted a Self-Report for an issue discovered in preparation for an upcoming Compliance Audit. MRO_URE1 stated it had an issue with CIP-004-6 R3, Part 3.5 because it granted an employee unescorted physical access privileges to its control room without having a personnel risk assessment (PRA) completed for that employee within the last seven years. The employee was a long time employee and had physical access privileges, but MRO_URE1's control room was not subject to CIP's physical access standards previously. The cause of this noncompliance was a lack of review during the implementation of CIP Version 5. During the implementation of CIP Version 5, MRO_URE1 did not review the individuals who had previous unescorted access privileges to the control room, as its prior PRA policy was sufficient to meet the PRA requirements of CIP Version 5. Prior to the start of the noncompliance, MRO_URE1 had a policy in place to conduct PRAs for individuals that had unescorted access privileges to the control room, but because of the unique circumstances around this employee's promotion, MRO_URE1 did not follow the standard process and a PRA was not conducted for this employee per MRO_URE1's policy. The duration of the noncompliance was approximately 2 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was limited to a single employee that had been employed with MRO_URE1 for more than ten years and was in good standing. Although he had been granted access to the control room without a PRA being conducted, the subsequent PRA did not raise any issues. The employee was not granted electronic access. Finally, this employee was not included in the associated audit sample, and there may not have been an associated finding without MRO_URE1's self-detection of this issue. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-004-6. | To mitigate this issue, MRO_URE1: 1) conducted a PRA for the employee; and 2) reinforced the PRA Policy. MRO_URE1 stated that mitigating activities are complete.
2017-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017658 | CIP-007-6 | R1 | MRO determined that MRO_URE1, had an issue with CIP-007-6 R1, Part 1.1. During sampling, MRO discovered a Physical Access Control System (PACS) device with a single unidentified open port. This device controls physical access to the control center and the unidentified port was necessary for the operation of the device. The cause of this noncompliance was an inaccurate understanding of the device's network connection. The device was connected through an Ethernet connection, however MRO_URE1 believed that the device was connected serially with no listening ports. The duration of the noncompliance was approximately 2 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. It was appropriate for this port to be open as it was needed. The issue was limited to a single device of the 16 devices that were sampled. Further, the device was not part of the EMS/SCADA system and was not responsible for grid operations. Additionally, there was no demonstrated impact by the port not being documented. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-007-6. | To mitigate this issue, MRO_URE1 approved the port and added it to the list of approved ports for the device. MRO_URE1 stated that mitigating activities are complete.
2017-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017659 | CIP-007-6 | R5 | MRO determined that MRO_URE1, had an issue with CIP-007-6 R5, Part 5.7. Two sampled Protected Cyber Assets (PCA) did not limit the number of unsuccessful authentication attempts or generate an alert after a threshold number of unsuccessful authentication attempts. The PCAs were printers that MRO_URE1 stated could not feasibly perform either function. The cause of this noncompliance was MRO_URE1's failure to understand the Technical Feasibility Exception (TFE) process, and its compliance obligations for PCAs that cannot technically meet the requirements of CIP-007-6 R5, Part 5.7. The duration of the noncompliance was approximately 2 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were protected from adversaries because they were located in an Electronic Security Perimeter (ESP) and behind firewalls. The devices were also located in a Physical Security Perimeter (PSP) and a user needed to have a user id and password to gain access to them. Further, logging was in place for users that did access the devices. Finally, the noncompliance can be accurately categorized as an administrative issue as MRO_URE1 reported that the printers could not feasibly perform either function, and the noncompliance could have been resolved with a TFE. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-007-6. | To mitigate this issue, MRO_URE1: 1) removed the printers from the SCADA System; and 2) studied the TFE process and its obligations under that process. MRO_URE1 stated that mitigating activities are complete.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016426 | CIP-005-3a | R3 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a R3. RFC_URE1 uses a centralized logging and alerting tool. The tool infrastructure was moved from RFC_URE1 headquarters to another data center. Regarding root cause, during the move, as anticipated, automated logging and alerting did not occur for approximately six hours while all appliances were shut down and relocated. And, it was not practical to conduct manual reviews of the security event logs originating from RFC_URE1’s CIP Cyber Assets. Accordingly, RFC_URE1 could not retain records of security events which may have occurred during the short outage. However, during the move, RFC_URE1’s layered, defense-in-depth security measures remained active, including, for example, advanced persistent threat tools monitoring intrusions from the external internet, host intrusion prevention and antivirus protecting against malicious software, two-factor authentication providing strong access controls, and firewalls and other tools securing the network perimeter. The duration of the noncompliance was approximately six hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, knowledge of the planned outage was limited to several members of RFC_URE1’s security team, which decreased the likelihood of exploitation. Second, although the service disruption affected alerting and logging capabilities, RFC_URE1’s other layered, defense-in-depth security measures remained active. Third, knowing ahead of time that there would be an outage, RFC_URE1 informed certain individuals on its security operations team so that the individuals could monitor the systems as closely as possible for abnormal activity. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 relocated infrastructure equipment to another data center in order to improve and maintain reliability and resiliency. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016423 | CIP-007-3a | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R1. RFC_URE1 upgraded a router’s operating system without executing one step of the cyber security test procedures in violation of CIP-007-3a R1. The substation router was used as a backup to send remote terminal unit (RTU) data from the substation to transmission dispatchers and also supported local security cameras and card readers. Personnel making the change knew the router was a CIP Cyber Asset, but were unaware that an operating system upgrade represented a significant change requiring full test procedures. Prior to production, RFC_URE1 tested the upgraded code in a non-production environment (including a comparison of ports and services), but failed to compare listening ports before and after the change in the production environment. Approximately three months later, the team discovered the omission and confirmed that existing security controls were unaffected by the change. The root cause was a combination of lack of awareness that a change constituted a significant change and ineffective controls to ensure personnel completed all necessary steps regarding change control activities. These causes involve the management practice of verification, which includes ensuring changes to assets are completed as intended according to the relevant process. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the change was tested in a nonproduction environment before deployment, thus reducing the likelihood that the change would have adversely affected security controls. Second, transmission personnel were at the substation during the change and could have switched back to the primary communication method to share RTU data with dispatchers if the change affected the router’s availability. Third, RFC_URE1 had other security controls in place that reduced the likelihood of compromise in the unlikely event that the change would open unnecessary ports. For example, RFC_URE1 had centralized logging and alerting systems monitoring the Electronic Security Perimeters (ESPs), strong access controls, and firewalls and other tools securing the network perimeters. As a result, the likelihood of compromise to RFC_URE1’s system as a result of this noncompliance was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) conducted and documented a port comparison, which completed the required change control activities; and 2) to prevent recurrence, added a step in its change control process of using task templates based on the task being entered in the change control system. The templates will act as checklists to ensure system or asset changes are completed correctly. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016422 | CIP-007-3a | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. During a periodic check of password aging, RFC_URE1 identified one default account, 6 generic accounts, and 12 interactive accounts with passwords that were not changed within the preceding 15 months. These accounts were used to support multiple functions within RFC_URE1’s operations group. The root cause was lack of clearly defined processes to ensure passwords on these accounts were changed within the required timeframe. This involves asset and configuration management, which includes tracking changes to assets to ensure necessary changes occur by the required date. The duration of the noncompliance was approximately 27 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the passwords met the complexity requirements, thus reducing the likelihood of compromise. Second, other protections were in place, such as alerting and logging, to reduce the likelihood of compromise. Third, RFC_URE1 identified the issue through a periodic review control, which reduced the amount of time there was an increased risk due to not changing the passwords. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) changed the expired passwords; and 2) implemented an “RFC_URE1 Password Age Requirements” script to prevent recurrence. This script will disable users whose password is over the limit and will encourage Service Accounts to follow the password age limit, but will not disable any Service Accounts. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016425 | CIP-007-3a | R6 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R6. RFC_URE1 uses a centralized logging tool. The tool is protected by a pair of firewalls. The tool experienced a 90-minute service disruption, which resulted in noncompliance because RFC_URE1 could not monitor system events pursuant to CIP-007-3a R6 because logs were not retained. This also violated CIP-005-3a R3.2, which requires security monitoring processes to “detect and alert for attempts at or actual unauthorized accesses” because event logs were not processed or retained during the disruption. RFC_URE1 determined that the issue occurred because the firewalls protecting the tool failed to synchronize. Firewalls are often deployed in pairs to provide redundancy and, in order to provide service continuity in case of a failover to the secondary firewall, the firewalls must be synchronized. The day before the noncompliance occurred, network support personnel discovered a secondary firewall that was “out of sync” with its primary firewall. The next day, RFC_URE1 personnel rebooted the secondary firewall to synchronize with its primary firewall. When the reboot occurred, the paired firewalls behaved differently than expected, causing the disruption in service. Security personnel immediately noticed the unusually low volume of security event logs received by the tool and notified the relevant personnel, who then reconfigured the firewalls to resolve the issue. This root cause involves the management practice of verification because the synchronization of firewalls should be verified before being placed into production. The duration of the noncompliance was approximately 90 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the noncompliance was short in duration as a result of RFC_URE1 immediately identifying and resolving the noncompliance. Additionally, RFC_URE1’s layered, defense-in-depth security measures remained active. These include, for example, distributed intrusion detection and intrusion prevention systems monitoring Electronic Security Perimeters, advanced persistent threat tools monitoring intrusions from the external internet, host intrusion prevention and antivirus protecting against malicious software, and two-factor authentication providing strong access controls. No harm is known to have occurred. . | To mitigate this issue, RFC_URE1: 1) re-synchronized the dual firewalls; and 2) verified event logging was functional. Additionally, in the unlikely event that a synchronization issue occurs again, RFC_URE1 has recovery plans in place to quickly bring the assets back online. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016428 | CIP-005-3a | R3 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-005-3a R3. RFC_URE2 uses a centralized logging and alerting tool. The tool infrastructure was moved from RFC_URE2 headquarters to another data center. Regarding root cause, during the move, as anticipated, automated logging and alerting did not occur for approximately six hours while all appliances were shut down and relocated. And, it was not practical to conduct manual reviews of the security event logs originating from RFC_URE2’s CIP Cyber Assets. Accordingly, RFC_URE2 could not retain records of security events which may have occurred during the short outage. However, during the move, RFC_URE2’s layered, defense-in-depth security measures remained active, including, for example, advanced persistent threat tools monitoring intrusions from the external internet, host intrusion prevention and antivirus protecting against malicious software, two-factor authentication providing strong access controls, and firewalls and other tools securing the network perimeter. The duration of the noncompliance was approximately six hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, knowledge of the planned outage was limited to several members of RFC_URE2’s security team, which decreased the likelihood of exploitation. Second, although the service disruption affected alerting and logging capabilities, RFC_URE2’s other layered, defense-in-depth security measures remained active. Third, knowing ahead of time that there would be an outage, RFC_URE2 informed certain individuals on its security operations team so that the individuals could monitor the systems as closely as possible for abnormal activity. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2 relocated infrastructure equipment to another data center in order to improve and maintain reliability and resiliency. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016430 | CIP-007-3a | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R1. RFC_URE2 upgraded a router’s operating system without executing one step of the cyber security test procedures in violation of CIP-007-3a R1. The substation router was used as a backup to send remote terminal unit (RTU) data from the substation to transmission dispatchers and also supported local security cameras and card readers. Personnel making the change knew the router was a CIP Cyber Asset, but were unaware that an operating system upgrade represented a significant change requiring full test procedures. Prior to production, RFC_URE2 tested the upgraded code in a non-production environment (including a comparison of ports and services), but failed to compare listening ports before and after the change in the production environment. Approximately three months later, the team discovered the omission and confirmed that existing security controls were unaffected by the change. The root cause was a combination of lack of awareness that a change constituted a significant change and ineffective controls to ensure personnel completed all necessary steps regarding change control activities. These causes involve the management practice of verification, which includes ensuring changes to assets are completed as intended according to the relevant process. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the change was tested in a nonproduction environment before deployment, thus reducing the likelihood that the change would have adversely affected security controls. Second, transmission personnel were at the substation during the change and could have switched back to the primary communication method to share RTU data with dispatchers if the change affected the router’s availability. Third, RFC_URE2 had other security controls in place that reduced the likelihood of compromise in the unlikely event that the change would open unnecessary ports. For example, RFC_URE2 had centralized logging and alerting systems monitoring the Electronic Security Perimeters (ESPs), strong access controls, and firewalls and other tools securing the network perimeters. As a result, the likelihood of compromise to RFC_URE2’s system as a result of this noncompliance was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) conducted and documented a port comparison, which completed the required change control activities; and 2) to prevent recurrence, added a step in its change control process of using task templates based on the task being entered in the change control system. The templates will act as checklists to ensure system or asset changes are completed correctly. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016434 | CIP-007-3a | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. During a periodic check of password aging, RFC_URE2 identified one default account, 6 generic accounts, and 12 interactive accounts with passwords that were not changed within the preceding 15 months. These accounts were used to support multiple functions within RFC_URE2’s operations group. The root cause was lack of clearly defined processes to ensure passwords on these accounts were changed within the required timeframe. This involves asset and configuration management, which includes tracking changes to assets to ensure necessary changes occur by the required date. The duration of the noncompliance was approximately 27 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the passwords met the complexity requirements, thus reducing the likelihood of compromise. Second, other protections were in place, such as alerting and logging, to reduce the likelihood of compromise. Third, RFC_URE2 identified the issue through a periodic review control, which reduced the amount of time there was an increased risk due to not changing the passwords. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) changed the expired passwords; and 2) implemented an “RFC_URE2 Password Age Requirements” script to prevent recurrence. This script will disable users whose password is over the limit and will encourage Service Accounts to follow the password age limit, but will not disable any Service Accounts. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016429 | CIP-007-3a | R6 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R6. RFC_URE2 uses a centralized logging tool The tool is protected by a pair of firewalls. The tool experienced a 90-minute service disruption, which resulted in noncompliance because RFC_URE2 could not monitor system events pursuant to CIP-007-3a R6 because logs were not retained. This also violated CIP-005-3a R3.2, which requires security monitoring processes to “detect and alert for attempts at or actual unauthorized accesses” because event logs were not processed or retained during the disruption. RFC_URE2 determined that the issue occurred because the firewalls protecting the tool failed to synchronize. Firewalls are often deployed in pairs to provide redundancy and, in order to provide service continuity in case of a failover to the secondary firewall, the firewalls must be synchronized. The day before the noncompliance occurred, network support personnel discovered a secondary firewall that was “out of sync” with its primary firewall. The next day, RFC_URE2 personnel rebooted the secondary firewall to synchronize with its primary firewall. When the reboot occurred, the paired firewalls behaved differently than expected, causing the disruption in service. Security personnel immediately noticed the unusually low volume of security event logs received by the tool and notified the relevant personnel, who then reconfigured the firewalls to resolve the issue. This root cause involves the management practice of verification because the synchronization of firewalls should be verified before being placed into production. The duration of the noncompliance was approximately 90 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the noncompliance was short in duration as a result of RFC_URE2 immediately identifying and resolving the noncompliance. Additionally, RFC_URE2’s layered, defense-in-depth security measures remained active. These include, for example, distributed intrusion detection and intrusion prevention systems monitoring Electronic Security Perimeters, advanced persistent threat tools monitoring intrusions from the external internet, host intrusion prevention and antivirus protecting against malicious software, and two-factor authentication providing strong access controls. No harm is known to have occurred. . | To mitigate this issue, RFC_URE2: 1) re-synchronized the dual firewalls; and 2) verified event logging was functional. Additionally, in the unlikely event that a synchronization issue occurs again, RFC_URE2 has recovery plans in place to quickly bring the assets back online. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016433 | CIP-010-2 | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-010-2 R1. The operations team monitors baselines through daily baseline reconciliations. An employee in the group was reviewing the daily baseline reconciliation reports for a high impact Bulk Electric System (BES) Cyber Asset and identified an unauthorized change made to an asset that supports the generation group. The employee determined that an encryption product had been installed on a dispatcher workstation in error. The employee notified the administrator that unauthorized software had been pushed to the asset. The asset owner then entered a change ticket in the change management system requesting a reimage of the workstation. The workstation was removed from service and reimaged the next day. Regarding the root cause, the administrator determined that the asset had been improperly tagged and placed in a “CORP” workstation branch of RFC_URE2’s asset and configuration system. This branch was configured to install encryption on all new workstations. This issue involves the manage practice of asset and configuration management, which requires defining configuration item attributes, such as the class or “branch” to which the configuration item belongs. The duration of the noncompliance was approximately one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Executing changes on CIP assets without properly executing test procedures could potentially introduce system instability or affect functionality. However, these risks were mitigated by the following factors. RFC_URE2 quickly detected the noncompliance (the same day it occurred) and thereafter quickly mitigated the noncompliance. Additionally, in the event the change would have caused the asset to malfunction, all units, except hydro units, were manned and could be controlled manually while the system is down. Accordingly, the issue posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) provided a complete listing of certain BES Cyber Assets supported by the group and worked to create an agreed upon tagging and branch structure that is clear to all groups. This structure was documented and shared with all team members. Once finalized, administrators implemented the new structure within the system and moved the incorrectly branched items to the proper branch; 2) will send an email message to an agreed upon email address and copy CIP compliance personnel any time they add or remove BES Cyber Assets. This manual step will help to ensure that new assets will be tagged and branched properly by the administrators. This step was be added to the change management template. Compliance personnel created a report to monitor the system for new assets and ensure that they have been reported as part of the manual mitigation; and 3) created a change request for the asset management system. This change will request the creation of a new template for the creation of BES Cyber Assets that includes a step to notify the administrators for each BES Cyber Asset being added to the group and adds a field to indicate the required tags for the new asset.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017364 | CIP-007-3a | R3; R3.1 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R3.1. Having completed a compliance investigation of the issue, RFC_URE3 determined that a possible issue had occurred involving CIP-007-3a R3.1. Specifically, a patch was released, which was applicable to versions of backup software up to and including 7.7.1. At the time of the release, the patch assessment team believed that RFC_URE3 energy management system (EMS) was in the process of installing backup version 7.7.2, which was released in earlier, on its 4 servers. This incorrect belief and the reliance on that belief is the root cause of the noncompliance. The patch assessment team did not verify this belief, however, and as a result a documented assessment of the patch was not performed within the required 30 day timeframe under CIP-007-3a R3.1. Subsequently, the vendor released software version 7.7.3. It was at this time, while assessing version 7.7.3, that the assessment team discovered that version 7.7.2 had not in fact been installed as it did not include a security release. Upon realizing the oversight, the patch was immediately assessed, documented, and then added to the EMS Deferred Patch Plan (DPP), as required under CIP-007-6 R2.1 to coincide with the scheduled implementation of version 7.7.3, which itself includes the security fix addressed by the patch. The duration of the noncompliance was approximately eight days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, RFC_URE3’s EMS systems are designed to include several layers of physical and electronic security controls, including but not limited to: secured Electronic Security Perimeters, enclosed Physical Security Perimeters (PSPs), continuous logging and monitoring, and access management controls limiting access rights solely to authorized personnel. With this in mind, an individual would need to transgress several physical security controls around the PSP (i.e., security guards, unique pin and badge controlled doors, and other personnel) in order to gain access to the EMS systems. Moreover, to protect against malicious code, protective anti-malware is installed on RFC_URE3’s EMS systems, including the 4 Backup Servers. In the event of malicious code detection, the anti-malware is configured to automatically quarantine the impacted area and send an event to a monitoring software. That software then generates and sends an alert to the appropriate Support Team for review and to take the appropriate actions. Finally, the issue was quickly identified and corrected by the personnel involved. While the patch assessment was completed 20 days beyond the initial CIP-007-3a 30 day requirement, timely identification of the issue under the CIP-007-6 program ensured that the patch was ultimately assessed and added to the DPP within the requisite post-assessment timeframe under CIP-007-6. In other words, while the assessment was delayed under CIP-007-3a, the patch was added in a timely manner to the DPP under CIP-007-6. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 completed a documented patch assessment immediately upon discovering the issue, and the patch was added to the DPP. To prevent such human performance issues in the future, all responsible personnel will be appropriately trained on the process enhancements. Specifically, RFC_URE3 enhanced its CIP-007-6 patch assessment process to include up-to-date information on current EMS products and software versions as part of the documentation compiled and used by the EMS patch assessment team in their regular assessment meetings. The patch assessment process was enhanced to provide additional verification process steps (e.g., sign-offs of assessment determinations by other team members).
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2017017367 | CIP-006-6 | R2; R2.1 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-006-6 R2.1. Following an evacuation, personnel were returning to work by way of a door at the rear of the building. The rear door is located at ground level and leads to a stairwell between the basement and first floor, providing access to the basement, first and second floors of the building. On the first floor (just off the stairwell in a small vestibule), is an access point to a Physical Security Perimeter (PSP) hallway. On this day, an employee new to the building and not authorized for unescorted physical access to the PSP, mistakenly entered the first floor doorway as opposed to the second floor doorway from which he had originally exited at the time of the evacuation. Disoriented, he then entered the vestibule and proceeded through the access point leading to the PSP hallway by piggybacking behind an authorized employee. That authorized employee had correctly used his two-factor access credentials to open the door, but was unaware of anyone behind him. Once through the door, the new employee proceeded to the end of the hallway only to realize he was in the wrong area. He then turned around in the direction from which he came and exited the secure area. As the employee was exiting the vestibule, he was stopped by a Facilities Manager and asked where he was coming from and why he was in the secure area. The employee responded that he was not familiar with the area as he was new to the building and that he was not aware that he was in a secure area. The employee's lack of awareness is the root cause of this noncompliance. The Facilities Manager provided awareness of the secure area to the employee and then immediately reported the incident to the physical security department. The hallway that the employee entered leads to several badge controlled rooms within which Cyber Assets reside. Given the badge controlled doors, the employee was not able to enter any of the secure rooms and gain access to the Cyber Assets therein. The employee was in the PSP hallway for approximately 2 minutes and was not escorted during that time as required under CIP-006-6, R2, P2.1. In the second issue, three visitors were appropriately logged and escorted by authorized personnel into a PSP to participate in a scheduled meeting. During a break, two of the visitors were appropriately escorted to the men’s room by an authorized employee. However, after the visitors entered the men’s room, the escort left the area in violation of RFC_URE3’s PSP visitor/escort policies, allowing the visitors to return to the meeting room on their own. After returning to the meeting room, one of the visitors asked if he could again leave the meeting room and go down the hall to fill his water bottle at a water fountain. Believing that his colleague (who had escorted the gentlemen to the men’s room) was still in the hallway, and needing to remain in the meeting room as an escort with the two other visitors, the employee permitted the visitor’s request not realizing that his colleague was not in the hallway to serve as an escort. This incorrect belief is another root cause of this noncompliance. As the visitor was returning to the meeting room from the water fountain, a manager sitting in his office located adjacent to the meeting room noticed an unfamiliar person walking unescorted in the hallway. He exited his office to investigate, but the visitor had already returned to the meeting room and was no longer in the hallway. The manager then proceeded to the PSP access point to review the visitor logs. Upon verifying that there were in fact visitors logged into the PSP that day, the manager immediately contacted the manager of control room operations and the physical security office to notify them of a possible escorting issue. Review of the security footage shows that the visitors walked directly to their destinations (i.e., men’s room and the water fountain) and back to the meeting room. The duration of first issue was approximately two minutes. The duration of the second issue was approximately two minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP-006-6 requirements. Moreover, the Plan expressly prohibits authorized personnel from allowing unauthorized access on their credentials, and requires that visitors be appropriately logged and continuously escorted while within a PSP. In the instances described, certain aspects of these security protocols were not followed, but nonetheless the issues were promptly identified and reported upon discovery. The subsequent investigation and review determined that no Cyber Assets were accessed or compromised by the unauthorized employee and unescorted visitors, and the duration of each incident was limited to no more than 2 minutes. Furthermore, effective additional controls were in place to protect against unauthorized, unmonitored access to cyber assets (e.g., badge controlled secure PSP rooms, alarms, and authorized personnel monitoring) and ensured immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) provided internal coaching to the individual(s) involved in the incidents; 2) developed and implemented targeted visitor control program awareness measure(s) to reinforce visitor and escorting responsibilities at the outset; 3) developed a role within the System Operations area to physically man the access point door(s) upon re-entry into the PSP after an evacuation emergency; 4) performed an assessment to determine the feasibility of creating additional security measures at the rear access point to the PSP (e.g. create a man-trap, egress only, etc.); and 5) established, based upon the assessment recommendation(s), an implementation plan for the additional security measure(s) as determined feasible.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016585 | CIP-010-2 | R1 | RFC_URE4 submitted a Self-Report stating that it had an issue with CIP-010-2 R1. RFC_URE4's overall change management program includes two key features one program that identifies the key work information, including the scope requested, and another program that facilitates the process and documentation for the authorization step of baseline changes for service tickets. These two programs work to ensure that changes to in-scope NERC CIP Assets are properly authorized. In addition to these controls, RFC_URE4 also performs monthly baseline monitoring as an additional detective control to identify unauthorized changes. When unauthorized changes are detected during the monthly baseline monitoring, RFC_URE4 performs an investigation to determine the appropriate next steps. RFC_URE4 identified all of the instances of noncompliance discussed below through its monthly baseline monitoring. In the first instance of noncompliance, a change ticket was submitted and pending an authorization for the application of patches to a domain controller. However, an associate performed additional work on the domain controller in preparation for the change that went beyond the scope of work authorized in the corresponding change ticket. Specifically, the associate removed three applications from the domain controller that were no longer necessary. In the second instance of noncompliance, as part of its annual Cyber Vulnerability Assessment remediation effort, RFC_URE4 created a service ticket to address various issues with switches, one of which was an update to a switch to close ports. The ticket was forwarded to the communications group, which was responsible for completing the work. That group completed the work, but failed to submit the necessary authorization ticket to the authorization program. In the third instance of noncompliance, an associate submitted a change authorization request, which was conditionally approved by the appropriate manager. However, the compliance group rejected the request and sought additional information. This rejection required the ticket to be re-submitted for final approvals, which was never completed. The associate completed the work believing that the conditional approval from the manager was sufficient authorization. In the fourth instance of noncompliance, an associate submitted a change authorization request to apply security patches to eight EACMS hosts. However, the associate completed the work before the authorization process was completed. The root cause of these instances of noncompliance was a lack of understanding of the overall change management process by responsible employees at RFC_URE4. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees, and asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although executing changes on CIP assets without proper authorization could potentially introduce system instability or affect functionality, these risks were mitigated by the following factors. First, RFC_URE4 identified all of these instances of noncompliance through its monthly monitoring of baselines. This additional internal, detective control allowed RFC_URE4 to quickly identify these issues and limit their duration. Second, in all of the instances, except for the second instance related to the switch, RFC_URE4 had completed security control impact assessments pursuant to CIP-010-2 R1.4 prior to implementing the change. These assessments would have alerted RFC_URE4 to any impacts the changes may have had on the cyber security controls in CIP-005 and CIP-007. ReliabilityFirst notes that the unauthorized changes did not introduce attack vectors from outside sources and did not adversely impact the affected devices. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 will complete the following mitigation activities by June 29, 2017: 1) issued a reminder email message of the need to have authorization prior to the implementation of a change to all users of the authorization program; 2) reviewed procedure for configuration controls and ports management and made updates to further support the need to have authorization prior to implementing a baseline impacting change; 3) held a “Lunch and Learn” opportunity for performers around CIP-010 and change management process expectations; 4) created training materials for stronger awareness of CIP-010, and change management expectations training will cover: Concepts of CIP-010, associated management documents, Training and Reference Material and Job Aids that RFC_URE4 uses for compliance with CIP-010, and will include hands on exercises in the authorization program with examples of common day-to-day activities; 5) will conduct “Train the Trainer” sessions to teach local trainers the training materials. At least two associates in each region will be trained; and 6) will deliver training to associates of relevant groups.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016630 | CIP-006-6 | R2 | RFC_URE4 submitted a Self-Report stating that it had an issue with CIP-006-6 R2. RFC_URE4 security personnel was reviewing the previous day’s security video of a Physical Security Perimeter (PSP) and noticed that a RFC_URE4 employee with authorized unescorted access to the PSP attempted to escort two visitors into the PSP for non-CIP related work. The RFC_URE4 employee went through the appropriate access process (RFC_URE4 PSPs utilize a card process to log entry of visitors into PSPs. This process entails a visitor swiping a visitor card, followed by an Authorized Escort ID badge swipe and PIN entry, which associates the visitor and escort and creates a log in the PACS for the visitor’s entry.) for the first visitor, who successfully entered the PSP. However, while performing the access process for the second visitor, the door to the PSP closed, leaving the first visitor within the PSP and the RFC_URE4 employee outside of the PSP with the second visitor. The RFC_URE4 employee spoke to a nearby employee with authorized unescorted access to the PSP, who entered the PSP to escort the first visitor, while the second visitor was properly logged in. As a result, the first visitor remained in the PSP without an escort for 1 minute and 31 seconds. The root cause of this violation was the RFC_URE4 employee’s failure to follow company procedure requiring continuous escorting of visitors. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately two minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the RFC_URE4 employee immediately realized the problem and corrected it in less than 2 minutes. Second, due to the very short period of time the visitor was unescorted, it is unlikely that he had access to any CIP assets, which reduces the likelihood that any significant harm could have occurred. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) sent an email to all RFC_URE4 employees reminding them of PSP escort requirements; 2) sent an email to all personnel with authorized unescorted access to RFC_URE4 PSPs reiterating the visitor card process and escort responsibilities; 3) developed a plan of action to remove the visitor cards from the access control systems; 4) implemented the plan to decommission the NERC visitor card process in the RFC_URE4 development system; 5) sent a communication to personnel with authorized unescorted access to RFC_URE4 PSPs detailing the new visitor logging process. This communication included scheduled implementation dates for the new visitor logging process; 6) decommissioned the NERC visitor card escort process in the RFC_URE4 production environment. RFC_URE4 installed new visitor log binders and standard visitor log signage at all RFC_URE4 PSPs; 7) updated the RFC_URE4 NERC CIP annual computer based training module to reflect the updated visitor logging process; and 8) updated RFC_URE4’s management document to reflect the decommissioning of the RFC_URE4 visitor card escort process.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016588 | CIP-010-2 | R1 | RFC_URE5 submitted a Self-Report stating that it had an issue with CIP-010-2 R1. RFC_URE5's overall change management program includes two key features one program that identifies the key work information, including the scope requested, and another program that facilitates the process and documentation for the authorization step of baseline changes for service tickets. These two programs work to ensure that changes to in-scope NERC CIP Assets are properly authorized. In addition to these controls, RFC_URE5 also performs monthly baseline monitoring as an additional detective control to identify unauthorized changes. When unauthorized changes are detected during the monthly baseline monitoring, RFC_URE5 performs an investigation to determine the appropriate next steps. RFC_URE5 identified all of the instances of noncompliance discussed below through its monthly baseline monitoring. In the first instance of noncompliance, a change ticket was submitted and pending an authorization for the application of patches to a domain controller. However, an associate performed additional work on the domain controller in preparation for the change that went beyond the scope of work authorized in the corresponding change ticket. Specifically, the associate removed three applications from the domain controller that were no longer necessary. In the second instance of noncompliance, an associate submitted a change authorization request to apply security patches to eight EACMS hosts. However, the associate completed the work before the authorization process was completed. The root cause of these instances of noncompliance was a lack of understanding of the overall change management process by responsible employees at RFC_URE5. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees, and asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although executing changes on CIP assets without proper authorization could potentially introduce system instability or affect functionality, these risks were mitigated by the following factors. First, RFC_URE5 identified all of these instances of noncompliance through its monthly monitoring of baselines. This additional internal, detective control allowed RFC_URE5 to quickly identify these issues and limit their duration. Second, in all of the instances, RFC_URE5 had completed security control impact assessments pursuant to CIP-010-2 R1.4 prior to implementing the change. These assessments would have alerted RFC_URE5 to any impacts the changes may have had on the cyber security controls in CIP-005 and CIP-007. ReliabilityFirst notes that the unauthorized changes did not introduce attack vectors from outside sources and did not adversely impact the affected devices. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 will complete the following mitigation activities by June 29, 2017: 1) issued a reminder email message of the need to have authorization prior to the implementation of a change to all users of the authorization program; 2) reviewed procedure for configuration controls and ports management and made updates to further support the need to have authorization prior to implementing a baseline impacting change; 3) held a “Lunch and Learn” opportunity for performers around CIP-010 and change management process expectations; 4) created training materials for stronger awareness of CIP-010, and change management expectations training will cover: Concepts of CIP-010, associated management documents, Training and Reference Material and Job Aids that RFC_URE5 uses for compliance with CIP-010, and will include hands on exercises in the authorization program with examples of common day-to-day activities; 5) will conduct “Train the Trainer” sessions to teach local trainers the training materials. At least two associates in each region will be trained; and 6) will deliver training to associates of relevant groups.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017365 | CIP-007-3a | R3; R3.1 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-007-3a R3.1. Having completed a compliance investigation of the issue, RFC_URE6 determined that a possible violation had occurred involving CIP-007-3a R3.1. Specifically, a patch was released, which was applicable to versions of backup software up to and including 7.7.1. At the time of the release, the patch assessment team believed that RFC_URE1 energy management system (EMS) was in the process of installing backup version 7.7.2, which was released in earlier, on its 4 servers. This incorrect belief and the reliance on that belief is the root cause of the noncompliance. The patch assessment team did not verify this belief, however, and as a result a documented assessment of the patch was not performed within the required 30 day timeframe under CIP-007-3a R3.1. Subsequently, the vendor released software version 7.7.3. It was at this time, while assessing version 7.7.3, that the assessment team discovered that version 7.7.2 had not in fact been installed as it did not include a security release. Upon realizing the oversight, the patch was immediately assessed, documented, and then added to the EMS Deferred Patch Plan (DPP), as required under CIP-007-6 R2.1 to coincide with the scheduled implementation of version 7.7.3, which itself includes the security fix addressed by the patch. The duration of the noncompliance was approximately eight days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, RFC_URE6’s EMS systems are designed to include several layers of physical and electronic security controls, including but not limited to: secured Electronic Security Perimeters, enclosed Physical Security Perimeters (PSPs), continuous logging and monitoring, and access management controls limiting access rights solely to authorized personnel. With this in mind, an individual would need to transgress several physical security controls around the PSP (i.e., security guards, unique pin and badge controlled doors, and other personnel) in order to gain access to the EMS systems. Moreover, to protect against malicious code, protective anti-malware is installed on RFC_URE6’s EMS systems, including the 4 Backup Servers. In the event of malicious code detection, the anti-malware is configured to automatically quarantine the impacted area and send an event to a monitoring software. That software then generates and sends an alert to the appropriate Support Team for review and to take the appropriate actions. Finally, the issue was quickly identified and corrected by the personnel involved. While the patch assessment was completed 20 days beyond the initial CIP-007-3a 30 day requirement, timely identification of the issue under the CIP-007-6 program ensured that the patch was ultimately assessed and added to the DPP within the requisite post-assessment timeframe under CIP-007-6. In other words, while the assessment was delayed under CIP-007-3a, the patch was added in a timely manner to the DPP under CIP-007-6. No harm is known to have occurred. | To mitigate this issue, RFC_URE6 completed a documented patch assessment immediately upon discovering the issue, and the patch was added to the DPP. To prevent such human performance issues in the future, all responsible personnel will be appropriately trained on the process enhancements. Specifically, RFC_URE6 enhanced its CIP-007-6 patch assessment process to include up-to-date information on current EMS products and software versions as part of the documentation compiled and used by the EMS patch assessment team in their regular assessment meetings. The patch assessment process was enhanced to provide additional verification process steps (e.g., sign-offs of assessment determinations by other team members).
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017368 | CIP-006-6 | R2; R2.1 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-006-6 R2.1. Following an evacuation, personnel were returning to work by way of a door at the rear of the building. The rear door is located at ground level and leads to a stairwell between the basement and first floor, providing access to the basement, first and second floors of the building. On the first floor (just off the stairwell in a small vestibule), is an access point to a Physical Security Perimeter (PSP) hallway. On this day, an employee new to the building and not authorized for unescorted physical access to the PSP, mistakenly entered the first floor doorway as opposed to the second floor doorway from which he had originally exited at the time of the evacuation. Disoriented, he then entered the vestibule and proceeded through the access point leading to the PSP hallway by piggybacking behind an authorized employee. That authorized employee had correctly used his two-factor access credentials to open the door, but was unaware of anyone behind him. Once through the door, the new employee proceeded to the end of the hallway only to realize he was in the wrong area. He then turned around in the direction from which he came and exited the secure area. As the employee was exiting the vestibule, he was stopped by a Facilities Manager and asked where he was coming from and why he was in the secure area. The employee responded that he was not familiar with the area as he was new to the building and that he was not aware that he was in a secure area. The employee's lack of awareness is the root cause of this noncompliance. The Facilities Manager provided awareness of the secure area to the employee and then immediately reported the incident to the physical security department. The hallway that the employee entered leads to several badge controlled rooms within which Cyber Assets reside. Given the badge controlled doors, the employee was not able to enter any of the secure rooms and gain access to the Cyber Assets therein. The employee was in the PSP hallway for approximately 2 minutes and was not escorted during that time as required under CIP-006-6, R2, P2.1. In the second issue, three visitors were appropriately logged and escorted by authorized personnel into a PSP to participate in a scheduled meeting. During a break, two of the visitors were appropriately escorted to the men’s room by an authorized employee. However, after the visitors entered the men’s room, the escort left the area in violation of RFC_URE6’s PSP visitor/escort policies, allowing the visitors to return to the meeting room on their own. After returning to the meeting room, one of the visitors asked if he could again leave the meeting room and go down the hall to fill his water bottle at a water fountain. Believing that his colleague (who had escorted the gentlemen to the men’s room) was still in the hallway, and needing to remain in the meeting room as an escort with the two other visitors, the employee permitted the visitor’s request not realizing that his colleague was not in the hallway to serve as an escort. This incorrect belief is another root cause of this noncompliance. As the visitor was returning to the meeting room from the water fountain, a manager sitting in his office located adjacent to the meeting room noticed an unfamiliar person walking unescorted in the hallway. He exited his office to investigate, but the visitor had already returned to the meeting room and was no longer in the hallway. The manager then proceeded to the PSP access point to review the visitor logs. Upon verifying that there were in fact visitors logged into the PSP that day, the manager immediately contacted the manager of control room operations and the physical security office to notify them of a possible escorting issue. Review of the security footage shows that the visitors walked directly to their destinations (i.e., men’s room and the water fountain) and back to the meeting room. The duration of first issue was approximately two minutes. The duration of the second issue was approximately two minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE6’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP-006-6 requirements. Moreover, the Plan expressly prohibits authorized personnel from allowing unauthorized access on their credentials, and requires that visitors be appropriately logged and continuously escorted while within a PSP. In the instances described, certain aspects of these security protocols were not followed, but nonetheless the issues were promptly identified and reported upon discovery. The subsequent investigation and review determined that no Cyber Assets were accessed or compromised by the unauthorized employee and unescorted visitors, and the duration of each incident was limited to no more than 2 minutes. Furthermore, effective additional controls were in place to protect against unauthorized, unmonitored access to cyber assets (e.g., badge controlled secure PSP rooms, alarms, and authorized personnel monitoring) and ensured immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) provided internal coaching to the individual(s) involved in the incidents; 2) developed and implemented targeted visitor control program awareness measure(s) to reinforce visitor and escorting responsibilities at the outset; 3) developed a role within the System Operations area to physically man the access point door(s) upon re-entry into the PSP after an evacuation emergency; 4) performed an assessment to determine the feasibility of creating additional security measures at the rear access point to the PSP (e.g. create a man-trap, egress only, etc.); and 5) established, based upon the assessment recommendation(s), an implementation plan for the additional security measure(s) as determined feasible.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2016016475 | CIP-006-6 | R1 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-006-6 R1. At approximately 8:47 A.M., RFC_URE7 experienced a Physical Access Control System (PACS) failure at its headquarters following a brief power loss. A single controller (which controls seven doors to the Physical Security Perimeter (PSP)) failed. When this failure occurred, four of the doors worked as designed and defaulted to “secure,” meaning the doors could not be opened. The remaining three doors failed to function as designed and instead could be opened by any RFC_URE7 access card and did not require a pin for dual authentication. RFC_URE7 employees immediately identified the issue, notified security by 9:00 a.m., and began manning the doors. By 9:35 a.m., RFC_URE7 security established alternate physical access control measures at all PSP doors, including security personnel checking RFC_URE7-issued IDs, cross-referencing the IDs with an authorized access list, and then manually entering the names into an access log. The PACS was restored by 11:26 a.m. The root cause of the controller failure was a wiring issue, which, after restoring power to the controller, adversely influenced the door card reader and electronic locking mechanism. This involves the management practice of verification, which includes taking steps to confirm that equipment is working as intended. The duration of the noncompliance was approximately 1 hour. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. RFC_URE7 immediately identified the noncompliance and began implementing security controls to ensure only individuals with unescorted access were permitted into the PSPs, thus reducing the time that there was an opportunity for unauthorized individuals to enter the PSP. Additionally, a RFC_URE7-issued access card was still required to enter the PSP, thus reducing the likelihood that an intruder could gain access to the PSP during the noncompliance. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) determined the cause of the failure, which was redundant or extraneous wiring. Upon determining the cause of the failure, RFC_URE7 developed a plan to repair or neutralize the cause. Also, RFC_URE7 completed the plan to remove, or neutralize, the bad wiring; 2) replicated the controller failure by intentionally powering it down and verified that all doors “fail secure” as intended; 3) conducted identical tests at other PSPs to ensure similar issues did not exist at other locations; and 4) updated the maintenance procedure to include functional testing of new equipment prior to commissioning in production
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2016016595 | CIP-006-6 | R2 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-006-6 R2. There were two sets of contractors performing construction work inside one of RFC_URE7’s Physical Security Perimeters (PSPs). Each set of contractors (visitors) was assigned an official escort. Around noon, one set of contractors left for a lunch break. As those contractors were returning from lunch, the other set of contractors were on their way out of the PSP. The escort for the exiting group allowed the first group to come back into the PSP, assuming that their escort was already inside the PSP waiting for them. The moment the construction crew entered the PSP, a System Supervisor inside the PSP noted that these visitors did not have an escort, and requested that the contractors exit the PSP. The visitors were always within view of the System Supervisor. The brief (approximately 30 seconds) breakdown in the escorted visitor policy was immediately reported to Corporate Security. The root cause was an error on the part of the employee in not verifying that the contractors’ escort was with them. The cause involves the management practice of workforce management in that additional training or coaching could have prevented the issue. This issue is not widespread as evidenced by the supervisor immediately identifying and mitigating the noncompliance. The duration of the noncompliance was approximately 1 minute. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The contractors were inside the PSP without their assigned escort for less than a minute and were always within view of the System Supervisor, thus reducing the possibility that the contractors could take an action to compromise the BPS. The System Supervisor immediately identified and mitigated the noncompliance by requiring the visitors to exit the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE7 issued a verbal reminder to the escort who permitted the contractors to enter the PSP without an escort. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016016587 | CIP-010-2 | R1 | RFC_URE8 submitted a Self-Report stating that it had an issue with CIP-010-2 R1. RFC_URE8's overall change management program includes two key features one program that identifies the key work information, including the scope requested, and another program that facilitates the process and documentation for the authorization step of baseline changes for service tickets. These two programs work to ensure that changes to in-scope NERC CIP Assets are properly authorized. In addition to these controls, RFC_URE8 also performs monthly baseline monitoring as an additional detective control to identify unauthorized changes. When unauthorized changes are detected during the monthly baseline monitoring, RFC_URE8 performs an investigation to determine the appropriate next steps. RFC_URE8 identified all of the instances of noncompliance discussed below through its monthly baseline monitoring. In the first instance of noncompliance, a change ticket was submitted and pending an authorization for the application of patches to a domain controller. However, an associate performed additional work on the domain controller in preparation for the change that went beyond the scope of work authorized in the corresponding change ticket. Specifically, the associate removed three applications from the domain controller that were no longer necessary. In the second instance of noncompliance, a change authorization request was submitted for changes to EACMS firewalls. However, the responsible individual completed the work before the authorization process was completed. In the third instance of noncompliance, an associate submitted a change authorization request to apply security patches to eight EACMS hosts. However, the associate completed the work before the authorization process was completed. The root cause of these instances of noncompliance was a lack of understanding of the overall change management process by responsible employees at RFC_URE8. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees, and asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although executing changes on CIP assets without proper authorization could potentially introduce system instability or affect functionality, these risks were mitigated by the following factors. First, RFC_URE8 identified all of these instances of noncompliance through its monthly monitoring of baselines. This additional internal, detective control allowed RFC_URE8 to quickly identify these issues and limit their duration. Second, in all of the instances, RFC_URE8 had completed security control impact assessments pursuant to CIP-010-2 R1.4 prior to implementing the change. These assessments would have alerted RFC_URE8 to any impacts the changes may have had on the cyber security controls in CIP-005 and CIP-007. ReliabilityFirst notes that the unauthorized changes did not introduce attack vectors from outside sources and did not adversely impact the affected devices. No harm is known to have occurred. | To mitigate this issue, RFC_URE8 will complete the following mitigation activities by June 29, 2017: 1) issued a reminder email message of the need to have authorization prior to the implementation of a change to all users of the authorization program; 2) reviewed procedure for configuration controls and ports management and made updates to further support the need to have authorization prior to implementing a baseline impacting change; 3) held a “Lunch and Learn” opportunity for performers around CIP-010 and change management process expectations; 4) created training materials for stronger awareness of CIP-010, and change management expectations training will cover: Concepts of CIP-010, associated management documents, Training and Reference Material and Job Aids that RFC_URE8 uses for compliance with CIP-010, and will include hands on exercises in the authorization program with examples of common day-to-day activities; 5) will conduct “Train the Trainer” sessions to teach local trainers the training materials. At least two associates in each region will be trained; and 6) will deliver training to associates of relevant groups.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2016016586 | CIP-010-2 | R1 | RFC_URE9 submitted a Self-Report stating that it had an issue with CIP-010-2 R1. RFC_URE9's overall change management program includes two key features one program that identifies the key work information, including the scope requested, and another program that facilitates the process and documentation for the authorization step of baseline changes for service tickets. These two programs work to ensure that changes to in-scope NERC CIP Assets are properly authorized. In addition to these controls, RFC_URE9 also performs monthly baseline monitoring as an additional detective control to identify unauthorized changes. When unauthorized changes are detected during the monthly baseline monitoring, RFC_URE9 performs an investigation to determine the appropriate next steps. RFC_URE9 identified all of the instances of noncompliance discussed below through its monthly baseline monitoring. In the first instance of noncompliance, a change ticket was submitted and pending an authorization for the application of patches to a domain controller. However, an associate performed additional work on the domain controller in preparation for the change that went beyond the scope of work authorized in the corresponding change ticket. Specifically, the associate removed three applications from the domain controller that were no longer necessary. In the second instance of noncompliance, an associate submitted a change authorization request to apply security patches to eight EACMS hosts. However, the associate completed the work before the authorization process was completed. In the third instance of noncompliance, an associate was performing troubleshooting activities on a server. The associate made changes to the device during the troubleshooting without submitting a change authorization request. The root cause of these instances of noncompliance was a lack of understanding of the overall change management process by responsible employees at RFC_URE9. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees, and asset and configuration management, which includes controlling changes to assets and configuration items and baselines. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although executing changes on CIP assets without proper authorization could potentially introduce system instability or affect functionality, these risks were mitigated by the following factors. First, RFC_URE9 identified all of these instances of noncompliance through its monthly monitoring of baselines. This additional internal, detective control allowed RFC_URE9 to quickly identify these issues and limit their duration. Second, in all of the instances, RFC_URE9 had completed security control impact assessments pursuant to CIP-010-2 R1.4 prior to implementing the change. These assessments would have alerted RFC_URE9 to any impacts the changes may have had on the cyber security controls in CIP-005 and CIP-007. ReliabilityFirst notes that the unauthorized changes did not introduce attack vectors from outside sources and did not adversely impact the affected devices. No harm is known to have occurred. | To mitigate this issue, RFC_URE9 will complete the following mitigation activities by June 29, 2017: 1) issued a reminder email message of the need to have authorization prior to the implementation of a change to all users of the authorization program; 2) reviewed procedure for configuration controls and ports management and made updates to further support the need to have authorization prior to implementing a baseline impacting change; 3) held a “Lunch and Learn” opportunity for performers around CIP-010 and change management process expectations; 4) created training materials for stronger awareness of CIP-010, and change management expectations training will cover: Concepts of CIP-010, associated management documents, Training and Reference Material and Job Aids that RFC_URE9 uses for compliance with CIP-010, and will include hands on exercises in the authorization program with examples of common day-to-day activities; 5) will conduct “Train the Trainer” sessions to teach local trainers the training materials. At least two associates in each region will be trained; and 6) will deliver training to associates of relevant groups.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2016016640 | CIP-007-6 | R4 | RFC_URE9 submitted a Self-Report stating that it had an issue with CIP-007-6 R4. During an internal review to evaluate its readiness for CIP-007 R4, RFC_URE9 reviewed all devices and found two protection relay devices classified as Medium Impact Bulk Electric System (BES) Cyber Assets that did not have logging settings enabled. Because CIP-007 R4 requires logging of events according to BES Cyber System or Cyber Asset capability, the first step in RFC_URE9’s initial CIP version 5 implementation project was to identify those systems or assets that were capable of such logging. However, RFC_URE9 missed the security event logging capabilities of these devices (i.e., relays) during this initial device capability analysis. Notably, the relays were the only missed devices out of numerous devices that were analyzed during the implementation project. Because the logging capabilities of these two relays were not initially identified, settings to enable security logging for these two devices were neither created nor deployed during the CIP version 5 implementation project. The logging capabilities were later identified and incorporated into a security technical specification, which was then used during the internal review to identify that these two relays did not have logging enabled. The root cause of this noncompliance was insufficient processes to evaluate security logging capabilities at the time the initial evaluation was performed. In short, RFC_URE9’s security technical specification document, which is now used as part of the capability review and change approval process, was not available at the time when work orders were issued to complete the analysis. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during the period of time when the devices were not performing logging, RFC_URE9 maintained the ability to track all access paths through other security event logging systems. Specifically, all remote access is logged at an intermediate jump server requiring two factor authentication. Furthermore, physical access is logged via card readers or cyberlock systems. Second, remote access communications to BES Cyber Assets at the relevant substations are serial based with no routable protocol, meaning that these devices do not use any routable connectivity. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) validated completeness of Security Technical Specification; 2) reviewed Device Settings to ensure logging enabled for capable devices; 3) issued relay settings to enable security event logging; 4) changed relay settings to enable security event logging at the substation; 5) provided training to relevant group covering CIP-007 system security controls and Security Technical Specification; and 6) changed relay settings to enable security event logging at the substation. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 10 (RFC_URE10) | NCRXXXXX | RFC2016016628 | CIP-004-6 | R2 | RFC_URE10 submitted a Self-Report stating that it had an issue of CIP-004-6 R2. A contractor was granted electronic access to RFC_URE10’s Physical Access Control System (PACS) without completing the required security training. As background, RFC_URE10 sent a contractor (receptionist) the required pre-hire training via email before coming onsite. The email instructed the contractor to log into RFC_URE10’s online training center and complete two specific training modules of the three available modules. The contractor mistakenly completed the incorrect training, the Code of Conduct training instead of the security training. The HR Analyst, who is tasked with checking that the required training is complete before completing the onboarding process, mistakenly thought that the correct training was completed and approved the contractor for onboarding. The contractor first signed into RFC_URE10's PACS ten days after her start date. RFC_URE10 identified the issue nine days later, through an internal control relating to new hires where, upon starting work, a second HR Analyst merges the contractor’s pre-hire account into a new account and verifies that proper training is completed. Immediately upon discovery of the issue, the contractor took the required training. The root cause was the HR Analyst’s error in not diligently reviewing the completed training despite clear indicators in the portal alerting the analyst that training was not completed. This involves the management practice of workforce management, including training on the importance of following the procedure. Also, it is important to note that RFC_URE10’s secondary verification control, where the second analyst checked to confirm that training information was accurate, was successful in identifying the noncompliance. The duration of the noncompliance was approximately sixteen days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The contractor did not have physical access into any Physical Security Perimeters or electronic access to any Bulk Electric System Cyber Systems. Rather, the contractor had read-only access to the PACS with limited functionality (“swipe and show” to the reception area front door to confirm that the badge photo matched the individual entering). The contractor was trained in the proper usage of RFC_URE10’s PACS and used the system appropriately. Accordingly, this limited access reduced the likelihood that the contractor could handle the information in a way that would put the BPS at risk of compromise. Additionally, RFC_URE10 quickly self-identified and mitigated the issue, thus reducing the amount of time the BPS was put at any increased risk as a result of the contractor not receiving the proper security training prior to RFC_URE10 granting electronic access. No harm is known to have occurred. | To mitigate this issue, RFC_URE10: 1) had the contractor complete the security orientation training; and 2) discussed the importance of following the procedure with the HR Analyst. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 11 (RFC_URE11) | NCRXXXXX | RFC2017017366 | CIP-007-3a | R3; R3.1 | RFC_URE11 submitted a self-log stating that it had an issue of CIP-007-3a R3.1. Having completed a compliance investigation of the issue, RFC_URE11 determined that a possible violation had occurred involving CIP-007-3a R3.1. Specifically, a patch was released, which was applicable to versions of backup software up to and including 7.7.1. At the time of the release, the patch assessment team believed that RFC_URE1 energy management system (EMS) was in the process of installing backup version 7.7.2, which was released in earlier, on its 4 servers. This incorrect belief and the reliance on that belief is the root cause of the noncompliance. The patch assessment team did not verify this belief, however, and as a result a documented assessment of the patch was not performed within the required 30 day timeframe under CIP-007-3a R3.1. Subsequently, the vendor released software version 7.7.3. It was at this time, while assessing version 7.7.3, that the assessment team discovered that version 7.7.2 had not in fact been installed as it did not include a security release. Upon realizing the oversight, the patch was immediately assessed, documented, and then added to the EMS Deferred Patch Plan (DPP), as required under CIP-007-6 R2.1 to coincide with the scheduled implementation of version 7.7.3, which itself includes the security fix addressed by the patch. The duration of the noncompliance was approximately eight days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, RFC_URE11’s EMS systems are designed to include several layers of physical and electronic security controls, including but not limited to: secured Electronic Security Perimeters, enclosed Physical Security Perimeters (PSPs), continuous logging and monitoring, and access management controls limiting access rights solely to authorized personnel. With this in mind, an individual would need to transgress several physical security controls around the PSP (i.e., security guards, unique pin and badge controlled doors, and other personnel) in order to gain access to the EMS systems. Moreover, to protect against malicious code, protective anti-malware is installed on RFC_URE11’s EMS systems, including the 4 Backup Servers. In the event of malicious code detection, the anti-malware is configured to automatically quarantine the impacted area and send an event to a monitoring software. That software then generates and sends an alert to the appropriate Support Team for review and to take the appropriate actions. Finally, the issue was quickly identified and corrected by the personnel involved. While the patch assessment was completed 20 days beyond the initial CIP-007-3a 30 day requirement, timely identification of the issue under the CIP-007-6 program ensured that the patch was ultimately assessed and added to the DPP within the requisite post-assessment timeframe under CIP-007-6. In other words, while the assessment was delayed under CIP-007-3a, the patch was added in a timely manner to the DPP under CIP-007-6. No harm is known to have occurred. | To mitigate this issue, RFC_URE11 completed a documented patch assessment immediately upon discovering the issue, and the patch was added to the DPP. To prevent such human performance issues in the future, all responsible personnel will be appropriately trained on the process enhancements. Specifically, RFC_URE11 enhanced its CIP-007-6 patch assessment process to include up-to-date information on current EMS products and software versions as part of the documentation compiled and used by the EMS patch assessment team in their regular assessment meetings. The patch assessment process was enhanced to provide additional verification process steps (e.g., sign-offs of assessment determinations by other team members).
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 11 (RFC_URE11) | NCRXXXXX | RFC2017017369 | CIP-006-6 | R2; R2.1 | RFC_URE11 submitted a self-log stating that it had an issue of CIP-006-6 R2.1. Following an evacuation, personnel were returning to work by way of a door at the rear of the building. The rear door is located at ground level and leads to a stairwell between the basement and first floor, providing access to the basement, first and second floors of the building. On the first floor (just off the stairwell in a small vestibule), is an access point to a Physical Security Perimeter (PSP) hallway. On this day, an employee new to the building and not authorized for unescorted physical access to the PSP, mistakenly entered the first floor doorway as opposed to the second floor doorway from which he had originally exited at the time of the evacuation. Disoriented, he then entered the vestibule and proceeded through the access point leading to the PSP hallway by piggybacking behind an authorized employee. That authorized employee had correctly used his two-factor access credentials to open the door, but was unaware of anyone behind him. Once through the door, the new employee proceeded to the end of the hallway only to realize he was in the wrong area. He then turned around in the direction from which he came and exited the secure area. As the employee was exiting the vestibule, he was stopped by a Facilities Manager and asked where he was coming from and why he was in the secure area. The employee responded that he was not familiar with the area as he was new to the building and that he was not aware that he was in a secure area. The employee's lack of awareness is the root cause of this noncompliance. The Facilities Manager provided awareness of the secure area to the employee and then immediately reported the incident to the physical security department. The hallway that the employee entered leads to several badge controlled rooms within which Cyber Assets reside. Given the badge controlled doors, the employee was not able to enter any of the secure rooms and gain access to the Cyber Assets therein. The employee was in the PSP hallway for approximately 2 minutes and was not escorted during that time as required under CIP-006-6, R2, P2.1. In the second issue, three visitors were appropriately logged and escorted by authorized personnel into a PSP to participate in a scheduled meeting. During a break, two of the visitors were appropriately escorted to the men’s room by an authorized employee. However, after the visitors entered the men’s room, the escort left the area in violation of RFC_URE11’s PSP visitor/escort policies, allowing the visitors to return to the meeting room on their own. After returning to the meeting room, one of the visitors asked if he could again leave the meeting room and go down the hall to fill his water bottle at a water fountain. Believing that his colleague (who had escorted the gentlemen to the men’s room) was still in the hallway, and needing to remain in the meeting room as an escort with the two other visitors, the employee permitted the visitor’s request not realizing that his colleague was not in the hallway to serve as an escort. This incorrect belief is another root cause of this noncompliance. As the visitor was returning to the meeting room from the water fountain, a manager sitting in his office located adjacent to the meeting room noticed an unfamiliar person walking unescorted in the hallway. He exited his office to investigate, but the visitor had already returned to the meeting room and was no longer in the hallway. The manager then proceeded to the PSP access point to review the visitor logs. Upon verifying that there were in fact visitors logged into the PSP that day, the manager immediately contacted the manager of control room operations and the physical security office to notify them of a possible escorting issue. Review of the security footage shows that the visitors walked directly to their destinations (i.e., men’s room and the water fountain) and back to the meeting room. The duration of first issue was approximately two minutes. The duration of the second issue was approximately two minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE11’s Physical Security Plan requires and implements controls to ensure that access points to PSPs are secured and monitored at all times in accordance with the CIP-006-6 requirements. Moreover, the Plan expressly prohibits authorized personnel from allowing unauthorized access on their credentials, and requires that visitors be appropriately logged and continuously escorted while within a PSP. In the instances described, certain aspects of these security protocols were not followed, but nonetheless the issues were promptly identified and reported upon discovery. The subsequent investigation and review determined that no Cyber Assets were accessed or compromised by the unauthorized employee and unescorted visitors, and the duration of each incident was limited to no more than 2 minutes. Furthermore, effective additional controls were in place to protect against unauthorized, unmonitored access to cyber assets (e.g., badge controlled secure PSP rooms, alarms, and authorized personnel monitoring) and ensured immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE11: 1) provided internal coaching to the individual(s) involved in the incidents; 2) developed and implemented targeted visitor control program awareness measure(s) to reinforce visitor and escorting responsibilities at the outset; 3) developed a role within the System Operations area to physically man the access point door(s) upon re-entry into the PSP after an evacuation emergency; 4) performed an assessment to determine the feasibility of creating additional security measures at the rear access point to the PSP (e.g. create a man-trap, egress only, etc.); and 5) established, based upon the assessment recommendation(s), an implementation plan for the additional security measure(s) as determined feasible.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016063 | CIP-010-2 | R1; R1.1.2 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-010-2 R1.1.2. During a review of pre- and post-scan files for an open change request, SPPRE_URE1 identified two applications on two Cyber Assets that were not included in SPPRE_URE1’s documented configuration baseline. While determining the scope of non-compliance, SPPRE_URE1 identified additional instances where three applications installed on one or more of 13 Cyber Assets was not documented in the configuration baselines. The duration of this instance of noncompliance was 164 days, beginning the effective date of the Standard, and ending the date all installed applications were documented in the configuration baselines. The root cause of this instance of noncompliance was SPPRE_URE1’s process for establishing and maintaining an accurate configuration baseline was inadequate to ensure all applications residing on SPPRE_URE1 Cyber Assets was identified and documented. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to maintain an accurate configuration baseline presents the risk that cyber systems in the test environment may not accurately reflect the cyber systems in the production environment. Thus, changes and patches to BES Cyber Systems in the production environment may not be adequately vetted before being installed. The failure to adequately test applications and patches for BES Cyber Systems before installation in the production environment can adversely affect the operation of such BES Cyber Systems and negatively impact the reliability of the BES. Notwithstanding, all Cyber Assets subject to this issue are within a secure network that has no direct connection to the Internet. Three of the applications were known but were simply not documented in SPPRE_URE1’s configuration baselines. Two of the three known applications have never had security vulnerabilities identified by the software vendor, and one of the three known applications had security patches that were consistently tracked and evaluated by SPPRE_URE1. No security vulnerabilities were unmitigated, and no harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) removed the two applications discovered during the CVA from two Cyber Assets; 2) updated baseline documentation to include all locations where the three known applications reside; 3) revised its Cyber Vulnerability Assessment process to improve the methods utilized to accurately inventory applications installed on all Cyber Assets; and 4) performed a Cyber Vulnerability Assessment. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2016016627 | CIP-007-3a | R6; R6.4 | SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-3a R6, specifically R6.4. During a routine security log review, SPPRE_URE2 discovered firewall alerts that indicated two newly installed switches used to monitor system events within SPPRE_URE2’s Electronic Security Perimeter (ESP), did not have access through the firewall to the secondary logging server; therefore logs for these two switches were not consistently retained for 90 calendar days. SPPRE_URE2 had installed two new switches that required firewall configuration changes to allow for logs to be sent from the switches and the firewalls to both the primary and the secondary syslog server so that logs were consistently captured when either syslog server was unavailable. During 29 days, there were a total of nine maintenance outages on SPPRE_URE2’s primary syslog server, and during those outages, no logs were written to the secondary syslog server. The combined time of the primary syslog server outages was less than 30 minutes. The duration of this instance of noncompliance was 119 days, beginning the date of the first primary syslog outage, and ending 90 days following the last outage of the primary syslog server. The root cause of this instance of noncompliance was lack of procedural control. SPPRE_URE2’s change control documentation did not state that configuration changes to the firewalls must be performed to implement logging to both the primary and secondary syslog servers when new switches were installed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to appropriately configure redundancy in logging for the two switches could result in loss of logs during an outage of the logging server. Had a cyber-incident occurred during a server outage, any valuable diagnostic or forensic logs would have been lost. Notwithstanding, SPPRE_URE2 utilizes a system to monitor and alarm for unauthorized access. The system is monitored during office hours by qualified personnel, and is configured to send all network traffic alerts to authorized personnel on a 24x7 basis, which increases the likelihood that SPPRE_URE2 would have detected a cyber-incident, had one occurred. The two switches reside within SPPRE_URE2’s defined Physical Security Perimeter, with access limited to only authorized personnel. Lastly, the duration of time the logs were not retained from all primary syslog server outages was less than 30 minutes collectively. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) reconfigured the firewalls to allow logs to reach the secondary syslog server; and, 2) changed the network test templates to specify that primary and secondary logging must be verified when changes to the SPPRE_URE2 network occur. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2016015996 | CIP-004-6 | R5; R5.2 | SPPRE_URE3 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-6 R5.2. An employee who had authorized unescorted physical access to the Physical Security Perimeter (PSP) transferred to a different job that did not require such access. The duration of this instance of noncompliance was three days, starting the date the employee’s physical access to the PSP was required to have been revoked, and ending the date the employee’s physical access was revoked. The root cause of this instance of noncompliance was a revocation process deficiency, i.e., lack of updated communication process to address the shortened deadline to revoke physical access under CIP-004-6 R5.2. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely revoke an employee’s physical access to the PSP has the potential to affect the reliability of the BPS by presenting a risk of unauthorized access to Bulk Electric System Cyber Assets, which could compromise the security of such assets essential to the operation of the BPS. Notwithstanding, the employee is a trusted employee who had not been terminated, but instead, transferred from a job requiring physical access to the PSP to a job not requiring such access. Additionally, the employee only had physical access. Thus, even had the employee accessed the PSP, firewalls limited connectivity to the electronic security perimeter to only recognized network users. The employee had a current personnel risk assessment and cyber security training on file. SPPRE_URE3 promptly self-identified, mitigated, and reported the noncompliance. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) revoked the transferred employee’s physical access to the PSP; 2) added its compliance department to the email distribution list for notifications of posted jobs, which alerts the department that someone may be moving into or out of a job approximately within two months before the job is vacated or filled; 3) added its compliance department to the email distribution list for notifications alerting the department that someone has been selected for a job approximately one month before the effective date of the transfer or new hire; and 4) implemented inclusion of future notifications referenced in mitigation activities #2 and #3 above in corporate wide communications within a few days of the emails being sent to the compliance department. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016596 | CIP-006-6 | R1; P1.8; P1.9; P1.10 | During a Compliance Audit, Texas RE determined that Unidentified Registered Entity 1 (TRE_URE1) had potential issues with CIP-006-6 R1, Parts 1.8, 1.9, and 1.10. Regarding TRE_URE1’s issue with CIP-006-6 R1, Parts 1.8 and 1.9, Texas RE determined that TRE_URE1 did not log entry of each individual with authorized unescorted physical access into each Physical Security Perimeter (PSP) and, correspondingly, did not retain physical access logs for such individuals for the required 90 day period. TRE_URE1 attempted to install a critical security patch on one of the servers communicating with its various Physical Access Control Systems (PACS). However, after rebooting the server, TRE_URE1 was not able to reestablish communications with its PACS, including the database used to store access logs to TRE_URE1’s PSPs. TRE_URE1 personnel then attempted to failover to a backup PACS server, but were still unable to reestablish communications with its local devices and associated databases. As a result, TRE_URE1 ultimately failed to log all authorized unescorted physical access instances into its PSPs for over 22 hours. The root cause of TRE_URE1’s issue with CIP-006-6 R1, Parts 1.8 and 1.9 was an insufficient process for managing security patch installations on its PACS servers. In particular, TRE_URE1’s existing PACS system did not include a test environment to ensure all security patches for PACS servers were adequately evaluated for their impacts on communications with field devices and associated databases. Regarding TRE_URE1’s issue with CIP-006-6 R1, Part 1.10, Texas RE determined that TRE_URE1’s documented physical security plan did not include language addressing the restriction of physical access to cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter. The root cause of this issue was that TRE_URE1 overlooked addressing CIP-006-6 R1, Part 1.10 in its physical security plan process document. The issue duration pertaining to CIP-006-6 R1 was over three months. | The issue pertaining to CIP-006-6 R1, Parts 1.8 and 1.9 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following five factors. First, throughout the duration of the issue, TRE_URE1’s PACS devices continued to function and control physical access into all affected TRE_URE1 PSPs. Second, TRE_URE1 immediately implemented its physical security plan in response to the issue, including conducting continuous roving patrols of all BES Cyber Asset areas to further control and monitor physical access while the PACS logging system was not functioning. Third, TRE_URE1 limited access to all TRE_URE1 PSPs during the PACS issue to either TRE_URE1 personnel or a single, continuously escorted vendor troubleshooting the affected systems. Fourth, TRE_URE1’s cameras monitoring affected PSP areas remained active and monitored by TRE_URE1 personnel during the issue. Fifth, TRE_URE1 did not have any Reportable Cyber Security Incidents during the duration of the issue. Texas RE has verified that TRE_URE1’s physical access controls and monitoring systems will remain in place to mitigate any risks while TRE_URE1 replaces its PACS system and creates a new test environment. No harm is known to have occurred. The issue pertaining to CIP-006-6 R1, Part 1.10 likewise posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, this noncompliance was documentary in nature. In particular, during the Compliance Audit, Texas RE determined that TRE_URE1 effectively implemented required physical access restrictions to all cabling and other nonprogrammable communications components as required, but did not document those measures. Second, duration of the documentation issue was short, lasting only approximately three months. Further, once the issue was identified, TRE_URE1 quickly revised its physical security plan to comply with CIP-006-6 R1, Part 1.10. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate the CIP-006-6 R1, Part 1.10 issue, TRE_URE1: 1) modified its physical security plan document to comply with CIP-006-6 R1, Part 1.10; and 2) provided its revised physical security plan document to affected staff. To mitigate the issue pertaining to CIP-006-6 R1, Parts 1.8 and 1.9, TRE_URE1 will complete the following actions TRE_URE1: 1) implement a new physical access control system using more current technology; and 2) build a test environment, with test panels included, in order to test the impact of a system change on the access control panels/servers.
2017-06-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016599 | CIP-005-5 | R2; P2.1; P2.2; P2.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had five instances of noncompliance pertaining to CIP-005-5 R2, Parts 2.1, 2.2, and 2.3. In particular, four TRE_URE1 employees attained Interactive Remote Access to Cyber Assets within Electronic Security Perimeters (ESPs) without using an Intermediate System. Four TRE_URE1 IT employees remotely accessed various Cyber Assets without utilizing an Intermediate System, encryption that terminated at an Intermediate System, or multi-factor authentication on five separate occasions. On each occasion, the TRE_URE1 IT personnel at issue were performing troubleshooting activities and had issues using the existing TRE_URE1 Intermediate System. As a result, the IT personnel in question opted to bypass the Intermediate System and perform troubleshooting activities on various servers without following the appropriate remote access procedures. TRE_URE1 discovered the issue through its daily system access monitoring activities and reported the issue to Texas RE during the ongoing Compliance Audit. The root cause of this noncompliance was an insufficient process to ensure all interactive remote access sessions utilized Intermediate Systems to access Cyber Assets within ESPs. In particular, TRE_URE1’s sole Intermediate System had issues fully accommodating the various IT troubleshooting activities at issue, resulting in the four IT employees bypassing that system to perform their work. The issue duration was approximately 25 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the four employees at issue had appropriate access rights to the Cyber Assets at issue and possessed valid personnel risk assessments (PRAs) during the issue duration. Second, TRE_URE1’s monitoring system detected each remote access attempt and timely issued email alerts to the proper security personnel. Third, TRE_URE1 confirmed that there have been no additional remote access instances bypassing Intermediate Systems following the five instances at issue. Finally, TRE_URE1 did not have any Reportable Cyber Security Incidents during the duration of the issue. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) terminated the last Interactive Remote Access session; 2) installed an additional Intermediate System to better accommodate all Interactive Remote Access sessions; 3) updated its applicable Interactive Remote Access process document to establish procedures for the use of an additional Intermediate System; and 4) conducted additional Intermediate Systems training for all affected employees, including specific training for the four IT employees at issue. Texas RE has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015620 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R4. Specifically, an employee of a WECC_URE1 contractor with unescorted physical access to WECC_URE1 Critical Cyber Assets (CCAs) left employment of the contractor, but the contractor failed to notify WECC_URE1 or return the contractor employee’s badge within the timeframe required by WECC_URE1’s policy. Therefore, the access of the terminated employee was not revoked within the seven calendar days required by CIP-004-3a R4. Subsequently, a WECC_URE1 security officer received the former contractor employee’s badge and notified the appropriate WECC_URE1 personnel. The badge access was later revoked. The cause of this issue was the failure of the contracting firm to follow WECC_URE1’s revocation notification procedure, as stipulated in their contract. The issue started eight days after the employee left employment of the WECC_URE1 contractor, and ended when access of the contractor in scope was completely removed, for approximately a week of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to revoke access to CCAs within seven calendar days for an employee of a WECC_URE1 contractor who no longer required such access. Failure to timely remove physical access to CCAs could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access could then be used to cause harm to CCAs essential to the operation of the bulk power system. However, the individual in scope only had unescorted physical access to CCAs at WECC_URE1’s substations, and, did not have unescorted physical access or electronic access to control centers. Additionally, further investigation showed that the individual’s badge was not used between the termination date and the revocation date. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) disabled the contractor employee’s access privileges to WECC_URE1 assets and facilities; 2) updated the its official list for physical access to WECC_URE1 CCAs and energized facilities; and 3) issued a directive to the contractor to remedy its performance. WECC has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016014 | CIP-007-6 | R5 | WECC_URE1 submitted a Self-Report stating tha it had a possible issue of noncompliance with CIP-007-6 R5 for failing to establish password complexity for a Medium Impact BES Cyber System (MIBCS). Specifically, WECC_URE1 put an MIBCS into operation with only two of the four available password character types, instead of three, as required by the Standard. The root cause was inadequate vendor support. WECC_URE1 had planned to update the password requirements on the MIBCS during a scheduled outage; however, due to technical reasons, the work was aborted and the system was returned to service without the required changes. As WECC_URE1 later attempted to make the required changes, it encountered issues. It was then unable to contact the vendor. The issue began when the Standard became mandatory and enforceable and ended when passwords were modified to meet the complexity requirements, for approximately four months of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to establish password complexity for an MIBCS, as required by CIP-007-6 R5.5. Failure to follow the password complexity requirements for an MIBCS could lead to assets that are more vulnerable to unauthorized access. If bad actors were able to successfully access a vulnerable asset, they would be able to take action that may have an adverse effect on that asset. However, WECC_URE1 implemented controls to prevent and detect any of the effects to the system. For example, the system is “air-gapped”, so that all connections to the system must go through an Intermediate System (IS), which performs security checks. The system security checks performed by the IS also provide monitoring, which would detect questionable activity being attempted. Additionally, the group of individuals with knowledge of the passwords at WECC_URE1 is limited to a small number of authorized personnel. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) changed passwords to meet complexity requirements for all system devices and accounts; and 2) updated processes and procedures. WECC has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016018 | CIP-007-3a | R3 | WECC_URE2 submitted a Self-Report stating that it had an issue with CIP-007-3a R3. WECC_URE2’s CIP standards lead discovered that he had not assessed a security patch for applicability within 30 days of the security patch being made available. WECC_URE2’s process is to use the output from a configuration analysis tool and compare it to an excel list of installed software to identify which software needs security patch assessments. Due to an error in a formula in the list, two applications were not flagged as needing to be assessed for security patches, resulting in security patches for the applications not being assessed for applicability within a timely manner. The root cause was a misconfigured formula in WECC_URE2’s security patch monitoring tool. WECC determined that this issue began when WECC_URE2 should have performed security patch assessments for applicability on the applications and ended WECC_URE2 completed its assessment of released security patches applicability to the applications, for a total of 73 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to assess security patches for applicability within 30 calendar days of the security patches being available. By not assessing applicability of security patches in a timely manner, WECC_URE2 was at risk of exploits of vulnerabilities on Critical Cyber Assets (CCAs) and Non-Critical Cyber Assets (NCCAs). which could adversely impact the reliability of the bulk power system (BPS). However, the likelihood of these events occurring were reduced because the applications were not installed on systems that provide control capabilities for the BES. WECC_URE2 implemented controls to eliminate the risks, to include administrative and technical controls; isolated networks; system port and services hardening; firewalls; authentication systems; and physical access monitoring. No harm is known to have occurred. WECC_URE2 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE2: 1) assessed the security patches for applicability; 2) corrected the formula error in the Excel spreadsheet list; and 3) tested the security patch management process to ensure its ability to identify all applications.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016621 | CIP-004-6 | R.4.1.3. | WECC_URE3 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-6 R4.1.3. WECC_URE3 failed to authorize all users who had access to its BES Cyber System Information (BCSI). Thirteen unauthorized users had logical access to WECC_URE3’s repositories of electronic BCSI. The unauthorized access was removed the day it was discovered. This issue started when the Standard became mandatory and enforceable, and ended when the unauthorized access was removed, for a total of 111 days of noncompliance. The root cause of this issue was WECC_URE3 failing to correctly configure its designated storage locations used to house BCSI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 has implemented controls to prevent unauthorized access to BCSI. It only uses two defined and logically separated storage locations for electronic BCSI and has a clearly defined procedure, including roles and responsibilities, for managing BCSI. WECC_URE3 has also implemented detective controls by performing internal checks on BCSI repository privileges, as it did in discovering this issue. WECC_URE3 uses account notification to log user access to BCSI and none of the authorized users were known to have accessed the BCSI. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) revoked unauthorized user access; 2) confirmed, through user logs, that the unauthorized users did not access the BCSI; 3) implemented a NERC CIP Access Request process within its IT Service Management application, which documents the necessary approvals for personnel access to BCSI, and maintains a list of all individuals with authorized access; 4) held a meeting with the NERC Manager and administrative team to reinforce the importance of documenting and managing all methods of access to BCSI; and 5) validated that the remaining users who have access to BCSI are authorized. WECC has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016015981 | CIP-007-6 | R4 | WECC_URE4 submitted a Self-Report stating that it had an issue with CIP-007-6 R4 Part 4.1.1 and Part 4.1.2. Specifically, WECC_URE4 reported that in preparation for a WECC audit, it identified two firewalls that were capable of being configured to log successful login attempts, failed access attempts, and failed login attempts, but were not configured to do so. The two firewalls were classified as access points to the Electronic Security Perimeter (ESP) at WECC_URE4’s control centers. The firewalls were placed into production under CIP Version 3 and configured for those requirements; however, they were not reconfigured to meet CIP-007-6 R4 Requirements. The root cause of this issue was a less than adequate process for configuration of devices as Reliability Standards and Requirements change. WECC determined that this issue began when the Standard became mandatory and enforceable for WECC_URE4, and ended when WECC_URE4 reconfigured the two firewalls to log successful login attempts, failed access attempts, and failed login attempts, for a total of 31 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to log successful login attempts and failed login attempts, and generate alerts on two firewalls. Such failure could result in WECC_URE4 not being able to identify or perform after-the-fact investigations of Cyber Security Incidents or act on the alerts generated based on the logs. This could potentially further prevent WECC_URE4 from being able to identify how an attacker compromised a system to prevent the same or similar attacks in the future. However, the likelihood of the risk occurring was reduced by the controls WECC_URE4 had implemented. WECC_URE4 utilizes a security information and event management (SIEM) that sends events to an alert dashboard, that displays events as they occur, as well as sends an email. Additionally, WECC_URE4 has separated networks; malicious software prevention tools are installed on all BES Cyber Assets within the ESP; and WECC_URE4 uses Access Control Lists to ensure SSH and Telnet are only originated from inside the ESP. No harm is known to have occurred. WECC_URE4 has no previous violations of this Standard and Requirement. | To mitigate this issue, WECC_URE4: 1) configured the two firewalls to log successful login attempts, failed access attempts, and failed login attempts; and 2) updated its procedures to include a checklist with required task to ensure all CIP Standards and Requirements are reviewed and complied with, prior to commissioning new hardware.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016463 | CIP-007-6 | R2 | WECC_URE4 submitted a Self-Report stating that it had an with CIP-007-6 R2 Part 2.1. Specifically, WECC_URE4 reported that, although it had a comprehensive patch management process that includes identification of a source or sources of cyber security patches for applicable Cyber Assets, it did not include a cyber security patch source or sources for all third-party software installed on its Cyber Assets at its control center. The root cause of this issue was a lack of understanding on how in-depth associated software residing on Cyber Assets should be evaluated for applicable cyber security patches. WECC determined that this issue began when the Standard became mandatory and enforceable for WECC_URE4, and ended when WECC_URE4 added a source or sources to its process of cyber security patches for all third-party software, for a total of 202 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to include a cyber security patch source or sources for all third-party software installed on its Cyber Assets, which could potentially result in an attacker using known attack methods to gain control of a Cyber Asset. If control was established the attacker could cause reboots, freezes, or install malware on the systems, thereby affecting the reliability of the bulk power system (BPS). However, the likelihood of the risk occurring was reduced by the controls WECC_URE4 had implemented. WECC_URE4 utilizes security information and event management (SIEM) that sends events to an alert dashboard, that displays events as they occur, as well as sends an email. Additionally, WECC_URE4 has segmented networks; malicious software prevention tools are installed on all BES Cyber Assets within the ESP; and WECC_URE4 uses Access Control Lists to ensure SSH and Telnet are only originated from inside the ESP. No harm is known to have occurred. WECC_URE4 has no previous violations of this Standard and Requirement. | To mitigate this issue, WECC_URE4: 1) identified all software running on its Cyber Assets; 2) updated its procedure to include a source to track cyber security updates for its software inventory; and 3) updated its evaluation tracking spreadsheets to evidence evaluation of all applicable security updates.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016016464 | CIP-007-6 | R3 | WECC_URE4 submitted a Self-Report stating that it had an issue with CIP-007-6 R3 Part 3.3. Specifically, WECC_URE4 reported that, although it had a method to deter, detect, or prevent malicious code, it did not document and implement a process for the updating of signatures or patterns on its Intrusion Detection System/Intrusion Protection System (IDS/IPS). WECC_URE4 implemented the IDS/IPS system to deter, detect, and prevent malicious code for those Cyber Assets that do not support traditional malware prevention software. The IDS/IPS is an add-on module for its Electronic Access Point. The root cause of this issue was a lack of understanding of the applicability of CIP-007-6 R3 Part 3.3 to its IDS/IPS. WECC determined that this issue began when the Standard became mandatory and enforceable for WECC_URE4, and ended on when WECC_URE4 updated the signatures or patterns for its IDS/IPS, for a total of 143 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to implement a process for updating the signatures or patterns for its IDS/IPS, which increases the risk of an attacker gaining access to WECC_URE4’s Cyber Assets. The attacker could then force reboots of the system, cause system freezes, or insert malware to the Cyber Assets within the MIBCS; thereby, potentially affecting the reliability of the BES. However, the likelihood of the risk occurring was reduced by the controls WECC_URE4 had implemented. WECC_URE4 utilizes security information and event management (SIEM) that sends events to an alert dashboard, that displays events as they occur, as well as sends an email. Additionally, WECC_URE4 has segmented networks; malicious software prevention tools are installed on all BES Cyber Assets within the ESP; and WECC_URE4 uses Access Control Lists to ensure SSH and Telnet are only originated from inside the ESP. No harm is known to have occurred. WECC_URE4 has no previous violations of this Standard and Requirement. | To mitigate this issue, WECC_URE4: 1) created a process for updating the signatures or patterns for its IDS/IPS; 2) updated signatures or patterns for its IDS/IPS; and 3) added it IDS/IPS to the regular security update cycle.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2016016707 | CIP-011-2 | R1.2. | WECC_URE5 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-011-2 R1 Part 1.2. WECC_URE5 reported that it did not maintain BES Cyber System Information (BCSI) in accordance with its information protection program procedures. A WECC_URE5 employee discovered that WECC_URE5 had received an unencrypted email which included BCSI from an external contractor. The BCSI included drawings and diagrams regarding WECC_URE5’s Physical Security Perimeters (PSPs) and the security equipment at WECC_URE5’s medium facilities. This issue started when an external contractor sent an email to WECC_URE5 that included unencrypted BSCI, and ended when WECC_URE5 confirmed all BCSI had been deleted, for a total of 34 days of noncompliance. The root cause of this issue was a contractor of WECC_URE5 did not follow documented procedures for handling BCSI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 implemented controls to prevent unauthorized access to the BCSI. Specifically, WECC_URE5 implemented a BCSI policy requiring encryption during transit for BCSI. Additionally, WECC_URE5 implemented detective controls which discovered this issue of noncompliance. WECC_URE5 also provided BCSI training to its contractors, and requires annual BCSI training for its employees. No harm is known to have occurred. | To mitigate this issue, WECC_URE5: 1) deleted the email containing BCSI; 2) confirmed the external contractor and the contractor’s employees deleted the email containing BCSI; and 3) created CIP-011-2 reference guides for its external contractors. WECC has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2016016644 | CIP-007-6 | R5.6 | WECC_URE6 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-6 R5 Part 5.6. While performing its annual password change process, WECC_URE6 discovered that one control system employee’s Active Directory (AD) administrator user account password had not been changed to achieve compliance with CIP-007-6 R5.6. The employee had authorized administrator access to Cyber Assets at WECC_URE6’s high and medium facilities. WECC_URE6 investigated the issue and determined that the AD flag for "password never expires" was inadvertently set for this account during WECC_URE6's initial build of its AD system, most likely to prevent WECC_URE6 from being locked out of the system during the build. WECC_URE6 utilizes a tool to audit its AD and to provide notifications of expiring passwords. WECC_URE6's AD group policy was configured to enforce password changes for all other accounts. However, the default settings on the tool were set to honor the "password never expires" flag as well, as the setting had a valid use on service and shared accounts. The setting should have been removed when the tool was reconfigured for the needs of WECC_URE6 but was not. Thus, a password change reminder notification was not sent to the user of this account. Under CIP Version 3, WECC_URE6 reviewed all user accounts to ensure passwords had been changed during the current calendar year utilizing a manual process for password changes. As part of its transition to CIP Version 6, WECC_URE6 handled individual user accounts exclusively by group policy. This issue started when when the password should have been changed to demonstrate compliance by the date the Standard and Requirement became mandatory and enforceable to WECC_URE6 and ended when WECC_URE6 changed the password, for a total of 150 days of noncompliance. The root cause was a lack of awareness of the default AD group policy settings on WECC_URE6’s auditing tool and the effect of those settings on its compliance obligation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 does not allow remote access to its control system private network; used a tool as an automated password and account management systems; required two-factor authentication through an Intermediate System; and utilized centralized account management systems including account lock-out after unsuccessful login attempts. WECC_URE6 discovered the expired password during its annual review of password changes. The employee to whom the account belonged had authorized access, a current Personnel Risk Assessment (PRA) and current CIP training. WECC_URE6 has documented policies regarding the use and approval of accounts, awareness of polices, and an abidance to a culture of compliance. WECC_URE6 verified that no unauthorized access attempts were made on the account in scope. Based on the controls in place, WECC determined that the issue had a minimal likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) changed the password; 2) removed the “password never expires” flag on the account, allowing the account to be properly managed by automation; 3) confirmed that no additional accounts were set to “password never expires;” and 4) reconfigured a tool to report daily on individuals whose user accounts are set to “password never expires.” WECC has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2017017461 | CIP-006-6 | R1 | WECC_URE7 submitted a Self-Report stating that it had an issue with CIP-006-6 R1 Part 1.9. Specifically, while performing its quarterly review of access authorization records, WECC_URE7 discovered its Physical Access Control System (PACS) was not configured correctly to retain physical access logs of entry to its two Physical Security Perimeters (PSPs) to for at least 90 calendar days. The PACS operating software was set to a default access log retention period of 90 calendar days. The root cause was a less than adequate understanding by its PACS service vendor of the default date configuration settings as it relates to compliance with CIP-006-6 R1. WECC determined that this issue began when the Standard and Requirement became effective for WECC_URE7, and ended when the physical access logs started generating, for a total of 5 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 failed to retain physical access logs for at least 90 calendar days. Such failure could result in WECC_URE7’s inability to support security event and incident response or system restoration activities, thereby, potentially affecting the reliable operation of the bulk power system (BPS) by allowing BES Cyber Assets to be compromised should an intruder gain access without WECC_URE7’s knowledge. However, the likelihood of the risk occurring was reduced by the controls WECC_URE7 had implemented. WECC_URE7 discovered this issue while performing an in-depth quarterly review of unescorted physical access. Additionally, WECC_URE7 contracted a security firm to configure and maintain its PACS which ensures that specialized software and hardware functions are supported for the PACS. WECC_URE7 has policies and training for management and employees with a focus on awareness of policies, and an abidance to a culture of compliance. All unescorted physical access for the period of time in question as verified to be only by people with authorized physical access. No harm is known to have occurred. WECC considered WECC_URE7's CIP-006 compliance history in determining the disposition track. WECC_URE7 has no relevant prior noncompliance with this Standard or Requirement. | To mitigate this issue, WECC_URE7: 1) instructed its PACS vendor’s authorized service representative to increase the log data retention time from 90 calendar days to 365 days; 2) verified the physical access log retention settings were functioning properly; 3) initiated monthly access reviews; and 4) reviewed its BES Cyber Security Policies to ensure it adequately speaks to the time requirements for retention of automated logging of physical access. WECC verified completion of those activities.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2016016557 | CIP-002-5.1 | R1 | WECC_URE8 submitted a Self-Report stating that it had an issue with CIP-002-5.1 R1. Specifically, WECC_URE8’s reported that the language throughout its R1 process document had terminology that referred to CIP-002-3 rather than CIP-002-5.1, and WECC_URE8 did not ensure all applicable asset types, as listed in CIP-002-5.1(R1.i through R1.vi), were included during its identification and documentation of the R1.1, R1.2, and R1.3 lists. The cause was due to WECC_URE8's less than adequate understanding of CIP-002-5.1., therefore WECC_URE8 did not update its documentation accordingly WECC determined that this issue began on when the Standard and Requirement became mandatory and enforceable to WECC_URE8, and ended when WECC_URE8 updated its process documentation to include the current Standard version terminology, and completed its evaluation and documentation for R1, for a total of 298 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE8 failed to ensure all applicable asset types, as listed in CIP-002-R.1.vi, were included in its process. Specifically, WECC_URE8’s process did not include consideration of specific assets as per R1.vi. Failure to identify the assets could potentially result in a loss, compromise, or misuse of BES Cyber Systems like Protection Systems, or UFLS and UVLS relays which could impact the reliable operation of the bulk power system (BPS). However, the likelihood of the risk occurring was minimal as WECC_URE8 did consider and had no applicable distribution assets in its determination of the low impact facility list, although WECC_URE8 did not document the consideration in its documentation. No harm is known to have occurred. WECC considered WECC_URE8's CIP-002 compliance history in determining the disposition track. WECC_URE8 had no relevant prior noncompliance Standard and Requirements . | To mitigate this issue, WECC_URE8: 1) updated its documentation to reflect categorization criteria vocabulary of CIP-002-5 2) integrated its function into its documented process to include: a. identification of each of the high impact BES Cyber Systems per Attachment 1, Section 1, if any, at each asset. b. identification of each of the medium impact BES Cyber Systemsper Attachment 1, Section 2, if any, at each asset. c. identification of each asset that contains a low impact BES Cyber System related per Attachment 1, Section 3, if any. 3) identified each asset in accordance with CIP-002-5 Attachement1, Section 3.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC2016016122 | CIP-007-6 | R4 | WECC_URE9 submitted a Self-Report stating that it had an issue with CIP-007-6 R2 Part 4.2.2. WECC_URE9 uses an enterprise security information and event management (SIEM) system to generate alerts associated with event logging as required by CIP-007-6 R4 P4.2.2. Logs themselves are generated by the individual devices, but each device sends its logs to the SIEM. The SIEM then generates alerts for event rule violations using the logs sent by each device being monitored. During the performance of periodic collection and assessment of evidence associated with access control and vulnerability assessments, WECC_URE9 discovered this issue. Specifically, when its Intermediate System was placed into production, the hardware associated with that system was set up to send logs to SIEM. The system installed to facilitate WECC_URE9's Interactive Remote Access was WECC_URE9's first application of virtual desktop technology in a CIP environment. However, the virtual desktop master image which facilitates Interactive Remote Access as the Intermediate System, and runs on that hardware, was not sending its event logs to the SIEM. During the implementation of the architecture, an assumption was made that the logs sent by the hardware would capture all the information necessary to achieve compliance with the CIP standards. WECC_URE9 determined after the installation that logins and attempted logins to the virtual desktop master image were not logged by the hardware. The transmission of logs to the SIEM generated by the virtual desktop master image had not been configured separately from the hardware. The root cause of this issue was a lack of detailed knowledge, and appropriate procedures for proper configuration of virtual machine master images. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE9, and ended when WECC_URE9 installed and properly configured the the SIEM agent on the virtual desktop master image, and verified that logs were being generated, for a total of 13 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 failed to generate alerts for security events, including successful login attempts, failed access attempts, and failed login attempts for one virtual desktop “master image”. Failing to alert on these attempts could lead to someone gaining access to the machine which allows access to BES equipment. With access to BES equipment someone could leave malicious code or utilize BES systems that could degrade or ramp up generation; thereby potentially affecting the reliability of the bulk power system (BPS). However, based on the controls in place, WECC determined that the issue had a minimal likelihood of occurring. WECC_URE9 was logging events at the Cyber Asset level that met the minimum requirement Parts 4.1.1, 4.1.2, 4.1.3. WECC_URE9 had antivirus installed on the jump host and could pull event logs showing successful login attempts. There were no failed login attempts during the 13 days the alerts were not being generated. WECC_URE9 could generate alerts for detected malicious code from the Symantec antivirus installed on the jump host. However, WECC_URE9 was not being alerted on detected failure of Part 4.1 event logging of the jump host. While no alerts generated, the logs could be pulled manually. WECC_URE9 had antivirus installed to detect and alert for malicious code. No harm is known to have occurred. WECC considered WECC_URE9’s CIP-007 compliance history in determining the disposition track. WECC_URE9 had no relevant prior violations of this, or similar Standards and Requirements. | To mitigate this issue, WECC_URE9: 1) installed and properly configured the agent on the virtual desktop master image, and verified that logs were being generated; 2) updated Group Policy to include Audit Policies and send logs to the SIEM; and 3) updated the master image to ensure future devices utilize the same settings. WECC verified completion of the mitigating activities.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 10 (WECC_URE10) | NCRXXXXX | WECC2016016382 | CIP-007-6 | R4 | WECC_URE10 submitted a Self-Report stating that it had an issue with CIP-007-6 R4 Part 4.3. WECC_URE10 staff performed a 90-day compliance review and discovered that one of its servers for its SCADA system was not retaining applicable event logs for at least the last 90 days, as required by CIP-007-6 R4 Part 4.3. The server in scope was configured to retain logs for only seven days. The root cause was an assumption by WECC_URE10’s SCADA system support staff that the server was retaining logs indefinitely. WECC determined that this issue began when the Standard and Requirement became mandatory and enforceable to WECC_URE10, and ended when WECC_URE10 reconfigured the server to retain logs for at least the last 90 days, for a total of 98 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE10 failed to retain event logs for at least the last 90 days on one server. Failure to retain event logs for 90 days could result in an inability to perform thorough after-the-fact investigations of Cyber Security Incidents on WECC_URE10's SCADA system, thereby, potentially affecting the reliability of the bulk power system (BPS). However, the likelihood of the risk occurring was reduced by the controls WECC_URE10 had implemented. WECC_URE10’s server was not connected to the Internet and only two employees had electronic access to the device. WECC_URE10 was logging the ‘Root’ user on the systems for at least 90 days which could have been reviewed had a Cyber Security Incident occurred. Malicious code prevention with alarming was enabled on the system. Additionally, WECC_URE10 has a backup and restoration plan for its SCADA system should a loss or degradation be detected. No harm is known to have occurred. WECC considered WECC_URE10's CIP-007 compliance history in determining the disposition track. WECC_URE10 had no relevant prior noncompliance with CIP-007. | To mitigate this issue, WECC_URE10: 1) reconfigured the one server to record event logs for at least 90 days; 2) verified that the server was retaining event logs for at least 90 days; and 3) updated its policy and procedure with language to direct the verification of event log retention for at least 90 days when commissioning new servers.
2017-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 11 (WECC_URE11) | NCRXXXXX | WECC2016015727 | CIP-004-3a | R3 | On May 6, 2016, WECC_URE11 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R3. Specifically, the Personnel Risk Assessment (PRA) for a long-term employee, with authorized unescorted physical access to Critical Cyber Assets (CCAs), was not renewed within the required seven-year timeframe and the employee's access was not revoked accordingly. The cause of this issue was a lack of clarity concerning the PRA requirement. The issue began when the PRA expired for the employee in scope and endedwhen WECC_URE11 revoked access of the employee in scope, for approximately two months of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE11 failed to update the PRA for one employee within seven years after the initial PRA. A PRA is an integral part of an overall cyber security program and provides an entity with information and awareness regarding a personnel’s status, which may have changed prior to their original PRA. This increases the risk of the employee performing unauthorized and potentially malicious actions, which could affect the reliability of the bulk power system. However, WECC_URE11 implemented controls to prevent or detect any unauthorized actions. For example, WECC_URE11 has electronic badge reader control systems, multiple physical barriers, and technical controls on BES Cyber Systems and Cyber Assets to prevent unauthorized login. WECC_URE11 also has authentication systems on its Cyber Assets, intrusion detection and logging of systems, security guards, and cameras as additional controls. No harm is known to have occurred. | To mitigate this issue, WECC_URE11: 1) revoked access of the employee with an expired PRA; 2) obtained renewed PRA for the employee; 3) reviewed and revised procedures to review PRA expiration dates, identify those that expire within six months, and immediately issue a request for renewal to human resources; and 4) notified and trained staff on the new procedures. WECC has verified the completion of all mitigation activity.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016016048 | CIP-003-3 | R4.1 | MRO_URE1 stated that a Subject Matter Expert (SME) sent an email with an attachment that contained an Electronic Security Perimeter (ESP) diagram. Shortly after sending the email, the SME discovered that there was an external email address in the "CC" field of the email that the SME did not recognize, and the SME did not intend to send the email to. The SME determined that the external email address auto-populated when the SME started typing the name of the intended internal email address. The SME attempted to recall the email, but learned the following business day that the recall was unsuccessful. The SME then contacted his supervisor and reported the issue. MRO_URE1 determined the external email address belonged to a contractor, and that the email was auto-forwarded to the personal email address of a contractor employee. MRO_URE1 contacted the contractor who reported that he deleted the email after not recognizing the sender and then permanently deleted the email at MRO_URE1's request. The cause of this issue was human error on the part of the SME when typing out the email addresses in the CC field. This duration of the noncompliance was less than one week. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had a documented information protection program in place that included training elements. The SME immediately recognized the issue, and escalated the issue when the email recall function was unsuccessful. This reduced the duration of the noncompliance, as well as demonstrating the strength of MRO_URE1's information protection program, the effectiveness of its training, and its strong culture of compliance that encourages employees to self-report noncompliance. Further, the actual risk was reduced because the contractor in question had a current Personnel Risk Assessment (PRA) on file with MRO_URE1 and had completed MRO_URE1's annual NERC CIP Cyber and Physical Security Awareness Training. Finally, the contractor reported that he did not actually read the email. No harm is known to have occurred. | To mitigate this issue, MRO_URE1: 1) contacted the contractor and requested that he permanently delete the email; 2) modified its email system to add alerts by making internal and external email addresses appear in different colors and enabling a display above the "send" button to notify the sender if the email contains an external email address; 3) MRO_URE1 implemented a best practice to use links to documents in emails as opposed to attachments when feasible; and 4) training materials regarding best practices were published on MRO_URE1's intranet site and distributed via email to MRO_URE1's contract workforce that is eligible for electronic access or unescorted physical access. MRO_URE1 stated that mitigating activities were complete.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2016015908 | CIP-007-3a | R3.1 | MRO_URE2 reported that a security patch, for software that was in use on a non-Critical Cyber Asset, had not been timely assessed. The patch should have been assessed within 35 days, but MRO_URE2 stated that it did not assess the patch before the device was retired. The cause of this issue was lack of training for its subject matter experts (SME) on the issue of security patches for software in transition between major releases. The SME in charge of assessing patches for this software at the time the patch was released, believed that since the software was in Version 7, there would be no more patch releases for Version 6, and was only searching for Version 7 patches. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was limited in scope as the issue only affected a single security patch for software run on a single device. The risk was also reduced because the device was physically protected from adversaries as it was located in a Physical Security Perimeter (PSP). Additionally, the issue was detected by a secondary control as the two SMEs that perform patch assessments have their responsibilities rotated. This issue was detected when the rotated SME reviewed whether there were any patches for this software. Finally, the security patch related to a feature that checked for updates via the internet. This device was not connected to the internet and the feature that was targeted by this patch had been disabled. Thus, there was no actual risk in failing to apply the patch to the device. No harm is known to have occurred. | To mitigate this issue, MRO_URE2: 1) retired the device; 2) performed a review of all software subject to the CIP Reliability Standards to search for additional instances; and 3) conducted reinforcement training regarding the issue during a department meeting. MRO_URE2 stated that it completed mitigating activities.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2017016817 | CIP-006-6 | R1 | MRO_URE3 stated that an unauthorized custodial employee had his access enabled to the Physical Security Perimeter (PSP). MRO_URE3 manages access in its Physical Access Control System (PACS) by utilizing a central database containing access privileges and card-reader devices referred to as "panels," that are network connected to the central database. The PACS is designed so that any change in the central database is pushed into the panels' local databases. In transitioning its PACS for CIP version 5, MRO_URE3 conducted a complete review of persons requiring PSP access, which resulted in the removal of numerous individuals from the access list in the central database, including the affected custodial employee. At the conclusion of the review, the updated central database was designed to push the updates to the panels' local databases. However, for reasons not fully understood, the update process failed to remove the affected employee's access privileges from the local database of the panel that controlled access to the PSP. MRO_URE3 discovered that erasing the panels' local databases and then reloading the local databases resulted in a more reliable operation than relying on an update pushed to the panels' local databases after an incremental change is made in the central database. The process that pushes the changes from the central database to the panel's local database failed to fully and correctly perform, and resulted in a failure to implement the affected employee's removal in the central database into the local database associated with the panel that grants access to the PSP. This duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the noncompliance was limited to a single employee and a single PACS device. The actual risk associated with the noncompliance was reduced because the employee's access privileges were not revoked because of any security concern associated with the employee. Rather, the revocation was motivated by MRO_URE3's efforts to enhance its security posture by allowing only a single custodial employee to have PSP access privileges as opposed to all of its custodial employees. Additionally, the issue was detected by the employee, who reported the issue to management, demonstrating the effectiveness of MRO_URE3's CIP security training and its strong culture of compliance. Further, the employee did not improperly utilize his access after the Standard was enforceable. Finally, MRO_URE3 is required to maintain a 24/7 staff presence in its control center PSP, limiting the potential harm from an adversary. No harm is known to have occurred. MRO_URE3 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE3: 1) revoked the employee's access in the local database and confirmed the employee's badge did not grant entry into the PSP; 2) contacted its PACS vendor to determine if this was a known problem; 3) the local database of the affected panel was erased and reloaded; and 4) updated the access review process to include a quarterly full erasure and reload of all the local databases of the PACS panels. MRO_URE3 stated that mitigating activities were complete.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO2017016830 | CIP-004-6 | R5 | MRO_URE4 stated it had an issue of CIP-004-6 R5 Part 5.3 after it failed to revoke a terminated employee's access to designated storage locations for BES Cyber System Information (BES CSI) by the end of the next calendar day after the employee's termination. Specifically, after the employee resigned, the former employee's physical access was promptly disabled, but the former employee's electronic access to two sites was not terminated until approximately two weeks later. As part of its process, MRO_URE4's Physical Security Department sent an email on the day of the resignation, informing the appropriate BES CSI approvers to disable the employee's access. One of the BES CSI approvers did not follow the directive because he assumed that the employee's Active Directory account would be disabled promptly, thereby disabling access to the sites. Approximately ten days later, an internal control alerted the Physical Security Department that the access had not been disabled. The Physical Security Department sent another directive and the access was disabled the next day. The cause of the issue was human error as the BES CSI approver assumed that the Active Directory would be disabled the same day of the employee's resignation. The duration of the noncompliance was less than two weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the issue was brief and was self-detected by a functional control. The potential risk was also reduced because the employee's physical access was promptly terminated. Additionally, the employee's separation from MRO_URE4 was voluntary, as he had given several weeks notice, reducing the likelihood that he would act maliciously towards MRO_URE4. Finally, MRO_URE4 confirmed that the former employee did not utilize his Active Directory account to authenticate during the period of noncompliance. No harm is known to have occurred. MRO_URE4 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE4: 1) disabled the former employee's access to the sites; 2) examined potential discrepancies between BES CSI storage locations and occurrences of BES CSI; 3) revised its NERC CIP Information Protection Plan to clarify BES CSI storage locations; 4) revised its NERC Cyber Security: Personnel and Training Program to align with the revised NERC CIP Information Protection Plan; and 5) provided training to applicable personal on the revised policies and procedures. MRO_URE4 stated that mitigating activities were complete.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO2017017293 | CIP-005-3a | R1.5 | MRO determined that MRO_URE5, had an issue of CIP-005-3a R1.5. Specifically, it was discovered on an Electronic Access Control and Monitoring (EACM) device, that an audit trail of account usage is not maintained for system generated logging for the SQL server administrator shared account known as "SA" in the manner specified by CIP-007-3a R5.1.2. MRO_URE5 did not establish a process to generate sufficient logs for this device because it relied upon the advice of its vendor who recommended not logging usage of the SA account on this device because it would generate a high volume of log information. The duration of noncompliance was approximately 18 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The device is used to house logs, a detective control, and improper access to this device would not allow an adversary to affect BPS operations. Additionally, the device was located in a functioning Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP), even though EACM devices are not required to be located in either a PSP or ESP, which provided significant protection from a potential adversary. MRO considered MRO_URE5's CIP-005-3a R1 compliance history in determining the disposition track. MRO_URE5’s relevant prior noncompliance with CIP-005-3a R1 includes: NERC Violation ID MRO2013012274 (CIP-005-1 R1). MRO determined that MRO_URE5's compliance history should not serve as a basis for applying a penalty. The prior issue was related to noncompliance relating to the identification and documentation of ESPs and access points to the ESPs. The current issue and the prior issue have distinct causes, additionally, the prior issue did not reasonably put MRO_URE5 on notice of compliance issues related to the current issue, and the current issue is not the result of a failure to mitigate the prior issue. | To mitigate this issue, MRO_URE5 implemented sufficient logging on the device. MRO verified that mitigating activities were complete.
2017-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO2017017295 | CIP-006-3c | R2.2 | MRO determined that MRO_URE5, had an issue of CIP-006-3c R1.5. Specifically, it was discovered on a Physical Access Control System (PACS) device (a Non Critical Cyber Asset) that an audit trail of account usage is not maintained for system generated logging for the SQL server administrator shared account known as "SA" in the manner specified by CIP-005-3a R3. MRO_URE5 did not establish a process to generate sufficient logs for this device because it relied upon the advice of its vendor who recommended not logging usage of the SA account on this device because it would generate a high volume of log information. The duration of noncompliance was approximately 16 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The device is used to house logs, a detective control, and improper access to this device would not allow an adversary to affect BPS operations. Additionally, the device was located in a functioning Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP), even though PACS devices are not required to be located in either a PSP or ESP, which provided significant protection from a potential adversary. MRO_URE5 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE5 implemented sufficient logging on the device. MRO verified that mitigating activities were complete.
2017-05-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017016943 | CIP-014-2 | R1; R1.2 | NPCC_URE1 submitted a self-log stating that it had an issue of CIP-014-2 R1; R1.2. NPCC_URE1 incorrectly identified one of its facilities as a primary control center and failed to include all applicable substations in its initial risk assessment. The non-compliance ended when NPCC_URE1 completed a correct follow-up risk assessment. The duration of the noncompliance was approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This is due to the fact that the single additional facility identified by the follow-up risk assessment to comply with CIP-014-2 R1 already had a high level of physical security protection under NPCC_URE1's Physical Security Program. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered NPCC_URE1's compliance history and determined there are no relevant instances of noncompliance. | To mitigate this issue, NPCC_URE1: 1) corrected the noncompliance by performing a follow-up Risk Assessment that correctly identified those facilities that need to comply with CIP-014-2 R1. 2) put in place a new procedure as a means of updating/enhancing its implementation process for CIP-014-2, and disseminated it to all its responsible personnel. This activity will prevent a recurrence of similar issues. NPCC has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016421 | CIP-003-3 | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R4. A RFC_URE1 employee discovered that she was still able to access some NERC CIP information through a site that she had saved in her favorites tab on her Internet browser. The RFC_URE1 employee recognized that something was wrong because in her current position, the RFC_URE1 employee was not authorized to have access to NERC CIP information. Immediately after making this discovery, the RFC_URE1 employee informed RFC_URE1 of this possible issue. The RFC_URE1 employee should not have been able to access any NERC CIP information after she changed positions within RFC_URE1 from a position that came with NERC CIP access into a position that no longer required NERC CIP access. When her position change became effective, RFC_URE1's compliance staff properly submitted requests to remove the employee’s access to NERC CIP information that same day. RFC_URE1’s access management system processed the removal for the employee at issue that same day. Due to an improper folder configuration within RFC_URE1’s access management system, the RFC_URE1 employee inadvertently retained NERC CIP information access after her access was no longer required and after RFC_URE1 compliance staff attempted to remove her access by submitting a removal request into the access management system. The access management system provisions and removes access to Active Directory components automatically for RFC_URE1 employees and the tool is programmed to perform this function by searching in a particular location in the Active Directory. This employee’s access, however, was stored in groups outside of the typical location in the Active Directory where access profiles are stored. Resultantly, the access management system tool did not remove the RFC_URE1 employee’s access to NERC CIP information when compliance staff made the removal request. RFC_URE1’s Access Management Program requires that all access to NERC CIP information must be removed by the end of the next calendar day from the time it was determined that access was no longer needed. After the RFC_URE1 employee discovered this issue, RFC_URE1’s team manually removed the employee’s access from the Active Directory the next day. RFC_URE1 conducted an investigation of this issue and determined that the employee’s manager followed all RFC_URE1 policies correctly. Also during this investigation, RFC_URE1 determined that it had identified a deficiency in the access management system related to storing information in Active Directory groups prior to the compliance date for CIP v5 and implemented a fix for these problems. RFC_URE1, however, did not promptly check for possible remaining access issues after implementing the fix and did not discover this issue until the RFC_URE1 employee reported this issue. This noncompliance involves the management practices of asset and configuration management, information management, and validation. A primary root cause of this issue is that the Active Directory group folders were located in the wrong place within RFC_URE1's system for the access management system to properly connect to the membership permissions and complete the removal. Because the access management system did not locate the Active Directory folders during ticket processing, the access management system did not identify any information access to remove during ticket processing. The access management system closed the tickets meant to remove the employee’s access to completion, but without successfully removing access. A secondary contributing cause is that RFC_URE1 did not promptly check for possible remaining access issues after it implemented the Active Directory groups’ related fix in the access management system. This failure to validate that there were no outstanding issue is a contributing cause of this issue. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that an employee without authorized access could gain access to Critical Cyber Assets (CCAs) and use those CCAs, or information gathered from those CCAs, to damage the BPS. In this instance, a RFC_URE1 employee retained unauthorized access to 14 CIP Information Repositories (CIRs) for approximately two months. That potential risk is minimized here because the RFC_URE1 employee involved had current NERC CIP training, a valid Personnel Risk Assessment, and is a trusted employee that has been with RFC_URE1 for more than 30 years. Lastly, the RFC_URE1 employee confirmed that she did not access any NERC CIP information, aside from clicking on the favorited site that she promptly reported, after changing job functions to a role that did not require access to NERC CIP information. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) moved the Active Directory Groups to the appropriate location which will allow the access management system to effectively and automatically remove access for personnel when necessary. This first mitigating action resolved the technical issue in the access management system that allowed this noncompliance to occur; 2) removed NERC CIP access from the employee’s account; 3) developed and distributed a Job Aid with a checklist that details actions for a manager to take in the event of a removal. RFC_URE1’s performing an extent of condition review to check for and fix any remaining issues and parts of these mitigating actions are ongoing; and 4) identified all entitlements that appear in the access management system and compared those Active Directory groups to the Active Directory groups that appear in the proper Active Directory location. To mitigate this issue, RFC_URE1 will complete the following mitigation activities: 1) will identify all users with access outside of their current roles, if any. If RFC_URE1 finds any users with access outside of their current roles, RFC_URE1 will identify the access (physical, electronic, information) that was loaded into a user’s access management system profile as an entitlement outside of a role; and 2) based on any identified discrepancies, RFC_URE1 will take action to remedy access issues by (a) incorporating entitlement to an existing role and requesting access for the identified user; (b) creating a new role and requesting the access for the identified user; (c) adding the user to an existing role with the desired entitlement; and (d) removing the access. As a whole RFC_URE1’s mitigation will communicate the tasks that need to be completed by the manager when processing access and removal requests and what changes will be reflected in the access management system tool when the work is completed properly. RFC_URE1 has also begun using the access management system for access certifications both quarterly and annually, which help the access management system to properly complete removals. RFC_URE1’s initial investigation into the issue identified a need for a guide to assist a manager in identifying when the access management system had completed the proper steps for a removal. Managers with direct reports with NERC CIP access believed a guide would help them be able to identify a proper removal. Lastly, increasing awareness of the access management system tool’s functionality, clarifying the tasks managers are assigned, and changes in the access management system tool itself are all designed to help prevent recurrence of this issue.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016005 | CIP-004-3a | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. This self-report contains two separate issues. RFC2016016005 addresses the first issue. RFC2017017950 addresses the second issue. First, a member of RFC_URE1’s team identified two instances where RFC_URE1 did not remove electronic access to Critical Cyber Assets (CCAs) within seven days after an employee left the company. Pursuant to CIP-004-3a R4, access is required to be removed within seven days of a voluntary termination (Examples of voluntary termination include a transfer, mutual separation, an expiration of a business need, and retirement.). After these two instances were discovered, they were escalated to the Manager and the team initiated an extent of condition review and identified 74 total instances in which access was not removed in a timely fashion. 19 instances occurred in RFC_URE1’s shared services group. All 74 instances were for users that transferred roles and no longer required access. Of the 74 instances, RFC_URE1 completed removals for 63 within one week of the seven day timeframe for removal. In 10 cases, RFC_URE1 completed removals within two weeks of the seven day timeframe for removal. In one case, RFC_URE1 completed the removal four weeks after the seven day timeframe for removal. At the time of the discovery, RFC_URE1’s team utilized an access revocation procedure that contained specific process steps for the revocation of access. As part of this access revocation procedure, RFC_URE1’s team employed a manual, dual verification process for all NERC CIP access tickets. This process requires two separate performers taking action on every NERC CIP access revocation request. Due to the high number of tickets that RFC_URE1 was processing and the amount of manual provisioning required per access revocation ticket, RFC_URE1 did not properly monitor the tickets and RFC_URE1 did not properly remove access within the timeframe required. RFC_URE1 attributed all access removal issues to manual processing errors. RFC_URE1’s team reviewed and confirmed for all instances that, although the access removal was completed beyond the seven day timeframe, the removals were fully completed, with no latent access remaining. This first noncompliance implicates the management practices of verification and work management. Verification is implicated because the manual, dual verification process for all NERC CIP access tickets was not effective as it did not catch these 74 overdue access revocations. A root cause of this noncompliance is an ineffective verification internal control that failed to catch these issues. Work management is implicated, because RFC_URE1 did not properly manage the workload for reviewing access revocation tickets because of the large number of tickets that RFC_URE1 was processing and the amount of manual provisioning required per access revocation ticket. The duration of the noncompliance was approximately ten months. | This first issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that by not removing access within seven days after a user’s voluntary termination, users who should not have access to CCAs have access to CCAs and an opportunity to use that access to damage CCAs and negatively affect the BPS. That potential risk is minimized because although the users’ accounts each retained an access privilege, the users were not able to utilize that access because the network ID for each user was timely disabled. This means that the 74 users could not log onto the RFC_URE1 network to use their electronic access to makes changes to CCAs. RFC_URE1 also promptly disabled badge access for these 74 users meaning they could not get into the physical locations housing the equipment that gives access to CCAs. Additionally, all 74 users at issue had current Personnel Risk Assessments (PRAs) and valid NERC CIP training at the time of their access removals. None of the 74 users used their access after it should have been removed. No harm is known to have occurred. | To mitigate this first issue, RFC_URE1: 1) removed access for all 74 users; 2) held a stand down meeting with all of its members to discuss the severity of the issue and to reinforce the importance of removing access within the seven day timeframe required by the Standard. The purpose of this meeting was to provide short term correction on performance while additional actions and investigation were underway; 3) defined the process for the revocation of NERC CIP access, NERC CIP Access Revocation Procedure, in order to meet the compliance requirements of CIP v5 and to prevent future occurrences. In this process, the newly installed access management system tool automatically disables the access for any exited user for connected systems. The tool takes the place of the manual process in place under the Version 3 Program that was at issue in this noncompliance. 4) developed an internal escalation procedure for use by the team for removal of NERC CIP access and RFC_URE1 provided training to impacted personnel as part of the implementation. The procedural control and training will help ensure proper and timely attention to meet removal timeframes; and 5) developed a job aid for use by provisioning groups for the removal of NERC CIP access to a disconnected system and posted that job aid on the portal page for use by performers. This will address cases in the future where removal is needed and a system is not directly connected to the access management system. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017017950 | CIP-004-3a | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. This self-report contains two separate issues. RFC2016016005 addresses the first issue. RFC2017017950 addresses the second issue. Second, during a review of the 2nd Quarter access control list, RFC_URE1 discovered that a technological error during ticket processing within the Access Request System (ARS) resulted in a trusted employee being granted access to a device without following the proper sequence of approval steps to ensure supervisor review and approval of the access request. As a result, this error in RFC_URE1’s ARS granted brief and limited access to a device to an employee that did not have a business need for that access. RFC_URE1 removed this employee’s access. The user at issue requested access to the device using ARS in order to be able to run reports in the system. The employee made the request to support the implementation and expansion of logging, monitoring, and alerting for RFC_URE1’s CIP v5 transition projects. To obtain access, RFC_URE1’s procedure in effect at the time requires (1) supervisor approval, (2) Personnel Risk Assessment (PRA) and NERC training verification, and (3) asset authorizer approval before a ticket is sent to the provisioning team to complete the access request. As part of each ARS workflow, each step must be completed before the ticket can proceed to the subsequent steps. Upon investigation by the ARS technical support team and RFC_URE1’s team, RFC_URE1 identified a “stuck” ticket was at issue. The ticket for this employee’s request was not moving normally through the workflow steps. Stuck tickets happened on rare occasions to certain requests that were missing some configuration data in the request. As part of the support activities, the ARS support team on a weekly basis looked for and identified any stuck/stalled tickets, addressed the root cause, and restarted the workflow for the given ticket. The ARS technical support team manually restarted the ticket within the system, and in doing so, ARS produced two identical tickets (with the same information and identification number for the same access request). One ticket was sent through the system to the supervisor for review, and a second ticket went directly to the access authorizers and the Active Directory group. In the typical sequence, the supervisor review would be completed prior to advancing the ticket to the access authorizers. As a consequence of two identical tickets, the Active Directory group processed the request and granted access, before the supervisor review was completed. Subsequently, the supervisor denied the second ticket because the supervisor determined that the user did not need access to this particular resource to support the CIP v5 transition projects. The provisioning team completed their task out of sequence prior to the supervisor’s review of the ticket. This second issue implicates the management practices of verification and workforce management. Verification is implicated because the ARS team did not remove the initial “stuck” ticket prior to restarting the request which led to two tickets processing through ARS once the ticket was initiated. A root cause of the issue was the first “stuck” ticket in the ARS system. A contributing cause is that the provisioning team erred in provisioning access without verifying that all necessary elements had been completed for proper provisioning. The provisioning team incorrectly completed the approval of the ticket at issue prior to the supervisor’s review of the ticket request. This mistake came from ineffective training, which implicates workforce management. The duration of the noncompliance was approximately one month. | This second issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that by incorrectly granting the employee access to a device, that employee could use that access to gain access to NERC CIP protected information and then use that information in a manner to negatively affect the BPS. That potential risk is minimized because with the limited level of access that RFC_URE1 granted the employee, the employee would only have been able to run an alert report in the device that would show information in the categories of “Location, Asset, Time of alert, User ID, Metric Category/Metric Name, and Description of alert”. A user with this access would know the location of the assets and the origin of an alert. Although the report would give specific information regarding the performance of devices, the level of access obtained by this user would not have allowed him to alter any system that would adversely impact operations. Additionally, the employee at issue is a trusted employee that held and continues to hold authorized NERC CIP Access to other RFC_URE1 CIP assets. The employee also had a current PRA and valid NERC CIP training during the noncompliance. Lastly, RFC_URE1 confirmed that the individual did not utilize the access during the time access was granted. No harm is known to have occurred. | To mitigate this second issue, RFC_URE1: 1) adjusted its process for resolving this type of issue with ARS to require removal/clean-up of the stuck ticket from ARS followed by reinitiating the ticket. This will prevent future occurrences of granting access due to the “stuck” ticket issue and in doing so, the ARS team would only have had one ticket in the system at all times during troubleshooting, thus preventing an opportunity for the creation of a duplicate ticket through a similar system error; and 2) has been using a new access management system tool that is governed by the RFC_URE1 document, NERC CIP: Access Request & Authorization Procedure. In this document, there are escalation protocols set forth which state that if no action is taken on a ticket in the requisite time period, the ticket will be denied by the system, and the user will be unable to obtain access with the denied request. This will assist in preventing similar “stuck” tickets from having to be manually restarted and risk having two workflows in the system for the same request. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016003 | CIP-004-3a | R3 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R3. RFC_URE2 identified an error in a background investigation date entered into its HR electronic tracking system for one of its employees. The tracking system incorrectly listed the background investigation date. The actual background investigation date for the RFC_URE2 employee was four years earlier. As a result of this error, the employee’s Personnel Risk Assessment (PRA) expired and was not renewed. This expired PRA violated RFC_URE2’s internal procedures, and CIP-004-3a R3, because RFC_URE2’s procedure requires all RFC_URE2 employees requesting access to NERC CIP assets to have a current PRA, renewed every seven years, for NERC CIP access. RFC_URE2 discovered this while processing a separate access request for access to a new Physical Security Perimeter (PSP) for the same RFC_URE2 employee with the expired PRA. Following RFC_URE2’s procedures, a request for access to a NERC CIP asset requires (1) supervisor approval, (2) PRA and NERC CIP training verification, and (3) asset authorizer approval. As part of Step 2, RFC_URE2’s access provisioning team manually inputs the requestor’s PRA date from the HR electronic tracking system in the Access Request System (ARS) tool used to process the access request. As part of the verification process, the access provisioning team compares the actual background investigation date to the date in the electronic system to ensure that the dates match. During that matching step, RFC_URE2’s access provisioning team identified the expired PRA error. Following identification, RFC_URE2 removed all of the employee’s NERC CIP access on that same day. As a result, the employee held NERC CIP access for over four months without a current PRA. As a result of this discovery, RFC_URE2’s team responsible for maintaining the PRA dates performed an extent of condition review to verify the PRA dates of all active CIP access holders. RFC_URE2 confirmed one additional instance where the user's PRA was incorrectly entered into the electronic record keeping system. The actual background investigation date did not match the entry in the record system. RFC_URE2’s team discovered the discrepancy and initiated a new PRA which was entered and adjudicated two days later for that employee. The second user retained access without a current PRA for approximately five months. The PRA initiated was returned with no adverse findings for the period the user retained unauthorized access. At the time of discovery the user was preparing to go on-shift, and RFC_URE2 was in storm duty operation. RFC_URE2 planned to remove access following the active storm duty shift to allow the employee to support BPS reliability. By the time the planned access removal time occurred, the new PRA had been adjudicated. This noncompliance involves the management practice of verification. RFC_URE2 did not have effective internal controls in place to verify that PRA documentation was accurately maintained. That lack of an effective internal control to keep all necessary PRA documentation is the root cause of this noncompliance. The duration of the noncompliance was approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that an unauthorized and untrusted individual could access and damage Critical Cyber Assets and other NERC CIP assets. That risk is minimized here because both employees were long standing and trusted employees. The first employee was a trusted employee with current CIP training that has been in his current role for ten years and has been at RFC_URE2 for more than 25 years. For the approximately four months that his PRA was expired, the employee maintained access to four Physical Security Perimeters (PSPs) at RFC_URE2 and had electronic access to a SCADA database that his team manages for data maintenance. For the second employee at issue, that employee’s PRA was expired for a total of five months. The employee was also a trusted employee, with current CIP training, and has been with RFC_URE2 for over eight years. For the five months that the second employee’s PRA was expired, the second employee retained information access, and NERC Physical Access as a SCADA Transmission Dispatcher. Both employees had on-going business needs for access to perform job duties and were in the same job before, during, and after the noncompliance. Lastly, their renewed PRAs showed no adverse findings from the date of PRA expiration through the date of PRA renewal. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) completed new PRAs for both individuals identified in the noncompliance; 2) developed and implemented a job aid for dual verification of each PRA performed to request NERC CIP access. This dual verification will reduce the likelihood of recurrence of this issue; 3) created a set of instructions explaining to a new performer how to execute a PRA in the background vendor system; and 4) retrained relevant employees on this new verification process and the new set of instructions. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016004 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. A member of RFC_URE2’s team identified two instances where RFC_URE2 did not remove electronic access to Critical Cyber Assets (CCAs) within seven days after an employee left the company. Pursuant to CIP-004-3a R4, access is required to be removed within seven days of a voluntary termination (Examples of voluntary termination include a transfer, mutual separation, an expiration of a business need, and retirement.). After these two instances were discovered, they were escalated to the Manager and the team initiated an extent of condition review and identified 74 total instances in which access was not removed in a timely fashion. 19 instances occurred in RFC_URE2’s shared services group. All 74 instances were for users that transferred roles and no longer required access. Of the 74 instances, RFC_URE2 completed removals for 63 within one week of the seven-day timeframe for removal. In 10 cases, RFC_URE2 completed removals within two weeks of the seven-day timeframe for removal. In one case, RFC_URE2 completed the removal four weeks after the seven-day timeframe for removal. At the time of the discovery, RFC_URE2’s team utilized an access revocation procedure that contained specific process steps for the revocation of access. As part of this access revocation procedure, RFC_URE2’s team employed a manual, dual verification process for all NERC CIP access tickets. This process requires two separate performers taking action on every NERC CIP access revocation request. Due to the high number of tickets that RFC_URE2 was processing and the amount of manual provisioning required per access revocation ticket, RFC_URE2 did not properly monitor the tickets and RFC_URE2 did not properly remove access within the timeframe required. RFC_URE2 attributed all access removal issues to manual processing errors. RFC_URE2’s team reviewed and confirmed for all instances that, although the access removal was completed beyond the seven-day timeframe, the removals were fully completed, with no latent access remaining. This noncompliance involves the management practices of verification and work management. Verification is involved because the manual, dual verification process for all NERC CIP access tickets was not effective as it did not catch these 74 overdue access revocations. A root cause of this noncompliance is an ineffective verification internal control that failed to catch these issues. Work management is involved because RFC_URE2 did not properly manage the workload for reviewing access revocation tickets because of the large number of tickets that RFC_URE2 was processing and the amount of manual provisioning required per access revocation ticket. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk from this noncompliance is that by not removing access within seven days after a user’s voluntary termination, users who should not have access to CCAs have access to CCAs and an opportunity to use that access to damage CCAs and negatively affect the BES. That potential risk is minimized because although the users’ accounts each retained an access privilege, the users were not able to utilize that access because the network ID for each user was timely disabled. This means that the 74 users could not log onto the RFC_URE2 network to use their electronic access to makes changes to CCAs. RFC_URE2 also promptly disabled badge access for these 74 users meaning they could not get into the physical locations housing the equipment that gives access to CCAs. Additionally, all 74 users at issue had current Personnel Risk Assessments (PRAs) and valid NERC CIP training at the time of their access removals. None of the 74 users used their access after it should have been removed. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed access for all 74 users; 2) held a stand-down meeting with all of its members to discuss the severity of the issue and to reinforce the importance of removing access within the seven-day timeframe required by the Standard. The purpose of this meeting was to provide short-term correction on performance while additional actions and investigation were underway; 3) defined the process for the revocation of NERC CIP access in NERC CIP Access Revocation Procedure in order to meet the compliance requirements of CIP v5 and to prevent future occurrences. In this process, the newly installed access management system tool automatically disables the access for any exited user for connected systems. The tool takes the place of the manual process in place under the Version 3 Program that was at issue in this noncompliance; 4) developed an internal escalation procedure for use by the team for removal of NERC CIP access and RFC_URE2 provided training to impacted personnel as part of the implementation. The procedural control and training will help ensure proper and timely attention to meet removal timeframes; and 5) developed a job aid for use by provisioning groups for the removal of NERC CIP access to a disconnected system and posted that job aid on the portal page for use by performers. This will address cases in the future where removal is needed and a system is not directly connected to the access management system. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016385 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. While performing a quarterly access certification for a RFC_URE2 secure area, a RFC_URE2 manager identified that an employee was listed as having provisioned access rights to a RFC_URE2 NERC Physical Security Perimeter (PSP). The manager knew the employee should not have access to any RFC_URE2 areas and promptly elevated the issue for further review. An investigation discovered that the HR System incorrectly reassigned a previously used RFC_URE2 contractor ID number to the profile of another employee. An ID number was assigned to more than one user, but not concurrently. The ID number was under the use of the first contractor and should have been marked “terminated” in the HR system when the first contractor who had previously held the number transitioned to full-time employee status. Once the first contractor transitioned to full-time employee status, however, he kept the same ID number. Because the ID number was not marked “terminated,” the profile, which included authorized access to the RFC_URE2 PSP, remained active and was updated with the second employee’s name. The second employee was not aware of the access rights attached to the reassigned profile, was never issued an RFC_URE2 badge or PIN and, therefore, never had any means of getting access to RFC_URE2's facilities. In addition, since the first employee's name had been replaced by the second employee's name in the badging system, all authorized uses of the first employee's badge for his entry into PSPs were logged as entries; however, the name entered was inaccurate due to the assignment of the second employee's name in the system. The logs will be corrected with the correct employee name to show the valid entries by the first employee. The first employee had valid NERC privileges (training, current Personnel Risk Assessment (PRA), and business need) during the time period of the noncompliance. RFC_URE2 removed the second employee’s access from the system. This noncompliance involves the management practice of verification. In this noncompliance, verification is involved because RFC_URE2 did not have an effective verification control in place to ensure that the HR System did not incorrectly reassign a previously used RFC_URE2 contractor ID number to the profile of a different employee. A root cause of this noncompliance is the lack of an effective verification control. The duration of the noncompliance was approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that by incorrectly granting access, the second employee who should not have access to CCAs has the potential to access CCAs and an opportunity to use that access to damage CCAs and negatively affect the BPS. That risk is minimized here because the second employee was not aware of the access rights that he was inadvertently given due to the reassigned profile, was never issued an RFC_URE2 badge or PIN and, therefore, never had any means of gaining access to any RFC_URE2 facilities. In addition, since the first employee's name had been replaced by the second employee's name in the badging system of record, all authorized uses of the first employee's badge for his entry into PSPs were logged as entries; however, the name entered was inaccurate due to the assignment of the second employee's name in the system. Lastly, the first employee that originally had the ID number and had the badge during the noncompliance had valid NERC privileges (training, current PRA, and business need) during the time period of the noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed access from the second employee’s account; 2) compared a list of deleted ID numbers to the list of ID numbers; 3) updated the record in the system to display a complete view of the changes to the employee’s account to each employee’s badge ID; 4) updated its Management Model document to reflect the policy change that ID numbers shall not be reused; 5) removed any deleted IDs from the pool of future ID numbers; and 6) developed and conducted training with the performer groups that support the ID number assignment.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016445 | CIP-004-6 | R3 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-6 R3. RFC_URE3 identified an error in a background investigation date entered into its HR electronic tracking system for one of its employees. As a result of this discovery, RFC_URE3’s team performed an extent of condition review to manually verify the Personnel Risk Assessment (PRA) dates in the system of all active CIP access holders. This extent of condition analysis identified an RFC_URE3 employee that had NERC CIP access without a valid PRA on file. The RFC_URE3 employee had a PRA date in RFC_URE3's access system of record, but had no PRA form on file that RFC_URE3 could use to verify the accuracy of the date in the system. RFC_URE3 reported this issue because it does not have the underlying evidence to support the employee’s listed PRA date. The RFC_URE3 employee at issue had access to one NERC CIP application that RFC_URE3 used to track NERC CIP prerequisites such as NERC training completion. Upon discovering this issue as a result of the extent of condition analysis, RFC_URE3 initiated a new PRA for the employee and the PRA was completed with no adverse issues, the next day. This noncompliance involves the management practices of verification and asset and configuration management. RFC_URE3 did not have effective internal controls in place to verify that PRA source documentation was maintained to show the validity of stored PRAs. That lack of an effective internal control to keep all necessary PRA documentation is the root cause of this noncompliance. Additionally, asset and configuration management is involved because RFC_URE3 did not know where the PRA documentation record for this employee was kept or how RFC_URE3 lost the source documentation for this employee. The duration of the noncompliance was approximately 8 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that an unauthorized and untrusted individual could access and damage BES Cyber Systems. That risk is minimized here because the employee in question is a trusted member of senior management and had information access to just one NERC CIP application only to ensure that all employees had taken annual NERC CIP training. The information that the employee had access to was not operational and only pertained to completion of NERC prerequisites for CIP training. Additionally, this is primarily a documentation issue because RFC_URE3 had on file that the employee in question last had a PRA, but RFC_URE3 could not verify the PRA date because the employee’s PRA form could not be located. PRAs are good for seven years so the employee’s PRA, if it could be validated, would have been valid through next year. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) initiated a new PRA for the employee and the PRA was completed with no adverse issues the next day; 2) developed and implemented a job aid for dual verification of each PRA performed to request NERC CIP access. This dual verification will reduce the likelihood of future occurrences; 3) created a set of instructions explaining to a new performer how to execute a PRA in the background vendor system; and 4) retrained relevant employees on this new verification process and the new set of instructions.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016008 | CIP-004-3a | R4 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. A member of RFC_URE3’s team identified two instances where RFC_URE3 did not remove electronic access to Critical Cyber Assets (CCAs) within seven days after an employee left the company. Pursuant to CIP-004-3a R4, access is required to be removed within seven days of a voluntary termination. (Examples of voluntary termination include a transfer, mutual separation, an expiration of a business need, and retirement.) After these two instances were discovered, they were escalated to the Manager and the team initiated an extent of condition review and identified 74 total instances in which access was not removed in a timely fashion. 19 instances that occurred in RFC_URE3’s shared services group. Of the 74 cases, RFC_URE3 completed removals for 63 within one week of the seven-day timeframe for removal. In 10 cases, RFC_URE3 completed removals within two weeks of the seven-day timeframe for removal. In one case, RFC_URE3 completed the removal four weeks after the seven-day timeframe for removal. At the time of the discovery, RFC_URE3’s team utilized an access revocation procedure that contained specific process steps for the revocation of access. As part of this access revocation procedure, RFC_URE3’s team employed a manual, dual verification process for all NERC CIP access tickets. This process requires two separate performers taking action on every NERC CIP access revocation request. Due to the high number of tickets that RFC_URE3 was processing and the amount of manual provisioning required per access revocation ticket, RFC_URE3 did not properly monitor the tickets and RFC_URE3 did not properly remove access within the timeframe required. RFC_URE3 attributed all access removal issues to manual processing errors. RFC_URE3’s team reviewed and confirmed for all instances that, although the access removal was completed beyond the seven-day timeframe, the removals were fully completed, with no latent access remaining. This noncompliance involves the management practices of verification and work management. Verification is involved because the manual, dual verification process for all NERC CIP access tickets was not effective as it did not catch these 74 overdue access revocations. A root cause of this noncompliance is an ineffective verification internal control that failed to catch these issues. Work management is involved because RFC_URE3 did not properly manage the workload for reviewing access revocation tickets because of the large number of tickets that RFC_URE3 was processing and the amount of manual provisioning required per access revocation ticket. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that by not removing access within seven days after a user’s voluntary termination, users who should not have access to CCAs have access to CCAs and an opportunity to use that access to damage CCAs and negatively affect the BPS. That potential risk is minimized because although the users’ accounts each retained an access privilege, the users were not able to utilize that access because the network ID for each user was timely disabled. This means that the 74 users could not log onto the RFC_URE3 network to use their electronic access to makes changes to CCAs. RFC_URE3 also promptly disabled badge access for these 74 users meaning they could not get into the physical locations housing the equipment that gives access to CCAs. Additionally, all 74 users at issue had current Personnel Risk Assessments (PRAs) and valid NERC CIP training at the time of their access removals. None of the 74 users used their access after it should have been removed. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed access for all 74 users; 2) held a stand-down meeting with all of its members to discuss the severity of the issue and to reinforce the importance of removing access within the seven-day timeframe required by the Standard. The purpose of this meeting was to provide short-term correction on performance while additional actions and investigation were underway; 3) defined the process for the revocation of NERC CIP access in NERC CIP: Access Revocation Procedure in order to meet the compliance requirements of CIP v5 and to prevent future occurrences. In this process, the newly installed access management system tool automatically disables the access for any exited user for connected systems. The tool takes the place of the manual process in place under the Version 3 Program that was at issue in this noncompliance; 4) developed an internal escalation procedure for use by the team for removal of NERC CIP access and RFC_URE3 provided training to impacted personnel as part of the implementation. The procedural control and training will help ensure proper and timely attention to meet removal timeframes; and 5) developed a job aid for use by provisioning groups for the removal of NERC CIP access to a disconnected system and posted that job aid on the portal page for use by performers. This will address cases in the future where removal is needed and a system is not directly connected to the access management system. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016446 | CIP-002-5.1 | R2 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-002-5.1 R2. During an internal audit, RFC_URE4 discovered that although it had identified and recorded the Bulk Electric System (BES) Cyber Assets at a generation plant, those assets were omitted from the corresponding BES Cyber Asset List signed by the CIP Senior Manager. The root cause of this noncompliance was the fact that under CIP version 5, RFC_URE4 transferred compliance responsibility for CIP-002-5.1 R2 to the asset owners within the RFC_URE4 footprint, who lacked sufficient familiarity with these obligations, without having an adequate process in place to walk them through their responsibilities. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE4 identified this issue quickly and proactively through a mock audit conducted shortly after the CIP version 5 Standards became effective. Second, this is a documentation issue because the BES Cyber Assets at issue were identified and recorded, but omitted from the signed list, which serves as a memorialization of the information gathered. Third, the assets at issue were accorded all the cyber and physical security protections in accordance with all relevant standards. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) added the missing BES Cyber Assets to the master BES Cyber Asset List; 2) reviewed and signed the BES Cyber Asset List once the BES Cyber Assets were added to the list; 3) modified the change management request form to contain a “Final Security Checklist” that includes a verification that any new devices be placed on the current BES Cyber Asset list; and 4) began conducting annual walkthroughs of all areas designated as Physical Security Perimeters during which Cyber Assets are reviewed and verified against the BES Cyber Asset list. Any new or removed devices are investigated.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016448 | CIP-007-6 | R5 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-007-6 R5. During an internal audit, RFC_URE4 discovered that it failed to produce a list of default/generic accounts at its various substations as required by CIP-007-6 R5. The root cause of this noncompliance was the fact that under CIP version 5, RFC_URE4 transferred compliance responsibility for CIP-007-6 R5 to the asset owners within the RFC_URE4 footprint, who lacked sufficient familiarity with these obligations, without having an adequate tools in place to help them complete their responsibilities. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the potential risk of unauthorized cyber access to these facilities was mitigated by the fact that RFC_URE4 identified this issue quickly and proactively through a mock audit conducted shortly after the CIP version 5 Standards became effective. Second, none of the devices at issue had external routable connectivity or remote login capability. Third, any potential risk of unauthorized physical access as mitigated by security controls in place such as 8-foot-high fencing, motion sensors/cameras, and control houses with multiple Physical Access Control Systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) added the default/generic account information received from the substation team to a standardized evidence form that is maintained by the infrastructure security compliance team; 2) received a complete list of default/generic accounts from the substations team and combined those accounts into one comprehensive document; and 3) verified the contents of the one comprehensive tracking document by having the subject matter expert for the substation team review and approve the document.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016447 | CIP-007-6 | R2 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-007-6 R2. During a mock audit, RFC_URE4 discovered that responsible personnel for generation and substations had not identified patch sources for all in-scope devices. Consequently, RFC_URE4 had not fully completed its first two patch evaluation cycles under CIP version 5. The root cause of this noncompliance was the fact that the responsible personnel involved had not been required to perform this particular documentation exercise under CIP version 3 and failed to have a sufficient process to ensure completion of this requirement under version 5. This major contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE4 identified this issue quickly and proactively through a mock audit conducted shortly after the CIP version 5 Standards became effective. Second, the device types at issue, by their nature, do not have frequent updates, which lowers the likelihood that there would have been a relevant patch during the time period of this noncompliance. Third, for the generation plant at issue, the Cyber Assets are all firmware based, located behind multiple firewalls to prevent access from external networks, and located within a defined Physical Security Perimeter protected with a Physical Access Control System that requires two factor authentication to prevent physical access. Fourth, the devices at substations are located within control houses that have been physically secured using a card access system that requires two factor authentication for access. None of the substations have external routable connectivity and cannot be accessed from outside of the control building. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) performed a look back for any patches missed during the two patch cycles where patch sources were not identified; 2) combined the generation and substation patch sources into the master patch matrix spreadsheet; 3) added the personnel responsible for patching for generation and substations to the roster of individuals who take part in the patch evaluation meeting that takes place towards the end of the thirty-five day patch evaluation cycle. This participation is a constant reminder for each of the participants to review their patch sources and update any new or obsolete patch sources as listed on the Patch management Matrix master list; and 4) updated its Security Patch Management Process to ensure that that patch sources are identified, updated, and communicated appropriately.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016009 | CIP-004-3a | R4 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. A member of RFC_URE5’s team identified two instances where RFC_URE5 did not remove electronic access to Critical Cyber Assets (CCAs) within seven days after an employee left the company. Pursuant to CIP-004-3a R4, access is required to be removed within seven days of a voluntary termination. (Examples of voluntary termination include a transfer, mutual separation, an expiration of a business need, and retirement.) After these two instances were discovered, they were escalated to the Manager and the team initiated an extent of condition review and identified 74 total instances in which access was not removed in a timely fashion. 19 instances that occurred in RFC_URE5’s shared services group. Of the 74 cases, RFC_URE5 completed removals for 63 within one week of the seven-day timeframe for removal. In 10 cases, RFC_URE5 completed removals within two weeks of the seven-day timeframe for removal. In one case, RFC_URE5 completed the removal four weeks after the seven-day timeframe for removal. At the time of the discovery, RFC_URE5’s team utilized an access revocation procedure that contained specific process steps for the revocation of access. As part of this access revocation procedure, RFC_URE5’s team employed a manual, dual verification process for all NERC CIP access tickets. This process requires two separate performers taking action on every NERC CIP access revocation request. Due to the high number of tickets that RFC_URE5 was processing and the amount of manual provisioning required per access revocation ticket, RFC_URE5 did not properly monitor the tickets and RFC_URE5 did not properly remove access within the timeframe required. RFC_URE5 attributed all access removal issues to manual processing errors. RFC_URE5’s team reviewed and confirmed for all instances that, although the access removal was completed beyond the seven-day timeframe, the removals were fully completed, with no latent access remaining. This noncompliance involves the management practices of verification and work management. Verification is involved because the manual, dual verification process for all NERC CIP access tickets was not effective as it did not catch these 74 overdue access revocations. A root cause of this noncompliance is an ineffective verification internal control that failed to catch these issues. Work management is involved because RFC_URE5 did not properly manage the workload for reviewing access revocation tickets because of the large number of tickets that RFC_URE5 was processing and the amount of manual provisioning required per access revocation ticket. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from this noncompliance is that by not removing access within seven days after a user’s voluntary termination, users who should not have access to CCAs have access to CCAs and an opportunity to use that access to damage CCAs and negatively affect the BPS. That potential risk is minimized because although the users’ accounts each retained an access privilege, the users were not able to utilize that access because the network ID for each user was timely disabled. This means that the 74 users could not log onto the RFC_URE5 network to use their electronic access to makes changes to CCAs. RFC_URE5 also promptly disabled badge access for these 74 users meaning they could not get into the physical locations housing the equipment that gives access to CCAs. Additionally, all 74 users at issue had current Personnel Risk Assessments (PRAs) and valid NERC CIP training at the time of their access removals. None of the 74 users used their access after it should have been removed. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) removed access for all 74 users; 2) held a stand-down meeting with all of its members to discuss the severity of the issue and to reinforce the importance of removing access within the seven-day timeframe required by the Standard. The purpose of this meeting was to provide short-term correction on performance while additional actions and investigation were underway; 3) defined the process for the revocation of NERC CIP access in NERC CIP: Access Revocation Procedure in order to meet the compliance requirements of CIP v5 and to prevent future occurrences. In this process, the newly installed access management system tool automatically disables the access for any exited user for connected systems. The tool takes the place of the manual process in place under the Version 3 Program that was at issue in this noncompliance; 4) developed an internal escalation procedure for use by the team for removal of NERC CIP access and RFC_URE5 provided training to impacted personnel as part of the implementation. The procedural control and training will help ensure proper and timely attention to meet removal timeframes; and 5) developed a job aid for use by provisioning groups for the removal of NERC CIP access to a disconnected system and posted that job aid on the portal page for use by performers. This will address cases in the future where removal is needed and a system is not directly connected to the access management system. ReliabilityFirst has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017280 | CIP-007-3a | R1 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-007-3a R1. RFC_URE6 personnel determined that software was installed on one Cyber Asset without performing the required cybersecurity testing. In support of activities for compliance to NERC CIP V5, RFC_URE6 increased the use of its automated program for security and threat detection including tracking of baselines. The increased monitoring and alerting from the security tool identified this issue. As part of the IT process for reconciling the alerts and in performing an extent of condition, RFC_URE6 identified that one piece of software was installed on a NERC CIP Cyber Asset (a server). RFC_URE6 worked with the software vendor and determined that the service supports keystroke logging. This service was automatically installed to the target device when an individual with ADMIN privileges connected to the server performing normal job duties. RFC_URE6 intended to enable keystroke logging in the software environment at a future time after performing additional research as the software vendor documentation did not describe the software install process. The installation of the software was not planned nor expected. Due to lack of vendor documentation and since the service is only installed with the initial login by a user with ADMIN credentials connects, the service was not installed on the development server and cybersecurity tested prior to production installation. The installation of the service was not identified at the time testing was performed in the development environment because the security monitoring tool was not configured and enabled at that time. The root cause of this potential violation was the timing of the installation of the security monitoring tool in the development environment. A contributing cause of this potential violation was lack of vendor documentation on the automatic installation of the keystroke logging service when an individual with ADMIN privileges connected via Remote Desktop Protocol (RDP) to the server. RFC_URE6 intended to enable keystroke logging in the environment at a future time after additional research as the vendor documentation did not describe the keystroke install process. The duration of the noncompliance was approximately 1 month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor. The service that was enabled without testing supports keystroke logging. The service was used in the development environment but not formally tested as the service was part of a future phase of implementation. There were no identified issues prior to moving the application to production. The application functioned as designed. RFC_URE6 considered the harm level was minimal and unlikely to be realized for the following reasons: • RFC_URE6 IT enabled the service in the development environment with no issues. • RFC_URE6 IT performed cybersecurity testing on the service post-identification and identified no issues. There are several internal controls in place to detect or prevent violation occurrence, including: • RFC_URE6 IT uses a security monitoring tool to identify changes in baselines of its NERC CIP Cyber Assets. • RFC_URE6 IT has a documented process for performing cybersecurity testing in a development environment. • RFC_URE6 IT has a documented process for performing change management including a checklist as a human performance tool to ensure all necessary compliance steps are completed. While the current controls did not prevent the issue, the first control identified the potential violation. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) disabled the keystroke logger function. By disabling the function, the software will not be installed on other target devices; 2) removed the service from the server; 3) confirmed the server configuration and baseline is correct; 4) implemented and configured the security monitoring tool in the NERC CIP development environments; and 5) delivered updated training on the new security monitoring alerts for IT personnel with roles and responsibilities in the reconciliation process.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2017017281 | CIP-003-3 | R5 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-003-3 R5. As part of its transition to NERC CIP V5/V6, specifically CIP-004-5 R4.2, RFC_URE6's Information Technology (IT) department implemented a daily control to reconcile access permissions to access authorization records. RFC_URE6 IT completed the transition reconciliation and, in addition to the quarterly review performed, identified the following conditions where access was not implemented as approved in the current RFC_URE6 Security Request System (SRS): A. 2 Individuals were approved for electronic access to an electronic storage location containing Confidential CIP Asset Information (CCAI)/BES Cyber System Information (BCSI) – Role was requested for Test environment and granted in Production environment. Role required was required in Production. Wrong role selected in SRS. B. 1 individual with electronic access to a Critical Cyber Asset – Individual transferred and access was removed timely. Incorrect role provisioned when access requested post transfer. Additionally, through the same control, RFC_URE6 IT identified the following conditions without an authorization record in the current RFC_URE6 Security Request System (SRS): A. 9 Individuals with electronic access to a Critical Cyber Asset – Access was provisioned outside of SRS for a variety of reasons including access provisioned during development process being carried through to production environment, software bug allowed for automatic account creation, or apparent lack of adherence to the SRS process. B. 2 Individuals with electronic access to a EACMS – Access was provisioned outside of SRS due to an apparent lack of adherence to the SRS process. C. 17 Individuals with electronic access to an electronic storage locations containing CCAI/BCSI – Access was provisioned outside of SRS for a variety of reasons including access was provisioned during development process and carried through to production environment or due to an apparent lack of adherence to the SRS process. Although there are no SRS authorization records for provisioned access, each individual’s access was reviewed by the individual’s supervisor and the NERC CIP access Authorizer during RFC_URE6’s Quarterly Validations. Each individual had completed NERC CIP cyber security training and had a successful PRA at that time. The root cause of this potential violation was from a variety of reasons, including: 1. Access to the applications or electronic storage locations was granted prior to implementation of RFC_URE6’s current Security Request System. 2. Automatic account creation due to software bug. 3. Various human performance errors including incorrectly completing tickets, granting incorrect access, and not following documented process. 4. Immature process when adding new asset or BCSI repository from test to production. The duration of the noncompliance was approximately 5-1/2 years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The potential harm to the reliability of the BPS that could have occurred during the situation was minor to none. In all cases, each individual had completed NERC CIP cyber security training and had a successful PRA at the time access was provisioned. Each individual’s access was reviewed by the individual’s supervisor and the NERC CIP access Authorizer during RFC_URE6’s Quarterly Validations and the access was either approved or removed at that time. If the access was held in error and identified during the quarterly validation, this would have entered the RFC_URE6 non-conformance condition process at that time. The harm level was minimal to be realized for the following reasons: • Access was deemed appropriate by the NERC CIP Authorizer during the quarterly validations. • Each individual had completed NERC CIP cyber security training and had a successful PRA at the time access was provisioned. There are several internal controls in place to detect or prevent violation occurrence, including: • RFC_URE6 IT performs a review quarterly of all accesses to NERC CIP assets, systems and BCSI repositories. • RFC_URE6 IT uses its SRS for requesting, authorizing and processing all security permissions for NERC CIP assets, systems and BCSI repositories. • RFC_URE6 IT implemented a new daily control that reconciles access permissions to access authorization records. While the current controls did not prevent the issue, the first and third controls identified the potential violation. The new daily reconciliation control assures any unauthorized access will be identified promptly for corrective action limiting risk to RFC_URE6 NERC CIP assets. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) submitted SRS tickets in RFC_URE6’s Security Request System to authorize each access; 2) submitted SRS tickets and processed to remove access implemented incorrectly; 3) implemented a new access request reconciliation tool which generates a daily report identifying individuals with NERC CIP Access and no authorization tickets in RFC_URE6’s Security Request System. The reports are reviewed by IT daily; 4) installed software to correct the bug allowing for automatic account creation; 5) implemented automatic provisioning and de-provisioning for CCAI/BCSI repositories and the RFC_URE6 NERC domain where technology allows; 6) reinforced process and human performance tools with RFC_URE6 access request processors to ensure tickets are processed as authorized; 7) implemented a new step in the turnover process to ensure SRS tickets exist with approval by current NERC CIP Authorizer prior to new asset/system/CCAI repository being placed into production; and 8) updated their process to update EMS Permit database timely and automate provisioning and de-provisioning of EMS AD access.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2017017335 | CIP-007-3a | R1.2 | RFC_URE7 submitted a self-log stating that it had an issue of CIP-007-3a R1.2. In support of activities for compliance to NERC CIP V5, RFC_URE7 IT increased the use of its automated program for security and threat detection which included the tracking of baselines. Due to the increased monitoring and alerting from the security tool, RFC_URE7 IT identified that a piece of software was installed on one of the production servers. A security alert (report) was issued. RFC_URE7 IT reviewed this report five days later, and identified this issue and notified RFC_URE7 IT. Six days after the security alert was issued, RFC_URE7 IT was performing an extent of condition and during this process; the software was pushed to an additional production server. RFC_URE7 IT worked with the software vendor and determined that the software has a service that supports keystroke logging. This service was automatically pushed to the target device when an individual with ADMIN privileges connected via Remote Desktop Protocol (RDP) to the server. The automatic pushing of the service to the target device is the root cause of this noncompliance. RFC_URE7 intended to enable keystroke logging in the software environment at a future time after additional research was completed. The software vendor documentation did not describe the install process. The installation of the software was not planned nor expected. Although the service was installed on the development server, cyber security testing was not performed prior to production installation. The duration of the noncompliance was approximately twelve days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors: 1. The software is merely a keystroke logging service and does not affect the BPS. 2. Substantial internal controls were in place to prevent and detect against installation of Cyber Assets without first conducting cybersecurity testing to confirm no adverse impact to existing cybersecurity controls. Those controls and procedures included (1) only a limited number of applications are used in the NERC environment; (2) cybersecurity testing (and verification of such testing) of all Cyber Assets is conducted in the development environment prior to installation in the production environment; and (3) the security monitoring tool is used to detect anything that may have inadvertently entered the production environment prior to cybersecurity testing. 3. Going forward, with the security monitoring tool now implemented and configured in the NERC CIP development environment as well, any hidden processes like the one involved here will be discovered even before entering the production environment. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) disabled the keystroke logger function. By disabling the function, the software will not be installed on other target devices; 2) removed the service from the server; and 3) confirmed that the server configuration and baseline is correct. Mitigation activities that fix the issue and also prevent recurrence, RFC_URE7: 1) has already addressed this issue by implementing and configuring the security monitoring tool in the NERC CIP development environments; and 2) delivered updated training on the new security monitoring Alerts for RFC_URE7 IT personnel with roles and responsibilities in the reconciliation process.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2017017336 | CIP-003-3 | R6 | RFC_URE8 submitted a self-log stating that it had an issue of CIP-003-3 R6. RFC_URE8 IT identified two instances where Change Management processes were either incomplete or not followed. The failure to follow or complete its Change Management processes is the root cause of this noncompliance. 1) a workstation was decommissioned without processing a change record. 2) RFC_URE8 IT performed a planned change prior to receiving all necessary approvals. Both instances were a result of a communication breakdown between multiple parties that were coordinating the planned work. The duration of the noncompliance was approximately two weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors: 1. Work on the console was performed as planned and tested for cyber security concerns prior to implementation. Meeting was held and verbal approvals were given. The issue was documentation errors, not equipment errors. 2. The change work on the firewall was planned and cybersecurity tested, but did not have final approval. 3. Low impact to BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) submitted an emergency change for the first incident to document the work that was performed; and 2) received business approval for the second incident, after the work was completed on the same day. Mitigation activities that fix the issue and also prevent recurrence, RFC_URE8 held meetings for both incidents to counsel the individuals who did not follow the change control process to enforce expectations to verify all approvals prior to executing work. A phone conversation was held for the first incident, and meetings were held to address the second incident.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2017017337 | CIP-003-3 | R5 | RFC_URE8 submitted a self-log stating that it had an issue of CIP-003-3 R5. As part of transition to NERC CIP V5/V6, specifically CIP-004-5 R4.2, RFC_URE8 IT implemented a daily control to reconcile access permissions to access authorization records. RFC_URE8 IT completed the transition reconciliation and, in addition to the quarterly review performed, identified the following conditions where access was not implemented as approved in the current RFC_URE8 Security Request System (SRS): A. 1 individual with electronic access to a Critical Cyber Asset – Individual transferred and access was removed timely. Incorrect role provisioned when access requested post transfer. Additionally, through the same control, RFC_URE8 IT identified the following conditions without an authorization record in the current SRS: A. 2 Individuals with electronic access to a EACMS – Access was provisioned outside of SRS due to an apparent lack of adherence to the SRS process. B. 17 Individuals with electronic access to an electronic storage locations containing CCAI/BCSI – Access was provisioned outside of SRS for a variety of reasons including access was provisioned during development process and carried through to production environment or due to an apparent lack of adherence to the SRS process. Although there are no SRS authorization records for provisioned access, each individual’s access was reviewed by the individual’s supervisor and the NERC CIP access Authorizer during RFC_URE8’s Quarterly Validations. Each individual had completed NERC CIP cyber security training and had a successful personnel risk assessment at that time. The root cause is weaknesses in RFC_URE8's former process to reconcile access permissions to access authorization records. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors: 1. Very unlikely to cause harm to the BPS. 2. This was more of a procedure violation. 3. Individuals were properly NERC CIP Cleared. No harm is known to have occurred. | To mitigate this issue, RFC_URE8 submitted new SRS tickets in RFC_URE8’s SRS to re-authorize each access. Mitigation activities that fix the issue and also prevent recurrence, RFC_URE8: 1) implemented a new access request reconciliation tool which generates a daily report identifying individuals with NERC CIP Access and no authorization tickets in RFC_URE8’s SRS. The reports are reviewed by RFC_URE8 IT daily; 2) implemented, where technology allows, automatic provisioning and de-provisioning for CCAI/BCSI repositories and the RFC_URE8 NERC domain; and 3) reinforced, through counseling, process and human performance tools with RFC_URE8 access request processors to ensure tickets are processed as authorized.
2017-05-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016016404 | CIP-004-6 | R4; R4.1 | SERC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-6 R2. SERC_URE1 failed to authorize an employee prior to granting electronic access to an Electronic Access Control and Monitoring (EACM) system. SERC determined that SERC_URE1 self-reported this issue under the wrong Requirement (CIP-004-6 R2.2). SERC is processing this issue under CIP-004-6 R4.1, which more aligns with the specifics of the failure. A SERC_URE1 system administrator mistakenly granted remote access to the SERC_URE1 CIP intermediate access system, classified as an EACM, to a SERC_URE1 field engineer. The engineer required access to a different system, not associated with the CIP protected systems or networks in order to conduct maintenance activities. Five days later, while conducting a regularly scheduled weekly review, SERC_URE1 discovered this inadvertent access permission. SERC_URE1’s extent-of-condition review consisted of a review of all individuals within the intermediate system Active Domain group against all authorization records. SERC_URE1 discovered no additional instances of noncompliance. The root-cause of this issue was a lack of training and training material specific to granting access, for the system administrator role. This issue lasted for five days from when the SERC_URE1 system administrator granted access to an EACM without proper authorization, until SERC_URE1 revoked the access to the EACM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 granting access to an unauthorized individual could have permitted the untrained and unscreened individual to access EACMS, BCAs, or PCAs to create operational impacts and jeopardize the BES. However, the SERC_URE1 employee at issue had a current Personnel Risk Assessment and was an employee in good standing. The employee also had received SERC_URE1’s cyber security training and been previously authorized for access to Critical Cyber Assets under CIP Version 3. In addition, the access that SERC_URE1 inadvertently granted was to the intermediate system; therefore, the employee did not have direct access to the Cyber Assets within the ESP. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) updated the Electronic Security Perimeter/Physical Security Perimeter Access Procedure to enhance control barriers (authorizations); and 2) provided training on the updated procedure to all individuals that have the ability to grant ESP or PSP access.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016194 | CIP-007-3a | R3; R3.1, R3.2 | SPPRE_URE1 submitted a Self-Log stating that it had two issues of noncompliance with CIP-007-3a R3 (SPP2016016194). SPPRE_URE1 later submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-3a R3 (SPP2016016064). SPP RE administratively dismissed SPP2016016064, consolidating the facts and circumstances of SPP2016016064 with SPP2016016194. In SPPRE_URE1’s Self-Log, SPPRE_URE1 identified two issues of noncompliance with CIP-007-3a R3. The first noncompliance issue was discovered during a review of SPPRE_URE1’s patch evaluation and tracking documentation. SPPRE_URE1 discovered that during a six-month period, the SPPRE_URE1 employee tasked with performing the patch review process had not been documenting assessments where a vendor patch was determined not to address a security vulnerability. As a result, one or more monthly patch evaluation and tracking tickets were not created for six products (R3). No security patches were missed from the six vendors. During an internal review conducted by SPPRE_URE1, it was discovered that the assessment for a patch was completed seven days after the patch was released, but the assessment was not documented per SPPRE_URE1’s patch management process until 22 days after the assessment was completed. Although this patch was not a cyber security patch, SPPRE_URE1’s patch management procedure requires a patch evaluation and tracking form be completed at the time the assessment is performed (R3). SPPRE_URE1 submitted a Self-Report because the security patches for two Cyber Assets had not been assessed or implemented within 30 calendar days of availability (R3.1), and no compensating measures had been documented to mitigate the risk of not installing the patches (R3.2). During a review of pre and post-scan files for an open change request, a network engineer identified software on two Cyber Assets that was not included in the Cyber Asset’s documented baseline. Because the two software installations were not documented in SPPRE_URE1’s software baseline, the installations were not monitored in SPPRE_URE1’s patch management program. SPPRE_URE1 utilizes scripts installed on BES Cyber Systems to develop its software baselines. Because the scripts failed to identify the software, SPPRE_URE1 did not identify and evaluate any patches released from the vendors’ patch source list. For 642 days, there were 38 applicable security patches that were not evaluated, applied or mitigated for one of the software programs installed on a Cyber Asset. For 1055 days, while the second software program was installed on the same and an additional Cyber Asset, there were seven applicable security patches that were not evaluated, applied or mitigated. Collectively, the duration of these issues of noncompliance was 1055 days, from the date the first software program was installed and the outstanding patches were not installed, until the date both software programs were removed from the two SPPRE_URE1 Cyber Assets. SPPRE_URE1 determined that the root cause of these issues of noncompliance was a combination of human error, i.e., failure to adhere to a policy/procedure, and a policy gap resulting in failure to establish an accurate baseline for Cyber Assets applicable to CIP-007-3a. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to track, evaluate, and implement security patches for Cyber Assets located in the ESP could expose essential Cyber Assets to cyber-attack, potentially compromising the operation of computer and telecommunications systems necessary for the operation of the Bulk Electric System. As to the incomplete or untimely documentation of patch assessments identified during SPPRE_URE1’s internal reviews, it was determined that none of the patches were security patches. As to the two Cyber Assets with the undocumented, unpatched software, these Cyber Assets operate within a secure network that has no direct connection to the Internet. No actual harm is known to have occurred. SPPRE_URE1 has no relevant prior violations of CIP-007-3a R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) removed the the two software programs from its Cyber Assets; 2) revised its CIP cyber vulnerability assessment process to improve the methods utilized to accurately inventory software on all Cyber Assets; 3) performed a Cyber Vulnerability Assessment; 4) recorded all identified software in the applicable baselines; and 5) counseled relevant SPPRE_URE1 staff on the CIP security patch management process. SPP RE has verified the completion of all mitigation activity.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2016015968 | CIP-004-3a | R3; R3.2 | SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-3a R3.2 because it failed to update an employee’s Personnel Risk Assessment (PRA) within the required seven-year timeframe. While reviewing authorization records for the implementation of CIP-004-6, SPPRE_URE2 found that it did not update an employee’s PRA within seven years of the prior PRA. It was determined that during the process of updating seven year PRAs, the expiration date of the PRA for one employee was mistakenly associated with a second employee with the same last name, causing the second employee to not be identified for a renewed PRA. The second employee's physical and electronic access was revoked when the issue was discovered, 356 days after expiration of his PRA. The duration of this instance of noncompliance was 365 days, from the date the seven-year time period for the second employee’s PRA expired, through the date all access was revoked for the second employee. The root cause of this instance of noncompliance was a combination of human error in determining the correct PRA date for the employee and lack of procedural control to ensure employees with access have appropriate authorization records. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failing to timely update a PRA could cause SPPRE_URE2 to miss changes in an individual’s criminal history, an element of potential risk for safety and security. Nevertheless, the risk of this noncompliance was mitigated because the employee: (1) is a long-term employee with no performance issues; (2) possessed a prior PRA; and (3) had received annual cybersecurity training. The updated PRA did not include any adverse findings and the employee’s previous access was reinstated. No actual harm is known to have occurred as a result of this instance of noncompliance. SPPRE_URE2 has no relevant prior violations for CIP-004-3a R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) implemented a quarterly access and authorization verification process; 2) removed electronic and physical access for the employee; and 3) completed the employee’s PRA. SPP RE has verified the completion of all mitigation activity.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016328 | CIP-006-6 R1 | R1, Part 1.1, 1.5, and 1.8 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of CIP-006-6 R1 Part 1.1, Part 1.5 and Part 1.8. Specifically, for the first instance R1.1, a WECC_URE1’s employee removed a fence panel on the control center PSP in preparation for Information Technology (IT) staff to perform the work of relocating the data servers into a new rack in the control center server cage. WECC_URE1 IT staff completed the required work; however, at the conclusion of the job, the staff did not replace the fence panel and did not notify anyone that the fence panel was still removed. Nor did the anyone return to the control center server cage site to ensure the fence panel had been reinstalled once the work was completed. WECC_URE1 discovered the removed fence panel and immediately contacted the appropriate staff to reinstall the fence panel. The root cause of the first instance was inadequate processes to fully identify steps to restore, or validate, the original design of the PSP before, during, or after a change. For the second instance related to CIP-006-6 R1 Part 1.5, during a review of the alarm history from the weekend, WECC_URE1 staff discovered an unacknowledged PSP alarm an employee exited the control center without badging out, which triggered a forced door alarm. WECC_URE1's initiated an investigation into the situation. Data history on the security workstation in the control center was reviewed to confirm that the PACS alarm page had received the alarm. Staff on duty did in fact receive the alarm page but had not acknowledged the alarm, i.e., the alarm was still in an active alarm mode and did not notify personnel identified in WECC_URE1’s BES Cyber Security Incident response plan within 15 minutes of detection. This level of alarm was also programmed to trigger a constant audible alarm in the control center The constant audible alarm was not activated in this case. When asked, the on-shift staff stated that they were not aware of the unacknowledged alarm. The root cause of the second instance was human error, specifically lack of attention and appropriate response to a PSP alarm. For the third instance related to CIP-006-6 R1 Part 1.8, WECC_URE1 removed the outside door biometric card reader, at one of two physical access points to its control center in order to make the outside door an egress only access point. When the outside biometric card reader was deactivated and removed, the connection to the internal biometric card reader (slave device) was also disabled, resulting in deactivation of the slave reader. Staff received an alarm for loss of communications at the exterior door to the control center Staff had received a work order indicating work was being performed at the site. Staff contacted the contracted staff performing the work regarding the loss of communications alarm. Contracted staff informed stated that the alarm was expected since they were working on removing the device and following completion of work, the alarm would reset. Staff noticed that the control center biometric card reader alarm had not returned to normal and was still indicating a loss of communication. On further review of the hardware screens, staff noticed that both interior and exterior card readers of the control center exterior door were disabled. After consulting with the Communications Manager, the determination was made that the exterior door contact monitoring was inadvertently disabled. The root cause of the third instance was a lack of adequate testing of physical security equipment following a scheduled change. WECC determined the first instance began when the Standard and Requirement became mandatory and enforceable to WECC_URE1, and ended when WECC_URE1 staff reinstalled the fence panel to the control center server cage PSP, for 19 days of noncompliance. WECC determined that the second instance began when WECC_URE1 staff failed to respond to a forced door alarm at a PSP and ended when WECC_URE1 installed speakers directly to the control center security workstation which will provide an audible alarm whenever a security alarm is posted on the security workstation, for 3 days of noncompliance. WECC determined that the third instance began when WECC_URE1 failed to maintain two-factor authentication at its control center PSP and ended when WECC_URE1 dispatched staff to the control center for continuous monitoring until the biometric card reader issue could be resolved, for 7 hours of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In the first instance, WECC_URE1 failed to maintain an established PSP at a control center; in the second instance, it failed to appropriately respond to a PSP forced door alarm at a control center; and in the third instance, it failed to maintain two-factor authentication at its PSP at a control center. Failing to maintain a PSP; notify appropriate personnel of unauthorized access to a PSP; and monitor personnel access to a PSP posed a risk to the operation of the bulk electric system due to WECC_URE1’s inability to control or monitor physical access, which could result in malicious activity to, or the removal or destruction of, CIP assets; thereby potentially affecting the reliability of the bulk power system (BPS). For all three instances, WECC_URE1 implemented preventive controls to reduce the risk of potential unauthorized physical access occurrences, as well as changes to its CIP assets. These controls include administrative, technical, and physical controls. CIP cyber assets are configured with authentication, authorization, and accounting controls to restrict who can login or make changes to devices. WECC_URE1 has 24 hour-a-day, seven-day-a-week alarm logging and monitoring; security event logging for CIP cyber assets, and policies and procedures restricting physical and electronic access to only authorized personnel who have personnel risk assessments. No harm is known to have occurred. WECC_URE1 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE1 1) Reinstalled the fence panel; 2) Enhanced CIP signage at its PSPs; 3) Reinforced understanding of PSPs and PACS procedures to CIP authorized staff; 4) Installed speakers directly to the workstation; 5) Established a forum to foster a team approach to its security programs, to include monthly steering committee meetings; 6) Dispatched at security officer to monitor access until the bio card reader issue could be resolved; 7) Installed a tamper switch for the bio card reader as an additional security measure to prevent compromising the reader in the future; and 8) Reconfigured the master and slave readers and successfully tested for access control, forced door, and master reader tamper functions. WECC_URE1 completed mitigating activities and WECC verified WECC_URE1’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016126 | CIP-006-6 | R1, Part1.3 | WECC_URE2 submitted a Self-Report stating that it had an issue of CIP-006-6 R1 Part 1.3. WECC_URE2 reported that during its CIP Version 6 transition period, it evaluated six Electronic Access Control and Monitoring System (EACMS) devices as being associated with only its Medium Impact BES Cyber Systems (MIBCS), when in fact they were associated with both its MIBCS and its High Impact BES Cyber Systems (HIBCS); therefore, they should have been afforded two or more different physical access controls at the two Physical Security Perimeter (PSP) cabinets where the EACMS were located. The root cause was human error in assessing the six EACMS associated with all applicable BES Cyber Systems. WECC determined that this issue began when CIP-006-6 R1 Part 1.3 became mandatory and enforceable for WECC_URE2, and ended when WECC_URE2 replaced the card- readers at the two cabinets with keypad card readers, which require a pin, as well as an identification badge, for a total of 42 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to utilize two or more different physical access controls to control access to two cabinet containing EACMS associated with its MIBCS and HIBCS which could potentially result in an individual gaining access to the EACMS within the cabinets. Since the EACMS were responsible for multifactor authentication, such access could potentially result in denial of access to the MIBCS or HIBCS, resulting in a loss of visibility or control of these systems and the Bulk Electric System (BES) elements within them; thereby, potentially affecting the reliability of the Bulk Power System (BPS). However, the likelihood of this happening is minimal. The cabinets required badge access and they were both inside are larger room with access restricted to authorized personnel only. The cabinets had card alarming systems that would alert Security personnel of an issue. Additionally, WECC_URE2 had monitoring cameras pointed at the cabinet. No harm is known to have occurred. WECC_URE2 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE2: 1) Added multifactor authentication at the two cabinets; and 2) Created a checklist for departments to use to validate that all the applicable CIP Standards and Requirements are addressed prior to adding an EACM into production. WECC_URE2 completed mitigating activities and WECC verified completion of those activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2017017038 | CIP-006-6 | R2; Part 2.1 | WECC_URE3 and WECC_URE4 submitted a Self-Log stating they had possible issues of noncompliance with CIP-006-6 R2 Part 2.1. Specifically, WECC_URE3 and WECC_URE4 reported that a WECC_URE3 employee (Escort #1) with authorized unescorted physical access rights, escorted a visiting WECC_URE4 employee (Visitor) who did not have authorized unescorted access. The Visitor was escorted into a training room inside WECC_URE3’s building, which is a designated Physical Security Perimeter (PSP) for both WECC_URE3 and WECC_URE4. During the training, Escort #1 informed another WECC_URE3 employee (Escort #2) that they needed to attend a conference call and asked Escort #2 to assist the Visitor, if needed. However, Escort #1 did not inform Escort #2 that the Visitor required continuous escort while in the building. After the training, the Visitor left the training room and attempted to exit the building without Escort #2. Shortly thereafter, WECC_URE3 Security Operations staff found the Visitor and escorted them out of the building. The root cause of this issue was human error due to lack of communication between Escort #1 and Escort #2. WECC determined that this issue began when the Visitor was briefly left inside the building unescorted, and ended when the Visitor was escorted out of the building, for a total of approximately 20 seconds of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 and WECC_URE4 failed to provide continuous escorted physical access for one Visitor within the PSP at WECC_URE3’s High Impact BES Cyber System. Such failure could allow an unauthorized individual to physically access systems and intentionally, or accidentally, disrupt or make changes to equipment and systems. This could interfere with WECC_URE3 and/or WECC_URE3’s ability to operate, control, or monitor its Bulk Electric System elements, thereby potentially affecting the reliability of the Bulk Power System However, the Visitor has been a trusted employee for 17 months, and was subject to WECC_URE3’s standard criminal history checks and identification confirmation processes at the time they were hired. In addition, the badge issued to the Visitor did not allow them access to critical areas of the PSP that contained BES Cyber Systems (BCS), so at no time did the Visitor have physical access to BCS. Further, WECC_URE3 discovered the issue within approximately 20 seconds and immediately continued escorting the Visitor. No harm is known to have occurred. | To remediate and mitigate this issue, WECC_URE3 and WECC_URE4: 1) Escorted the visitor out of the building; 2) Provided additional training to the Escort and Visitor in this incident that when they sign-in any visitor into the EMC building, or when they are escorted, they must keep track of their respective visitor and escort; 3) Installed additional informational signs on the exterior and interiors of building PSP doors to reinforce visitor escort responsibility; and d. Reminded all employees with access to WECC_URE3’s High and Medium Impact PSPs of their obligations when acting as an escort to visitors in these locations. Also, reminded them of the informational flyer that was given to all visitors and escorts upon signing in with security operations at the building and the control room (another designated PSP). WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2017017039 | CIP-006-6 | R2; Part 2.1 | WECC_URE3 and WECC_URE4 submitted a Self-Log stating they had possible issues of noncompliance with CIP-006-6 R2 Part 2.1. Specifically, WECC_URE3 and WECC_URE4 reported that a WECC_URE3 employee (Escort #1) with authorized unescorted physical access rights, escorted a visiting WECC_URE4 employee (Visitor) who did not have authorized unescorted access. The Visitor was escorted into a training room inside WECC_URE3’s building, which is a designated Physical Security Perimeter (PSP) for both WECC_URE3 and WECC_URE4. During the training, Escort #1 informed another WECC_URE3 employee (Escort #2) that they needed to attend a conference call and asked Escort #2 to assist the Visitor, if needed. However, Escort #1 did not inform Escort #2 that the Visitor required continuous escort while in the building. After the training, the Visitor left the training room and attempted to exit the building without Escort #2. Shortly thereafter, WECC_URE3 Security Operations staff found the Visitor and escorted them out of the building. The root cause of this issue was human error due to lack of communication between Escort #1 and Escort #2. WECC determined that this issue began when the Visitor was briefly left inside the building unescorted, and ended when the Visitor was escorted out of the building, for a total of approximately 20 seconds of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 and WECC_URE4 failed to provide continuous escorted physical access for one Visitor within the PSP at WECC_URE3’s High Impact BES Cyber System. Such failure could allow an unauthorized individual to physically access systems and intentionally, or accidentally, disrupt or make changes to equipment and systems. This could interfere with WECC_URE3 and/or WECC_URE3’s ability to operate, control, or monitor its Bulk Electric System elements, thereby potentially affecting the reliability of the Bulk Power System However, the Visitor has been a trusted employee for 17 months, and was subject to WECC_URE3’s standard criminal history checks and identification confirmation processes at the time they were hired. In addition, the badge issued to the Visitor did not allow them access to critical areas of the PSP that contained BES Cyber Systems (BCS), so at no time did the Visitor have physical access to BCS. Further, WECC_URE3 discovered the issue within approximately 20 seconds and immediately continued escorting the Visitor. No harm is known to have occurred. | To remediate and mitigate this issue, WECC_URE3 and WECC_URE4: 1) Escorted the visitor out of the building; 2) Provided additional training to the Escort and Visitor in this incident that when they sign-in any visitor into the building, or when they are escorted, they must keep track of their respective visitor and escort; 3) Installed additional informational signs on the exterior and interiors of building PSP doors to reinforce visitor escort responsibility; and 4) Reminded all employees with access to WECC_URE4’s High and Medium Impact PSPs of their obligations when acting as an escort to visitors in these locations. Also, reminded them of the informational flyer that was given to all visitors and escorts upon signing in with security operations at the building and the control room (another designated PSP). WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2016016567 | CIP-010-2 | R2, Part 2.1 | WECC_URE5 submitted a Self-Report stating that, it had an issue of CIP-010-2 R2.1. WECC_URE5 installed five BES Cyber Assets (BCAs) at its control center. Where the capability exists, WECC_URE5 utilizes software to automatically monitor baseline configuration changes to BCAs within the control center. WECC_URE5 performed a ‘first check’ to determine whether the five BCAs in scope could utilize the software as an automated process. They determined that the BCAs were capable and should have had the software installed; however, there was no item in WECC_URE5’s new build checklist to remind them to add this software for automated baselining, resulting in a lapse in monitoring, documenting, and investigating detected unauthorized changes. The root cause was a lack of effective preventive controls to ensure appropriate software is installed on applicable BCAs prior to putting them into the production environment. WECC determined that this issue began when the five BCAs were put into production, and ended when the software was added to all five BCAs and monitoring for changes to the baseline configuration commenced, for a total of 23 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to monitor at least once every 35 calendar days for changes to the baseline configuration, and document and investigate detected unauthorized changes on five BCAs. Failing to monitor for baseline changes could result in the BCA being changed without WECC_URE5’s knowledge. Unknown changes could result in BCA system instability, introduction of malicious code, or control of the system operator console resulting in loss of visibility to generation, transmission, and/or balancing that the WECC_URE5 performs. The likelihood of the risk occurring was minimal. WECC_URE5 has a change management control in place which requires authorization to any configuration changes to its BCAs. WECC_URE5 has a calendar reminder to perform manual baseline comparisons every 35 days for BCAs that require it. There were no unauthorized changes to the baseline configuration during the period that the five BCAs were not being monitored. No harm is known to have occurred. WECC_URE5 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE5: 1) Added security software to the five BCAs in scope and commenced automated baseline configuration monitoring; and 2) Added security software to its commissioning checklist to ensure it is installed on applicable BCAs prior to adding the asset to the production environment. WECC_URE5 completed mitigating activities and WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2016016033 | CIP-006-3c | R1.6.2 | WECC_URE6 submitted a Self-Report stating that, it had an issue of CIP-006-3c R1.6.2. Specifically, as part of an emergency preparedness exercise, an WECC_URE6 employee was tasked to perform a structural inspection at a control center which resides within a Physical Security Perimeter (PSP). The employee signed into the PSP as a visitor and was escorted into the PSP by another employee who was authorized to act as an escort. The escort left the visitor in the PSP unescorted while the escort went on a break. The escort continued his escorting responsibilities until both the escort and the visitor exited the PSP and signed the access log, for a total of three minutes of noncompliance. WECC_URE6 Security personnel observed the unescorted visitor in the PSP at reported the issue to the Security Administrator. The root cause of this issue was WECC_URE6 personnel not following established processes when acting as a physical escort in a PSPs. This issue started when WECC_URE6 failed to provide continuous physical escorting within the control center PSP and ended when WECC_URE6 resumed escorting of the visitor within the control center PSP. | WECC_URE6 failed to provide continuous escorting of a visitor within a PSP. An unauthorized visitor in a PSP poses a potential risk due to their ability to physically access systems which operate, control, and monitor Bulk Electric System elements at WECC_URE6. Unauthorized visitors could also allow other unauthorized individuals into the PSP, to intentionally or accidentally disrupt or make changes to equipment and systems, thus potentially affecting the reliability of the Bulk Power System (BPS). This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. WECC_URE6 implemented preventive and detective controls to reduce the potential risk to the BPS, which included electronic badge card reader systems to control physical access. Additionally, WECC_URE6 performed Personnel Risk Assessments and CIP training for both role separation and function. WECC_URE6 also had authentication systems that control access to its Critical Cyber Assets, to include 24 hours-a-day, seven days-a-week security monitoring of the control center PSP. No harm is known to have occurred. WECC_URE6 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE6: 1) Resumed physical escorting of the visitor in the PSP; 2) Had its facilities security administrator send a memorandum to all security personnel to provide directions for briefing on escort responsibilities, which was acknowledged by the Security personnel as being received; 3) Incorporated the directions of the memorandum into the next post order update; and 4)Performed one-on-one physical security guideline refresher training with the escort, his supervisor and the Security Administrator.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2016016692 | CIP-004-6 | R5.1 | WECC_URE7 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-6 R5 Part 5.1. Specifically, WECC_URE7 reported that it failed to revoke unescorted physical access for an employee within 24 hours of their documented termination action. The employee voluntarily terminated employment with WECC_URE7 and the WECC_URE7 did not remove the employee's ability for unescorted physical access within 24 hours. The employee had physical access to WECC_URE7’s Physical Security Perimeter (PSP), but did not have any electronic access to WECC_URE7’s BES Cyber Systems. This issue started when unescorted physical access was not revoked for one employee within a timely manner and ended when the access badge was disabled for the terminated employee. The root case of this issue was WECC_URE7 personnel not following the physical access revocation procedure and policy. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The termination was voluntary and the employee left in good standing. Additionally, the terminated employee did not have any electronic access to WECC_URE7’s BES Cyber Systems. WECC_URE7 has implemented controls to prevent unauthorized physical access to BES Cyber Systems, including using a Physical Access Control System (PACS) with badge access cards at the access points to control center PSPs. WECC_URE7 has also implemented detective controls by performing monthly reviews of physical access by comparing the access system live data accounts with the authorized list of personnel. This noncompliance was discovered through an internal spot check on physical access and WECC_URE7 confirmed through a review of access logs that the terminated employee’s access card had not been used since the termination date. No harm is known to have occurred. | To mitigate this issue, WECC_URE7: 1) disabled the terminated employees access badge; 2) held a meeting with management and supervisors to re-enforce its policy to obtain company access cards and/or fobs when an employee terminates; 3) emailed all employees with unescorted physical and/or electronic access to BES Cyber Systems a copy of a guidance document, which included a summary of this issue of noncompliance, and a reminder of the notification requirements currently in its policies applicable to termination or transfer of employees with authorized access to BES Cyber Systems; and 4) added instructions to the policy pertaining to the retrieval of access cards and/or fobs from departing personnel. WECC has verified the completion of all mitigation activity.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2016016127 | CIP-006-6 | R1, Part 1.2 | WECC_URE8 submitted a Self-Report stating that it had an issue of CIP-006-6 R1, Part 1.2. WECC_URE8 discovered that it had incorrectly configured its Physical Access and Control System (PACS) when updating physical access profiles. In the process of updating access profiles within its PACS, WECC_URE8 did not remove its Physical Security Perimeter (PSP) doors at its Medium Impact BES Cyber System (MIBCS) from the new profiles, resulting in unauthorized physical access being mistakenly granted to 10 employees. The root cause of this issue was a lack of adequate procedures, specifically for updating WECC_URE8’s PACS access profiles. WECC determined that this issue began when CIP-006-6 R1 became mandatory and enforceable for WECC_URE8, and ended when WECC_URE8 disabled the 10 employees’ unauthorized physical access, and removed the PSPs from the new profile, for a total of 57 days of noncompliance. | WECC_URE8 failed to follow defined operation and procedural controls to restrict physical access to its MIBCS . Specifically, it did not ensure that all PACS profiles were properly configured to restrict access to PSPs. Such failure could result in access to employees who are not authorized to access Bulk Electric System (BES) elements, where intentional or unintentional harm could be done; thereby, potentially affecting the reliability of the bulk power system (BPS). This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The likelihood of the risk occurring was reduced by the controls WECC_URE8 had implemented. WECC_URE8 locks all its computers and equipment in the MIBCS when the SCADA technician is not in the room and WECC_URE8’s PSPs are staffed with authorized employees 24 hours-a-day. Based on the controls in place, WECC determined that the issue had a low risk of causing minor harm. No harm is known to have occurred. WECC_URE8 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE8: 1) Disabled the 10 employees’ unauthorized physical access; 2) Removed the PSPs from the new profile; 3) Created appropriate profiles and deleted those no longer needed; 4) Installed a standalone access control system for controlled areas as identified by the physical security program; and 5) Implemented two separate access protocols; one for CIP access and one for corporate, to include alerting via email for access attempts that have not been authorized for said access.
2017-04-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2016016458 | CIP-007-6 | R2 | FRCC_URE1 submitted a Self-Report that it had an issue of CIP-007-6 (R2). FRCC_URE1 failed to apply the applicable patches within 35 days of the evaluation completion, as required by part 2.3. Several unique security patches were assessed to be applicable. The majority of the installations were completed more than 35 days after the assessment. The final patch was installed 60 days after the assessment. The root cause of possible violation is insufficient resources assigned to patch management, and insufficient monitoring and reporting. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). FRCC determined that the issue posed a minimal risk as the delayed application of security patches may prolong the presence of software vulnerabilities, which if exploited, could grant access to unauthorized personnel. All of the devices were located within networks which are firewall-protected, with encryption and two-factor remote authentication, thus reducing the risk of unauthorized remote access to the devices. All of the devices were located within the physical security perimeter. This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) verified that patches do not apply to BES cyber assets; 2) verified that no physical or electronic access related cyber security incidents were reported during the time that the patches were not applied; 3) verified that access to subject devices requires two-factor authentication using a device that has been authorized and configured for access; and 4) verified that activities to prevent recurrence were successful by tracking next patch cycle to completion (all applicable patches for next cycle installed on time). To prevent recurrence, FRCC_URE1: 1) added one (1) additional resource which allowed an existing full-time employee to be dedicated to patch related activities (scanning all the devices and validating that patches were installed on the appropriate devices); 2) transferred tasks to an existing resource of creating and tracking change tickets for patch assessment, testing and implementation of the patches. Prior to closing the tickets, this resource must verify the evidence that patches were implemented and that the corresponding baseline(s) have been updated; and 3) instituted an internal control of weekly reporting on patching status by compliance (independent of operations).
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016180 | CIP-007-6 | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-6 R2. After the implementation date for CIP-007-6 R2, RFC_URE1 was required to evaluate the applicability of security patches within 35 days of the release of the security patches. For security patches released on CIP Version 5 enforceable date, RFC_URE1 had to evaluate the applicability of those security patches and updates within 35 days. RFC_URE1 performed a compliance review to determine if it had timely assessed the security patches and determined that it did not evaluate 35 software inventory items for the applicability of security patches within the requisite 35 days. This issue was discovered because RFC_URE1 implemented self-monitoring internal controls to detect errors or irregularities and to support effective compliance with respect to its newly implemented CIP v5 compliance program. RFC_URE1’s review determined that this timely evaluation did not occur because its subject matter experts (SMEs) did not use a complete software inventory form to monitor and evaluate security patches and updates. This was in conflict with RFC_URE1’s CIP v5 program, which requires SMEs to use a complete software inventory form to monitor and evaluate security patches and updates. In this case, however, the SMEs did not follow the program and created a software inventory independent of existing baseline information. This noncompliance involves the management practice of workforce management as a result of ineffective training as well as the management practice of implementation due to the ineffective roll out of RFC_URE1’s CIP v5 Program. RFC_URE1 instituted new processes and a new program to satisfy compliance with new CIP v5 Standards and Requirements and this was the first time RFC_URE1 was required to implement it. This included creating a complete software inventory to monitor and evaluate security patches and updates. The SMEs were ineffectively trained on the new patching process and failed to implement it and that ineffective training is the root cause of this noncompliance. Although RFC_URE1 SMEs failed to follow its CIP v5 patching process, RFC_URE1 implemented strong self-monitoring internal controls to detect errors or irregularities in its newly implemented CIP V5 program, which demonstrates stronger capabilities in reliability quality management. One of these internal controls was promptly performing a compliance review after the due date for the security patch assessment process and that internal control worked as designed and discovered this noncompliance. The duration of the noncompliance was approximately thirteen days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although RFC_URE1 did not assess the applicability of all security patches within 35 days of their release and did not create a dated mitigation plan prior to the completion of that 35-day assessment period (CIP-007-6 R2.2), RFC_URE1 did assess and install all applicable security patches involved in this noncompliance during the 35-calendar-day patch implementation cycle (CIP-007-6 R 2.3). CIP-007-6 R2 allows RFC_URE1 up to a total of 70 days to assess and implement applicable security patches, but patch assessment must be completed within 35 days of the patches’ release. RFC_URE1 implemented all applicable security patches involved in this noncompliance within that 70-day window. All applicable patches were installed 49 days after the patches were released. RFC_URE1 did quickly identify, assess, and correct this noncompliance illustrating that their patching controls are functioning effectively. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) re-examined the inventory to determine what assessments were missed. These patch assessments were then all completed; 2) worked with consultants to provide the SMEs with training on the use of the software inventory from the baseline so as to monitor available security patches from the appropriate software inventory; 3) revised and improved its documented security patch monitoring procedures; and 4) provided the SMEs with increased support from a contractor that helps to maintain the baseline software inventory. This provides RFC_URE1 personnel with additional controls during the process to ensure that all patch assessments are completed timely.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015997 | CIP-002-5.1 | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-002-5.1 R1. During a routine data validation effort, RFC_URE2 identified Remote Management Interface Cards (RMICs) in the SCADA environment that should have been included in RFC_URE2’s Bulk Electric System (BES) Cyber Systems List pursuant to CIP-002-5 R1. RFC_URE2 performed a scan of the SCADA environment and identified the RMIC devices, but did not consider them separately from their server assets (or parent assets), and therefore did not include them separately in RFC_URE2’s Critical Cyber Asset list pursuant to CIP-002-3 R3. Although not included in RFC_URE2’s Critical Cyber Asset list, the assets were secured because they were in a defined Electronic Security Perimeter (ESP) and had all other CIP protections except recovery procedures. After reevaluation based on additional clarity in CIP-002-5.1 R1, RFC_URE2 determined that the RMICs should be identified in its asset list separately from the servers. The root cause of the noncompliance was lack of clarity in RFC_URE2’s BES Cyber System Identification Methodology due to lack of understanding relating to the configuration of the RMICs. This involves the management practice of workforce management, which includes ensuring staff are properly trained and have expertise in, and understanding of, the subject matter. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk of not including an asset on the BES Cyber Systems list is that RFC_URE2 will not implement the required protections. However, this instance is mostly a documentation type noncompliance because, except for not having recovery plans, the assets included all of the protections required by the CIP Standards, including being in a defined ESP. Additionally, RFC_URE2 quickly self-identified the issue through a detective control, which limited the duration of any risk to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) added the RMICs to the asset list; 2) updated its recovery procedures to include the RMICs; 3) revised its BES Cyber System Identification Methodology to specifically address a review for embedded and remotely configured devices; and (4) updated it BES Cyber System walkdown process to identify cross-domain or dual-homed assets. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016177 | CIP-004-6 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-6 R5. RFC_URE3 has a documented policy that requires all supervisors to send an email to a dedicated Human Resources (HR) mailbox when an individual’s employment is terminated. HR then completes an Access Revocation Form, which alerts the appropriate department to remove the individual’s physical and electronic access. The HR team member monitoring the Access Revocation Mailbox is responsible for timely processing all personnel status changes. A RFC_URE3 intern, who had unescorted physical access to critical locations and electronic access to Bulk Electric System (BES) Cyber System Information, completed the internship. The RFC_URE3 supervisor sent the required email to HR’s dedicated mailbox. However, when the HR analyst saw the email in the mailbox, it was flagged as being “read,” which lead the analyst to believe that the email had already been processed by another member of the HR team and no additional action was needed. The HR team member did not complete an Access Revocation Form and the intern’s access was not removed within 24 hours. However, RFC_URE3 collected the intern’s access badge before the individual left the premises and the intern never had Interactive Remote Access. On the following business day, another HR analyst noticed the supervisor’s email and reviewed it for completion and discovered that it had not been processed. The HR analyst immediately processed and completed the Access Revocation Form. Both relevant departments were notified and all access was removed within 2 hours. The root cause of this noncompliance was the fact that the relevant process did not specifically assign ownership of an access removal request to a particular HR analyst. This major contributing factor involves the management practice of workforce management, which includes managing employment status changes. The duration of the noncompliance was approximately two days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk of this noncompliance is that the intern could have accessed protected information either physically or electronically when he was not authorized to do so. This potential risk was mitigated by the following factors. First, RFC_URE3 collected the intern’s access badge before the individual left the premises, which eliminated the possibility that the intern could have physically accessed any protected information. Second, the intern never had Interactive Remote Access, which eliminates the possibility that the intern could have electronically access any protected information after leaving the premises. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed physical and electronic access for the intern immediately upon discovery of the error; 2) improved its internal process by specifically identifying ownership and monitoring of the HR Access Revocation mailbox and specifying the process for hand off of the Access Revocation Mailbox between HR personnel. The HR supervisors will continue to own/monitor the Access Revocation mailbox during the evenings, weekends and holidays; 3) held a dedicated staff meeting to explain the details of the incident and communicate expectations moving forward. At this meeting the new internal process was reviewed with the impacted HR personnel; and 4) took disciplinary action with the HR Analyst who failed to timely process the Access Revocation Form. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016057 | CIP-005-5 | R2 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-005-5 R2. RFC_URE4 discovered that eight cyber assets associated with RFC_URE4's phone system did not implement multi-factor authentication as required by CIP-005-5 R2 P2.3. The cyber assets and related network subnets were designated as CIP assets on the eve of the CIP version 5 transition. However, at that time, RFC_URE4 did not properly update the firewall configurations to require two- factor authentication. RFC_URE4 updated the firewall configuration to require two-factor authentication. The root cause was an error in not following RFC_URE4’s process. When cyber assets are designated as CIP in RFC_URE4’s environment, the process requires RFC_URE4 to review all firewalls to ensure compliance with CIP Standards, including CIP-005-5 R2. Here, a communication breakdown occurred where one group mistakenly thought the review was compete. This involved the management practice of workforce management, which includes effective training regarding the required processes. The duration of the noncompliance was approximately 26 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The purpose of requiring two-factor authentication is to make it more difficult for a bad actor to gain unauthorized access to a system. Here, only a small subset of individuals had authorized access, thus leaving less opportunity for someone to obtain their credentials. Also, access was further restricted in that onsite users needed to first use a corporate jump server and traffic was encrypted and, for remote users, RFC_URE4 utilized the required two-factor authentication to access the corporate network prior to accessing the jump server. Thus, there were additional protections or barriers in place to prevent unauthorized access to the subject cyber assets. Lastly, the issue affected only eight cyber assets, and RFC_URE4 quickly identified and mitigated the issue. Accordingly, the issue posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) updated the firewall configuration for the assets to apply the rules that only allow the required methods of interactive access; and 2) conducted an awareness campaign that includes a reminder that all applicable CIP requirements need to be applied to a cyber asset before it is classified as a CIP asset. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016055 | CIP-007-3a | R5 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. RFC_URE4 discovered that it did not change the password within the required 15-month timeframe on the local Windows administrator account on 16 CIP servers. Regarding the root cause, the passwords were missed during a project where RFC_URE4 migrated to new Active Directory domains and, as a result, renamed local administrator accounts, including the servers at issue. However, RFC_URE4 failed to update its annual password reset tracking documentation to reflect the new domain names and, as a result, did not update the passwords on schedule. This issue involves asset and configuration management as RFC_URE4’s processes lacked sufficient controls to manage the effects of implementing changes to assets. More specifically, RFC_URE4 did not recognize that it needed to update its annual password reset tracking documentation to reflect the new domain names. The duration of the noncompliance was approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, access to the Windows servers and local administrator account passwords is tightly controlled as only a very limited number of people have knowledge of the password and access the assets, a user would first have to use a virtual private network (VPN) and/or multi-factor authentication before gaining access. Additionally, all local server accounts are monitored for failed login attempts (and there were none during the time period of the noncompliance), thus reducing the likelihood that a bad actor could have identified the passwords and gained access. Also, for most of the accounts, RFC_URE4 was less than six weeks late in changing the passwords. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) changed the passwords for the local administrator accounts; and 2) implemented a process change to require system administrators to validate accounts with passwords that require changing with the accounts configured on the cyber asset, to prevent recurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016016054 | CIP-010-2 | R1 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-010-2 R1. RFC_URE4 executed 11 separate change requests to cyber assets. These changes were all identified as impacting the configuration baseline of assets. As part of the new CIP version 5 process, RFC_URE4 analysts were required to run a baseline comparison between the test assets and the production assets to account for any differences in operation between the test and production environments. However, the RFC_URE4 analysts overlooked this comparison step in the 11 instances and therefore were not able to provide documentation on the differences between the test asset and production assets as required by CIP-010-2 R1 Part 5.2. Regardless, as required by RFC_URE4 policy, all changes were tested on comparable test assets prior to deploying the change. Further, the production deployment change request documentation included test procedures data for all security controls on the production assets before and after the change. The root cause related to errors in following new CIP version 5 processes that required additional documentation as compared to version 3 processes. This involves the management practice of workforce management, which includes sufficient training to ensure employees understand and follow new processes. The duration of the noncompliance was approximately three weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The purpose of the baseline comparison between the test assets and the production assets is to identify and account for any differences in operation between the test and production environments so that a change does not adversely affect the production environment. This risk was mitigated here because RFC_URE4 designates specific systems for testing changes to align with production assets, and monitors and controls baselines in the testing environment, to ensure close alignment between the production and test assets such that differences are minor and do not require additional steps to account for the differences. Thus, the likelihood of having meaningful differences between testing and production was reduced. Additionally, per RFC_URE4 policy, all security controls were tested on the CIP Cyber Assets before and after the change to ensure the change did not have unintended adverse effects, including those that could have unknowingly resulted from having different baselines in test versus production assets. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) assigned an analyst to its Change Control Review Board to ensure all required documentation is complete for any change impacting a CIP Cyber Asset prior to approving the change request prior to deployment; 2) counseled the analysts on new requirements; 3) reviewed all applicable change requests to identify request tickets that have missing CIP-010 R1 Part 5.2 evidence components; 4) automated the baseline comparison testing between production and test and included the test results in all relevant change control tickets; and 5) modified the change control ticketing system to perform a live lookup in the asset management system database to identify if target assets are Bulk Electric System (BES) Cyber Assets and, if the asset is a BES Cyber Asset, the submitter is required to add the comparison document to change control ticketing system if the change is expected to modify the existing baseline.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017212 | CIP-004-6 | R2 P2.1 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-004-6 R2.1. RFC_URE5 has employees who have access to one or more RFC_URE5 NERC CIP Bulk Electric System (BES) Assets (locations that house Medium Impact BES Cyber Systems). In order to obtain access, these employees follow the RFC_URE5 processes and procedures for access to a NERC CIP Medium Impact Asset, which includes NERC CIP training and a Personnel Risk Assessment (PRA). It was identified that the computer-based training (CBT) module used at RFC_URE5 for CIP initial and annual requalification training was not updated in to reflect the current NERC training materials. The RFC_URE5 NERC CIP training is reviewed and updated as required annually. If there are changes made to the training material, the training module is updated in all locations that the training is stored. For RFC_URE5 employees, the training module is e-mailed to the RFC_URE5 Analyst. Once the RFC_URE5 Analyst receives the updated training material, they forward it to the RFC_URE5 Training Department to be updated in the RFC_URE5 CBT system. The noncompliance occurred due to the training not being updated in the RFC_URE5 CBT system. The RFC_URE5 CBT system is the only system in which the NERC CIP training update is not directly provided by or is not accessible by the NERC CIP database administrator. All other instances of distribution of the NERC CIP training content are updated and/or are accessible by the NERC CIP Database Administrator. Other instances of distribution of the NERC CIP training content include: • NERC CIP training in the Learning Management System, • training content links on RFC_URE5 SharePoint sites, • self-training e-mails (an e-mail sent to personnel that require NERC CIP training which includes the training content to review and a self-training attestation form that must be filled out, signed and returned to the NERC CIP Database administrator), and • classroom training (in person or webex training provided by the NERC CIP Database administrator or other members of the NERC Central department). These other instances of distribution above have all been reviewed and the current training material is being used. The issue was identified by the NERC CIP Database Administrator when contacted via e-mail. The instructor was performing a review in preparation to update the RFC_URE5 CBT system to include the current training module. Upon receipt of the e-mail, the NERC CIP Database Administrator identified that the training content discussed in the e-mail was from an outdated version of the training module. Failing to update the CBT used at RFC_URE5 for CIP initial and annual requalification training is the root cause of this noncompliance. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential impact to the BPS is that personnel may have access to the BES Cyber Systems without a full understanding of the responsibilities and risks associated with their access privileges. RFC_URE5 reviewed the differences in the two sets of NERC training materials. Although CIP training was performed using the previously provided NERC training materials, it was determined that the changes between the outdated training material and current training material were minor. All personnel identified also had a current PRA. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) updated the RFC_URE5 CBT System to the current NERC CIP training module; 2) implemented a new internal control for the NERC CIP Database Administrator to request a confirmation that the RFC_URE5 CBT system has been updated with the current training module after the training is forwarded to the Point of Contact; 3) issued an email to RFC_URE5 personnel describing the differences between the two sets of NERC training materials. The purpose of this action is to notify personnel promptly of any differences pending completion of the revised CBT training module; 4) implemented the structure to drive completion of the revised CBT training module. This training will be performed outside of the normal annual requalification pattern for most personnel. It will require not only notification of affected personnel but the setup of any computer infrastructure to allow entry and completion to the CBT training module; 5) tracked and verified that all RFC_URE5 CIP Personnel who previously took outdated NERC CIP training through CBT have completed retraining with current training content; 6) added an Order to track the annual review of the CBT training module; and 7) identified a RFC_URE5 point of contact to update the NERC CIP training in the RFC_URE5 CBT system and ensure that they are trained on how to update the content.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2017017213 | CIP-004-3a | R2 R2.3 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-004-3a R2.3. IT tracked NERC CIP training for RFC_URE5 employees and contractors with cyber access and access to protected information exclusively on a spreadsheet. It was discovered that four individuals had not received their annual NERC CIP training within the 15-month window after their yearly training (in all cases, Personnel Risk Assessments (PRAs) were up to date). One individual only had access to protected information (now referred to as Bulk Electric System (BES) Cyber System Information (BCSI)), while the other three had cyber access as well. Each month, IT generates a list of individuals who last were trained 12 months prior. The list is restricted to those individuals who require, or may require, access to the IT SharePoint BES Cyber System information repository or to BES Cyber Assets. However, the filters resulted in some individuals being inadvertently dropped from those lists. The drops were not noticed in the next month’s review because the filters were based on the previous year's training. The training issue occurred because the spreadsheet was not filtered to show the correct personnel and contractors due for training during the monthly review and this filtering issue is the root cause of the noncompliance. The mistake was identified as the spreadsheet was being updated with PRA and training dates for new contractors. The duration of the noncompliance was approximately seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These individuals had previously received the NERC CIP training and all of their PRAs were current. The individuals retained cyber access and/or access to BCSI in which they had previously had access to. Additionally, the annual training that had been missed was not significantly different from the prior training they received. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) initiated the removal of access for all identified employees and contractors; 2) ensured the four identified personnel have completed the annual NERC CIP training; 3) reviewed the IT Accounts and Access spreadsheet to verify that every individual’s training is up to date without filtering; 4) reviewed IT Access list to verify that every individual’s Personnel Risk Assessment (PRA) is up to date; 5) reviewed access lists and verified that every individual’s training and PRA is up to date; 6) ensured all employees and contractors on the IT access list(s) have the NERC CIP task, NERC CIP training and NERC CIP PRA qualification listed; and 7) ensured all employees and contractors on the access list(s) have the NERC CIP task, NERC CIP training and NERC CIP PRA qualification listed.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2016016176 | CIP-007-6 | R2 | RFC_URE6 submitted a Self-Report stating that it had an issue with CIP-007-6 R2. As part of its plan for transitioning to CIP version 5, RFC_URE6 introduced a specific internal policy for managing the target installation date for certain security patches. Specifically, this policy stated that any patch which had been assessed as applicable more than 35 days prior to the CIP Version 5 enforceable date, should be installed by that date, or had a mitigation plan created. A vendor released a particular patch primarily addressing a vulnerability associated with internet browsing. RFC_URE6 assessed that patch as CIP applicable the next day. Later that day, a corporate vendor notified RFC_URE6 that the patch should not be deployed due to a conflict with that vendor’s application. Because the vendor’s application was only present in the corporate environment and not present in the CIP environment, RFC_URE6 agreed that the patch should be delayed from deployment to corporate workstations only. To accomplish this task, RFC_URE6 issued a manual override to specifically exclude this patch from the patch availability data set for the corporate environment. However, RFC_URE6 inadvertently copied this incomplete patch availability data set over to the CIP environment as well. As a result, the responsible personnel lost track of the need to install this patch in the CIP environment by the CIP Version 5 enforceable date. The root cause of this noncompliance was inadequate documentation and training. The personnel responsible for exporting the patch availability data set over to the CIP environment did not understand that this particular patch should not have been excluded from the CIP environment. This major contributing factor involves the following management practices: (a) workforce management, which includes providing training, education, and awareness to employees; (b) asset and configuration management, which includes controlling changes to assets; and, (c) information management, which includes managing information item risk, identifying and assessing information item risk, and addressing information item risk. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the patch at issue addressed a vulnerability that would typically be exploited through internet access. Because the workstations missing the patch have no internet access, there was a minimal likelihood that an external or non-trusted source could have exploited this vulnerability on the impacted workstations. Second, RFC_URE6 assessed the patch at issue as having a vulnerability risk rating of 0, which provides further support for the conclusion that possible exploitation of this vulnerability was unlikely in this case. Third, RFC_URE6 had deployed malware detection software which would have alerted and sought to prevent any attempted exploit. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) recommended corrective feedback for employee, including discussion of process adherence, attention to detail, and reminder of expectations set in policy and training for reporting potential issues of noncompliance; 2) created a plan to mitigate risk of the related vulnerabilities until patch installation can be completed; 3) enhanced the vulnerability assessment procedure to address all missing patches identified as vulnerabilities regardless of vulnerability rating; 4) documented, as a formal NERC CIP Compliance procedure, the process of acquiring patch availability data into the corporate environment and exporting it to the NERC CIP environment. Ensured that the procedure is written in a manner which will result in the complete data set being transferred to the NERC CIP environment. The procedure shall include steps to create a compliance artifact of successful transfer for each transfer performed; 5) trained all personnel (primary and backups) who might be involved in the patch availability acquisition and export process to ensure they understand the expectations and are able to execute the procedure successfully; 6) created a (monthly) compliance control activity to document the successful transfer of patch availability information to the NERC CIP environment and creation of success artifact; and 7) continued analysis of vulnerability scan results for those items below the procedural mitigation threshold to ensure that no additional vulnerabilities are due to missing patches. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2016016175 | CIP-007-6 | R2 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-007-6 R2. As part of its plan for transitioning to CIP version 5, RFC_URE7 introduced a specific internal policy for managing the target installation date for certain security patches. Specifically, this policy stated that any patch which had been assessed as applicable more than 35 days prior to the CIP Version 5 enforceable date, should be installed by that date, or had a mitigation plan created. A vendor released a particular patch primarily addressing a vulnerability associated with internet browsing. RFC_URE7 assessed that patch as CIP applicable the next day. Later that day, a corporate vendor notified RFC_URE7 that the patch should not be deployed due to a conflict with that vendor’s application. Because the vendor’s application was only present in the corporate environment and not present in the CIP environment, RFC_URE7 agreed that the patch should be delayed from deployment to corporate workstations only. To accomplish this task, RFC_URE7 issued a manual override to specifically exclude this patch from the patch availability data set for the corporate environment. However, RFC_URE7 inadvertently copied this incomplete patch availability data set over to the CIP environment as well. As a result, the responsible personnel lost track of the need to install this patch in the CIP environment by the CIP Version 5 enforceable date. The root cause of this noncompliance was inadequate documentation and training. The personnel responsible for exporting the patch availability data set over to the CIP environment did not understand that this particular patch should not have been excluded from the CIP environment. This major contributing factor involves the following management practices: (a) workforce management, which includes providing training, education, and awareness to employees; (b) asset and configuration management, which includes controlling changes to assets; and, (c) information management, which includes managing information item risk, identifying and assessing information item risk, and addressing information item risk. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the patch at issue addressed a vulnerability that would typically be exploited through internet access. Because the workstations missing the patch have no internet access, there was a minimal likelihood that an external or non-trusted source could have exploited this vulnerability on the impacted workstations. Second, RFC_URE7 assessed the patch at issue as having a vulnerability risk rating of 0, which provides further support for the conclusion that possible exploitation of this vulnerability was unlikely in this case. Third, RFC_URE7 had deployed malware detection software which would have alerted and sought to prevent any attempted exploit. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) recommended corrective feedback for employee, including discussion of process adherence, attention to detail, and reminder of expectations set in policy and training for reporting potential issues of noncompliance; 2) created a plan to mitigate risk of the related vulnerabilities until patch installation can be completed; 3) enhanced the vulnerability assessment procedure to address all missing patches identified as vulnerabilities regardless of vulnerability rating; 4) documented, as a formal NERC CIP Compliance procedure, the process of acquiring patch availability data into the corporate environment and exporting it to the NERC CIP environment. Ensured that the procedure is written in a manner which will result in the complete data set being transferred to the NERC CIP environment. The procedure shall include steps to create a compliance artifact of successful transfer for each transfer performed; 5) trained all personnel (primary and backups) who might be involved in the patch availability acquisition and export process to ensure they understand the expectations and are able to execute the procedure successfully; 6) created a (monthly) compliance control activity to document the successful transfer of patch availability information to the NERC CIP environment and creation of success artifact; and 7) continued analysis of vulnerability scan results for those items below the procedural mitigation threshold to ensure that no additional vulnerabilities are due to missing patches. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015896 | CIP-004-6 | R4; R4.1 | SERC sent SERC_URE1 an audit detail letter notifying it of a compliance audit. SERC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-6 R4.1. SERC_URE1 authorized electronic access to Bulk Electric System (BES) Cyber Systems without establishing the need for such access. Under its existing access management program, when personnel were authorized either physical or electronic access, SERC_URE1 created an Active Directory (AD) account that it used to track and manage access requests and approvals. When SERC_URE1 generated the AD account, the SERC_URE1 system administrator created a unique user account and password for each individual. Upon granting approved electronic access, the system administrator provided the individual the user account details and password. However, if SERC_URE1 only authorized physical access, the system administrator would not share the user account details and password. While the SERC_URE1 compliance group was reviewing access revocations for a terminated employee, it discovered that a week earlier, it had authorized and granted unescorted physical access to eight employees into two Control Centers containing Medium Impact BES Cyber Systems. SERC_URE1’s process to create the accounts inadvertently granted the employees unauthorized electronic access to the BES Cyber Systems. SERC_URE1 did not provide the individuals with the user account details or passwords, but the system administrator set, upon creation of the account, the password that was associated to each of the user accounts. The user accounts and passwords granted electronic access to BES Cyber Systems, and the system administrator knew the user accounts and associated passwords. Therefore, the potential for unauthorized electronic access existed. SERC_URE1 determined that the root cause was human error. SERC_URE1 was not aware that when the system administrator created the AD account to track access the account would also provide electronic access to BES Cyber Systems. SERC_URE1 conducted the extent-of-condition review by comparing the individuals in AD with physical access, and determined that these eight employees were the complete scope of the issue. These were the only employees with physical only access. This issue lasted a week, from when SERC_URE1 granted the opportunity for electronic access, until SERC_URE1 authorized electronic access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1 creating user accounts in AD to track the unescorted physical access as well as the electronic access provided the system administrator, as well as the individual if they became aware of the user account and password, the opportunity to gain unauthorized electronic access to BES Cyber Systems and affect the BPS. However, the system administrator was not aware of the potential to use the user account and password to gain electronic access to BES Cyber Assets. SERC_URE1 did not provide the user account or password to the eight employees. The password used when creating the account was not stored in clear text, and the system hashed the password when the system administrator was entering it. The issue existed a relatively short duration, and the employees in question were current in CIP Cyber Security training and a recent personnel risk assessment was on file. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) performed extent of condition to ensure no other areas of noncompliance existed; 2) resubmitted the access requests in question to authorize unescorted physical access and electronic access; 3) verified access provisioning of the accounts; 4) restricted electronic access for those personnel that do not require electronic access even though they have an AD account; 5) updated the access management procedure and access request forms for clarity; and 6) provided awareness to the system administrators on the user account creation impacts.
2017-04-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016016065 | CIP-004-6 | R5; R5.1 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk issue of noncompliance with CIP-004-6 R5.1. Specifically, SPPRE_URE1 did not remove the unescorted physical access privileges for three employees within 24 hours of their retirement (R5.1). SPPRE_URE1 utilizes a Data Transfer Utility (DTU) process to initiate the requirement to revoke unescorted physical access within 24-hours of an employee termination. When a termination occurs, all information pertaining to the required access change for the employee is entered in the DTU, which sends the necessary information regarding the access change to SPPRE_URE1’s Physical Security Access Control System (PACS) and Identity Management (IDM) system. The PACS uses the termination date received from the DTU to remove physical access to the SPPRE_URE1 Physical Security Perimeter (PSP). The IDM uses the information from the DTU to send a notification to SPPRE_URE1 Physical Security personnel. When an upgrade was installed on the PACS System that affected the transfer of information from the DTU to the PACS System, the upgrade was installed on the PACS primary server but was inadvertently not installed on the PACS secondary server. Fifteen days following the upgrade, the PACS primary server failed over to the secondary server. Because the PACS upgrade had not been installed on the backup server, the termination date for the three employees in the DTU record was not communicated to the active PACS server. As a result, the access to the PSP was not removed for the three employees within 24 hours of their termination. A physical security analyst subsequently discovered that an IDM notification had not been received regarding the access change for the three retiring employees. PSP access for two employees was removed four days after the termination actions occurred, and PSP access for the third employee was removed seven days after the termination action occurred. The duration of this instance of noncompliance was six days, from 24 hours after the termination actions occurred, until the third employee’s access was removed. The root cause of this instance of noncompliance was human error because when the upgrade was implemented on the primary server, SPPRE_URE1 believed that the secondary server was also receiving the upgrade, and no further configuration was necessary. When the failover occurred to the secondary server the DTU service failed because the upgrade had not been implemented on the secondary server. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to remove an employee’s unescorted physical access within 24 hours of termination could lead to unauthorized access to critical cyber assets. Notwithstanding, the employees at issue did not have Interactive Remote Access and did not attempt physical access to any PSP after termination. Additionally, the employees were not fired for cause but retired voluntarily. No harm is known to have occurred. SPPRE_URE1 has no relevant prior noncompliance for CIP-004-6 R5 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) removed physical access from the three individuals; 2) added a step to the PACS test script for testing DTU functionality following a change; and 3) created a script on the task scheduler, located on the PACS servers, to ensure the DTU job is running. If it is not running, a notification email will be sent to the Physical Security Team. SPP RE has verified the completion of all mitigation activity.
2017-04-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014955 | CIP-009-3 | R1.1 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had a minimal risk issue of noncompliance with CIP-009-3 R1.1. Specifically, although SPPRE_URE2’s Disaster Recovery Plan listed specific response actions for certain disaster events associated with Critical Cyber Assets (R1.1) and defined roles and responsibilities of the responders (R1.2), it did not include the specific actions required to recover the Critical Cyber Assets as required by R1.1. SPPRE_URE2’s Disaster Recovery Plan was reviewed during the previous SPP RE Compliance Audit, which resulted in a “no findings” determination by the audit team. However, two years later SPPRE_URE2 revised its Disaster Recovery Plan and removed specific confidential information required to recover its Critical Cyber Assets to comply with federal regulations that require SPPRE_URE2 to have a SPPRE_URE2 written Emergency Restoration Plan (ERP). More specifically, because the federal government provides funding to assist SPPRE_URE2 in maintaining, expanding, upgrading, and modernizing its electric infrastructure, SPPRE_URE2 is required to submit documents to the federal government, some of which will be made public. As a result, SPPRE_URE2 must adhere to federal requirements when submitting documents containing sensitive information. Because the specific actions required to recover Critical Cyber Assets in SPPRE_URE2’s Disaster Recovery Plan contained sensitive information, SPPRE_URE2 was required to redact or remove such sensitive information from the Disaster Recovery Plan prior to submitting it to the federal government. Although SPPRE_URE2 maintained both versions of the Disaster Recovery Plan, i.e., the revised redacted public version and the previous un-redacted nonpublic version, the redacted public version was inadvertently saved as the formal Disaster Recovery Plan for purposes of satisfying CIP-009-3 R1.1. The duration of this instance of noncompliance was 18 months, 22 days from the date SPPRE_URE2 revised its Disaster Recovery Plan to exclude the specific actions required to recover Critical Cyber Assets in the event of a disaster, through the date SPPRE_URE2 completed its mitigation of the noncompliance. The root cause of this violation was human error due to SPPRE_URE2 personnel inadvertently saving the redacted Disaster Recovery Plan as the formal Disaster Recovery Plan for purposes of satisfying CIP-009-3 R1.1. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to include the specific actions required to recover Critical Cyber Assets has the potential to affect the reliability of the BPS by increasing the risk that SPPRE_URE2 personnel would not respond appropriately to effectively recover Critical Cyber Assets in the event of a disaster, which could cause a delay in the recovery of such assets. Notwithstanding, the noncompliance was a documentation deficiency. Although the redacted version of the Disaster Recovery Plan was inadvertently saved as the formal plan to show compliance with CIP-009-3 R1.1, SPPRE_URE2 continued to utilize the previous un-redacted version of the plan when conducting annual exercises per CIP-009-3 R2. As a result, all affected personnel would have been able to effectively recover Critical Cyber Assets had a disaster occurred. No harm is known to have occurred. SPPRE_URE2 has no relevant prior violations for CIP-009 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) revised its Disaster Recovery Plan, clearly identified as “CONFIDENTIAL”, to include the specific action required to recover Critical Cyber Assets in the event of a disaster; and 2) for any future submittals of its Disaster Recovery Plan to the federal government, SPPRE_URE2 agreed to maintain a separate public version of the Disaster Recovery Plan, which will not be used to document or evidence compliance with NERC CIP Standards or Requirements. SPP RE has verified the completion of all mitigation activity.
2017-04-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016597 | CIP-008-5 | R1; P1.2 | During a Compliance Audit of TRE_URE1, Texas RE determined that TRE_URE1 had an issue with CIP-008-5 R1, Part 1.2. Specifically, Texas RE determined that TRE_URE1 did not have an adequately documented Cyber Security Incident response plan that requires its personnel to notify the Electricity Sector Information Sharing and Analysis Center (ES-ISAC) of Reportable Cyber Security Incidents within one hour from the determination of a Reportable Cyber Security Incident. The root cause of this issue was that TRE_URE1’s documentation did not fully address all applicable requirements in CIP-008-5 R1, Part 1.2. Specifically, TRE_URE1’s documentation included sufficient processes to determine if an identified Cyber Security Incident constituted a Reportable Cyber Security Incident, but did not sufficiently address the requirement that such Cyber Security Incidents be reported to ES-ISAC within one hour. The duration of the noncompliance was approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The noncompliance was limited to a minor documentation issue. The TRE_URE1 process documents addressed reporting for Reportable Cyber Security Incidents and provided contact information for ES-ISAC via NERC. However, the CIP-008-5 R1, Part 1.2 requires initial notification to ES-ISAC within one hour of the determination of a Reportable Cyber Security Incident, and the process documents provided by TRE_URE1 did not clearly contain this directive. Additionally, TRE_URE1 did not identify any Cyber Security Incidents to be Reportable Cyber Security Incidents during the audit period. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) modified its applicable process document to fully comply with CIP-008-5 R1, Part 1.2; 2) demonstrated that the modified applicable process document was reviewed and approved by the relevant managers; and 3) demonstrated that it notified the affected employees of the modified applicable process document. Texas RE has verified the completion of all mitigation activity.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016325 | CIP-006-6 | R2; R2.1, R2.2 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-6 R2. WECC_URE1's received a forced door alarm at the Physical Security Perimeter (PSP) to the control center. WECC_URE1 personnel granted unauthorized physical access to the PSP for two WECC_URE1 employees, a general laborer and a truck driver. On two separate occasions the WECC_URE1 employee escorted one of the individuals outside of the PSP, leaving the other individual unescorted within the PSP. The unauthorized employees' ingress/egress within the PSP was not logged. Continuous escorted access of visitors within a PSP was not performed for one individual for two instances, Additionally, manual or automated logging of visitor ingress into and egress from the PSP, for two individuals for a single visit, was not performed. WECC determined that this issue began when an WECC_URE1 employee failed to provide continuous escorting of a visitor within the PSP and ended when the two visitors were escorted out of the PSP, for a total of 8 seconds of noncompliance The root cause was a lack of WECC_URE1 personnel following documented escorting processes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to provide continuous escorting of visitors within the PSP and failed to log ingress and egress for those visitors. Lack of continuously escorting and logging of visitors in a PSP could potentially cause risk to the operation of the control center, as well as the Bulk Electric System (BES) due to the inability of WECC_URE1 to ensure that unauthorized personnel do not accidently or purposely perform activities in the PSP. Such activities could include allowing other unauthorized personnel to gain physical access to the PSP to cause harm by power cycling or destroying equipment or making unauthorized changes to BES Cyber Assets (BCAs); thereby potentially affecting the reliability of the BPS. However, WECC_URE1 implemented controls to eliminate the likelihood of unauthorized physical or electronic access to BCAs, to include administrative, technical, and physical controls in the form of an electronic biometric two-factor authentication badge card reader systems at the PSP; badge readers at the control center door; and limited physical and electronic access to PSPs to authorized personnel only. The BCAs within the PSP were configured with authentication, authorization and accounting, to control whom can login or make changes to a BCA. WECC_URE1 had 24 hour-a-day, seven days-a-week alarm logging and monitoring at the PSP and security event logging for all BCAs. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) Removed the visitor from the PSP; 2) Removed unescorted physical access from the offending escort’s badge; and 3) Conducted CIP refresher training, for applicable staff, focusing on CIP-004, CIP-006, and CIP-008.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016550 | CIP-006-6 | R2.1 | WECC_URE2 submitted a Self-Log stating it had a possible issue of noncompliance with CIP-006-6 R2.1. Specifically, WECC_URE2 reported that an WECC_URE2 employee with authorized unescorted physical access rights, escorted a visiting WECC_URE2 employee who did not have authorized unescorted access into the Physical Security Perimeter (PSP). While escorting the visitor out of the PSP, the WECC_URE2 employee and visitor did not scan their badges correctly in order to avoid a door alarm. In an effort to reset the exit door, the WECC_URE2 employee escort exited the PSP without the visitor. The WECC_URE2 employee escort then re-entered the PSP and escorted the visitor out of the PSP, briefly leaving the visitor unescorted in the PSP. The root cause of this instance was human error due to not fully understanding their escorting responsibilities. WECC determined that this issue began on when the visitor was briefly left inside the PSP unescorted, and ended when both the WECC_URE2 employee and visitor left the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to provide continuous escorted access for one visitor within the PSP. Such failure could allow an unauthorized individual to physically access systems and intentionally, or accidentally, disrupt or make changes to equipment and systems. Which could interfere with WECC_URE2’s ability to operate, control, or monitor its bulk electric system (BES) elements. However, WECC_URE2 had controls in place to reduce the risk posed from having unauthorized individuals inside a PSP without an authorized escort. These controls included dedicated security personnel; authentication systems, which prevent unauthorized logical access; 24 hour-a-day, 7 days-a-week security monitoring; disabled USB ports; security event logs; and awareness training. Further, WECC_URE2 immediately discovered the issue and escorted the unauthorized visitor out of the PSP. No harm is known to have occurred. | To remediate and mitigate this issue, WECC_URE2: a. Continued escorting the visitor out of the PSP; b. Developed and delivered written communication to WECC_URE2 leadership who have employees and/or contract workers whose primary work location is within the PSP. WECC_URE2 leadership shared this communication with their employees and/or contract workers whose primary work location is within the PSP. This communication included information related to continuously escorting visitors; and c. Created CIP-restricted area awareness posters. These awareness posters were placed throughout the PSP. on each door of the mantrap (i.e. the outer entry door, inner entry door, and the interior exit door). Each sign includes the specific step(s) required for going through each of the specified mantrap doors. WECC has verified the completion of all mitigation activity
2017-04-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016032 | CIP-007-6 | R2.2 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-6 R2.2. For the first instance, WECC_URE3 discovered that its security patch review documentation was incomplete. No evidence was obtained to validate that security patches for Bulk Electric System (BES) Cyber Assets were reviewed. Furthermore, newer systems implemented as required by CIP Version 6 were not included in the monthly security patch review. WECC_URE3 also reported three instances of security patches not being assessed for applicability within 35 calendar days since the last assessment. WECC determined that the first instance began when WECC_URE3 failed to document its security patch assessment for all of its BES Cyber Assets and ended when WECC_URE3 completed its security patch assessment, for a total of 21 days of noncompliance. WECC determined that the second instance began when WECC_URE3 failed to assess security patches for applicability within 35 days of the last assessment for BES Cyber Assets and ended when WECC_URE3 performed the security patch assessment, for a total of one day of noncompliance. WECC determined that the third instance began when WECC_URE3 failed to assess security patches for applicability within 35 days of the last assessment for two of its BES Cyber Assets and ended when WECC_URE3 performed the security patch assessment, for a total of 6 days of noncompliance. WECC determined that the fourth instance began when WECC_URE3 failed to assess security patches for applicability within 35 days of the last assessment for two BES Cyber Assets and ended when WECC_URE3 performed the security patch assessment, for a total of 6 days of noncompliance. The root cause of the first instance was less than adequate procedures for addressing key changes in personnel who were part of WECC_URE3’s established patch management workflow. The root cause of the three remaining instances was human error; specifically, WECC_URE3 not enforcing its rules and processes within its task management system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 failed to assess applicability of security patches within 35 days of the last assessment for BES Cyber Assets. Failure to perform security patch assessments in a timely manner could potentially result in an attacker gaining access to WECC_URE3’s BES Cyber Systems to cause disruptions to its operating capabilities; thereby, affecting the reliability of the BPS. However, WECC_URE3 implemented controls to reduce the likelihood of these results from occurring. Specifically, it had documented procedures for CIP-007-6 and its task management system sent email reminders of upcoming tasks, with escalations to supervisors when tasks were either coming due or not performed. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) Assessed all available security patches for applicability; 2) Created task notifications for security patching review to be sent both two weeks and 3 days before an established month end due date; and 3) Escalated incomplete tasks to be sent one day after the due date to both the Internal Auditor of Compliance, and the Telecom Engineering Supervisor. WECC verified completion of WECC_URE3’s mitigating activities.
2017-03-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016790 | CIP-004-6 | R3 | MRO_URE1 granted temporary unescorted physical access to two contractors for access to a Physical Security Perimeter (PSP) without having an active Personnel Risk Assessment (PRA) for either of the contractors. One contractor's PRA expired seven days prior to having access granted, and the other contractor's PRA expired ten days prior to having access granted. The cause of the issue was in the assumptions of MRO_URE1's Temporary Access Request Function (TARF). When a request for temporary access is processed through the TARF, the system assumed that the subject has a current PRA. The issue began when access was granted to the two contractors and ended when access was revoked. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was extremely brief as MRO_URE1 discovered the issue the next day after being alerted by a secondary control and revoked the access. Additionally, the PRAs had both recently expired, and when the PRAs were subsequently updated, there was no adverse information about either contractor. Finally, the issue was self-identified as the result of a functioning detective control. No harm is known to have occurred. | To mitigate this issue, MRO_URE1: 1) revoked the contractors' access; 2) controls on the system were augmented so that contractors without a valid PRA may not be selected for access through the TARF; and 3) reclassified a request for temporary access as a CIP access authorization request which resulted in MRO_URE1 monitoring the status of PRAs so that PRAs nearing expiration will be flagged.
2017-03-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016791 | CIP-007-6 | R4 | MRO_URE1 stated that it had an issue of CIP-007-6 R4 Part 4.2. Specifically, MRO_URE1 failed to detect that a Cyber Asset was not sending logs to MRO_URE1's centralized Security Information and Event Management System (SIEM System). The issue was discovered when IT personnel were performing a periodic manual review of logs sent to the SIEM System. IT personnel discovered that logs from this Cyber Asset were not in the SIEM System. MRO_URE1 was not aware the Cyber Asset stopped sending logs because the system did not produce an alert when the Cyber Asset stopped sending logs. The cause of this issue was a misconfiguration with the alerting criteria of the SIEM System that resulted in no alert being issued when the Cyber Asset stopped sending logs. The issue began when the Cyber Asset stopped sending logs, and ended when MRO_URE1 corrected the misconfiguration to enable an alert to be issued if the Cyber Asset stops sending logs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 confirmed through a comprehensive review that the noncompliance was limited to a single Cyber Asset. Further, no logs were lost as a result of the noncompliance as event logs were collected and retained locally on the affected Cyber Asset. A review of those logs confirmed that no anomalies occurred during the duration of the noncompliance. Finally, a functioning secondary detective control (the periodic manual inspection of logs) limited the duration of the noncompliance. No harm is known to have occurred. | To mitigate this issue, MRO_URE1: 1) corrected the misconfiguration; and 2) retrieved logs from backups of the affected Cyber Asset and retained in accordance with the timeframes prescribed in Part 4.3.
2017-03-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016792 | CIP-007-6 | R5 | MRO_URE1 stated that it had an issue of CIP-007-6 R5 when it failed to submit a TFE for assets that were unable to comply with CIP-007-6 R5 Part 5.6. MRO_URE1 had a different interpretation of the standard. MRO_URE1 interpreted the standard so that a device would only need a TFE for Part 5.1, where as MRO interpreted the standard to mean that any device that required a TFE for Part 5.1, also required a separate TFE for Part 5.6 if the device could not meet the requirements of Part 5.6. MRO_URE1 submitted a TFE under Part 5.1 for 347 Cyber Assets, but only submitted a TFE under Part 5.6 for 23 Cyber Assets. The cause of this issue was a misinterpretation of the TFE Requirements for CIP-007-6 R5 Parts 5.1 and 5.6. The issue began when the Standard and Requirement became mandatory and enforceable on MRO_URE1, and ended when the TFE request was approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The TFE was subsequently granted, and the noncompliance can be accurately categorized as an administrative issue as opposed to an issue that threatens the reliability of the BPS. Finally, the duration of the noncompliance was relatively short. No harm is known to have occurred. | To mitigate this issue, MRO_URE1 submitted a TFE that was subsequently approved. MRO verified that mitigating activities were complete.
2017-03-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017016793 | CIP-010-2 | R1 | MRO_URE1 stated that it had an issue of CIP-010-2 R1 Part 1.4.1. An MRO_URE1 IT employee detected that a software update was installed on a Physical Access Control System (PACS) production database without determining if any of the required cyber security controls in CIP-005 and CIP-007 could be impacted by the change. A subsequent evaluation of the patch confirmed that none of the required cyber security controls were impacted by the change. The cause of this issue was lack of awareness as to the impact of the patch, as MRO_URE1 was not aware that the patch would be associated with a high impact BES Cyber System. The issue began when the MRO_URE1 installed a software update on a PACS server, and ended when MRO_URE1 evaluated the patch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is minimal due to the short duration of the noncompliance. Specifically, MRO_URE1 discovered the issue within 24 hours and ended the noncompliance within two days. Further, the issue was self-identified which is a strong indication of functioning detective controls. Finally, no security controls were actually impacted by the change. No harm is known to have occurred. | To mitigate this issue, MRO_URE1: 1) evaluated the patch to determine if it impacted the cybersecurity controls of CIP-005 and CIP-007, and documented the evaluation; and 2) modified its workflow process for change request tickets to verify the regulatory status of the Cyber Asset for which a change is being considered. MRO_URE1 stated that mitigating activities were complete.
2017-03-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2016015625 | CIP-004-3a | R3.2 | MRO_URE2 stated that it allowed a Personnel Risk Assessment (PRA) to expire for a user with unescorted physical access permissions. The user's PRA expired early in the year. MRO_URE2 became aware of this when it reviewed the user's PRA. MRO_URE2 revoked the user's access, and updated the user's PRA, which contained no adverse information. The cause of this issue is weak controls regarding expiring PRAs. Specifically, MRO_URE2's policy was to review PRAs that were to expire during the calendar year, early in the calendar year. This review did not occur until after the user's PRA expired. The issue started when the user's PRA expired, and ended when MRO_URE2 revoked the user's physical access privileges. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The period of noncompliance was brief, and the user did not access the secure area during the period of time that the PRA was expired. Additionally, a comprehensive review verified that this was the only PRA that had expired. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE2: 1) revoked the user's access and updated the user's PRA; 2) reviewed all other PRAs to confirm this was the only issue; and 3) changed from an annual review process to a semi-annual review process to target PRAs that are approaching six and a half years, as opposed to targeting PRAs that are approaching seven years. MRO_URE2 stated that it completed mitigating activities.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015559 | CIP-003-3 | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE1 determined that two trusted employees serving as Active Directory (AD) domain administrators had access to CIP protected information file share repositories (CIRs) without proper CIP credentials. RFC_URE1 hosts multiple CIP CIRs on a Corporate Data Network (CDN), which uses AD for user authentication and authorization. RFC_URE1’s NERC CIP Access Control Overview Procedure requires each individual to have a valid personnel risk assessment (PRA) and to have taken CIP training prior to accessing CIP protected information. In this case, the two AD domain administrators did not have a valid PRA or up to date CIP training. RFC_URE1 hosts multiple CIP CIRs on a CDN, which uses AD for user authentication and authorization. RFC_URE1, through its CIP Operations and Transmission Strategy and Compliance groups, conducted an extent of condition review to confirm the scope of this issue. RFC_URE1 uses several types of administrator groups which allow access to IT groups supporting the CDN file share environment. In reviewing access to those environments, CIP Operations reviewed CIP credentials for 126 individuals within various administrative groups that had access to the CDN, and, therefore, to the CIRs in question hosted in the CDN. Of those 126, CIP Operations identified 17 additional instances of employees that had access to CIP protected information without the proper CIP credentials specified in the RFC_URE1 program. In total, 19 individuals did not have proper CIP credentials. Of those 19, 16 individuals did not have a current PRA and CIP training. In one case, the individual had current training, but not a current PRA. In two cases, the individual had a current PRA, but not current training. To mitigate these 19 issues, RFC_URE1 completed PRA and CIP training for the two Active Directory administrators. RFC_URE1 then removed CIR access for the eleven individuals that were members of the two local administrative groups. Lastly, RFC_URE1 completed PRA and CIP training for the six administrators having access to CIP CIRs. This noncompliance involves the management practices of workforce management and work management. RFC_URE1 determined that there are three contributing causes of these issues. First, RFC_URE1 personnel made an incorrect assumption regarding how the CDN file share environment would be used with respect to hosting NERC CIP protected information. Second, there are no common/consistent procedural requirements for acquiring CIP credentials within these administrative groups when granting administrative access to a CIR. In general, each administrative group adheres to strict access control processes, but these processes do not reflect the requirements for CIR access as prescribed under RFC_URE1’s NERC CIP Access Control Overview Procedure. Third, RFC_URE1 identified that it did not have adequate procedural controls for the creation of, management of, and removal of a CIR. The root cause of this noncompliance was the lack of consistent procedural requirements for acquiring CIP credentials across RFC_URE1. The duration of the noncompliance was approximately eighteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from this noncompliance is that an unauthorized individual could gain access to the CIR and use the sensitive information contained therein to harm the BPS. The potential risk and harm is minimized because the administrators are trusted employees and the administrators receive a general background investigation that is equivalent to a PRA when they are hired. Additionally, new administrators receive training on general security controls, including the handling of sensitive information. The CDN file share environment contains thousands of files and only a small fraction of those files are CIP Protected. Without specific knowledge that the repositories contained CIP protected information, it would be unlikely that an administrator would accidently locate the files in question. Lastly, none of the administrators involved accessed any CIP Protected files in the CIRs. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) completed PRA and CIP training for the two Active Directory administrators; 2) removed CIR access for the eleven individuals that were members of the two local administrative groups; 3) completed PRA and CIP training for the six administrators having access to CIP CIRs; 4) completed review of administrative accounts on hardware hosting CIP CIRs; 5) created/updated CIR administrative access procedures to ensure completion of PRA and CIP training during onboarding; 6) developed a CIR commissioning and decommissioning process. This will ensure that RFC_URE1 follow the same process when setting up a CIR and granting initial access to that CIR and the same process when closing down a CIR and removing access from that CIR; and 7) confirmed its new access management system functionality automatically removes CIR access for administrators without proper CIP credentials. RFC_URE1 is in the final stages of implementing its new access management system to manage access to CIP BSCAs, Physical Security Perimeters and CIRs. This system will replace many manual access control processes that have been prone to human error in the past. The functionality of the system includes interfaces with RFC_URE2’s systems of records for completion of both cyber security training and PRA. No access can be granted without successful completion of both CIP requirements. In addition, if either credential expires, the system would automatically remove access within 24 hours. This should effectively prevent further violations with CIP-003 R5 where CIR access is granted with insufficient CIP credentials. The combination of the tool and CIP Commissioning procedure are intended to effectively address all causal factors associated with the originating issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015711 | CIP-003-3 | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. During an annual access review, RFC_URE1 discovered two employees on the Access Control List (ACL) for a RFC_URE1 File Share CIP Information Repository (CIR) with no corresponding Access Request System (ARS) tickets granting them access to the file share. These two RFC_URE1 employees were placed on the ACL without following RFC_URE1’s ticketing process. The administrator that granted these two RFC_URE1 employees access did not follow RFC_URE1’s process for granting access to CIRs. RFC_URE1 removed the two employees’ access upon discovery. To obtain access to the CIR, RFC_URE1’s procedure in effect at the time required supervisor approval, Personnel Risk Assessment (PRA) and NERC training verification, and asset authorizer approval in the ARS. RFC_URE1 could not locate evidence that the ARS was used to grant the two employees access and believes that their access was manually provisioned directly to the Active Directory group associated to the file share by an administrator. This noncompliance involves the management practice of workforce management because RFC_URE1 personnel did not follow RFC_URE1’s procedure to use the ARS to grant the two employees’ access to the CIR. Ineffective training of RFC_URE1 personnel to follow RFC_URE1's procedure is the root cause of this noncompliance. The duration of the noncompliance was approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that unauthorized individuals get access to a CIR. The potential harm is minimized here because both employees are current employees with RFC_URE1 and during the noncompliance were up to date on their current NERC CIP training and each had a valid PRA. The two employees with unauthorized access were intended to have access and had a legitimate business need to have access, but RFC_URE1 failed to follow the documented process on proper ticketing through the ARS. To access the CIR, personnel need to be able to log into RFC_URE1’s system and navigate to where the CIR is stored. If non-RFC_URE1 personnel were incorrectly manually provisioned access, they could not access the CIR because they could not log into the RFC_URE1 system. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed access to the CIR and re-provisioned access with proper documentation; 2) implemented the new access management system to provide the capability to send daily notification to users regarding access discrepancies; 3) distributed a communication to stress the importance of not provisioning access without a ticket. The communication clearly defines the responsibilities of any employee with manual provisioning privileges and stresses that no provisioning should occur without an authorized request. Additional content includes an overview of the NERC CIP Prerequisites (i.e. PRA, valid business need, completed NERC CIP training etc.) as well as the new access management system Request Timeline; and 4) updated NERC CIP Access Management Program to emphasize the point that access should always be provisioned using the new access management system to ensure proper documentation exists. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016006 | CIP-003-3 | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE1’s project management team for the implementation of its new access management system determined that during the final production cutover, RFC_URE1 granted or retained NERC CIP access for 18 users where the users did not meet the prerequisites for valid access. RFC_URE1 removed all access for the 18 users seven days later. RFC_URE1 initially discovered this issue when an RFC_URE1 Subject Matter Expert conducting a post cutover validation identified that a team member that should not have access was part of an access role with enabled access. That expert raised this issue to the project team and the team identified that this user received access to the role because of a manual error in the bulk data upload where a typing mistake led to the incorrect user getting access to the system. (RFC_URE1 has introduced Role Based Access as part of the implementation for managing access. Access to assets in scope for NERC CIP Requirements is granted through requests for an Access Role selected from a role catalog in the system. An Access Role is the set of Access Privileges required for an individual to perform a job function, for instance, "SCADA Operator.") The project team initiated an extent of condition review based on the initial RFC_URE1 inquiry to determine if there were any other users who obtained access as a part of the new access management system release without NERC CIP prerequisites of a valid Personnel Risk Assessment (PRA) and valid CIP training. RFC_URE1’s extent of condition review discovered that a total of 18 users were granted physical, electronic, or information access by the new system to either NERC Version 3 Critical Cyber Assets (CCAs) or Critical Information Repositories (CIRs) without having the required NERC CIP prerequisites in place. The 18 users’ access involved RFC_URE1 shared IT service CIRs or Critical Cyber Assets and as a result had impacts for multiple business units at RFC_URE1: i. Seven users obtained access to CIP information stored in CIRs. Of those seven, six cases involved shared electronic access. Of those six, one did not have a PRA or CIP training and five users had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. ii. Five users gained or retained electronic access to Critical Cyber Assets. Of those, four users involved shared electronic access. Of those four, three did not have a PRA or CIP training and one had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. iii. Six users obtained physical access to Physical Security Perimeters (PSPs). Of those, one user involved shared access. This user did not have a PRA or CIP training. The remaining five cases involved physical access to business unit specific PSPs. Two users did not have a PRA or CIP training, and three users had a valid PRA, bud did not complete CIP training. This noncompliance involves the management practice of asset and configuration management. After reviewing the noncompliance, the project team determined that communications from the project team did not explicitly require that the bulk load data must only include previously authorized users and should not contain new users that had a business need for future access. This lack of clarity in communication contributed to the granting of unauthorized access to 18 users during the bulk data upload. In addition, due to data synchronization issues between the new system and the training record system, the PRA/training validation process was not run while the issue was being resolved. This allowed the final bulk load performed to inadvertently bypass validation, which would have prevented access being granted to the eighteen users. Miscommunication regarding what users were meant to be part of the bulk upload and a failure to follow RFC_URE1’s designed process by not running the PRA/training validation process were the root causes of this noncompliance. The duration of the noncompliance was approximately seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance occurred during a data migration effort related to the implementation of the new access management system. In all cases, the users had no knowledge that access had been provisioned. The users included in the bulk upload without completed CIP training or PRAs were in the process of being on-boarded for CIP access and had been selected by management in the specific business units for inclusion because the users were intended to receive access after they completed their PRAs and CIP training. RFC_URE1 performed a post launch validation that identified the issue one day after it occurred and removed all unauthorized access eight days after it was originally granted, which shows that RFC_URE1’s detective and corrective controls are working effectively. Lastly, RFC_URE1 verified that physical access permissions were not used for the six cases where physical access was mistakenly granted. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed access for all individuals granted access as a result of the data loading error; 2) set the validation process (To maintain compliance with CIP standards and conform to RFC_URE1's procedures for access management, the new access management system was designed with an automated validation routine which conducts a daily verification of the training expiration date and PRA expiration date for every user with NERC CIP physical, logical, or information access.) to run automatically on a daily basis to check for proper PRA and CIP trainings as part of the provisioning process and implemented synchronization process corrections for certain training data used by the new system; 3) prepared a job aid addressing the requirements necessary for processing the bulk load of access lists in the future, which will include a peer check to validate that data is entered correctly and in the correct format as an additional precaution to running the validation process. The job aid also includes instructions to limit the bulk load to existing CIP-cleared users only and to verify that the validation process is running before and after all up loads; and 4) updated procedure to address approvals required for bulk uploads of authorized access for users.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015557 | CIP-003-3 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE2 determined that two trusted employees serving as Active Directory (AD) domain administrators had access to CIP protected information file share repositories (CIRs) without proper CIP credentials. RFC_URE2 hosts multiple CIP CIRs on a Corporate Data Network (CDN), which uses AD for user authentication and authorization. RFC_URE2’s NERC CIP Access Control Overview Procedure requires each individual to have a valid personnel risk assessment (PRA) and to have taken CIP training prior to accessing CIP protected information. In this case, the two AD domain administrators did not have a valid PRA or up to date CIP training. RFC_URE2, through its CIP Operations and Transmission Strategy and Compliance groups, conducted an extent of condition review to confirm the scope of this issue. RFC_URE2 uses several types of administrator groups which allow access to IT groups supporting the CDN file share environment. In reviewing access to those environments, CIP Operations reviewed CIP credentials for 126 individuals within various administrative groups that had access to the CDN. Of those 126, CIP Operations identified 17 additional instances of employees that had access to CIP protected information without the proper CIP credentials specified in the RFC_URE2 program. In total, 19 individuals did not have proper CIP credentials. Of those 19, 16 individuals did not have a current PRA and CIP training. In one case, the individual had current training, but not a current PRA. In two cases, the individual had a current PRA, but not current training. To mitigate these 19 issues, RFC_URE2 completed PRA and CIP training for the two Active Directory administrators. RFC_URE2 then removed CIR access for the eleven individuals that were members of the two local administrative groups. Lastly, RFC_URE2 completed PRA and CIP training for the six administrators having access to CIP CIRs. This noncompliance involves the management practices of workforce management and work management. RFC_URE2 determined that there are three contributing causes of these issues. First, RFC_URE2 personnel made an incorrect assumption regarding how the CDN file share environment would be used with respect to hosting NERC CIP protected information. Second, there are no common/consistent procedural requirements for acquiring CIP credentials within these administrative groups when granting administrative access to a CIR. In general, each administrative group adheres to strict access control processes, but these processes do not reflect the requirements for CIR access as prescribed under RFC_URE2’s NERC CIP Access Control Overview Procedure. Third, RFC_URE2 identified that it did not have adequate procedural controls for the creation of, management of, and removal of a CIR. The root cause of this noncompliance was the lack of consistent procedural requirements for acquiring CIP credentials across RFC_URE2. The duration of the noncompliance was approximately eighteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from this noncompliance is that an unauthorized individual could gain access to the CIR and use the sensitive information contained therein to harm the BPS. The potential risk and harm is minimized because the administrators are trusted employees and the administrators receive a general background investigation that is equivalent to a PRA when they are hired. Additionally, new administrators receive training on general security controls, including the handling of sensitive information. The CDN file share environment contains thousands of files and only a small fraction of those files are CIP Protected. Without specific knowledge that the repositories contained CIP protected information, it would be unlikely that an administrator would accidently locate the files in question. Lastly, none of the administrators involved accessed any CIP Protected files in the CIRs. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) completed PRA and CIP training for the two Active Directory administrators; 2) removed CIR access for the eleven individuals that were members of the two local administrative groups; 3) completed PRA and CIP training for the six administrators having access to CIP CIRs; 4) completed review of administrative accounts on hardware hosting CIP CIRs; 5) created/updated CIR administrative access procedures to ensure completion of PRA and CIP training during onboarding; 6) developed a CIR commissioning and decommissioning process. This will ensure that RFC_URE2 follow the same process when setting up a CIR and granting initial access to that CIR and the same process when closing down a CIR and removing access from that CIR; and 7) confirmed its new access management system functionality automatically removes CIR access for administrators without proper CIP credentials. RFC_URE2 is in the final stages of implementing its new access management system to manage access to CIP BSCAs, Physical Security Perimeters and CIRs. This system will replace many manual access control processes that have been prone to human error in the past. The functionality of the system includes interfaces with RFC_URE2’s systems of records for completion of both cyber security training and PRA. No access can be granted without successful completion of both CIP requirements. In addition, if either credential expires, the system would automatically remove access within 24 hours. This should effectively prevent further violations with CIP-003 R5 where CIR access is granted with insufficient CIP credentials. The combination of the tool and CIP commissioning procedure are intended to effectively address all causal factors associated with the originating issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015710 | CIP-003-3 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE2 was performing an extent of condition review related to another issue and discovered that three RFC_URE2 individuals retained previously authorized access to a privileged account security product after they had transitioned out of their roles that had required that access. The privileged account security product is used by RFC_URE2 to host NERC CIP Information Repositories (CIRs), known as safes. These information safes contain information associated with Critical Cyber Assets (CCAs) in the form of Shared Accounts, passwords, and, in some cases, host names. RFC_URE2 began consolidating RFC_URE2 Active Directory domains. During this consolidation, individuals and groups existed simultaneously in more than one domain with identically named user and group objects in both a legacy Active Directory domain and a consolidated Active Directory domain. RFC_URE2’s version of security product in use at the time did not properly recognize identically named, user and group objects in multiple domains. A RFC_URE2 IT employee reported that the security product did not recognize his valid credentials. RFC_URE2 engaged an RFC_URE2 IT Shared Services group to introduce explicit permissions as a temporary workaround connecting several users to the security product, including the three individuals in question, to allow valid access to already authorized users while troubleshooting and resolving the security product access. Shortly thereafter, RFC_URE2 had resolved the access issue, but did not initiate steps to remove the explicit permissions at that time. Following this failure to remove explicit permissions, three employees were transferred to different groups while retaining these explicit permissions. Their explicit permissions should have been removed when they were transferred to different groups. On further investigation, RFC_URE2 confirmed that the three individuals properly obtained access to the security product, when the system was initially configured to store RFC_URE2 Shared Account credentials. At that time all three individuals were authorized for and assigned privileges corresponding to their existing roles within RFC_URE2 IT. All had current NERC CIP Training and valid Personnel Risk Assessments (PRAs) on record. When their roles changed, all three remained trusted employees, were authorized for different NERC CIP access on other assets and maintained their NERC CIP Training and PRAs throughout the period in question. When the three employees were transferred, RFC_URE2 removed all Active Directory group entitlements normally used for access to the safes and RFC_URE2 thought it removed all the employees’ explicit permissions. Rather than removing their explicit permissions, RFC_URE2 accidentally duplicated the employees’ access in the system. Resultantly, these three employees incorrectly retained access without a valid business need to a CIR. RFC_URE2’s IT Shared Services removed all remaining explicit permissions for the three employees twelve days after the extent of condition review. This noncompliance involves the management practice of workforce management. RFC_URE2 identified two contributing causes. First, the security product was not adequately tested for Business Unit functionality as part of the Active Directory migration to a consolidated Active Directory domain. The change agent assigned to RFC_URE2 for the Active Directory migration did not test the security product in a manner that would have identified the issue associated with the identically named user and group objects. Second, the administrative team supporting the security product did not know that explicit permissions needed to be removed following resolution of the temporary access issues due to ineffective training. This lack of knowledge is the root cause of the noncompliance. The security product also did not have a review process in place to ensure that the explicit permissions were removed for these employees following resolution of the temporary access issues. There was also a breakdown in communications where RFC_URE2 did not effectively communicate the need to remove the three employees’ explicit permissions after the temporary workaround for those three employees was no longer needed. The duration of the noncompliance was approximately sixteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All three implicated individuals were trusted long term RFC_URE2 IT system administrators familiar with NERC CIP systems and procedures and maintained current NERC CIP training and PRAs throughout the noncompliance. The three individuals did not know they retained access because they had been incorrectly informed that their access had been revoked per the standard process. RFC_URE2 confirmed that the three individuals that retained access through these explicit permissions did not utilize the information contained in the safes to gain access to the systems related to the information. They also did not attempt to access the safes. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed all remaining unauthorized explicit permissions that provided access to the shared account credentials stored in the safes for all three employees; 2) upgraded the security product to a version that will recognize two identically named Active Directory groups from multiple domains simultaneously; 3) revoked all explicit permissions that granted access to shared account credentials stored in the safes; 4) implemented the new access management system; 5) published and implemented a procedure describing a policy to standardize the structure and object naming (where technically feasible) of any shared Active Directory, or other directory, leveraged for NERC CIP regulated systems; and 6) published and implemented a procedure to incorporate language to address recovering from a non-standard urgent break fix workaround. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016001 | CIP-003-3 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE2’s project management team for the implementation of its new access management system determined that during the final production cutover, RFC_URE2 granted or retained NERC CIP access for 18 users where the users did not meet the prerequisites for valid access. RFC_URE2 removed all access for the 18 users seven days later. RFC_URE2 initially discovered this issue when an RFC_URE2 Subject Matter Expert conducting a post cutover validation identified that a team member that should not have access was part of an access role with enabled access. That expert raised this issue to the project team and the team identified that this user received access to the role because of a manual error in the bulk data upload where a typing mistake led to the incorrect user getting access to the system. (RFC_URE2 has introduced Role Based Access as part of the implementation for managing access. Access to assets in scope for NERC CIP Requirements is granted through requests for an Access Role selected from a role catalog in the system. An Access Role is the set of Access Privileges required for an individual to perform a job function, for instance, "SCADA Operator.") The project team initiated an extent of condition review based on the initial RFC_URE2 inquiry to determine if there were any other users who obtained access as a part of the new access management system release without NERC CIP prerequisites of a valid Personnel Risk Assessment (PRA) and valid CIP training. RFC_URE2’s extent of condition review discovered that a total of 18 users were granted physical, electronic, or information access by the new system to either NERC Version 3 Critical Cyber Assets (CCAs) or Critical Information Repositories (CIRs) without having the required NERC CIP prerequisites in place. The 18 users’ access involved RFC_URE2 shared IT service CIRs or Critical Cyber Assets and as a result had impacts for multiple business units at RFC_URE2: i. Seven users obtained access to CIP information stored in CIRs. Of those seven, six cases involved shared electronic access. Of those six, one did not have a PRA or CIP training and five users had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. ii. Five users gained or retained electronic access to Critical Cyber Assets. Of those, four users involved shared electronic access. Of those four, three did not have a PRA or CIP training and one had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. iii. Six users obtained physical access to Physical Security Perimeters (PSPs). Of those, one user involved shared access. This user did not have a PRA or CIP training. The remaining five cases involved physical access to business unit specific PSPs. Two users did not have a PRA or CIP training, and three users had a valid PRA, bud did not complete CIP training. This noncompliance involves the management practice of asset and configuration management. After reviewing the noncompliance, the project team determined that communications from the project team did not explicitly require that the bulk load data must only include previously authorized users and should not contain new users that had a business need for future access. This lack of clarity in communication contributed to the granting of unauthorized access to 18 users during the bulk data upload. In addition, due to data synchronization issues between the new system and the training record system, the PRA/training validation process was not run while the issue was being resolved. This allowed the final bulk load performed to inadvertently bypass validation, which would have prevented access being granted to the eighteen users. Miscommunication regarding what users were meant to be part of the bulk upload and a failure to follow RFC_URE2’s designed process by not running the PRA/training validation process were the root causes of this noncompliance. The duration of the noncompliance was approximately seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance occurred during a data migration effort related to the implementation of the new access management system. In all cases, the users had no knowledge that access had been provisioned. The users included in the bulk upload without completed CIP training or PRAs were in the process of being on-boarded for CIP access and had been selected by management in the specific business units for inclusion because the users were intended to receive access after they completed their PRAs and CIP training. RFC_URE2 performed a post launch validation that identified the issue one day after it occurred and removed all unauthorized access eight days after it was originally granted, which shows that RFC_URE2’s detective and corrective controls are working effectively. Lastly, RFC_URE2 verified that physical access permissions were not used for the six cases where physical access was mistakenly granted. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed access for all individuals granted access as a result of the data loading error; 2) set the validation process (To maintain compliance with CIP standards and conform to RFC_URE2's procedures for access management, the new system was designed with an automated validation routine which conducts a daily verification of the training expiration date and PRA expiration date for every user with NERC CIP physical, logical, or information access.) to run automatically on a daily basis to check for proper PRA and CIP trainings as part of the provisioning process and implemented synchronization process corrections for certain training data used by the new system; 3) prepared a job aid addressing the requirements necessary for processing the bulk load of access lists in the future, which will include a peer check to validate that data is entered correctly and in the correct format as an additional precaution to running the validation process. The job aid also includes instructions to limit the bulk load to existing CIP-cleared users only and to verify that the validation process is running before and after all up loads; and 4) updated procedure to address approvals required for bulk uploads of authorized access for users.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016002 | CIP-003-3 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. While performing a review of access to shared account credentials, RFC_URE2 identified a user account on the security account actual list that was not on the corresponding list of authorized users and had unauthorized access. (RFC_URE2 has established a program that is more stringent than the NERC CIP-003-3 R5 requirement to review access to CIP information annually because it requires RFC_URE2 to review access to shared account credentials stored in CIP Information Repositories (CIRs) known as safes, on a quarterly basis in parallel to each quarterly electronic access review.) The shared ID credentials stored in the security product are protected according to RFC_URE2’s CIP Information Protection Program. RFC_URE2 did not find any Access Request tickets that would authorize or grant this individual’s access to the Active Directory group controlling access to the security product. The individual did have a current PRA and CIP training at the time and a review showed that the individual did not use the access. As part of a corollary process, RFC_URE2 runs a script against the Active Directory that captures the security product actual lists. This information is analyzed on a quarterly basis in conjunction with the quarterly electronic access review process. This shared account appeared after the quarter Access Review cycle and was therefore identified in the new review cycle. This noncompliance involves the management practice of verification and work management because RFC_URE2 identified a user account on the security product account actual list that was not on the corresponding list of authorized users. RFC_URE2 did not verify that the user account was on both lists. RFC_URE2 personnel’s failure to follow its process by not having any Access Request tickets that would authorize or grant this individual’s access to the Active Directory group controlling access to the security product is the root cause of this noncompliance. The duration of the noncompliance was approximately four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The user in question had a valid personnel risk assessment (PRA) and current NERC CIP training and was a trusted individual. RFC_URE2 reviewed the security product access logs and those logs show that the unauthorized access was never used to access any shared account credentials. RFC_URE2 also discovered this noncompliance during its next quarterly access review which shows that those access reviews are serving their purpose as a detective control to identify noncompliances. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed access for the unauthorized user and verified the removal by running a script, which provides the security product actual list, and reviewing those results; 2) sent an email to all relevant personnel stressing the importance of not provisioning access without a ticket; 3) updated its procedure to emphasize that it is not appropriate to grant access manually; and 4) implemented its new access management system to improve access provisioning to the security product by performing a reconciliation to identify unauthorized accounts and remove access as needed. The new system will also serve as the system of record for access.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017016911 | CIP-004-6 | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-6 R4. RFC_URE2’s access management system reconciliation and discrepancy process identified two manually provisioned access permissions that required further review. RFC_URE2 identified that different view only access permissions were inadvertently granted to two individual accounts on RFC_URE2's SCADA system, allowing access to BES Cyber System Information (BCSI) without prior authorization or business need. Both individuals granted access are trusted individuals with current Personnel Risk Assessments (PRAs) and valid credentials to access BCSI. Although the two individuals had proper authorization to access the data at issue, the view only access that they were granted presented the data in a different manner than the typical view along with some additional configuration data not normally accessible to the two individuals. The issue here arises from the two individuals being able to view the additional configuration data, which is BCSI, that they did not have authorization to view and did not have a business need to see. While provisioning access for other users, a RFC_URE2 SCADA system performer inadvertently granted the two individuals at issue view only access to this additional configuration data. The RFC_URE2 SCADA system performer was not aware that he had granted additional unauthorized view only rights to the two RFC_URE2 individuals at issue. This noncompliance involves the management practices of workforce management through ineffective training, reliability quality management, and verification. RFC_URE2 identified the root cause as an insufficient peer review technique. The quality control inspection technique utilized by the peer check in these two cases was performed correctly, but failed to isolate the errors which involves reliability quality management. The technique verified only that expected changes were made; it did not further verify that inadvertent changes were not made. A root cause of this noncompliance is the failure of the peer check to identify that inadvertent changes were made. The duration of the noncompliance was approximately one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The two individuals implicated in this noncompliance are both trusted employees with current PRAs and valid credentials to access BCSI. Additionally, the two individuals were already authorized and trained for roles connected to the SCADA system and were authorized to access and view the data at issue. The only issue here is that the view only access the two individuals received presented some additional configuration data that the two employees were not authorized to view or access. Lastly, the potential risk is minimized here because the two individuals were given view only access meaning they could not change any of the additional system configuration data that they were not authorized to view. No harm is known to have occurred | To mitigate this issue, RFC_URE2: 1) completed the removal of the two individuals’ unauthorized view access rights; 2) updated the RFC_URE2 SCADA system account provisioning process to remind performers to slow down when they are performing their initial task and to include an expanded peer check of the “event viewer” SCADA screen to verify that only intended access has been granted during provisioning. This additional emphasis will alert the performer of the risk of inadvertent changes during manual provisioning and mandate use of filtering techniques to minimize what is on screen during editing before access is provisioned. The previous peer check included a step verifying that each individual's access was correct after a change – the changes in this event were not associated with the individual accounts that were being intentionally modified. Therefore, an expanded peer check that includes a step for verifying the event viewer will allow the peer checker to see all activity, intentional and inadvertent, on any impacted account; and 3) revised job aid and implemented and communicated with required performers and their backup performers to ensure they are familiar with the changes and the reasons the changes were made.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015417 | CIP-003-3 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE3 discovered, while reviewing and verifying access permissions for a CIP Information Repository (CIR), that an administrator had explicit access to a RFC_URE3 CIR without having authorization explicitly documented in the authorized list for the CIR. During an investigation of how the administrator got access, RFC_URE3 learned that the administrator inadvertently provided himself access when attempting to troubleshoot access connectivity for a submitted request. During the troubleshooting attempt, the administrator received a pop-up message stating “[y]ou don’t currently have permissions to access this folder.” Because the administrator could not complete the task without access permissions, the administrator proceeded to abandon the task. The pop-up window with the error pop-up had an option to “continue,” which the administrator incorrectly assumed would return the administrator to the prior screen as a result of the error message. The administrator clicked “continue” and recorded in the provisioning ticket that the administrator did not have permission to provision the requested access. The administrator, however did not notice the small text on the pop-up message that said “click ‘continue’ to permanently get access to this folder” before he clicked “continue.” As a result, the administrator granted himself access without realizing that the system had granted him access. This noncompliance involves the management practice of workforce management because the administrator did not understand that clicking “continue” would grant him unauthorized access to the CIR. The administrator’s lack of attention to detail when utilizing the operating system dialog boxes resulted in him getting access to the CIR without having authorization explicitly documented in the authorized list for the CIR. The only reason why clicking “continue” granted the administrator access was because he was logged in as an administrator when he clicked “continue.” In the process of coming up with its Mitigating Activities, RFC_URE3 discovered that the pop-up is a standard operating system prompt that cannot be changed. Ineffective training is the root cause of this noncompliance because the administrator was not properly trained to know that by clicking “continue,” he would give himself unauthorized access to the CIR. RFC_URE3 also did not make clear that access to the CIR is on a need to know only basis. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from this noncompliance is that an unauthorized individual could gain access to the CIR and use information from the CIR to harm the BPS. The potential harm is minimized because to even get to the prompt in question, the administrator had to be logged into the RFC_URE3 system and have authorization to get to the point on the system where he could begin troubleshooting the access connectivity issue. Only RFC_URE3 administrators with valid login credentials could ever get to the point where the prompt would come up. Additionally, the administrator in question is a trusted employee that had a current Personnel Risk Assessment and current CIP training at the time of the noncompliance. Additionally, the administrator was unaware that he had access to the CIR and he did not access the CIR at any point. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed the administrator’s access to the Compliance Information Repository; 2) reviewed whether the pop-up could be changed. The pop-up, however, is a standard operating system prompt that cannot be changed; 3) engaged administrator staff to raise awareness of the operating system dialog box text to prevent future occurrences and promote greater attention to detail; 4) hosted an additional session to review the facts of this issue and reinforce the lessons learned to raise awareness to ensure all domain administrators received this information. The only individuals that would ever see the prompt and pop-up are administrator staff because they are the only people that have access to the area of the system where the pop up would come up. RFC_URE3 also routinely crosschecked the access permissions for CIRs and the authorized access list for the CIRs to ensure that no other system administrators received unauthorized access. Furthermore, a new automated system for access provisioning is currently being developed and implemented at RFC_URE3 with access provisioning including the type of provisioning for CIR access in this case. The RFC_URE3 CIP V5 implementation program includes an Access Controls and Automation (AC&A) project to improve and support access control and access governance. The AC&A project includes design and implementation of an Identity and Access Management solution which will centralize access management and governance processes and procedures at RFC_URE3. The solution will provide a number of centralized services including roles-based access control, user account life-cycle management, access certification (governance), password management, access requesting and approvals (authorization), and auditing and reporting functions. The Identity and Access Management solution will assist in preventing similar access issues from reoccurring in the future under CIP Version 5 by centralizing and streamlining the process of granting access and the procedures surrounding requesting access.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015558 | CIP-003-3 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE3 determined that two trusted employees serving as Active Directory (AD) domain administrators had access to CIP protected information file share repositories (CIRs) without proper CIP credentials. RFC_URE3 hosts multiple CIP CIRs on a Corporate Data Network (CDN), which uses AD for user authentication and authorization. RFC_URE3’s NERC CIP Access Control Overview Procedure requires each individual to have a valid personnel risk assessment (PRA) and to have taken CIP training prior to accessing CIP protected information. In this case, the two AD domain administrators did not have a valid PRA or up to date CIP training. RFC_URE3 hosts multiple CIP CIRs on a CDN, which uses AD for user authentication and authorization. RFC_URE3, through its CIP Operations and Transmission Strategy and Compliance groups, conducted an extent of condition review to confirm the scope of this issue. RFC_URE3 uses several types of administrator groups which allow access to IT groups supporting the CDN file share environment. In reviewing access to those environments, CIP Operations reviewed CIP credentials for 126 individuals within various administrative groups that had access to the CDN, and, therefore, to the CIRs in question hosted in the CDN. Of those 126, CIP Operations identified 17 additional instances of employees that had access to CIP protected information without the proper CIP credentials specified in the RFC_URE3 program. In total, 19 individuals did not have proper CIP credentials. Of those 19, 16 individuals did not have a current PRA and CIP training. In one case, the individual had current training, but not a current PRA. In two cases, the individual had a current PRA, but not current training. To mitigate these 19 issues, RFC_URE3 completed PRA and CIP training for the two Active Directory administrators. RFC_URE3 then removed CIR access for the eleven individuals that were members of the two local administrative groups. Lastly, RFC_URE3 completed PRA and CIP training for the six administrators having access to CIP CIRs. This noncompliance involves the management practices of workforce management and work management. RFC_URE3 determined that there are three contributing causes of these issues. First, RFC_URE3 personnel made an incorrect assumption regarding how the CDN file share environment would be used with respect to hosting NERC CIP protected information. Second, there are no common/consistent procedural requirements for acquiring CIP credentials within these administrative groups when granting administrative access to a CIR. In general, each administrative group adheres to strict access control processes, but these processes do not reflect the requirements for CIR access as prescribed under RFC_URE3’s NERC CIP Access Control Overview Procedure. Third, RFC_URE3 identified that it did not have adequate procedural controls for the creation of, management of, and removal of a CIR. The root cause of this noncompliance was the lack of consistent procedural requirements for acquiring CIP credentials across RFC_URE3. The duration of the noncompliance was approximately eighteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from this noncompliance is that an unauthorized individual could gain access to the CIR and use the sensitive information contained therein to harm the BPS. The potential risk and harm is minimized because the administrators are trusted employees and the administrators receive a general background investigation that is equivalent to a PRA when they are hired. Additionally, new administrators receive training on general security controls, including the handling of sensitive information. The CDN file share environment contains thousands of files and only a small fraction of those files are CIP Protected. Without specific knowledge that the repositories contained CIP protected information, it would be unlikely that an administrator would accidently locate the files in question. Lastly, none of the administrators involved accessed any CIP Protected files in the CIRs. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) completed PRA and CIP training for the two Active Directory administrators; 2) removed CIR access for the eleven individuals that were members of the two local administrative groups; 3) completed PRA and CIP training for the six administrators having access to CIP CIRs; 4) completed review of administrative accounts on hardware hosting CIP CIRs; 5) created/updated CIR administrative access procedures to ensure completion of PRA and CIP training during onboarding; 6) developed a CIR commissioning and decommissioning process. This will ensure that RFC_URE3 follow the same process when setting up a CIR and granting initial access to that CIR and the same process when closing down a CIR and removing access from that CIR; and 7) confirmed its new access management system functionality automatically removes CIR access for administrators without proper CIP credentials. RFC_URE3 is in the final stages of implementing its new access management system to manage access to CIP BSCAs, Physical Security Perimeters and CIRs. This system will replace many manual access control processes that have been prone to human error in the past. The functionality of the system includes interfaces with RFC_URE3’s systems of records for completion of both cyber security training and PRA. No access can be granted without successful completion of both CIP requirements. In addition, if either credential expires, the system would automatically remove access within 24 hours. This should effectively prevent further violations with CIP-003 R5 where CIR access is granted with insufficient CIP credentials. The combination of the tool and CIP Commissioning procedure are intended to effectively address all causal factors associated with the originating issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016007 | CIP-003-3 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE3’s project management team for the implementation of its new access management system determined that during the final production cutover, RFC_URE3 granted or retained NERC CIP access for 18 users where the users did not meet the prerequisites for valid access. RFC_URE3 removed all access for the 18 users seven days later. RFC_URE3 initially discovered this issue when an RFC_URE3 Subject Matter Expert conducting a post cutover validation identified that a team member that should not have access was part of an access role with enabled access. That expert raised this issue to the project team and the team identified that this user received access to the role because of a manual error in the bulk data upload where a typing mistake led to the incorrect user getting access to the system. (RFC_URE3 has introduced Role Based Access as part of the implementation for managing access. Access to assets in scope for NERC CIP Requirements is granted through requests for an Access Role selected from a role catalog in the system. An Access Role is the set of Access Privileges required for an individual to perform a job function, for instance, "SCADA Operator.") The project team initiated an extent of condition review based on the initial RFC_URE3 inquiry to determine if there were any other users who obtained access as a part of the new access management system release without NERC CIP prerequisites of a valid Personnel Risk Assessment (PRA) and valid CIP training. RFC_URE3’s extent of condition review discovered that a total of 18 users were granted physical, electronic, or information access by the new system to either NERC Version 3 Critical Cyber Assets (CCAs) or Critical Information Repositories (CIRs) without having the required NERC CIP prerequisites in place. The 18 users’ access involved RFC_URE3 shared IT service CIRs or Critical Cyber Assets and as a result had impacts for multiple business units at RFC_URE3: i. Seven users obtained access to CIP information stored in CIRs. Of those seven, six cases involved shared electronic access. Of those six, one did not have a PRA or CIP training and five users had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. ii. Five users gained or retained electronic access to Critical Cyber Assets. Of those, four users involved shared electronic access. Of those four, three did not have a PRA or CIP training and one had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. iii. Six users obtained physical access to Physical Security Perimeters (PSPs). Of those, one user involved shared access. This user did not have a PRA or CIP training. The remaining five cases involved physical access to business unit specific PSPs. Two users did not have a PRA or CIP training, and three users had a valid PRA, bud did not complete CIP training. This noncompliance involves the management practice of asset and configuration management. After reviewing the noncompliance, the project team determined that communications from the project team did not explicitly require that the bulk load data must only include previously authorized users and should not contain new users that had a business need for future access. This lack of clarity in communication contributed to the granting of unauthorized access to 18 users during the bulk data upload. In addition, due to data synchronization issues between the new system and the training record system, the PRA/training validation process was not run while the issue was being resolved. This allowed the final bulk load performed to inadvertently bypass validation, which would have prevented access being granted to the eighteen users. Miscommunication regarding what users were meant to be part of the bulk upload and a failure to follow RFC_URE3’s designed process by not running the PRA/training validation process were the root causes of this noncompliance. The duration of the noncompliance was approximately seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance occurred during a data migration effort related to the implementation of the new access management system. In all cases, the users had no knowledge that access had been provisioned. The users included in the bulk upload without completed CIP training or PRAs were in the process of being on-boarded for CIP access and had been selected by management in the specific business units for inclusion because the users were intended to receive access after they completed their PRAs and CIP training. RFC_URE3 performed a post launch validation that identified the issue one day after it occurred and removed all unauthorized access eight days after it was originally granted, which shows that RFC_URE3’s detective and corrective controls are working effectively. Lastly, RFC_URE3 verified that physical access permissions were not used for the six cases where physical access was mistakenly granted. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed access for all individuals granted access as a result of the data loading error; 2) set the validation process (To maintain compliance with CIP standards and conform to RFC_URE3's procedures for access management, the new access management system was designed with an automated validation routine which conducts a daily verification of the training expiration date and PRA expiration date for every user with NERC CIP physical, logical, or information access.) to run automatically on a daily basis to check for proper PRA and CIP trainings as part of the provisioning process and implemented synchronization process corrections for certain training data used by the new system; 3) prepared a job aid addressing the requirements necessary for processing the bulk load of access lists in the future, which will include a peer check to validate that data is entered correctly and in the correct format as an additional precaution to running the validation process. The job aid also includes instructions to limit the bulk load to existing CIP-cleared users only and to verify that the validation process is running before and after all up loads; and 4) updated procedure to address approvals required for bulk uploads of authorized access for users.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015035 | CIP-005-3a | R2 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue of CIP-005-3a R2. RFC_URE4 deployed a new phone system in its Control Room. However, while reviewing certain settings on its system, RFC_URE4 discovered that it had misconfigured the new phones on a network that allowed access to Electronic Security Perimeter (ESP) subnetworks when no business need existed for such access. Generally, RFC_URE4 controls ports and services access at all access points to the ESP through two means: (a) role-based access control; and, (b) standard access control lists at networking equipment. When a user attempts to access any RFC_URE4 network, a combination of the firewall rulesets and the role-based access control determine whether the user should be granted access. In this case, RFC_URE4 provisioned the new phone system network that mistakenly did not route traffic with role-based access control protection. The root cause of this noncompliance was RFC_URE4’s improper design of its infrastructure during a migration of its data center. This major contributing factor involves the management practice of implementation, which focuses on ensuring that a registered entity implements or modifies an asset in a manner that does not compromise grid reliability or resilience. The duration of the noncompliance was approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, multiple protections related to the new phone system greatly reduced the potential risk to the BPS. For instance, the new phones have a stripped down operating system since they are designed for use as a phone and not as a full-featured PC. This fact reduces the opportunity for malware or other tools to be installed and used to conduct activities that could impact the BPS. Second, the new phones were located within a previously defined PSP and this limited the physical access to personnel with the appropriate permissions. Third, even if a device was compromised, the protections on the applications and systems themselves (e.g. login accounts, anti-virus, etc.) would have provided a robust line of defense. ReliabilityFirst also notes that RFC_URE4 verified that no improper access from the misconfigured networks occurred to any ESP. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) Corrected network configuration for the new phone system and performed an investigation of network traffic logs throughout the 149-day period and determined that no improper access to ESP networks occurred from the misconfigured network; 2) performed a validation of the corrected network configuration; 3) refined the firewall rule that allowed this access to only include active user networks that are subject to role-based access control; and 4) worked with vendor to design and deploy a new intermediate device between users and critical assets, as designated by the CIP Version 5 Standards. This project is being implemented as a result of the CIP Version 5 Standards becoming mandatory and enforceable; not as a result of the self-report.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015131 | CIP-009-3 | R2 | ReliabilityFirst determined that RFC_URE4 had an issue of CIP-009-3 R2 identified during a Compliance Audit. ReliabilityFirst reviewed evidence related to RFC_URE4’s obligation to exercise its recovery plan(s) at least annually. RFC_URE4 could only provide lessons learned documents and meeting invitation requests as evidence. As a result, ReliabilityFirst determined that RFC_URE4 was unable to provide sufficient and appropriate evidence that it had exercised these recovery plans at least annually. The root cause of this noncompliances was RFC_URE4’s failure to appreciate the level of detail required in the documentation associated with the exercise of recovery plans. This major contributing factor involves the management practice of reliability quality management, which focuses on performing annual process reviews to validate the processes. The duration of the noncompliance was approximately twenty-two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that this noncompliance was a documentation issue. From the evidence reviewed, it appeared that RFC_URE4 had conducted some exercises, but failed to provide enough detail to demonstrate actions taken, decisions made, etc. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) added a scenario section that would cause the recovery plan to be invoked based on one or more of the triggering events; 2) added injects to the scenario as part of the scenario; 3) added lessons learned log details; and 4) added a signup sheet to capture the name, signature, and roles for each participant in the exercise.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016015541 | CIP-003-3 | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE5 determined that two trusted employees serving as Active Directory (AD) domain administrators had access to CIP protected information file share repositories (CIRs) without proper CIP credentials. RFC_URE5 hosts multiple CIP CIRs on a Corporate Data Network (CDN), which uses AD for user authentication and authorization. RFC_URE5’s NERC CIP Access Control Overview Procedure requires each individual to have a valid personnel risk assessment (PRA) and to have taken CIP training prior to accessing CIP protected information. In this case, the two AD domain administrators did not have a valid PRA or up to date CIP training. RFC_URE5 hosts multiple CIP CIRs on a CDN, which uses AD for user authentication and authorization. RFC_URE5, through its CIP Operations and Transmission Strategy and Compliance groups, conducted an extent of condition review to confirm the scope of this issue. RFC_URE5 uses several types of administrator groups which allow access to IT groups supporting the CDN file share environment. In reviewing access to those environments, CIP Operations reviewed CIP credentials for 126 individuals within various administrative groups that had access to the CDN. Of those 126, CIP Operations identified 17 additional instances of employees that had access to CIP protected information without the proper CIP credentials specified in the RFC_URE5 program. In total, 19 individuals did not have proper CIP credentials. Of those 19, 16 individuals did not have a current PRA and CIP training. In one case, the individual had current training, but not a current PRA. In two cases, the individual had a current PRA, but not current training. To mitigate these 19 issues, RFC_URE5 completed PRA and CIP training for the two Active Directory administrators. RFC_URE5 then removed CIR access for the eleven individuals that were members of the two local administrative groups. Lastly, RFC_URE5 completed PRA and CIP training for the six administrators having access to CIP CIRs. This noncompliance involves the management practices of workforce management and work management. RFC_URE5 determined that there are three contributing causes of these issues. First, RFC_URE5 personnel made an incorrect assumption regarding how the CDN file share environment would be used with respect to hosting NERC CIP protected information. Second, there are no common/consistent procedural requirements for acquiring CIP credentials within these administrative groups when granting administrative access to a CIR. In general, each administrative group adheres to strict access control processes, but these processes do not reflect the requirements for CIR access as prescribed under RFC_URE5’s NERC CIP Access Control Overview Procedure. Third, RFC_URE5 identified that it did not have adequate procedural controls for the creation of, management of, and removal of a CIR. The root cause of this noncompliance was the lack of consistent procedural requirements for acquiring CIP credentials across RFC_URE5. The duration of the noncompliance was approximately eighteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from this noncompliance is that an unauthorized individual could gain access to the CIR and use the sensitive information contained therein to harm the BPS. The potential risk and harm is minimized because the administrators are trusted employees and the administrators receive a general background investigation that is equivalent to a PRA when they are hired. Additionally, new administrators receive training on general security controls, including the handling of sensitive information. The CDN file share environment contains thousands of files and only a small fraction of those files are CIP Protected. Without specific knowledge that the repositories contained CIP protected information, it would be unlikely that an administrator would accidently locate the files in question. Lastly, none of the administrators involved accessed any CIP Protected files in the CIRs. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) completed PRA and CIP training for the two Active Directory administrators; 2) removed CIR access for the eleven individuals that were members of the two local administrative groups; 3) completed PRA and CIP training for the six administrators having access to CIP CIRs; 4) completed review of administrative accounts on hardware hosting CIP CIRs; 5) created/updated CIR administrative access procedures to ensure completion of PRA and CIP training during onboarding; 6) developed a CIR commissioning and decommissioning process. This will ensure that RFC_URE5 follow the same process when setting up a CIR and granting initial access to that CIR and the same process when closing down a CIR and removing access from that CIR; and 7) confirmed its new access management system functionality automatically removes CIR access for administrators without proper CIP credentials. RFC_URE5 is in the final stages of implementing its new access management system to manage access to CIP BSCAs, Physical Security Perimeters and CIRs. This system will replace many manual access control processes that have been prone to human error in the past. The functionality of the system includes interfaces with RFC_URE5’s systems of records for completion of both cyber security training and PRA. No access can be granted without successful completion of both CIP requirements. In addition, if either credential expires, the system would automatically remove access within 24 hours. This should effectively prevent further violations with CIP-003 R5 where CIR access is granted with insufficient CIP credentials. The combination of the tool and CIP commissioning procedure are intended to effectively address all causal factors associated with the originating issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016016010 | CIP-003-3 | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. RFC_URE5’s project management team for the implementation of its new access management system determined that during the final production cutover, RFC_URE5 granted or retained NERC CIP access for 18 users where the users did not meet the prerequisites for valid access. RFC_URE5 removed all access for the 18 users seven days later. RFC_URE5 initially discovered this issue when an RFC_URE5 Subject Matter Expert conducting a post cutover validation identified that a team member that should not have access was part of an access role with enabled access. That expert raised this issue to the project team and the team identified that this user received access to the role because of a manual error in the bulk data upload where a typing mistake led to the incorrect user getting access to the system. (RFC_URE5 has introduced Role Based Access as part of the implementation for managing access. Access to assets in scope for NERC CIP Requirements is granted through requests for an Access Role selected from a role catalog in the system. An Access Role is the set of Access Privileges required for an individual to perform a job function, for instance, "SCADA Operator.") The project team initiated an extent of condition review based on the initial RFC_URE5 inquiry to determine if there were any other users who obtained access as a part of the new access management system release without NERC CIP prerequisites of a valid Personnel Risk Assessment (PRA) and valid CIP training. RFC_URE5’s extent of condition review discovered that a total of 18 users were granted physical, electronic, or information access by the new system to either NERC Version 3 Critical Cyber Assets (CCAs) or Critical Information Repositories (CIRs) without having the required NERC CIP prerequisites in place. The 18 users’ access involved RFC_URE5 shared IT service CIRs or Critical Cyber Assets and as a result had impacts for multiple business units at RFC_URE5: i. Seven users obtained access to CIP information stored in CIRs. Of those seven, six cases involved shared electronic access. Of those six, one did not have a PRA or CIP training and five users had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. ii. Five users gained or retained electronic access to Critical Cyber Assets. Of those, four users involved shared electronic access. Of those four, three did not have a PRA or CIP training and one had a valid PRA, but did not complete CIP training. The remaining one user had a valid PRA, but did not complete CIP training. iii. Six users obtained physical access to Physical Security Perimeters (PSPs). Of those, one user involved shared access. This user did not have a PRA or CIP training. The remaining five cases involved physical access to business unit specific PSPs. Two users did not have a PRA or CIP training, and three users had a valid PRA, bud did not complete CIP training. This noncompliance involves the management practice of asset and configuration management. After reviewing the noncompliance, the project team determined that communications from the project team did not explicitly require that the bulk load data must only include previously authorized users and should not contain new users that had a business need for future access. This lack of clarity in communication contributed to the granting of unauthorized access to 18 users during the bulk data upload. In addition, due to data synchronization issues between the new system and the training record system, the PRA/training validation process was not run while the issue was being resolved. This allowed the final bulk load performed to inadvertently bypass validation, which would have prevented access being granted to the eighteen users. Miscommunication regarding what users were meant to be part of the bulk upload and a failure to follow RFC_URE5’s designed process by not running the PRA/training validation process were the root causes of this noncompliance. The duration of the noncompliance was approximately seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance occurred during a data migration effort related to the implementation of the new access management system. In all cases, the users had no knowledge that access had been provisioned. The users included in the bulk upload without completed CIP training or PRAs were in the process of being on-boarded for CIP access and had been selected by management in the specific business units for inclusion because the users were intended to receive access after they completed their PRAs and CIP training. RFC_URE5 performed a post launch validation that identified the issue one day after it occurred and removed all unauthorized access eight days after it was originally granted, which shows that RFC_URE5’s detective and corrective controls are working effectively. Lastly, RFC_URE5 verified that physical access permissions were not used for the six cases where physical access was mistakenly granted. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) removed access for all individuals granted access as a result of the data loading error; 2) set the new access management system validation process (To maintain compliance with CIP standards and conform to RFC_URE5's procedures for access management, the new access management system was designed with an automated validation routine which conducts a daily verification of the training expiration date and PRA expiration date for every user with NERC CIP physical, logical, or information access.) to run automatically on a daily basis to check for proper PRA and CIP trainings as part of the provisioning process and implemented synchronization process corrections for certain training data used by the new system; 3) prepared a job aid addressing the requirements necessary for processing the bulk load of access lists in the future, which will include a peer check to validate that data is entered correctly and in the correct format as an additional precaution to running the validation process. The job aid also includes instructions to limit the bulk load to existing CIP-cleared users only and to verify that the validation process is running before and after all up loads; and 4) updated procedure to address approvals required for bulk uploads of authorized access for users.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016016172 | CIP-002-5.1 | R2; R2.2. | SERC sent a SERC_URE1 affiliate an audit detail letter notifying it of a compliance audit. SERC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-5.1 R2.2. The CIP Senior Manager, or delegate, did not approve an accurate SERC_URE1 Bulk Electric System (BES) Cyber Systems list. SERC_URE1’s CIP Senior Manager approved a list of BES Cyber Systems that SERC_URE1 identified as its complete list of BES Cyber Assets (BCAs). A month and half later, SERC_URE1 was preparing for an upcoming SERC audit of an SERC_URE1’s affiliate and discovered the approved BES Cyber System list was missing BCAs. SERC_URE1 utilizes a database to track, inventory information about its BCAs, and produce the BES Cyber System list for approval. However, subject-matter-experts (SMEs) must manually transfer Cyber Asset information from working spreadsheets into the database. Prior to SERC_URE1 approving the list, the SMEs transferred the data from the medium impact BES Cyber System spreadsheets into the database, but the SME did not properly select flags some of the BCAs. The SME's failure to check the flag resulted in the omission of the seven BCAs from the printed BES Cyber System list that the CIP Senior manager reviewed and approved. SERC_URE1 determined that the root cause of this issue was human performance. The SME failed to check the flag on the BCAs while manually transferring data from the spreadsheets to the database. This issue lasted approximately three and a half months from when the CIP Version 5 Standard became enforceable until the CIP Senior Manager approved the list of all BCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1s failure to have the complete list of BCAs approved by the CIP Senior Manager or delegate can lead to the application of inadequate or non‐existent cyber security controls that can lead to compromise or misuse that can affect the real‐time operation of the BES. However, SERC_URE1 only omitted 0.01% of the total BCAs. The SERC_URE1 error in data entry and list creation did not result in any neglected or negated security measures for the BCAs at issue. SERC_URE1 afforded the BCAs the required CIP protections and security measures via the working spreadsheets which contained all BCAs. The SERC_URE1 failure was administrative in nature. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) completed an additional verification review of Substations BES Cyber Systems to ensure no other in-scope assets were excluded from the lists reviewed and approved by the CIP Senior Manager; 2) created and officiated an addendum to be signed by the CIP Senior Manager showing the devices added to the official Substations list of Medium Impact BES Cyber Systems; and 3) trained personnel on the need to properly identify any BES Cyber Assets/Systems placed in service within the Substations database with the “Cyber Asset” flag, which allows for the associated Cyber Asset details to be exported when producing a report or spreadsheet for review by the CIP Senior Manager.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016016173 | CIP-002-5.1 | R2; R2.2 | SERC sent a SERC_URE2 affiliate, an audit detail letter notifying it of a Compliance Audit. SERC_URE2 submitted a Self-Report stating that it had an issue of CIP-002-5.1 R2.2. The CIP Senior Manager, or delegate, did not approve an accurate SERC_URE2 Bulk Electric System (BES) Cyber Systems list. SERC_URE2’s CIP Senior Manager approved a list of BES Cyber Systems that SERC_URE2 identified as its complete list of BES Cyber Assets (BCAs). Almost three months later, SERC_URE2 was performing an extent-of-condition analysis based on an affiliates noncompliance, and discovered the approved BES Cyber System list was missing BCAs. SERC_URE2 utilizes a database to track, inventory information about its BCAs, and produce the BES Cyber System list for approval. However, subject-matter-experts (SMEs) must manually transfer Cyber Asset information from working spreadsheets into the database. Prior to the date SERC_URE2 approved the list, the SMEs transferred the data from the medium impact BES Cyber System spreadsheets into the database, but the SME did not properly select flags for three of the BCAs. The SME's failure to check the flag resulted in the omission of the three BCAs from the printed BES Cyber System list that the CIP Senior manager reviewed and approved. SERC_URE2 determined that the root-cause of this issue was human performance. The SME failed to check the flag on three BCAs while manually transferring data from the spreadsheets to the database. This issue lasted approximately three and a half months from when the CIP Version 5 Standard became enforceable until the CIP Senior Manager approved the list of all BCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2s failure to have the complete list of BCAs approved by the CIP Senior Manager or delegate can lead to the application of inadequate or non‐existent cyber security controls that can lead to compromise or misuse that can affect the real‐time operation of the BES. However, SERC_URE2 only omitted 0.14% of the total BCAs. The SERC_URE2 error in data entry and list creation did not result in any neglected or negated security measures for the BCAs at issue; SERC_URE2 afforded the BCAs the required CIP protections and security measures via the working spreadsheets which contained all BCAs. The SERC_URE2 failure was administrative in nature. SERC considered SERC_URE2’s, and its affiliate companies’, compliance history, and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2 and each affiliate company: 1) completed an additional verification review of Substations BES Cyber Systems to ensure no other in-scope assets were excluded from the lists reviewed and approved by the CIP Senior Manager; 2) created and officiated an addendum to be signed by the CIP Senior Manager showing the devices added to the official Substations list of Medium Impact BES Cyber Systems; and 3) trained personnel on the need to properly identify any BES Cyber Assets/Systems placed in service within the Substations database with the “Cyber Asset” flag, which allows for the associated Cyber Asset details to be exported when producing a report or spreadsheet for review by the CIP Senior Manager.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2016016371 | CIP-006-6 | R2; R2.1 | SERC_URE3 submitted a Self-Report stating that it had an issue of CIP-006-6 R2.1. SERC_URE3 did not provide continuous escort for a visitor within a Physical Security Perimeter (PSP). A cleaning contractor with authorized unescorted access to the SERC_URE3 back-up control center permitted a SERC_URE3 employee into the secured PSP for a meeting. However, SERC_URE3 had not authorized the employee for unescorted access. Approximately one minute later, the employee entered a downstairs meeting room and SERC_URE3 meeting participants recognized the employee as a visitor. The employee did not display a visitor badge lanyard, so SERC_URE3 staff immediately documented the visitors PSP access and initiated continuous escort. The visitor badge lanyard is part of an internal control implemented for CIP Version 5. All visitors are required display a visitor lanyard when visiting a PSP. SERC_URE3 determined that the root cause of this issue was human error. The cleaning contractor failed to follow the Physical Security Plan training received as well as established polices and procedures, and permitted the employee PSP access without confirming access authorization. SERC_URE3 Corporate Security staff performed an extent-of-condition by randomly sampling camera footage of PSP access doors and determining if any similar issues had occurred. SERC_URE3 did not discover any additional unauthorized access instances. This issue lasted approximately one minute, from when a visitor entered the PSP unescorted until SERC_URE3 documented the visitors PSP access and initiated escorting. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE3’s failure to properly escort an individual without authorized unescorted access permissions could have permitted an individual the opportunity to maliciously, or through ignorance of the criticality of the facility, impose actions that could be detrimental the BPS. However, SERC_URE3 identified the issue through an established internal control and confirmed through video footage that the total time between the visitor being admitted entry into the PSP by the cleaning contractor and the entry of the visitor into the meeting room as being less than one minute. The visitor at issue is a SERC_URE3 employee, in good standing with over 37 years of service. The path the employee walked did not take the employee near any BES Cyber Assets (BCAs), and an operator within the PSP saw the employee coming through the back-up control center and was able to confirm that the employee never entered any room where BCAs were located. SERC considered SERC_URE3's CIP-006-6 R2.1 compliance history in determining the disposition track. The applicable compliance history includes assessing CIP-006-3 R1.6 violations for relevance. SERC determined that SERC_URE3’s CIP-006-6 R2.1 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE3: 1) conducted a face-to-face meeting with the cleaning contractor that did not follow SERC_URE3’s established visitor control program. This included discussing the incident, reviewing the procedures, and emphasizing the importance of visitor control; and 2) held a training session with all cleaning contractor staff members with PSP access. SERC_URE3 reviewed the visitor control program and stressed the importance of following all visitor control processes.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2016016375 | CIP-010-2 | R1; R1.1 | SERC_URE3 submitted a Self-Report stating that it had an issue of CIP-010-2 R1.1. SERC_URE3 did not develop a baseline configuration, individually or by group, which included current security patch levels. A SERC_URE3 electrical engineer was performing work at a site and discovered the documented baselines for two Cyber Assets within a medium impact BES Cyber System without External Routable Connectivity (ERC) were inaccurate. The engineer discovered that the documented baselines were different from what SERC_URE3 had deployed on the Cyber Assets. SERC_URE3 has a manual process for updating medium impact BES Cyber Systems without ERC where the field technicians are responsible for updating the configuration monitoring software following baseline configuration changes. SERC_URE3 utilizes a software solution to automate the documentation of changed baseline configurations for Cyber Assets with ERC. Six months prior, a SERC_URE3 field technician performed a change on the two Cyber Assets without ERC and captured the new baseline configuration to be loaded into the configuration monitoring software application. However, the technician inadvertently uploaded the original pre-change baseline configuration file from the file repository instead of the new post-change baseline configuration. The error created a discrepancy in the documented baseline configuration required for CIP-010-2 compliance on July 1, 2016, and the deployed baseline configuration. SERC_URE3 conducted an extent-of-condition review by exporting all existing medium impact BES Cyber System without ERC baseline configurations and comparing the results to the documented baseline within the configuration monitoring software application. SERC_URE3 determined there were no additional discrepancies. SERC_URE3 determined that the root cause of this issue was a deficient process. The SERC_URE3 process for updating the configuration monitoring software application did not contain adequate instructions to update the configuration monitoring software application with baseline configurations of BES Cyber Systems without ERC. This issue lasted approximately two months, from when CIP Version 5 became enforceable, until SERC_URE3 updated the configuration monitoring software with the correct baseline for both Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3’s failure to document the baseline configuration of its BES Cyber Systems could have permitted unauthorized changes to occur and potentially go undetected. However, the correct and appropriate software was running in the production environment on the two Cyber Assets at issue. The duration of the discrepancy between the documented system baseline configuration and the running configuration was less than 60 days. Changes uploaded into the configuration monitoring software application for these two Cyber Assets would have identified a discrepancy and triggered an alert to investigate. Additionally, this issue only affected 5% of the total BES Cyber Assets in a single Medium Impact BES Cyber System without ERC. The BES Cyber Assets had no remote connectivity; therefore, malicious alterations to either of these Cyber Assets would have had to occur by being physically present. SERC_URE3 has physical access controls deployed for alerting and monitoring for unauthorized access and access attempts. SERC considered SERC_URE3’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE3: 1) updated the configuration monitoring software with the correct baseline for both Cyber Assets; 2) updated relay work instructions to include more detailed directions on how to export and upload the baseline configurations from the relays to the configuration management software; 3) held a meeting with the Transmission substation CIP team describing the updated Relay Work Instruction document. The meeting was intended to educate personnel about the updated baseline configuration section and to stress the importance of following all documented processes; and 4) completed a comparison review of all baselines exported from the Substation BES Cyber Assets versus the baselines documented within the configuration monitoring software.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016015973 | CIP-006-6 | R2; R2.2 | SERC sent SERC_URE4 an audit detail letter notifying it of a compliance audit. SERC_URE4 submitted a Self-Report stating that it had an issue of CIP-006-6 R2. SERC_URE4 did not log visitor access into and out of a Physical Security Perimeter (PSP). SERC_URE4 provides access badges to escorted visitors to automate the logging of visitor entry into and exit from the PSP. SERC_URE4 requires the authorized escort to have each visitor scan the badge upon entry to and exit from the PSP. A SERC_URE4 employee with authorized unrestricted physical access escorted three visitors into the PSP. Unbeknownst to the escort, one of the visitors did not badge upon entry to the PSP. Approximately 12 minutes later, the escort and three visitors exited the PSP. A week later, a different SERC_URE4 employee with authorized unescorted physical access escorted a visitor into the same PSP. Approximately three minutes later, the escort and visitor exited the PSP, but the visitor did not badge upon exit of the PSP. Eight days later, SERC_URE4 was performing its quarterly internal control log review and discovered the visitor log issues. SERC_URE4 performed a root cause analysis and determined human performance as the primary root cause. The escorts did not ensure the visitors badged upon entry into or exit out of the PSP. SERC_URE4 performed an extent of condition by reviewing all logs pertaining to PSP’s and discovered no further occurrences. The issue lasted approximately 15 days, from when SERC_URE4 failed to log visitor accessuntil SERC_URE4 discovered the issue and documented the visitor exit times. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4’s failure to log visitors in or out of a PSP could result in unauthorized personnel being unaccounted for within a PSP, and could inflict physical damage to BES Cyber Systems (BCS). However, SERC_URE4 did provide continuous escort while the visitors were inside the PSP. In addition, SERC_URE4 has video surveillance at the PSP in question. Subsequently, SERC_URE4’s BCS devices reside within access controlled system racks inside the PSP; therefore, the visitors did not have physical access to the BCS devices. SERC considered SERC_URE4’s CIP-006-6 R2 compliance history in determining the disposition track. SERC determined SERC_URE4’s CIP-006-6 R2 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE4: 1) temporarily suspended the escort's PSP access upon the discovery of the incident to allow time for retraining; 2) retrained the escorts on expected behaviors and responsibilities of visitor control inside the PSP; and 3) provided additional visitor access control training to all other individuals in the cybersecurity operations group.
2017-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2016015974 | CIP-010-2 | R1; R1.1 | SERC sent SERC_URE4 an audit detail letter notifying it of a compliance audit. SERC_URE4 submitted a Self-Report stating that it had an issue of CIP-010-2 R1.1. SERC_URE4 did not develop a complete baseline configuration individually, or by group, that includes all logical network accessible ports. Twelve days after the CIP Version 5 enforceable date, while conducting a CIP V5 controls review, a SERC_URE4 employee discovered a discrepancy in a network device’s documented baseline configuration compared to the devices running configuration. SERC_URE4 discovered that one network device’s running configuration showed an additional network accessible simple network management protocol (SNMP) port open, but SERC_URE4 had not documented the port on the baseline configuration. Prior the CIP Version 5 enforceable date, SERC_URE4 deployed a common configuration on its networking devices, but it did not document the SNMP port on the baseline configuration. SERC_URE4 performed an extent of condition and discovered that specific network device models deployed at the same time had similar issues. SERC_URE4 did not identify issues with other network devices. SERC_URE4 determined the root cause to be human performance and inadequate process. Upon deploying the network device, SERC_URE4 initiated a software update to disable the SNMP port, but the update was not successful. SERC_URE4’s process did not include baseline checks and SERC_URE4 did not verify the running configuration against the baseline after the software update. The issue lasted 28 days, from when CIP Version 5 became enforceable until SERC_URE4 updated the baseline configuration. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE4’s failure to document logical ports on a network switch may allow an attacker to leverage that port unnoticed and render logical and damage to the switchyard’s operations. However, SERC_URE4 determined that the port was required to be open for that model of networking devices. SERC_URE4 has facility physical security protections deployed to monitor and alert for unauthorized access attempts. In addition, the devices in question have no external routable connectivity; therefore, network accessibility is limited to the local network and limits the potential of network-based attacks against the open port. SERC considered SERC_URE4’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE4: 1) conducted a review on the specific networking device in question; 2) established and approved a baseline configuration to include SNMP; 3) developed new commissioning and configuration instructions for the specific network model; and 4) communicated the details of the current issue, lessons learned, and the updated commissioning process to staff.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016015918 | CIP-004-6 | R4.1.3 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-004-6 R4.1.3. During an internal review, SPPRE_URE1 discovered that an Active Directory group, consisting of 17 employees, was erroneously granted read-only access to Cyber System Information (CSI) for one Bulk Electric System (BES) storage location. The 17 employees were a subset of a group included on an Excel spreadsheet containing multiple Active Directory groups, some of which should have had access granted and others that should have had access revoked. The administrator responsible for implementing the access changes did not scroll to the far right of the spreadsheet to see instructions that the 17 members of the Active Directory group in question should have all rights to the CSI at this BES storage location revoked. The duration of this instance of noncompliance was five days, from the effective date of the standard through the date SPPRE_URE1 removed CSI electronic storage location access for the 17 employees. The root cause of this instance of noncompliance was human error in failing to implement specific instructions to revoke access to the Active Directory Group. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to restrict electronic access to SPPRE_URE1’s CSI electronic storage location to only those employees with a business need has the potential to affect the reliability of the BPS by providing employees without the appropriate level of personnel risk assessment, training, and security awareness access to protected information, which could be misused and compromise a BES cyber system. Notwithstanding, all 17 employees had received NERC Cyber Security Training in the prior year, which addressed protecting sensitive information, and were also provided quarterly cyber security awareness materials. Additionally, 13 of the 17 employees are authorized for CIP-004 Version 6 CSI access to other storage locations, and 10 of the 17 employees are authorized for CIP-004 Version 6 electronic and unescorted physical access. Furthermore, SPPRE_URE1 attested that they found no evidence that the CSI was accessed nor used to access or affect any BES cyber system. No harm is known to have occurred. SPP RE considered SPPRE_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) removed access of those employees who did not have a business need for the CSI; 2) held a meeting with the System Administrators who are responsible for modifying Access Control Lists for electronic CSI storage locations and explained the intent of the process and reviewed the process for changes to electronic CSI access; and 3) reviewed work orders to verify that no additional errant CSI access remained for anyone who should not have had access to the CSI electronic storage locations. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016416 | CIP-007-6 | R5; Part 5.7 | WECC_URE1 submitted a Self-Report stating that, it had an issue of CIP-007-6 R5.. WECC_URE1 failed to submit a Technical Feasibility Exception (TFE) for devices that were incapable of limiting the number of unsuccessful authentication attempts or generating alerts after a threshold of unsuccessful authentication attempts per CIP-007-6 R5.7. In an effort to ensure compliance with the CIP Version 6 Reliability Standards, WECC_URE1 contracted with an outside consultant to develop WECC_URE1's CIP compliance program. The consultant provided inaccurate information regarding the timeline for submitting TFEs. Initially, WECC_URE1 was told by the consultants that they would be preparing TFEs prior the mandatory and enforceable date for Version 6. As that date approached, the consultants requested to wait until after the exact date to submit TFEs, indicating it was a low priority and that the delay would not present any issues. WECC_URE1 performed a 90-day compliance review of the CIP Program, during which, WECC_URE1 discovered that the TFEs had not been prepared or submitted to WECC. WECC_URE1 The root cause of this issue was WECC_URE1’s reliance on its contractors’ inaccurate knowledge of newly enforceable NERC CIP Standards and Requirements. This issue started when WECC_URE1 should have submitted a TFE and ended when WECC_URE1 submitted the TFE to WECC for approval, for a total of 120 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to submit by the CIP Version 6 enforcement date, a TFE request to WECC for approval on the grounds that strict compliance with CIP-007-6 R5 P5.1 was not technically possible or was precluded by technical limitations. Failure to comply with this Standard through the use of compensating and/or mitigating measures to achieve at least a comparable level of security to the bulk electric system (BES) could result in an attacker gaining access to Critical Assets. Such access could allow an attacker to install malware which could compromise the reliability of the bulk power system (BPS). WECC_URE1 had controls in place to reduce the risk to the BPS. Specifically, WECC_URE1 had malicious code prevention on its systems, which alarms at a central location, and does not permit external access to its system. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) Submitted a TFE request to WECC for approval; and 2) Updated its policy to include a section on its TFE process. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013520 | CIP-007-3a | R9 | WECC_URE2 submitted a Self-Certification stating that it had a possible issue of noncompliance with CIP-007-3a R9. WECC_URE2 failed to document changes resulting from modifications to the system or controls within 30 calendar days of the change being completed, as required by CIP-007 R9. Specifically, WECC_URE2 did not update the inventory list or the network diagram within 30 days of the installation of a single view node. The view node had all of the protections, but the documents were not updated. The root cause of this issue was improper documentation. The duration of the noncompliance was approximately nine months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to update its inventory list and network diagrams with a single one view node workstation. Not updating the inventory and diagrams could potentially result in the entity being unaware of all the devices within the Electronic Security Perimeter (ESP) that need to be protected. However, WECC_URE2 implemented strong compensating controls. This device was used as an operator interface at the control center, but was not a Critical Cyber Asset (CCA). WECC_URE2 maintained this device within a physically restricted facility, requiring authorized access. The device was also logically protected behind the WECC_URE2's firewall, which restricted network access to and from this device. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). | To mitigate this issue, WECC_URE2: 1) completed the Cyber Vulnerability Assessment for the installed hardware and updated the required documentation; 2) updated the policy of account access and permissions for the newly installed hardware; and 3) updated the network diagrams for the Supervisory Control and Data Acquisition (SCADA), including the addition of the newly installed hardware. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014578 | CIP-004-3 | R2 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3 R2. WECC_URE2 failed to provide CIP training to personnel before granting cyber and/or unescorted physical access and to provide this training on an annual basis, as required by CIP-004-3 R2. This issue concerned many individuals. Of the individuals in scope, approximately 50% received logical and physical access to Critical Cyber Assets (CCAs) prior to receiving proper training; approximately 70% were not trained annually for one or more years; and approximately 10% were granted access prior to completing proper training and did not have annual training for one or more years. The root cause of this issue was less than adequate tracking of training information, and maintaining such information in multiple locations. The duration of the noncompliance was approximately three years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to provide CIP training to personnel before granting cyber and/or unescorted physical access to CCAs, and provide such training on an annual basis, as required by CIP-004-3 R2. Without proper training, personnel may not know the proper use of CCAs, the physical and electronic access controls, the proper handling of CCA information, or the action plans to recover or re-establish CCAs. However, WECC_URE2 implemented strong preventive and detective controls to lessen the risk to the reliability of the BPS. Specifically, WECC_URE2 has other personnel, who have the proper CIP training, present in the control center 24 hours-a-day, seven days-a-week, to prevent and detect improper use of CCAs. WECC_URE2 also has logical account controls and antivirus in place to prevent logical access and malware attacks. Additionally, WECC_URE2 is required to perform various cyber awareness trainings. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE2: 1) reviewed and updated its training procedures and tracking list to ensure all individuals with access to the Supervisory Control and Data Acquisition (SCADA) system have completed training requirements; 2) trained authorizing personnel regarding the updated procedures; and 3) performed the updated procedures as a check to ensure all requirements have been met. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014584 | CIP-004-3 | R4 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3 R4. WECC_URE2 failed to maintain accurate access lists of personnel with unescorted physical and/or logical access to CCAs and to update that list within seven days of a change in access rights, per CIP-004 R4.1. WECC_URE2 used multiple access lists to comply with this Standard, which resulted in inconsistencies regarding which individuals had access to CCAs and the type of access those individuals had. Although the lists reflected WECC_URE2’s generally good practice for maintaining changes and access revocations, this issue ultimately involved many individuals. The root cause of this issue was less than adequate tracking of information regarding physical access, as the information was maintained in multiple locations. The duration of the noncompliance was approximately three years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to maintain accurate lists of personnel with unescorted physical access and logical access to CCAs. WECC_URE2 was using multiple lists for one Physical Security Perimeter (PSP), none of which contained the accurate, comprehensive access rights of personnel with physical and/or logical access to CCAs. Failing to maintain accurate lists of personnel with unescorted physical access and/or logical access to CCAs increases the risk of unauthorized access to CCAs. If WECC_URE2 does not have an accurate access list, some personnel may have access who should not have access. However, WECC_URE2 had strong controls in place to prevent and detect unauthorized access to CCAs. WECC_URE2 had policies and processes in place for granting both logical and physical access, which state that certain authorization needs to be obtained before granting access. WECC_URE2 also had processes and procedures in place to address instances in which an individual's access does not work; per these processes and procedures, access cannot be granted on the spot. Nevertheless, had this issue resulted in unauthorized access, WECC_URE2 had other personnel present in the control center 24 hours-a-day, seven days-a-week, to prevent and detect improper use of CCAs. WECC_URE2 also had monitoring and alerting on its devices, which would detect and alert if an individual attempted to disrupt generation. WECC_URE2 uses antivirus and other software to prevent and detect malware. As further compensation, in conjunction with the access processes and procedures in place, WECC_URE2 revoked access rights where needed. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE2: 1) re-evaluated and modified processes and access forms, as needed; 2) trained and reauthorized employees on the new process to establish a baseline; 3) implemented new access list processes and controls; and 4) identified electronic means to aid in generating reports to be used in verification that compliance requirements are being met. This mechanism will be utilized as a reminder to check the lists of any access changes every seven days. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014883 | CIP-007-3a | R5 | WECC_URE2 submitted a Self-Certification stating that it had a possible issue of noncompliance with CIP-007-3a R5. WECC_URE2 failed to secure shared accounts in the event of personnel changes and maintain an audit trail of shared account use, as required in CIP-007 R5.2.3. Specifically, WECC_URE2 failed to implement steps to secure accounts following changes of assignment or termination of personnel for the following device types: servers, network switches, firewall, printers, controllers, workstations, ethernet-to-serial converters, and PSPs. The root cause of this issue was less than adequate audit trails of account use on the devices, which precluded WECC_URE2’s ability to effectively implement procedural controls in accordance with the Standard. The duration of the noncompliance was approximately 18 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to secure shared accounts in the event of personnel changes. Failing to secure shared accounts in the event of personnel changes increases the risk of unauthorized access to the devices and/or the system to which the devices are connected. However, WECC_URE2 had strong controls in place to prevent and detect unauthorized access to its devices and systems. In the event of employee termination, WECC_URE2 disables the individual's Active Directory account, including the individual user account. To access the shared accounts on these devices, the individual would first need to log into their Active Directory account; if the account is disabled, the person cannot access the shared account. Additionally, upon termination, WECC_URE2 obtains the individual's physical access card, which prevents the individual from gaining physical access to the devices. Additionally, WECC_URE2 put an air-gap around its Supervisory Control and Data Acquisition (SCADA) environment, which adds a layer of defense on the system, making it difficult to gain remote access into the devices. WECC_URE2 has other personnel in the control center 24 hours-a-day, seven days-a-week, to prevent and detect improper use of CCAs. WECC_URE2 also uses software to log and alert any issues. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). | To mitigate this issue, WECC_URE2: 1) changed ESP and PACS shared account passwords; 2) configured, installed, and deployed account tracking devices; 3) trained authorizing personnel on the updated account logging procedure; and 4) updated installation procedures to include configuring logging settings for devices for tracking accounts. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014884 | CIP-007-3a | R3 | WECC_URE2 submitted a Self-Certification stating that it had a possible issue of noncompliance with CIP-007-3a R3. WECC_URE2 failed to assess one security patch for applicability within 30 days of the patch release date, per CIP-007-3a R3. This issue concerned a legacy system, which increased the difficulty and necessary timeframe to perform the assessment. The device types that were affected included firewalls, servers, network switches, printers, controllers, and workstations. The root cause of this issue was an inadequate process; WECC_URE2 evaluated security patches for the legacy system every 90 days, which exceeded the timeframe prescribed by the Standard. The duration of the noncompliance was approximately 18 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to assess a security patch within 30 days of the patch becoming available. The patch was for several devices in WECC_URE2’s Supervisory Control and Data Acquisition (SCADA) system. Failing to assess security patches for applicability increases the risk of vulnerabilities on the devices. Specifically, the patch could address a new malicious software (malware) attack or address a vulnerability discovered on the device. However, WECC_URE2 had strong controls in place to prevent and detect vulnerabilities on the devices. Specifically, WECC_URE2 put an air-gap around its SCADA environment, which adds a layer of defense on the system, making it more difficult to gain remote access into the devices. WECC_URE2 also uses two-factor authentication for access into the Physical Security Perimeter (PSP), which would require a malicious person to obtain both factors to gain physical access to the devices. To detect and/or prevent a malware attack, WECC_URE2 uses two antivirus applications and a passive Intrusion Detection System. Additionally, WECC_URE2 uses software to log and alert any issues. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE2: 1) reviewed the patch assessment process and procedures for improvements; 2) revised patch assessment processes and procedures; 3) trained staff on the new assessment processes and procedures; and 4) executed patch process for compliance according to new procedures and work orders. WECC has verified the completion of all mitigation activity.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016016061 | CIP-004-6 | R4.1 | WECC_URE3 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-6 R4 Part 4.1. Specifically, WECC_URE3 reported that during a routine monitoring of its access reports, WECC_URE3’s corporate security discovered that in the process of provisioning non-CIP physical access for an employee, it accidentally provisioned to this employee’s badge unescorted physical access to its computer room Physical Security Perimeter (PSP) at its High Impact BES Cyber System (HIBCS). The root cause of this issue was less than adequate controls in place to ensure that WECC_URE3’s corporate security does not select more than the intended badge reader group while provisioning physical access. WECC determined that this issue began when WECC_URE3’s corporate security provisioned unauthorized unescorted physical access for an employee to its computer room PSP, and ended when the unauthorized unescorted physical access was removed from the employee's badge, for a total of 4 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to authorize, based on need, unescorted physical access to the PSP at its HIBCS, prior to provisioning said access on an employee’s badge. Such failure could allow an unauthorized individual to access systems and intentionally, or unintentionally, interfere with WECC_URE3’s ability to operate, control, or monitor its bulk electric system elements, therefore potentially affecting the reliability of the Bulk Power System (BPS). However, WECC_URE3 had controls in place to eliminate the risk posed from an unauthorized individual having unescorted physical access to the PSP. These controls included two-factor authentication to the HIBCS. Even though the employee had access provisioned on their badge, they were not issued a valid pin code for entry into the PSP. WECC_URE3 has 24 hour-a-day, 7 days-a-week monitoring of its PSP, and a process to monitor its access reports on a regular basis, which lead to timely detection of the issue. No harm is known to have occurred. | To remediate and mitigate this issue, WECC_URE3: a. Removed the unauthorized individuals unescorted physical access; b. Limited the number of employees in corporate security that can provision CIP physical access; and c. Moved the reader groups that contain the badge readers for CIP PSP access points to the bottom of the list of reader groups, in an effort to prevent future reoccurrence of this issue. WECC verified completion of WECC_URE3’s mitigating activities.
2017-02-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015722 | CIP-005-3a | R1.5 | MRO_URE1 stated that it had an issue of CIP-005-3a R1.5 because it did not meet the requirements of CIP-007-3a R6 when MRO_URE1's device management system (DMS) was incorrectly configured following a configuration change on a corporate Cyber Asset, preventing the logging of successful and failed operating system user logins on the DMS. MRO_URE1 considers the DMS to be an Electronic Access, Control and Monitoring System (EACMS). The cause of this issue was that MRO_URE1 did not verify that logging was still occurring after a non-significant configuration change on a Cyber Asset. This issue started when the configuration change on the Cyber Asset prevented logging on the DMS from occurring and ended when the configuration was adjusted to re-enable logging on the DMS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue had a very brief (10 day) duration. The scope of the issue only applied to successful and failed operating system user logins on the DMS; the logging of other security events on the DMS was unaffected. The logging of other Cyber Assets within the Energy Management System (EMS) domain was unaffected. Further, the DMS system was only used in the support of substations, and had no impact on Control Centers. Finally, an unauthorized login to the DMS from outside the Enhanced Security Domain (ESD) would have been observable on the security system logs, which are reviewed at least every 15 days. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE1: 1) reconfigured the DMS to re-enable user account logging; and 2) implemented a system that will monitor, detect, and alert on configuration changes. MRO has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015905 | CIP-007-3a | R3 | RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R3. RFC_URE1's Self-Report consisted of two issues. The first issue related to a security patch, which was released but was not assessed until 59 days after the release. The release date preceded the date on which RFC_URE1 deployed a new vulnerability management solution. Prior to the deployment of the new vulnerability management solution, RFC_URE1's IT staff was responsible for monitoring patch sources. In this case, the IT staff was not aware that the patched program had been installed on the workstations, and therefore, did not identify the patch for assessment. However, after the vulnerability management solution was deployed, the program detected this gap and the patch was then assessed and implemented. The second issue related to four vendor patches for operating system servers that had been identified and assessed by the vulnerability management solution within the required time frame. However, RFC_URE1 was using a separate program to validate the implementation of patches. After the vulnerability management solution-initiated assessment, the vendor security program reported that the patches were implemented. However, a secondary scan by the vulnerability management solution program revealed that the patches were not actually implemented. Upon identification, RFC_URE1 implemented these patches. (RFC_URE1 investigated the cause of the erroneous report. In the end, RFC_URE1 concluded that the best course of action would be to stop using the prior program as its patch validation tool and instead utilize the vulnerability management solution to perform this function.) The root cause of the first instance of noncompliance was the fact that RFC_URE1 relied on a manual process for patch source identification. The root cause of the second instance of noncompliance was the erroneous reports from the prior program. Both of these major contributing factors involve the management practice of asset and configuration management, which includes controlling changes to assets and configuration items. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Failure to implement patches within the required time frame creates a risk that certain assets may be exploited. However, this risk was mitigated by the following factors. Regarding the first issue, RFC_URE1 quickly caught the single missed patch through an internal control and assessed it only 29 days later than required, thus reducing the likelihood that the delay would allow for the vulnerability to otherwise be exploited. Regarding the second issue, RFC_URE1 assessed the four patches within 3 days of availability and had a mitigation plan in place to address the vulnerability 49 days later. Although RFC_URE1 implemented this mitigation plan more than 35 days following the assessment, the mitigation plan was still in place 52 days after the patches were available. Under CIP-007-6, entities can take up to 70 days following the date on which a patch is available to implement the patch. The fact that RFC_URE1 implemented a mitigation plan well within this maximum amount of time allowed for implementation by the current CIP-007-6 minimizes the risk posed by this noncompliance. Moreover, like the first issue, the duration of the second issue is relatively short as a result of RFC_URE1 identifying the issue on its own through internal controls, thus reducing the risk of exploitation. Additionally, ReliabilityFirst also notes that RFC_URE1's layered defense-in-depth strategy provides comprehensive, additional protections. For example, RFC_URE1's firewalls are configured without a default route, which makes it very difficult for malware to contact the command and control servers. Second, RFC_URE1's ESP workstations, servers, and switches are deployed with a certain type of protocol, which ensures that a failure does not result from a single device outage. Furthermore, RFC_URE1 utilizes redundant paths and active failover clusters to resolve single points of failure at the network and firewall level. These additional protections help ensure that any compromise of assets can be isolated from causing widespread issues throughout RFC_URE1's operations. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) completed the assessment and implementation of the patch across all workstations; 2) completed the implementation of the patches across all applicable devices; 3) completed the vulnerability management solution deployment so that the vulnerability scan report includes all applicable CIP assets; 4) will ensure that the additional patches identified are installed and/or otherwise mitigated; 5) modified the change control process and/or related monitoring to ensure that IT Security staff responsible for monitoring patch sources are aware when new software or a new hardware type is introduced into the production CIP environment; and 6) modified the patch validation process to utilize the vulnerability management solution for patch validation instead of the prior program. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015928 | CIP-005-3a | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue with CIP-005-3a R1. While preparing for its upcoming audit, RFC_URE2 discovered a spare server that was routably connected in the primary control center Electronic Security Perimeter (ESP) prior to the certification of RFC_URE2’s new control center. RFC_URE2 failed to identify this spare server as a non-critical Cyber Asset within an ESP as required by CIP-005-3a R1.4. However, this server was afforded other protections as required by CIP-005-3a. Notably, controls put in place after the certification would have identified this issue immediately and prevented the server from being implemented improperly. Upon discovery, RFC_URE2 immediately disconnected the server until it could be moved to the Demilitarized Zone (DMZ). (A DMZ is a physical or logical subnetwork that adds an additional layer of security to an organization’s local area network. An external network can access only what is exposed in the DMZ, while the rest of the organization’s network is firewalled). The root cause of this noncompliance was the fact that a vendor installed the server in the wrong environment prior to the certification of the new control center. At the time that this server was installed, RFC_URE2 lacked the preventive, detective, and corrective controls to address this type of issue. This major contributing factor involves the management practices of external interdependencies, which includes managing external entity performance, and implementation, which includes implementing a system element in a way that satisfies specified requirements, including the Reliability Standards. The duration of the noncompliance was approximately eighteen months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the server did not communicate with systems outside of the ESP, which reduces the risk that it could be used to inject malware into the ESP. Second, the device was protected by layers of security including firewalls, intrusion detection systems, including automated alerting, and physical security controls. These additional internal controls operated as preventative and corrective controls against any devices connected to this particular server. Third, this issue was the result of unique circumstances unlikely to occur again. Specifically, this server was implemented in an environment that only existed prior to the control center certification. Current controls put in place after the certification would automatically alert of any unaccounted for Cyber Assets introduced into any ESP environment. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) immediately disconnected the backup server from the ESP upon discovery; 2) implemented real-time, automated MAC address monitoring and reporting pursuant to which SNMP traps will be generated when a MAC address changes, is added, or deleted on a physical port; 3) disabled by default all physical switch ports; 4) implemented the Cyber Security Test Case Catalog, which procedurally requires the evaluation and implementation of new assets to ensure installation in the appropriate environment; 5) implemented a quarterly Virtual Network Discovery Reconciliation Process, which includes reconciling Cyber Asset lists to network diagrams, then issuing a series of commands to electronically verify that devices are connected properly; and, 6) implemented a quarterly Physical Walkthrough Reconciliation Process, which includes reconciling Cyber Asset lists to a physical inspection of what devices are connected.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015803 | CIP-003-3 | R5 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. During Version 5 transition activities for Information Protection, RFC_URE3 reviewed all CIP Critical Asset Information (CCAI) folders within RFC_URE3’s Document Management System for compliance with CIP-003-3 R5. RFC_URE3 determined that an annual review of access groups assigned to certain folders that contain CCAI was not completed. This annual review control had been previously implemented, but did not transition when RFC_URE3 moved from its previous Document Management System product to another. As a result, RFC_URE3 discovered that two groups (totaling 17 people) were granted access to five CCAI folders without going through the proper process for such authorization. And, because RFC_URE3 did not conduct an annual review, RFC_URE3 did not timely discover the access issue. Each of the 17 individuals required access to the CCAI folders at issue; however, the individuals were granted access in a manner that was inconsistent with RFC_URE3’s procedure for granting such access. Upon discovery, RFC_URE3 removed access for the individuals and submitted appropriate authorization requests. RFC_URE3 ultimately granted each of these 17 individuals access using the correct Information Protection procedure. RFC_URE3 also reinstated the annual review control. The CCAI folders to which the individuals were granted access contained Standard Operating Procedures utilized by RFC_URE3’s IT Operations center for diagnosing and troubleshooting common problems with CIP-scoped systems (e.g., restarting system components, unlocking user accounts, etc.). The root cause of the issue was a combination of a failure to follow proper procedures for granting access, a lack of sufficient controls regarding authority to grant access, and an error in not updating its procedures when transitioning to a new document system. Additionally, improved information management processes may have prevented the noncompliance by having more effective controls around permitting access to certain information. The duration of the noncompliance was approximately two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The seventeen individuals at issue were trusted individuals with proper NERC CIP qualifications. These individuals should have had access to the folders, and did properly have access to other similar CCAI folders, thus reducing the risk that they would have used the information in a way that would compromise the BPS. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) removed personnel who were not properly approved to access the information within the relevant folders and then submitted proper authorization requests for the individuals; 2) restricted ability to grant access to certain folders/documents to DMS Administrators only, to prevent recurrence; 3) developed and tested a new control that automatically removes personnel and groups from folders or documents they are not authorized to access via Access Manager (application used to manage all access requests), also to prevent recurrence; and 4) implemented a control to send a notification when unauthorized individuals are removed.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015836 | CIP-007-3a | R2 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R2. Seven Physical Access Controls System (PACS) door controllers were promoted to CIP cyber assets and classified as PACS. For four of the door controllers, RFC_URE3 completed port scans to identify a list of open ports, but failed to document the operational justification for the open ports. For the remaining three door controllers, RFC_URE3 failed to complete port scans to identify open ports prior to re-classifying the assets as CIP and, as a result, there was no operational justification documented as required by R2.1. The root cause was that there was confusion as to which of two groups (Physical Security or Information Technology) owned the process for documenting the business justification for open ports. As a result, each group assumed it was the other group’s responsibility to document this justification. This issue was discovered during the Cyber Vulnerability Assessment process. Once discovered, RFC_URE3 confirmed that the ports that were currently open were necessary for the operation or monitoring of the assets. A contributing cause was ineffective workforce management practices in that RFC_URE3 failed to train and communicate to its groups regarding ownership of the process for documenting justification of open ports. The duration of the noncompliance was approximately two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This was a documentation issue as all of the enabled ports on all seven door controllers were necessary for the operation or monitoring of the door controllers. Additionally, even if a bad actor obtained access to the door controllers as a result of enabled ports, they would have needed additional access privileges in order to actually open the door. Thus, potential harm from this noncompliance is minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) developed a list of approved ports and services by scanning the open ports on the cyber assets and compared the results against vendor supplied documentation; 2) updated the master ports and services list by adding a new tab to the master ports and services document to capture the relevant information; and 3) updated the test procedures document by adding a port scan to the centralized test procedure document.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015206 | CIP-006-3c | R2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had four minimal risk instances of noncompliance with CIP-006-3c R2.2 for not affording the protective measures specified in CIP-003-3a R6 and CIP-007-3 R1.1, R3.1, and R3.2 to its Physical Access Control System (PACS). CIP-003-3a R6 – Instance No. 1: CIP-003-3a R6 (as made applicable by CIP-006-3c R2.2) requires SPPRE_URE1 to “establish and document a process of change control and configuration management for adding . . . [PACS] . . . software . . . .” SPPRE_URE1 had a documented Change Control Process for adding software to PACS devices; however, software was installed on the PACS badging workstation without adherence to the process. Specifically, a request ticket had not been submitted and approval had not been obtained prior to the installation of the software. Although the SPPRE_URE1 employee who installed the software was authorized to access and utilize the badging workstation, he was not one of the employees identified in the process as being authorized to install software to PACS devices. The duration of this instance of noncompliance was one day, the date the software was installed on the PACS badging workstation without adherence to SPPRE_URE1’s documented Change Control Process. CIP-007-3a R1.1 – Instance No. 2: CIP-007-3a R1.1 (as made applicable by CIP-006-3c R2.2) requires SPPRE_URE1 to “maintain cyber security procedures in a manner that minimizes adverse effects on the production system or its operation.” Because the software had been installed without adherence to SPPRE_URE1’s Change Control Process (Instance No. 1), the software had been installed on the PACs badging workstation while in the production environment without first testing the software to ensure that it would not adversely affect existing cyber security controls. The duration of this instance of noncompliance was 490 days, from the date the software was installed on the PACS badging workstation until the software was uninstalled. CIP-007-3a R3.1 – Instance No. 3: CIP-007-3a R3.1 (as made applicable by CIP-006-3c R2.2) requires SPPRE_URE1 to “document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades.” Because the software had been installed without adherence to SPPRE_URE1’s Change Control Process (Instance No. 1), personnel responsible for installing applicable patch updates were unaware to apply the software patch updates to the PACS badging workstation. Once the software was installed on the PACS badging workstation, SPPRE_URE1 was required to assess security patches and security upgrades for the software within 30 calendar days. Twenty-five patches were never assessed for applicability. The 25 applicable patches included 23 software security patches and two software non-security patches. The duration of this instance of noncompliance was 460 days, from the date the earliest released patch was required to have been assessed for applicability until the software was uninstalled from the PACS badging workstation. CIP-007-3a R3.2 – Instance No. 4: CIP-007-3a R3.2 (as made applicable by CIP-006-3c R2.2) requires SPPRE_URE1 to “document the implementation of security patches” and “[i]n any case where the patch is not installed, [SPPRE_URE1] shall document compensating measure(s) applied to mitigate risk exposure.” Two of the 25 applicable software patches that had not been assessed for applicability (Instance No. 3) were non-security patches and thus not required to have been installed on the PACS badging workstation. The remaining 23 security patches were not installed within one year after the expiration of SPPRE_URE1’s 30-day patch assessment period, and there were no documented compensating measures applied to mitigate risk exposure for any of these patches as required by R3.2. The duration of this instance of noncompliance was 460 days, from the date SPPRE_URE1 was required to have either installed the earliest released patch or documented compensating measures to mitigate risk exposure, until the software was uninstalled from the PACS badging workstation. The root cause of these four instances of noncompliance was a combination of personnel not following SPPRE_URE1’s Change Control Process and lack of internal controls, i.e., configuring user account rights of the badging workstation to allow only authorized personnel the ability to install software, to ensure full adherence to SPPRE_URE1’s Change Control Process. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R2.2 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur. Notwithstanding, the only affected PACS was the badging workstation, which is outside SPPRE_URE1’s Electronic Security Perimeter (ESP). SPPRE_URE1 attested that the sole purpose of the badging workstation is to prepare badges. Therefore, any potential vulnerability that could have been introduced to the badging workstation would have been isolated from Critical Cyber Assets located inside the ESP. Additionally, the badging workstation is located inside SPPRE_URE1’s Physical Security Perimeter; thus, access to the badging workstation was limited to only those individuals with authorized physical access rights. No harm is known to have occurred. SPP RE considered SPPRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) uninstalled the software that had been installed on the PACS badging workstation; and 2) configured user account rights of the PACS badging workstation to allow only authorized personnel the ability to install software. SPP RE has verified the completion of all mitigation activity.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017016728 | CIP-006-6 | R1; P1.3 | TRE_URE1 submitted a self-log stating that it had an issue with CIP-006-6, P1.3. Specifically, TRE_URE1 failed to utilize two or more different physical access controls to collectively allow unescorted physical access into Physical Security Perimeters (PSPs) to only those individuals who have authorized unescorted physical access. A TRE_URE1 security guard escorted four TRE_URE1 contractors into a PSP to perform certain planned maintenance activities. Neither the TRE_URE1 security guard nor the TRE_URE1 contractors had authorized unescorted access into this particular TRE_URE1 PSP. When the TRE_URE1 security guard initially attempted to enter the PSP in question using his ID badge, TRE_URE1’s physical access control system properly denied access and issued an invalid access alert. However, because the lock on the PSP door did not properly engage, the TRE_URE1 security guard was able to open the door and escort the TRE_URE1 contractors into the PSP. Subsequently, TRE_URE1 performed inspections on the lock at issue. TRE_URE1 subsequently replaced the PSP door lock. The root cause of this issue was an unexpected equipment failure. Specifically, the lock used on the PSP door at issue failed to fully lock when closed. This failure allowed individuals to bypass the access controls in place to access the PSP. The duration of the noncompliance was approximately 11 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following six reasons. First, the specific PSP at issue is within another TRE_URE1 PSP that has manned security and security monitoring systems in place. As such, any intruder would have to pass through multiple physical access controls before reaching the specific PSP at issue. Second, TRE_URE1 deploys cameras both outside and inside the specific PSP at issue that could detect any malicious activities within the PSP. Third, although the TRE_URE1 security guard was not authorized to have unescorted physical access to the specific PSP at issue, the TRE_URE1 security guard had authorized access to other TRE_URE1 PSPs, had successfully completed a background check, and had received cyber security training. Fourth, the TRE_URE1 security guard escorted the four TRE_URE1 contractors within the PSP at issue at all times. Fifth, the four contractors were performing planned maintenance activities and logged their entry and exit into all TRE_URE1 PSPs in the proper manner. Finally, TRE_URE1 did not identify any other instances in which the specific PSP door locks failed to operate during the duration of the issue. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) inspected the door and replaced the lock on the inner PSP door; 2) implemented a system of email alerts for access alarms, including invalid access attempts, to multiple TRE_URE1 operations personnel and management, as well as to a shared-duty cell phone; 3) provided memos to relevant TRE_URE1 personnel with authorized access to TRE_URE1 PSPs regarding TRE_URE1’s visitor escort and physical security incident response policies; and 4) posted signs to improve visibility of the PSP boundary between the inner and outer PSPs. Texas RE verified completion of TRE_URE1's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017016729 | CIP-006-6 | R2; P2.1 | TRE_URE1 submitted a self-log stating that it had an issue with CIP-006-6, P2.1. Specifically, TRE_URE1 failed to require continuous escorted access of visitors within each Physical Security Perimeter (PSP) as required by its visitor control program. A TRE_URE1 security guard escorted four TRE_URE1 contractors into a PSP to perform certain planned maintenance activities. Neither the TRE_URE1 security guard nor the TRE_URE1 contractors had authorized unescorted access into this particular TRE_URE1 PSP. When the TRE_URE1 security guard initially attempted to enter the PSP in question using his ID badge, TRE_URE1’s physical access control system properly denied access and issued an invalid access alert. However, because the lock on the PSP door did not properly engage, the TRE_URE1 security guard was able to open the door and escort the TRE_URE1 contractors into the PSP. The TRE_URE1 security guard and contractors remained in the PSP for approximately one hour, at which time a TRE_URE1 employee with authorized access discovered the security guard and contractors working in the PSP and began providing the appropriate escort. Approximately 17 minutes later, TRE_URE1 personnel escorted the TRE_URE1 security guard and four contractors out of the PSP at issue upon completion of the maintenance activities. The root cause of this issue was an inadequate process to ensure TRE_URE1 personnel were aware of all applicable PSP boundaries and their associated access rights. In particular, the TRE_URE1 security guard in question possessed authorized access rights to the exterior PSP outside the specific PSP at issue. However, the TRE_URE1 security guard did not understand that entry into the interior PSP required distinct access rights and the boundary between the two PSPs was not clearly delineated. In addition, the unexpected equipment condition of the lock not working allowed the TRE_URE1 security guard and TRE_URE1 contractors to bypass the interior PSP’s other physical access controls in place and enter the PSP. The duration of the noncompliance was approximately one hour. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following five reasons. First, although the TRE_URE1 security guard was not authorized to have unescorted physical access to the specific PSP at issue, the TRE_URE1 security guard had authorized access to other TRE_URE1 PSPs, had successfully completed a background check, and had received cyber security training. Second, the TRE_URE1 security guard escorted the four TRE_URE1 contractors within the PSP at issue at all times. Third, the specific PSP at issue is within another TRE_URE1 PSP that has manned security and security monitoring systems in place, including cameras located outside and inside the specific PSP at issue. As such, TRE_URE1 security personnel could have detected any malicious activity within the specific PSP and quickly responded. Fourth, the four contractors were performing planned maintenance activities and logged their entry and exit into all TRE_URE1 PSPs in the proper manner. Finally, Texas RE confirmed that no other entry was made to the PSP during the duration of the issue. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) provided an escort that was authorized for unescorted physical access to accompany the four visitors from the inner PSP; 2) posted signs to improve visibility of the PSP boundary between the inner and outer PSPs; 3) provided memos to relevant TRE_URE1 personnel with authorized access to TRE_URE1 PSPs regarding TRE_URE1’s visitor escort and physical security incident response policies; 4) inspected the door and replaced the lock on the inner PSP door; and 5) implemented a system of email alerts for access alarms, including invalid access attempts, to multiple TRE_URE1 operations personnel and management, as well as to a shared-duty cell phone. Texas RE verified completion of TRE_URE1's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016016203 | CIP-007-6 | R2; P2.2 | TRE_URE2 submitted a self-log stating that it had an issue with CIP-007-6 R2. Specifically, TRE_URE2 did not perform an evaluation of numerous security patches for applicability to its High and/or Medium Impact BES Cyber Systems and their associated Electronic Access Control or Monitoring Systems (EACMS), Physical Access Control Systems (PACS), and Protected Cyber Assets (PCAs) within 35 days of the last evaluation of those cyber security patches from the applicable monitored sources identified in its patch management process. TRE_URE2’s remote security scanning tool experienced an issue which caused it to stop scanning for and downloading patches from a single monitored source identified in TRE_URE2’s patch management process. As a result, TRE_URE2 failed to identify and assess multiple security patches by CIP-006-6, P2.2’s required initial performance date. In addition, the same monitored patch source released additional patches. As such, TRE_URE2 should have performed the required evaluation of these patches within 35 days, but again did not do so. TRE_URE2 discovered the issue during a review of reports from its configuration management tool and performed the required evaluation of the patches in question. The root cause of this noncompliance was that TRE_URE2 did not have a well-defined process to detect and address issues with its remote security scanning tool. In particular, TRE_URE2 lacked a process to actively monitor its remote security scanning system to ensure its was identifying all patches from TRE_URE2’s monitored source list, as well as a process to verify that the patches requiring evaluations have been properly identified by the remote security scanning tool. The duration of the noncompliance was approximately 20 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following five factors. First, duration of the issue was short, lasting only 20 days. Because of the short duration of the evaluation issue, TRE_URE2 ultimately was able to install all applicable patches within 35 days of the date upon which it should have completed its evaluation of the patches in question. Second, the issue affected only one of TRE_URE2’s monitored patch sources and TRE_URE2 continued to evaluate and install patches from all other monitored sources throughout the duration of the issue. Third, the BES Cyber Systems associated with the patches at issue were located within a segregated network with no direct external access to or from the Internet. Fourth, TRE_URE2 uses an intrusion protection system that protects all critical environments including the ones at issue here, as well as security zones defined by access privilege/application data communication to segregate systems and firewalls. Finally, TRE_URE2 monitors all of the devices at issue on a continuous basis for unauthorized intrusions and configuration changes and did not detect any unauthorized activity in connection with these devices during the duration of the patching issue. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) performed an evaluation of the patches missed during the period in question; 2) installed all applicable patches; 3) deployed systems to monitor its remote security scanning tool to detect issues and provide alerts to TRE_URE2 personnel; 4) updated its Patch Management Process to require TRE_URE2 personnel to verify that remote security scanning tool has identified applicable patches prior to performing patch evaluations; and 5) provided the updated Patch Management Process to affected TRE_URE2 personnel. Texas RE verified completion of TRE_URE2's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2016016181 | CIP-006-6 | R1; P1.1 | TRE_URE3 submitted a Self-Report stating that it had an issue with CIP-006-6 R1. Specifically, TRE_URE3 did not implement its documented physical security plan as required under CIP-006-6, P1.2 to utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter (PSP) to only those individuals who have authorized unescorted physical access at four substations. TRE_URE3’s documented physical security plan states that TRE_URE3 will use either access card readers or PIN pads to control physical access to its substations. However, during a review of its physical access controls at its substation locations, TRE_URE3 determined that the access card reader and PIN pads at two substations were not operational. Instead, TRE_URE3 personnel used mechanical locks to control physical access at the two applicable substation sites. Subsequently, TRE_URE3 determined that two additional substations had functional mechanical locks that could permit individuals to bypass the physical access controls designated in its physical security plan. As such, TRE_URE3 did not implement the physical access controls set forth in its physical security plan to allow unescorted physical access into four substation PSPs to only those individuals who have authorized unescorted physical access to them. The root cause of this issue was that TRE_URE3 did not have a sufficient process in place to ensure the correct implementation of its physical security plan. In particular, TRE_URE3 failed to initially verify that all physical access controls described in its physical security plan were operational and corresponded to the actual physical access controls in place at its substations when these substations became subject to new CIP physical security requirements. Texas RE determined the issue duration to be less than eight months. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the issue was documentary in nature. In particular, TRE_URE3 possessed at least one type of physical access control in the form of a mechanical locks at all four substations for the duration of the issue. However, TRE_URE3 did not document this form of physical access control in its physical security plan. Second, all TRE_URE3 personnel physically accessing the four substations during the duration of this issue possessed the appropriate physical access authorizations or were later granted physical access authorizations. Third, TRE_URE3 employs door alarms that would have triggered an alert on the SCADA displays to notify TRE_URE3 operators of any unauthorized entry into a substation PSP using the mechanical lock and key system. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) revised its physical security plan to designate mechanical locks as a physical access control to be used only in circumstances in which TRE_URE3’s other physical access controls were not operational; 2) installed a functional card reader at the two substations where such devices were not operational; 3) verified that it had installed appropriate physical access controls at all other TRE_URE3 substations and such physical access controls were operational; 4) provided training to TRE_URE3 personnel regarding the requirement in TRE_URE3’s physical security plan to use TRE_URE3’s badge access to enter all TRE_URE3 PSPs except in emergency circumstances; and 5) provided additional training materials to TRE_URE3 operations and construction staff, vendors, and contractors on applicable physical access controls, including visitor access and visitor logging requirements. Texas RE verified completion of TRE_URE3's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2016016182 | CIP-006-6 | R2; P2.2 | TRE_URE3 submitted a Self-Report stating that it had an issue with CIP-006-6 R2. Specifically, TRE_URE3 did not implement its documented visitor control program as required under CIP-006-6, P2.2 to manually or automatically log visitor entries into and out of a Physical Security Perimeter (PSP), including the date and time of initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor on four occasions at a single substation. TRE_URE3’s visitor control program requires the use of a visitor access log to document the entry and exit of visitors for each PSP. The TRE_URE3 visitor logs at each PSP in turn require entry of, among other things, the visitor’s name and the TRE_URE3 staff person being visited and/or reason for the visit. Two visitors signed into the TRE_URE3 visitor access log at a TRE_URE3 substation, but inadvertently listed another visitor instead of their actual TRE_URE3 contact and escort as required. On two subsequent occasions, visitors failed to provide their names as required in the TRE_URE3 visitor access log at the same substation upon their escorted entry into the substation’s PSP. Instead, these two visitors both provided their TRE_URE3 employee escort’s name in lieu of their own names. The root cause of this issue was human performance error. TRE_URE3 provided logs at the single substation at issue and the visitors, and TRE_URE3 personnel understood the requirement to log entry into the substation PSP. However, the visitors and TRE_URE3 personnel escorts did not properly complete the logs as required. The duration of the noncompliance was approximately two days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, TRE_URE3 personnel escorted all visitors in question while the visitors were inside the TRE_URE3 substation PSP at issue. Second, TRE_URE3 continuously monitors the TRE_URE3 substation in question using video displays and surveillance. As such, TRE_URE3 could have detected and recorded any unauthorized or unescorted entry into the TRE_URE3 substation. Third, TRE_URE3 employs door alarms that would have triggered an alert on TRE_URE3’s SCADA displays to notify TRE_URE3 operators of any unauthorized entry into a substation PSP. Finally, TRE_URE3 reviewed all other TRE_URE3 substation logs and determined that they were properly completed. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) reviewed all other TRE_URE3 substation visitor log books to confirm that there were no other incomplete logging instances; 2) provided training to TRE_URE3 personnel regarding the requirement to fully complete all visitor logs upon each entry into a TRE_URE3 PSP; and 3) provided additional training materials to TRE_URE3 operations and construction staff, vendors, and contractors on visitor access and visitor logging requirements. Texas RE verified completion of TRE_URE3's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2017016746 | CIP-004-6 | R4; P4.1.2 | TRE_URE3 self-reported a possible noncompliance with CIP-006-6 R2. After reviewing the issue, Texas RE determined that the noncompliance described in TRE_URE3's Self-Report was also a possible violation of CIP-004-6, P4.1 for TRE_URE3. Specifically, TRE_URE3 failed to implement its documented access management process to authorize unescorted physical access into a Physical Security Perimeter (PSP) based on need. On four occasions, three TRE_URE3 contractors entered three different TRE_URE3 substation Physical Security Perimeters (PSP) to perform certain planned maintenance activities. At the time the three contractors entered the TRE_URE3 PSPs at issue, TRE_URE3 had not authorized these contractors to have unescorted physical access into these PSPs. The root cause is that TRE_URE3 did not possess adequate internal controls to ensure that only individuals with authorized unescorted physical access to TRE_URE3’s substation PSPs could enter those PSPs. In particular, TRE_URE3 had previously distributed both PIN access codes and keys to the contractors at issue and did not take sufficient steps to disable these forms of access once the substations at issue became subject to physical access control requirements. The duration of the noncompliance was approximately 29 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, in all four instances, the contractors contacted TRE_URE3 System Operators to alert TRE_URE3 they were accessing the PSP. Second, the contractors manually logged their names, as well as entry and exit times during the four instances at issue. Third, TRE_URE3 subsequently granted unescorted physical access rights to the PSPs at issue to all three contractors. Finally, TRE_URE3 employs door alarms that would have triggered alerts on TRE_URE3’s SCADA displays to notify TRE_URE3 Operators of any other unauthorized entry into a substation PSP. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) authorized the three contractors to have unescorted physical access to the substation PSPs at issue; 2) changed all PIN numbers and locks at TRE_URE3 substations; 3) revised its physical security plan to clarify that PINs and mechanical locks may only be used to provide access to substation PSPs in emergency situations or when other physical access controls have failed; 4) provided additional training materials to TRE_URE3 operations and construction staff, vendors, and contractors on applicable physical access controls, including visitor access and visitor logging requirements; and 5) established a process to provide memoranda concerning physical access policies to all individuals receiving keys to the mechanical locks. Texas RE verified completion of TRE_URE3's mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015809 | CIP-006-3c | R1 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue of CIP-006-3c R1.6. In the first instance, two WECC_URE1 employees failed to continuously escort three contractors within the Physical Security Perimeter (PSP) during contracted work. The two employee escorts left the contractors unescorted in the PSP and went to the break room. Once the on-duty security officer discovered that the two employee escorts were not with the visitors, he notified the manager of IT operations, who retrieved the visitors and escorted them to the security officer's desk in the lobby. The contractors stayed in the lobby with the security officer until an escort could remain with them for the duration of their work. In the second instance, a security officer with unescorted physical access privileges escorted a construction crew into the PSP. During this timeframe, the first security officer needed to leave to cover another shift, so he swiped his badge to let a second security officer into the PSP; however, the second security officer did not have authorized unescorted physical access privileges pursuant to CIP-004-3 R4. The second security officer escorted the construction crew (even though he was not an authorized escort) until a third security officer was called to let the second security officer and the construction crew out of the PSP. Based on a review of the sign-in logs from that timeframe, the second security officer never signed in on the visitor log; therefore, there was no log to document his entry or exit per CIP-006-3c R1.6.1. The first instance started when WECC_URE1 failed to continuously escort two contractors within the PSP and ended, when WECC_URE1 removed the two contractors from the PSP, for a total of 45 minutes of noncompliance. The second instance started, when WECC_URE1 failed to use an authorized escort to escort a construction crew within the PSP and ended when WECC_URE1 removed the construction crew from the PSP, for a total of 75 minutes of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to log, monitor and/or escort visitors with unauthorized physical access to and from its PSPs per CIP-006-3c R1.6.2, and failed to log the entry and exit of visitors per CIP-006-3c R1.6.1.Specifically, an authorized escort did not monitor personnel per the visitor escort requirements and secondly, a security officer accessed the PSP and acted as an authorized escort, but did not have authorization to either access the PSP or perform the role of an authorized escort, and failed to log their entry and exit as a visitor. Unauthorized personnel pose a risk to the operation of the Bulk Electric System (BES) due to their ability to physically access and make changes, such as power cycling equipment, breaching access points, and disrupting operations at PSPs, which has a potential of causing harm to the BES. WECC_URE1 implemented controls to eliminate potential unauthorized physical access occurrences. This included administrative, technical, and physical controls, such as electronic badge card reader systems to control physical access to the PSPs; personnel risk assessments (PRA), for both role separation and function; and authentication systems to control who can access systems. WECC_ URE1 implemented detective controls which consisted of 24 x 7 security monitoring of the PSPs, to include video monitoring. Administrative controls include policies and procedures restricting access to only authorized personnel as well as the regular review of the list of personnel with electronic and unescorted physical access to Critical Cyber Assets and their specific access privileges. WECC_URE1 did not experience any physical security events or incidents, anomalous system events or incidents during the duration of the unauthorized access to the PSPs. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. No harm is known to have occurred. WECC considered WECC_URE1's CIP-006-R1 compliance history in determining the disposition track. WECC_URE1 had no prior noncompliance history with CIP-006 R1. | To mitigate this issue, WECC_URE1: 1) Removed the two contractors from the PSP; 2) Removed the construction crew from the PSP; 3) Required all security officers working at WECC_URE1 to go through the CIP-004 authorization, training, and PRA requirement to have CIP unescorted physical access; 4) Created and posted at all PSP sign-in areas, written guidance on escort procedures for escorts and visitors; 5) Required all escorts and visitors entering a PSP to review the guidance and sign or initial the visitor log to acknowledge they have read and understand the procedures; 6) Performed a documented re-training for all security officers which stressed the importance, and rules, around escorting; and 7) Collaborated with the other departments on the feasibility of adding additional controls to better specify whether additional CIP requirements apply during contracted work. WECC verified completion of the mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016015818 | CIP-004-3a | R3 | WECC_URE2 submitted a Self-Report to WECC stating it had an issue of CIP-004-3a R3. WECC_URE2 reported that Personnel Risk Assessments (PRAs) for approximately 40 individuals were not updated at least every seven years after the initial PRA or for cause per CIP-004-3a R3.2. WECC_URE2 discovered this issue during a review of a list of employees and contractors with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). A subsequent investigation confirmed that 20 individuals were past due, with the oldest expired PRA being 20 days past due from the initial PRA date. Several additional individuals had PRAs that were scheduled to expire soon. WECC_URE2 was not able to update, within seven years, 20 of those additional individuals, for 40 expired PRAs. WECC_URE2 reported that 19 of the 40 individuals in scope utilized their CIP access during the time PRAs were expired. The process in place at the time required that a specific department (Dept 1) send a list to another department (Dept 2) of the PRA renewals that needed to be performed. Dept 2 would then initiate and track the renewals, and Dept 1when it was time to review the PRA results report. Dept 1 had no visibility into the status of the renewals; therefore, could not effectively oversee the progress. Dept 1 sent a list of all PRAs expiring to Dept 2. A subset of that list was again sent from Dept 1 to Dept 2 to check the status of PRAs for WECC_URE2 employees that had access to several substations owned by another entity, as part of that entity’s quarterly review. Dept 2 mistook the second list as the only one that needed PRAs renewed. The root cause of this issue was ineffective processes resulting in a misunderstanding between WECC_URE2 business units. This issue started when the first of the 40 PRAs should have been renewed, and ended when WECC_URE2 renewed the last of the 40 PRAs that had expired, for approximately 30 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to update 40 PRAs at least every seven years after the initial PRA was performed. These actions could potentially result in improperly vetting the identity and criminal history of personnel with access to or managing CCAs, which could result in malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the Bulk Electric System (BES), which could negatively impact the BES. WECC_URE2 had controls in place to reduce the risk to the BES. Specifically, the 40 individuals in scope had initial PRAs performed and had completed CIP training. WECC_URE2 had implemented strong passwords to prevent an individual from gaining unauthorized logical access to CCAs within the PSPs. Additionally, the CCAs within the PSPs had antivirus and malware prevention tools installed which would reduce the risk of malicious software from being introduced onto the CCAs. PSP access points were monitored 24 hours-a-day, seven days-a-week and alarmed to notify security of unauthorized physical access. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC considered WECC_URE2's CIP-004-3a R3 compliance history in determining the disposition track. WECC_URE2 had no prior noncompliance with CIP-004-3a R3. | To mitigate this issue, WECC_URE2: 1) Completed PRAs on the 40 individuals in scope; 2) Modified and clearly documented the process to reflect that employee services is responsible for identifying which PRAs need to be renewed, and to initiate that renewal; and 3) Implemented weekly and quarterly PRA reports that are automatically generated and sent to the appropriate departments. WECC verified completion of the mitigating activities.
2017-01-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015512 | CIP-007-3a | R6.1 | MRO_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. Specifically, local user account failed login attempts were not logged on 23 servers that were Critical Cyber Assets (CCAs). This was due to incorrect settings on the servers that did not log failed login attempts for the local user accounts. During MRO's review of this issue, it was determined that CIP-007-3a R6.1 was the most applicable Requirement for this issue. The cause of this issue was that MRO_URE1 failed to test or verify that local user logging controls related to security event monitoring were functioning properly, and MRO_URE1 limited testing of failed logins to domain accounts. The issue began when the first server was deployed, and ended when MRO_URE1 corrected the settings on the servers to log failed login attempts from local user accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 does not allow Interactive Remote Access (IRA) into either its Primary Control Center or Back-Up Control Center's Electronic Security Perimeter (ESP). Additionally, dial-up access to the ESP firewall is not enabled, and external interactive access to the firewalls is not permitted. This restricted electronic access is a strong and uncommon control for a registered entity of MRO_URE1's size. Further, the issue was specific only to local accounts for MRO_URE1's servers running a particular operating system, and failed login attempts for its servers running other operating systems were still being logged. Moreover, the were located in a functioning Physical Security Perimeter (PSP), and the risk of exposure was limited to approximately 20 individuals who had access to the server room. These individuals are presumed to have had up-to-date Personnel Risk Assessments (PRAs), due to the recent Compliance Audit that identified no findings related to CIP-004-3 R3. Finally, the local accounts were subject to additional controls, such as the passwords being changed every 90 days, local account lockout thresholds were enabled, and the local guest account was disabled. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-007-3a R5. | To mitigate this issue, MRO_URE1: 1) adjusted the settings on the servers to log the local user account failed login attempts; and 2) to prevent reoccurrence, implemented new change controls as part of its CIP Version 5 implementation. MRO_URE1 stated that mitigating activities were complete.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016570 | CIP-007-3a | R5.1.1 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-007-3a R5.1.1. A request for access to a CIP password safe was provisioned manually, and the provisioner inadvertently granted the user 'Admin' level access to the CIP password safe instead of 'Modify' access as requested. ‘Admin’ level access to a CIP password safe allows the user to create/delete/rename/update password files, in addition to other permissions not allowed by the ‘Modify’ access level. ‘Modify’ access to a CIP password safe allows the user to update existing password files, but does not allow the user to create/delete/rename password files. Access to a single CIP password safe is controlled by four groups, one each for 'List', 'Modify', 'Read Only', or 'Admin' level access to the safe. Regarding the root cause, in this instance, the name of the safe itself contained the word 'Admin', and so the provisioner assumed the user needed the 'Admin' or highest level of access to the safe, when in fact they needed only 'Modify'. This mis-provisioned access was detected by the Daily Reporting process the following mornings (Saturday and Sunday). The access was corrected by a member of the provisioner's team on Monday morning. The duration of the noncompliance was approximately 3 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the only capability the person got that he should not have had was the ability to delete password files in the vault. Had that happened, it could have temporarily disrupted Transmission operators only if they had forgotten their password and needed to access the vault for retrieval. Second, the person did not know excessive access had been granted, thus reducing the likelihood that he would have used it. Third, the issue was timely detected by the daily automated exception report, which reduced the duration of the noncompliance. As a result, the likelihood of compromise to RFC_URE1's system as a result of this access grant is minimal. Also, RFC_URE1 reviewed the access logs and determined the user did not use the excess access. Thus, no harm is known to have occurred. | To mitigate this issue, RFC_URE1: Upgraded the application, and with that upgrade, all membership in RFC_URE1's directory groups, including groups with access to CIP Password Safes, is done by 'auto-provisioning' and is no longer manually provisioned. The Roles deployed are much more explicit, distinguishing the ‘Modify’ level of access from the ‘Admin’ level access.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016571 | CIP-007-3a | R5.3.3 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-007-3a R5.3.3. An IT Admin granted an IT Data Storage Server Admin (the user) ‘Root’ and Personal Login access to the server without submitting a request through the electronic access request system to formally obtain and document the approvals for the access. The user was a Data Storage Server Administrator. When asked about the incident, the user explained that an emergency event required him to be granted the access because there was a risk of backup failure on the two servers at issue and RFC_URE1 could potentially lose data if something would have happened to those servers. Regarding the root cause, on that day, the Unix Admin verbally granted the user "Root" password/access, but, due to human error, did not record the granting of access as he should have done. The user then used his personal login id to log into the servers, and then successfully switched to the ‘Root’ account on the server to do the backup/restore activities. The Daily Exception report identified this discrepancy (a new account with no matching request and approvals). The next day, the user formally requested and was approved for this access through the electronic access request system. The duration of the noncompliance was approximately two days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the user had both a completed background check and NERC CIP training at the time the access was granted. The individual is a member of the appropriate IT infrastructure group that needs this level of access to the servers. Second, RFC_URE1 detected the issue through a daily exception report, reducing the likelihood that this issue would be exploited. As a result, the likelihood of compromise to RFC_URE1's system as a result of this issue is minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) confirmed that new accounts on the servers cannot be requested through the OUR (Online User Registration) Application, an older electronic access request system which is no longer being used to request NERC CIP access, but is still in use for Non-NERC CIP electronic access requests; 2) added a message banner to the login screen for the servers indicating that new accounts should not be created without a fully approved request; and 3) added selections into the electronic access request system for requesting access to the Root password manager application. The Root password would only be accessible online, and for authorized users only. The electronic access request system application ensures that only users with cleared background check and training can request and keep this access.
2017-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016202 | CIP-006-6 | R1; P1.4; P1.6 | TRE_URE1 submitted a self-log stating that it had an issue with CIP-006-6 R1. Specifically, TRE_URE1 did not Monitor for unauthorized physical access through physical access points into its Physical Security Perimeters (PSPs) and Monitor each Physical Access Control System (PACS) for unauthorized access as required under CIP-006-6, P1.4 and 1.6, respectively, for approximately two hours. TRE_URE1 information technology (IT) personnel began certain maintenance activities on the TRE_URE1 corporate network that required a full network outage. Although TRE_URE1 security personnel were aware of the planned outage, they did not understand that the planned outage would affect the PACS at various TRE_URE1 locations. As such, when the planned network outage occurred, TRE_URE1 security personnel lost the ability to monitor for unauthorized physical access into PSPs and their associated PACS at the locations in question. Moreover, although the TRE_URE1 security personnel on duty during the outage recognized the loss of their primary physical access monitoring methods, they did not understand that they needed to immediately implement alternative physical access monitoring methods because of the planned nature of the network outage. As a result, TRE_URE1 security did not monitor physical access into the locations in question for approximately two hours. The root cause of this noncompliance was that TRE_URE1 did not have a well-defined process to ensure continuous monitoring of PSPs and associated PACS during planned network outages. Specifically, maintenance personnel did not adequately communicate that the planned network outage would affect the ability of TRE_URE1 security personnel to monitor for unauthorized physical access to certain PSPs and their associated PACS. In addition, TRE_URE1’s PSP operations procedure did not clearly identify the need to immediately implement alternative physical access monitoring methods, including directly posting security personnel on-site, in response to planned network outages. The issue duration was for approximately two hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following five factors. First, the designated physical access controls for the affected PSPs continued to operate to control access and deny any potential unauthorized access throughout the duration of the issue. Second, each PSP at issue was located within secure facilities with limited physical access, reducing the likelihood that an individual could have gained physical access to the PSPs. Third, the duration of the issue was short, lasting less than two hours. Fourth, TRE_URE1’s security personnel subsequently determined that there was no unauthorized physical access during the duration of the issue. Finally, even if an unauthorized individual had gained physical access to the PSPs in question, such an unauthorized individual would still require appropriate credentials and permissions to electronically access Critical Cyber Assets within the PSP. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) resumed monitoring physical access to the PSPs in question and their associated PACS; 2) updated its process for notifying TRE_URE1 security personnel of potential and planned network outages, including providing automatic notifications to security personnel when any network maintenance activities will impact network functionality at PACS and monitoring system locations; 3) updated its PSP operations procedure to clearly provide that security personnel should immediately implement alternative monitoring methods when TRE_URE1’s primary monitoring method is not functioning as a result of a network outage; and 4) performed training on emergency response activities as described in the PSP operations procedure, including the need to continuously monitor for unauthorized access during network and equipment outages, as well as the appropriate response to such events. Texas RE has verified the completion of all mitigation activity.
2017-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016016183 | CIP-002-5.1 | R1 | TRE_URE2 submitted a Self-Certification stating that it had an issue with CIP-002-5.1 R1. Specifically, TRE_URE2 failed to implement a process that identifies each of its high/medium impact BES Cyber Systems and assets that contain a low impact BES Cyber System. The root cause of this noncompliance is that TRE_URE2 did not provide sufficient time or resources to implement its BES Cyber System categorization process. The duration of the noncompliance was less than two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for four reasons. First, upon completing the required BES Cyber System categorization process, TRE_URE2 identified a single generation asset containing only low impact BES Cyber Systems. Second, the duration of this issue was relatively short, lasting less than two months. Third, TRE_URE2 had a number of compensating measures in place, including physical access controls, monitoring systems, and electronic access controls. Finally, TRE_URE2 is a relatively small generating unit and is not a documented blackstart unit. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) implemented a BES Cyber System categorization procedure, which outlines the methodology through which TRE_URE2 will implement its BES Cyber System categorization; 2) categorized its BES Cyber Systems and determined it possesses only a single asset with low impact BES Cyber Systems; 3) hired an on-site manager with overall responsibility for overseeing TRE_URE2’s compliance obligations, including upcoming NERC CIP compliance obligations for low impact BES Cyber Systems; and 4) developed a new Internal Compliance Program, which further defines TRE_URE2’s responsibilities for meeting its compliance obligations under the NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015994 | CIP-006-3c | R1.6.2 | WECC_URE1 submitted a Self-Log stating that it had four separate instances of possible noncompliance with CIP-006-3c R1. Each of the four instance of noncompliance took place inside WECC_URE1’s Physical Security Perimeter (PSP). Specifically, for the first instance, WECC_URE1 reported that a WECC_URE1-contracted Security Officer (Security Officer) with authorized unescorted physical access rights, escorted two visiting contract workers into the PSP to clean the carpets. After the Security Officer escorted the first contract worker into the PSP, the Security Officer exited the PSP to escort the second contract worker, briefly leaving the first contract worker unescorted in the PSP. The root cause of this instance was due to human error due to lack of experience escorting in restricted areas and using the mantrap. WECC determined that the first instance began when a contract worker was left inside the PSP unescorted, and ended when the Security Officer resumed escorting of the contract workers within the PSP, for approximately 1 minute and 47 seconds of noncompliance. For the second instance, WECC_URE1 reported that a WECC_URE1 employee with authorized unescorted physical access rights, escorted three visiting WECC_URE1 employees who did not have authorized unescorted physical access, into the PSP. Once inside the PSP, the WECC_URE1 employee escort left one visitor unescorted in a conference room in order to escort another visitor out of the PSP, briefly leaving the visitor unescorted in the PSP. The root cause of this instance was human error due to the distraction cause by an increase in foot traffic in and out of the PSP that day. WECC determined that this instance began when the visitor was left inside the PSP unescorted, and ended when the WECC_URE1 employee resumed escorting the visitors within the PSP, for approximately 3 minutes of noncompliance. For the third instance, WECC_URE1 reported that a WECC_URE1 employee with authorized unescorted physical access rights, escorted a visiting WECC_URE1 employee who did not have authorized unescorted access to the PSP. While escorting the visitor out of the PSP, the WECC_URE1 employee and visitor did not scan their badges correctly in order to avoid a door alarm. In an effort to avoid a door alarm, the WECC_URE1 employee escort exited the PSP without the visitor. The WECC_URE1 employee escort then re-entered the PSP and escorted the visitor out of the PSP, briefly leaving the visitor unescorted in the PSP. The root cause of this instance was human error due to not fully understanding their escorting responsibilities. WECC determined that this instance began when the visitor was left inside the PSP unescorted, and ended when the WECC_URE1 employee resumed escorting the visitor within the PSP, for, approximately 16 seconds of noncompliance. For the fourth instance, WECC_URE1 reported that a WECC_URE1 employee with authorized unescorted physical access rights, assumed responsibility of an “escort” for an WECC_URE1 employee (visitor) who did not have authorized unescorted physical access to the PSP. While escorting the visitor around the PSP, the WECC_URE1 employee stepped into a separate room for a brief moment, leaving the visitor unescorted. The root cause of this instance was human error due to the escort not fully understanding their escorting responsibilities. WECC determined that the fourth instance began when the visitor was left inside the PSP unescorted, and ended when the WECC_URE1 employee resumed escorting the visitor within the PSP, for approximately three seconds of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In all four instances, WECC_URE1 failed to provide continuous escorted access for four visitors within the PSP. Such failure could allow an unauthorized individual to physically access systems and intentionally, or accidentally, disrupt or make changes to equipment and systems, which could interfere with WECC_URE1’s ability to operate, control, or monitor its bulk electric system elements. However, WECC_URE1 had controls in place to eliminate the risk posed from having unauthorized individuals inside a PSP without an authorized escort. These controls included dedicated security personnel; authentication systems, which prevent unauthorized logical access; 24 hour-a-day, 7 days-a-week security monitoring; disabled USB ports; security event logs; and awareness training. Further, WECC_URE1 discovered each instance within two minutes and immediately escorted unauthorized personnel out of the PSP or resumed appropriate escorting of the visitors. No harm is known to have occurred. For these reasons,WECC_URE1 determined that this noncompliance posed a minimal risk to the reliability of the BPS. WECC considered WECC_URE1’s CIP-006-3c R1.6.2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, WECC_URE1: 1) Completed the CIP access training for independent contractors and contract workers tutorial; 2) Signed WECC_URE1's independent contractors and contract worker CIP access training acknowledgement; 3) Completed security's updated CIP access awareness training; 4) Updated the security's CIP access awareness training tutorial to include guidance on escorting multiple visitors through a CIP restricted area mantrap; 5) Updated the training checklist to include a step associated with touring the applicable CIP restricted area (including the applicable mantrap). This training checklist is completed with all new security officers (Day, Swing, and Weekend) upon placement at any WECC_URE1 location; 6) Met with and/or communicated, via WECC_URE1's security awareness program, with the groups who have authorized unescorted physical access to CIP-restricted areas to review, discuss, and answer any questions related to escorting responsibilities in CIP-restricted areas; 7) Updated the CIP access training to include additional information related to what individuals should do if there is an issue with the mantrap-controlled CIP-restricted area access authorization sequence. Additional information was also included related to whom to call if the CIP-restricted area mantrap does not operate as expected or if there are questions related to the operation of the CIP-restricted area mantrap; and 8) Updated the mantrap visitor instructions to include information related to WECC_URE1's visitor control program. WECC_URE1's visitor control program covers escort and visitor responsibilities and reiterates that visitors are to be continuously escorted while inside CIP-restricted areas. WECC verified completion of WECC_URE1’s mitigating activities.
2016-12-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2016015988 | CIP-007-6 | R4; R4.3 | FRCC_URE1 submitted a Self-Report stating that it was in noncompliance with CIP-007-6. FRCC_URE1 failed to retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days. The FRCC_URE1 system operations Logging Event Manager (LEM) experienced three instances of logging failure for an aggregate of 30 hours and 9 minutes in July 2016. During the first instanace LEM failed to log between the hours of 0440 to 1517. During the second instanace LEM failed to log between the hours of 1534 to 1545. During the third instanace LEM failed to log between the hours of 1652 through 1215 the next day. The LEM is a virtual appliance that has no storage capacity of its own which collects security logs as required by CIP-007-6 R4 and pushes them to a Storage Area Network (SAN). The SAN was overcommitted and reached full capacity before expected. The SAN was known to be near end of life, but the memory usage forecast projected adequate space until the upgrade arrived. The assumptions in the usage model were incorrect, resulting in the SAN reaching capacity and shutting down the LEM logging function. There was no system alerting for SAN nearing capacity. The failure of the LEM was identified when network personnel checked the shared email account that was notified by the monitoring software Solarwinds Orion. The root cause for this noncompliance was the SAN was overcommitted and reached full capacity before expected. The SAN was known to be near end of life, but the memory usage forecast projected adequate space until the upgrade arrived. The memory usage assumptions in the usage model were incorrect, resulting in the SAN reaching capacity and shutting down the LEM logging function. There was no system alerting for SAN nearing capacity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The risk is minimal because if a cyber incident had occurred during the time that logging was down, the "after-the-fact investigations" per CIP-007-6 R4.1 would have been hampered by a lack of security logs. Per FRCC_URE1's Event Reporting Operating Plan, potential cyber security events are reported by all personnel System Operators in FRCC_URE1 control center. No potential cyber security events were reported when the SAN was down. As there were no alerts of potential cyber security incidents during the time that logging was down, there was negligible risk to the BPS. No harm is known to have occurred. | To mitigate this violation, FRCC_URE1: 1) cleared the SAN of unnecessary data and the SAN was restarted; and 2) reconfigured the SAN for dedicated space in the storage array so that security logs are prioritized (other system data will be lost in favor of security logs); and 3) monitored the SAN daily (network personnel) until the upgrade is installed; and 4) installed new Storage Array Network Systems (SAN) and configure to store logs. To mitigate this violation, FRCC_URE1 will: 1) Implement an alternate/backup logging system.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015546 | CIP-004-3a | R4.2 | MRO_URE1 stated that it had two instances of noncompliance with CIP-004-3a R4. The first instance of noncompliance, MRO_URE1 was informed that two individuals employed by a contractor that had access rights to the Control Center Physical Security Perimeter (PSP) were rotated as part of an apprentice program to another contractor. A rotation in an apprentice program is considered a personnel change for purposes of the Standard and Requirement. The access should have been revoked a week after the occurrence. In the second instance of noncompliance, MRO_URE1 failed to revoke an employee's logical access to the Energy Management System (EMS) within seven days. This occurred after a timely revocation access request was not automatically distributed by MRO_URE1's automated system to its EMS administrators. The employee's access should have been revoked earlier. The first instance of noncompliance was caused by the contractor's failure to accurately and timely inform MRO_URE1 that the individuals had been rotated to another contractor. MRO_URE1 sends weekly emails to its contractors asking if unescorted physical access for specific individuals is still required. The contractor responded to these emails by stating that these two individuals required physical access on multiple occasions. The second instance of noncompliance was caused by an underestimation of the capabilities of its automated provisioning system, as this type of access removal requires manual execution. MRO_URE1 was noncompliant for a total of 149 days over the course of 379 days. The noncompliance began when access was not revoked in the first instance of noncompliance, and ended when access was revoked in the second instance of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In the first instance of noncompliance, the individuals were in possession of 'timed' badges that were only active during standard office hours, and any unauthorized or malicious access during standard business hours would have had a high probability of being detected. Additionally, these individuals did not have electronic access. Further, these individuals had current personnel risk assessments (PRA) and up-to-date CIP Training. Finally, these individuals did not utilize their access during the period of noncompliance. For the second instance of noncompliance, the employee did not resign his employment, but remained in good standing, but whose job duties were transitioned from EMS cyber assets to System Protection cyber assets. Additionally, the employee has a current PRA and has up-to-date CIP Training. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-004-3a R4. | To mitigate this issue, MRO_URE1: 1) revoked physical access privileges and deactivated the badges for the individuals involved in the first instance of noncompliance; 2) to prevent reoccurrence of the first instance of noncompliance, MRO_URE1 met with executives from the instant contractor to stress the contractor's obligations under its policies; 3) to prevent reoccurrence of the first instance of noncompliance, MRO_URE1 sent an email to all contractors to stress a contractor's obligations under its policies; 4) disabled cyber access to the EMS system for the individual involved in the second instance of noncompliance; and 5) to prevent reoccurrence of the second instance of noncompliance, MRO_URE1 created an automated bi-daily report to help staff identify instances in which user access must be revoked manually. MRO verified that mitigating activities were complete.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2016015510 | CIP-005-3a | R1 | MRO_URE2 identified two instances where it was noncompliant with CIP-005-3a R1.5 because it did not adhere to the requirements of CIP-007-3a R3. The noncompliance was related to three Cyber Assets involved in MRO_URE2's Intrusion Detection System (IDS) that monitor or perform access control of the Electronic Security Perimeter (ESP). The first issue of noncompliance involved two Cyber Assets that had two security patches that were no evaluated for applicability within 35 days of the software patch being available. MRO_URE2 did not assess the patches for 90 days. The second issue of noncompliance involved MRO_URE2 overlooking two software patches for a hypervisor used to host a device that collects IDS sensor data. MRO_URE2 did not assess the patches for 102 days. The issue was caused by MRO_URE2's failure to track software patch sources with sufficient detail to detect all related cyber security related software patches for assessment. In the first instance of noncompliance, the patch source changed but the support group was unaware of this change and was not monitoring the proper alerts. The second instance of noncompliance was due to the fact that the support group was unaware that the vendor for the hypervisor did not list all security software patches on its security bulletin. The issue began 35 days after the first patch became available, and ended when the last security patch was assessed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both instances of noncompliance had relatively short durations, were detected, self-reported, and the two instances of noncompliance that overlapped did not create an additional vulnerability. The first instance of noncompliance involved devices that were Electronic Access Control and Monitoring Systems (EACMS), used for monitoring, as opposed to Bulk Electric System Cyber Assets and the mitigation the patches would have provided was already in place. The second instance of noncompliance was minimal because it involved a device that also was an EACMS, the device had limited impact to Critical Cyber Assets (CCAs) because it was located outside of the Electronic Security Perimeter (ESP), was afforded protective measure through network access restrictions, and the mitigation the patches would have provided was already in place. No harm is known to have occurred. MRO_URE2 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE2: 1) reviewed and assessed the outstanding patches; 2) to prevent reoccurrence of the first instance of noncompliance, MRO_URE2 registered to receive software patch notices with the new patch source; and 3) to prevent reoccurrence of both instances of noncompliance, MRO_URE2 developed a Patch-Vulnerability Management application. MRO_URE2 stated that mitigating activists were complete.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2015015005 | CIP-004-1 | R4 | MRO_URE3 stated that it had three instances of noncompliance with CIP-004-1 R4. Specifically, it inadvertently granted 12 trusted users access to additional Critical Cyber Assets (CCAs) beyond what was necessary; seven Communication Infrastructure employees were granted non-administrator access to more CCAs than necessary and five System Operation Support Staff employees were granted access to one more CCA than necessary. MRO_URE3 also approved access to nine users, but incompletely documented their access; specifically, six employees had administrator access to the software used to manage the two factor authentication system and three employees had access to CCA shared account logins. Finally, MRO_URE3 did not update its NERC CIP Personnel list to include those with authorized cyber access to CCAs after the periodic quarterly access reviews. The cause of this noncompliance is inadequate documentation and a lack of understanding of the specifications of the Standard and Requirement. Specifically, when it came to the documentation of authorization errors, there was a lack of understanding and awareness regarding the level of documentation that was required. The noncompliance related to granting too much access was caused by MRO_URE3's failure to clearly document what access should have been granted. The noncompliance related to the NERC CIP Personnel list was a lack of training as the new Supervisor of the SCADA System Support group did not know how to incorporate the changes to the periodic access review. The issue began when a Senior Manager first signed off on an inaccurate NERC CIP Personnel list, and is expected to end when mitigating activities will be complete. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All employees involved in the noncompliance were current employees that had been trained, had the required background checks, and were already tracked on MRO_URE3's CIP Access list for other systems. The risk presented from the employees that were granted additional access rights was minimal. All the employees were trusted individuals who had access to other CCAs in the Energy Management System (EMS), additionally, none of the users that were given additional access utilized those privileges, and the employees that were given access to additional CCAs were only provided with non-administrator privileges. The risk presented from the employees that had their access granted, but not documented was minimal. All the employees were properly authorized for CCA access and this issue is principally a documentation issue. Further, the employees involved in the two-factor authentication noncompliance had documented access to the operating system running the software, but did not have documented access to the specific application. The risk presented from the failure to update the NERC CIP Personnel list was minimal, as the updates that should have been made to the list were documented and passed onto Security who failed to incorporate the updates. MRO_URE3 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE3 will: 1) remove unnecessary employee access to CCAs and removed unnecessary administrator rights; 2) fully document all necessary access; 3) update the NERC CIP Personnel list; 4) change the EMS Active directory policies; 5) create a more granular EMS Active directory group policy; 6) improve the processes related to quarterly/annual reviews to include a detailed overall process, a new form for review validation tracking; and a process if discrepancy is found; and 7) conduct training on the new processes for CIP Standard owners and Asset owners; Mitigating activities are expected to be complete by or before January 31, 2017.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2016015762 | CIP-005-3a | R1 | MRO_URE3 stated that it was noncompliant with the requirements of CIP-007-3 R5 by not annually changing a password, associated with one system, that is part of the access point authentication process. The system is part of the dual-factor authentication process that is used by MRO_URE3 to allow access into the Electronic Security Perimeter (ESP). The cause of this noncompliance was a lack of ownership regarding what support group was responsible for this system. One group is responsible for the security and compliance of a one-time password system, while another group is responsible for the operating system. MRO_URE3 did not have any clear processes in place to delegate responsibility for changing the Database account password. The issue began when the password was not changed and ended when the password was changed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the risk is limited to only one device that is part of the two-factor authentication process of gaining access into the ESP. Further, two-factor authentication is not required for CIP Version 3, therefore, MRO_URE3 was going above and beyond the requirements. Additionally, separate single-factor authentication was still in place for the duration of the noncompliance. Finally, the password complexity controls were enabled and technically enforced. No harm is known to have occurred. MRO_URE3 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE3: 1) changed the password; 2) set up an annual alert in the password vault, which also captured the date the password was changed; and 3) updated the password change procedure, which included a clarification as to what support group was responsible for the password change. MRO_URE3 stated that mitigating activities were complete.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2015015006 | CIP-005-3a | R5 | MRO_URE3 stated that it removed two Critical Cyber Assets (CCAs) from its network during a network modification, but failed to remove the CCAs from the network diagram within 90 calendar days. The cause of this noncompliance was a lack of a formal and documented processes to update the network diagrams after network modifications. MRO_URE3 had an informal and undocumented process that relied upon the standard owner and NERC Cyber Security Team to update the network diagrams when making modifications to the CCA List. The issue began 91 days after the CCAs were removed from the network, and ended when MRO_URE3 updated its network diagram. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the noncompliance is limited to a documentation error in the network diagram and did not impact the CCA list. Additionally, the CCAs that remained on the network diagram were decommissioned. Finally, the risk was further reduced by MRO_URE3's detective controls, specifically the duration of the noncompliance was relatively brief because it was discovered during an internal review of its network diagram and a comparison to its CCA list to detect any discrepancies. No harm is known to have occurred. MRO_URE3 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE3: 1) updated its network diagram; 2) augmented and documented a process. MRO_URE3 stated that mitigating activities were complete.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO2015014978 | CIP-002-1 | R3 | MRO_URE4 stated that it failed to document three cyber assets within its control center as Critical Cyber Assets (CCAs). The cause of this noncompliance was a copying and pasting error by staff, and a lack of detective controls to confirm whether the CCA entries were complete. The issue began when the standard became mandatory and enforceable and ended when MRO_URE4 documented the CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue can be properly regarded as only a documentation error, as the three assets were afforded all the required physical and electronic protection afforded to a CCA despite not being documented as a CCA. Additionally, the scope of the noncompliance was limited to only three CCAs of the approximately 150 CCAs in the Control Center. Finally, the risk was reduced by MRO_URE4's strong secondary controls, specifically, the issue was discovered during a comprehensive review, which is not required by the CIP Standards. No harm is known to have occurred. MRO_URE4 has no relevant history of noncompliance with CIP-002-1. | To mitigate this issue, MRO_URE4: 1) documented the CCAs; 2) updated its procedure; 3) provided training to staff; 4) integrated the requirements of CIP-002-5.1 that no longer incorporates the CCA concept. MRO_URE4 reported that mitigating activities were complete.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015763 | CIP-006-3c | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. RFC_URE1 compliance personnel were reviewing logs of card reader swipes for the RFC_URE1 Generation Dispatch Room, a NERC CIP Physical Security Perimeter (PSP). Those compliance personnel identified discrepancies in the sequence of entry and exit entries that indicated possible tailgating (Tailgating is failing to swipe a badge upon entering the PSP behind another employee.) into the PSP. RFC_URE1 compliance personnel further investigated the identified discrepancies by reviewing video records for the area in question and confirmed five instances where trusted RFC_URE1 employees with current NERC CIP credentials and a valid business need to access the PSP engaged in tailgating. A total of three RFC_URE1 employees were involved in the five instances. In all five instances, the employee in question followed another employee who had properly badged into the PSP. RFC_URE1’s Physical Access Control Procedure requires all employees to present their ID badge to a card reader every time they enter a controlled area or security sensitive area, even if the door or gate is open ahead of them. In addition, RFC_URE1’s CIP Access Control Procedure (which was the procedure in effect at the time of the noncompliance) sets forth the expectations and requirements for NERC Physical Access, including not allowing people to tailgate when entering a NERC PSP and requiring everyone to utilize their badge for access. This noncompliance involves the management practices of verification and workforce management. RFC_URE1 was not effectively verifying that all employees entering a NERC PSP had swiped their badges before entering without tailgating. Workforce management is involved because the employees were not properly trained on how important it was to follow RFC_URE1’s policies prohibiting tailgating. The root cause was ineffective training, as the employees failed to follow the policy to both not tailgate behind another employee and to prohibit an employee from tailgating into a PSP behind him or her. This issue started when the first RFC_URE1 employees tailgated into the PSP and ended when the last RFC_URE1 employees that had tailgated into the PSP left the PSP and the employees’ entrance and exit were properly logged after tailgating into the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All of the RFC_URE1 employees that were involved in the five separate tailgating instances had current CIP Credentials including a valid PRA and up-to-date NERC CIP training and were approved for unescorted access to the PSP. RFC_URE1’s review of the video footage confirmed that only three individuals were involved in all five instances of tailgating. The employees were also all trusted employees. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) sent an email reminder from RFC_URE1’s Manager for NERC Compliance to all Generation Dispatchers of their obligations to comply with company policy for holding unescorted access and responsibilities for access to a NERC PSP. Later that day, the Vice President responsible for Generation Dispatchers sent an email message reinforcing the earlier email communication from the Manager of NERC Compliance; 2) held a meeting with the two employees initially identified as being involved in the tailgating incidents to review the video, discuss the events, reiterate the employees’ responsibilities for physical access control, and to document the employees’ acknowledgement of their responsibilities. RFC_URE1 subsequently discovered during an initial extent of condition analysis that a third employee was involved in tailgating and that third employee was included in follow-up meetings that reinforced the policy. RFC_URE1 held these follow-up meetings with all of the Generation Dispatchers to reinforce and reiterate the Generation Dispatchers’ obligations of having unescorted access and responsibilities for access to a NERC area; 3) installed and activated the use of a keypad for two-factor authentication into the PSP. RFC_URE1 has been monitoring employee behavior since installing the keypad and has observed that the additional authentication level through the use of the keypad and emphasis on the expected behavior has resulted in better adherence to RFC_URE1’s policy; 4) completed reviewing additional videos of the PSP in question and did not observe other tailgating incidents; and 5) recorded a reprimand internally for each of the employees involved in the tailgating incidents to highlight the importance of adhering to company security policy and to strongly discourage repeat behavior.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015920 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R4.2. Specifically, during WECC_URE1’s quarterly access review, it discovered that the request to revoke unescorted physical access to WECC_URE1’s control centers' Physical Security Perimeters (PSPs) for one employee who no longer had a business need for said access, was not revoked as requested. This issue began when unescorted physical access to the PSPs should have been removed for one employee who no longer required said access. This issue ended when WECC_URE1 revoked unescorted physical access to the PSPs for the employee in scope for this issue of noncompliance, for a total of four days of noncompliance. The root cause of this issue of noncompliance was lack of adequate controls in WECC_URE1’s administrative process for revocation of unescorted physical access to PSPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance WECC_URE1 failed to revoke unescorted physical access to PSPs for one employee within seven days of the employee no longer requiring the access. Failure to revoke unescorted physical access to PSPs in a timely manner could allow unauthorized individuals to have malicious physical access to the Critical Cyber Assets (CCAs), which could compromise the security of the CCAs that control the Bulk Electric System (BES). This unauthorized physical access could be exploited to cause damage, loss of generation, or widespread outages of the BES. However, the employee in scope had an approved personnel risk assessment and had completed CIP training; was still employed by WECC_URE1; and did not have logical access to CCAs. WECC_URE1 had technical authentication controls which reduced the risk of unauthorized logical access to CCAs. Additionally, WECC_URE1 had detective controls that consisted of automated quarterly and annual administrative recurring tasks to review the list of personnel with logical and unescorted physical access to CCAs, and their specific access privileges, which detected this issue of noncompliance. The duration of unauthorized physical access was limited to four days and the employee did not access the PSPs during the violation timeframe. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue(s) WECC_URE1: 1) revoked the employee’s unescorted physical access; 2) modified the process for sending access requests via email to ensure individual emails are sent per its form; and 3) ensured the subject line clearly states “revocation” or “grant” for access request.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016016 | CIP-004-3a | R2 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R2.3.Specifically, during a review of WECC_URE1’s Annual Training List, WECC_URE1’s Training Coordinator identified that one employee had not completed annual CIP training by the specified time period. In accordance with WECC_URE1’s training program, the Training Coordinator was required to notify the access approver to ensure the individual’s access is removed within seven days of the notification; however, that notification never occurred. This issue began when one employee should have completed annual CIP training. The issue ended when WECC_URE1 revoked unescorted physical access to WECC_URE1’s control centers PSPs for the one employee who had not completed annual CIP training, for a total of 140 days of noncompliance. The root cause of this issue of noncompliance was a lack of management policy guidance being well-defined, understood, or enforced. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance WECC_URE1 failed to revoke unescorted physical access to PSPs for one employee within seven days of the employee no longer requiring the access. Failure to revoke unescorted physical access to PSPS in a timely manner could allow unauthorized individuals to have malicious physical access to the Critical Cyber Assets (CCAs), which could compromise the security of the CCAs that control the Bulk Electric System (BES). This unauthorized physical access could be exploited to cause damage, loss of generation, or widespread outages of the BES. However, the employee in scope had an approved personnel risk assessment and had completed CIP training; was still employed by WECC_URE1; and did not have logical access to CCAs. WECC_URE1 had technical authentication controls which reduced the risk of unauthorized logical access to CCAs. Additionally, WECC_URE1 had detective controls that consisted of automated quarterly and annual administrative recurring tasks to review the list of personnel with logical and unescorted physical access to CCAs, and their specific access privileges, which detected this issue of noncompliance. The duration of unauthorized physical access was limited to four days and the employee did not access the PSPs during the violation timeframe. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue(s) WECC_URE1: 1) revoked the employee's access; 2) created monthly training reports to replace the annually report, for access review; 3) invoked its CIP-004-6 R5 CIP Access revocation procedure on the day annual training expires to ensure access is removed according to CIP-004 Requirements; and 4) had the CIP-004 Standard Owner meet with the Training Coordinator to reinforce adherence with WECC_URE1's Cyber Security Training program to ensure the program requirements are executed as prescribed.
2016-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015462 | CIP-006-1 | R1 | MRO_URE1 submitted a Self-Report stating that during an annual Cyber Vulnerability Assessment (CVA), MRO_URE1 discovered that a 14 inch by 39 inch (546 square inches) opening was located beneath the floor panels in an office area adjacent to the Physical Security Perimeter (PSP). This opening was a remnant of ductwork from the original HVAC system that had been removed. This opening was not documented and alternate measures to control access through this opening were not in place. The issue occurred due to a lack of transitional awareness on the part of the entity. Events that occurred before the enforcement date were not realized, and the previous CVA review processes were not sufficiently rigorous to detect the opening in the six-wall perimeter. The issue lasted approximately six years until MRO_URE1 secured the opening. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced to the small size (under 4 square feet) and obscure nature (under a desk, under the floor) of the opening. Additionally, to exploit the opening, an adversary would need to gain access to the building's interior which was protected by dual-factor electronic locks. Finally, although physical controls are still required under CIP V5, the six-wall perimeter requirement was not incorporated in CIP V5, and this issue would no longer constitute noncompliance. No harm is known to have occurred. MRO considered MRO_URE1's CIP-006-1 R1 compliance history in determining the disposition track. MRO_URE1’s relevant prior noncompliance with CIP-006-1 R1 includes: NERC Violation ID MRO2012009156 (CIP-006-1 R1) and MRO2013012277 (CIP-006-1 R1). MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. MRO2013012277 involved multiple instances of noncompliance, but none of that noncompliance related to the six-wall requirement. MRO2012009156 involved failure to adhere to the six-wall requirement, however, the current issue was not caused by any failure to mitigate MRO2012009156. | To mitigate this issue, MRO_URE1: 1) secured the opening; and 2) inspected the PSP to ensure that it was intact. MRO_URE1 stated that mitigating activities were complete.
2016-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015463 | CIP-007-3a | R5 | MRO_URE1 submitted a Self-Report stating that during an annual Cyber Vulnerability Assessment (CVA), MRO_URE1 discovered that an account used for system to system communication, had a password that had not been changed in more than two years. The cause of noncompliance was weak controls around passwords, specifically, the user responsible for the password change failed to make the change despite recurring system reminder emails that were sent prior to system deadline to change the password; however, once the deadline passed, the emails stopped, and the account was still active. The issue lasted approximately six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The account password is only known by administrators of the system, and there were no changes in the administrators during the noncompliance. Additionally, the account has no remote access capabilities; an adversary would need to enter Physical Security Perimeter (PSP) to gain access to the account, as the account can only be logged onto devices within an Electronic Security Perimeter (ESP). No harm is known to have occurred. MRO considered MRO_URE1's CIP-007-3a R5 compliance history in determining the disposition track. MRO_URE1’s relevant prior noncompliance with CIP-007-3a R5 includes: NERC Violation ID MRO2012010180 (CIP-007-1 R5) and MRO2012011289 (CIP-007-1 R5). MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty because MRO_URE1's compliance history does not contain noncompliance that would constitute current noncompliance. MRO2012010180 and MRO2012011289 involved MRO_URE1's failure to enforce technical and procedural controls for passwords. These prior issues would not constitute noncompliance as registered entities are currently only required to have technical or procedural controls for passwords. Further, MRO2012011289 involved controls related to password length and complexity which is not at issue in the current instance of noncompliance. | To mitigate this issue, MRO_URE1: 1) changed the password; and 2) the email script was set to continue sending daily password change reminders until the account password is changed. MRO_URE1 stated that mitigating activities were complete.
2016-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015874 | CIP-006-3c | R4 | NPCC_URE1 submitted a Self-Report stating that it had an instance of noncompliance of CIP-006-3c R4. A wireless communications upgrade was being performed in the facility containing the NPCC_URE1 control room by the landlord of the facility, using the services of a contractor. The work was being performed adjacent to the NPCC_URE1 control room in a non-CIP area, and contractor personnel were being escorted by a project manager (PM). While trying to locate an antenna, the PM and contractor personnel attempted to swipe the PM's employee ID card, and gained unauthorized access to the NPCC_URE1 control room. A control room operator immediately confirmed that they did not have authorized access and escorted them out of the control room. When the control room operator tried the PM's employee ID card again, it resulted in an "Access Denied" indication and the door remained locked. The duration of the noncompliance was approximately 5 minutes, from the time the PM and contractor personnel gained access to the control room to when they were escorted out. The root cause of the noncompliance was determined to be a motion sensor that controlled the door magnets for the entrance to the control room. When the motion sensor was activated by someone exiting the control room, the door magnet would be released for 15 seconds. Since the PM ID card did not grant access, it was concluded that an individual had exited the control room and the PM tried the handle within the 15 second time frame. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The unauthorized individuals had access to the control room for a minimal amount of time as the operator immediately recognized they were unauthorized and escorted them out. The facility is manned 24/7, therefore any unauthorized entry would be detected by control room operators and credentials would be requested. The log for the door in question was requested to confirm the invalid log attempts. Log review for the entire day only identified two invalid attempts, when the PM and contractor personnel originally swiped, and when the NPCC_URE1 control room operator tested the PM's employee ID card. No harm is known to have occurred as a result of this noncompliance. | To mitigate this instance of noncompliance, NPCC_URE1: 1) Performed a survey of all access doors to the control room and identified two doors where the door magnet is controlled by a motion sensor. 2) Changed door programming to stop motion sensor from unlocking affected doors. Exit now requires a push button. 3) Instructed control room personnel to remain vigilant with heightened awareness to unauthorized access until final recommendations for door controls were implemented. 4) Procureed and installed new "smart handles" on the two doors where the door magnet is controlled by a motion sensor. These "smart handles" eliminate the motion sensor control that caused the unauthorized access. NPCC has verified the completion of all mitigation activities.
2016-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016015837 | CIP-007-3a | R5.3; R5.3.3 | NPCC_URE2 submitted a Self-Report stating that it had an instance of noncompliance of CIP-007-3a R5. During preparation for CIP version 5, NPCC_URE2 discovered 3 accounts that were never managed by the procedural control for password management. Specifically, the passwords for the 3 accounts were not changed on an annual basis as required by CIP-007-3a. The root cause of the noncompliance was the domain administrators being unaware that the 3 accounts were available for potential interactive login. Only when that ability was tested in preparation for CIP version 5 was it discovered that login was possible. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three accounts had no elevated privileges and any access to the energy management system (EMS) command and control application required additional logins. Two accounts were never authenticated against, and the third account was last authenticated against in 2010, so no actual risk materialized. One account was used by an application exclusively for one-way file transfers from the EMS system to a back office server environment. The other two accounts were created to test an application for which developmental efforts were ceased, and only had access to the Windows domains that they were installed in. The accounts had passwords created specifically by NPCC_URE2 admins, and did not have default passwords that could have been freely available. No harm is known to have occurred as a result of this noncompliance. | To mitigate this instance of noncompliance, NPCC_URE2: 1) Disabled one account on for testing, and subsequently deleted the account from the domain. 2) Disabled the other two accounts for testing, and subsequently deleted the accounts from the domain. NPCC has verified the completion of all mitigation activities.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015612 | CIP-004-3a | R3 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R3. RFC_URE1’s Human Resources department ran a report to produce a list of employees with personnel risk assessments (PRAs) that needed to be updated. At the time the report was run, 17 employees had PRAs that needed to be updated. However, union employees refused to sign the release form because it included a credit check. Numerous rounds of protracted negotiations took place to develop a release and PRA acceptable to the union. Ultimately, the credit check was removed from the PRA process. As a result of this delay, RFC_URE1 failed to update the PRAs for 15 employees on time. The root cause of this noncompliance was a labor dispute between RFC_URE1 management and the union employees. This contributing factor implicates the management practice of workforce management. The issue started on the date RFC_URE1 was required to renew the first PRA and ended when RFC_URE1 completed updated PRAs for all employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following factors. First, all 15 employees with expired PRAs previously had valid PRAs and had unescorted physical access. Second, RFC_URE1’s internal controls worked as designed by notifying the responsible individuals that certain PRAs had to be renewed. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) completed updated PRAs for all 15 employees; and, 2) added a month to the PRA renewal process so that the Human Resources department has more time to complete PRA renewals.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014840 | CIP-006-3c | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R2. As part of RFC_URE1’s installation of a new Primary Control Center (PCC) and a new EMS system, RFC_URE1 was also expanding the physical size of its Backup Control Center (BCC). In carrying out this task a contracted technician, under the direction of RFC_URE1’s Facilities Team Lead began cutover from the card-reading security system to the access control system at the BCC. However, this cutover was initiated without properly scheduling with RFC_URE1’s CIP Compliance Coordinator, which resulted in an interruption of the automated physical access card reader monitoring and reporting from the BCC to the PCC for approximately 24 hours. However, as an additional detective and preventative control, RFC_URE1 had a System Control Supervisor stationed at the BCC to manually: a. Monitor access of the Physical Security Perimeter (PSP) that was being physically expanded; b. Log access by staff and contractors that did not have unauthorized access into the PSP during working hours; c. Escort such staff into the PSP. The root cause of this noncompliance was a communication breakdown between RFC_URE1’s Facilities Team Lead and RFC_URE1’s CIP Compliance Coordinator resulting in the cutover being started without first consulting with the CIP Compliance Coordinator. Normally, this type of project would have been managed by RFC_URE1’s Manager of Safety, Training, and Security. However, at the time of this change, that position was vacant due to an unexpected death, resulting in a gap in responsibilities. This contributing factor implicates the management practices of workforce management and implementation. The issue started on the date RFC_URE1 began the cutover and ended when RFC_URE1 completed the project and launched the automated access and logging controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following factors. First, during the time that the automated physical access card reader was down, RFC_URE1 stationed a System Control Supervisor at the BCC as an additional detective and preventative control to monitor and log access, and escort relevant staff into the PSP. Second, RFC_URE1 identified and responded to the issue quickly, demonstrating effective internal controls. Third, this issue was an isolated incident and not indicative of a systemic failure because the issue occurred as a result of a unique set of circumstances not normally encountered by RFC_URE1. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) updated the Cyber Asset list; 2) created a baseline for the access control system and reconciled configuration changes daily; 3) created an emergency change ticket to document and approve the implementation; 4) identified and documented all necessary ports and services, and disabled non-essential ports and services; 5) brought the access control system server and application up-to-date with security patches and included in the update process to ensure future security patches are applied as required; 6) installed malicious software prevention on the access control system server and included in the signature update process; 7) approved and documented access control system access including: (1) documenting and limiting shared account access; (2) logging account usage; and, (3) enforcing password requirements; 8) automatically monitor and alert system events; 9) filled the role of Manager Safety, Training, and Security, which was vacant during the period of noncompliance; 10) modified the internal form required for approval of capital expenditures to require notification to the CIP Compliance department for any changes/upgrades/additions that have potential CIP impact as a new preventative control; 11) provided training on new internal form for approval of capital expenditures; and, 12) created the new position of Manager of Facilities with responsibility for facilities maintenance.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015743 | CIP-007-3a | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. An RFC_URE2 IT Administrator (IT Administrator) granted an IT Data Storage Server Administrator (the user) ‘root’ and personal login access to a server prior to the user’s electronic access request ticket being submitted and approved. RFC_URE2’s procedures for granting access to equipment that contains CIP protected information require that an electronic access request ticket be submitted and approved before access is granted. RFC_URE2’s daily exception report for its electronic access request system identified this error because the user’s new account had no matching request for access and approvals, from the day before. RFC_URE2 runs and checks the daily exception report every day to look for instances of unauthorized access. RFC_URE2 discovered the error one day after the error occurred. When the user was interviewed about why this error occurred, he explained that he did not wait for the approval of an electronic access request ticket because of an ongoing emergency event. The user observed backup failure on two servers and realized the possibility of data loss if anything happened to those servers. The user used his personal login id to log into the servers and successfully switched to the ‘root’ account on the server to perform the backup/restoration activities. The user performed these activities two days before his access to the ‘root’ account was approved through the electronic access request system. To allow the user to perform these emergency activities, the IT Administrator verbally granted the user the ‘root’ password and access. This verbal approval was in violation of RFC_URE2’s procedures as the user’s access request for access to the server had not yet been approved. The IT Administrator should have found another user with authorized access to make the necessary changes. Two days after the error had occurred, RFC_URE2 remediated the noncompliance by properly documenting the earlier given access through the submission and approval of an electronic access request ticket. This noncompliance implicates the management practice of workforce management because RFC_URE2 struggled at managing the granting of access permissions to individuals that needed specified CIP access. The root cause was ineffective training because the IT Administrator did not follow RFC_URE2’s procedure when he granted access to the user before the user’s access request had been approved. This issue started when access was granted to the user without prior approval and ended when the previously given access was properly approved through the electronic access request system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the user that was improperly granted access without the submission and approval of an electronic access request ticket had both a completed background check and valid NERC CIP training at the time the access was granted. The user is a member of the appropriate IT infrastructure group that needs this level of access to the servers. Furthermore, the user’s access was verbally given by the IT Administrator to address an emergency situation and the user only had access for two days before his access was properly documented and approved through the electronic access request system. Second, the issue was detected through a daily exception report the day after it occurred, which shows that RFC_URE2’s detective controls are working effectively. The short duration of the noncompliance also minimizes the risk because it reduces the opportunity for the issue to be exploited. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) confirmed that new accounts on the servers cannot be requested through the Online User Registration Application, an older electronic access request system which is no longer being used to request NERC CIP access, but is still in use for non-NERC CIP electronic access requests; 2) added a message banner to the login screen for the servers indicating that new accounts should not be created without a fully approved request in the electronic access request system; 3) added selections into the electronic access request system for requesting access to the ‘root’ password manager application, specifically for these type of servers, the only CIP servers at this time. The ‘root password’ would only be accessible on line, and for authorized users only. The electronic access request system application ensures that only users with cleared background check and training can request and keep this access; 4) retrained all relevant employees on these new procedures. Specifically, in future emergency situations, the relevant employees were retrained to find an authorized user with already approved access rather than give verbal access to an unauthorized user. The relevant employees were reminded that they are not to give verbal access and that all requests for access must go through the electronic access request system.
2016-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015990 | CIP-004-6 | R2; R2.2 | SERC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-6 R2.2. SERC_URE1 granted an employee authorized access to Critical Cyber Assets without completing the required cyber security training. SERC_URE1 mistakenly granted an employee unescorted physical access to the control room without having completed the appropriate cyber security training. The employee was a returning employee who previously had authorized CIP access. SERC_URE1 recently implement an automated software program that verifies if the requesting individual has completed cyber security training within the last 15 months and has a current personnel risk assessment (PRA). However, during installation, the vendor incorrectly configured the software and it validated whether the requesting individual had either a valid PRA or current cyber security training. SERC_URE1 did not configure the software to verify that the individual met both requirements. The employee in question had a current PRA, but did not attend cyber security training within the last 15 months. Three days after SERC_URE1 granted the individual access, a SERC_URE1 analyst discovered the issue when logging into the access request workflow software to determine the status of this employee’s request. The analyst noticed the employee’s cyber security training was expired. The same day, SERC_URE1 revoked the employee’s access until training was complete. SERC_URE1 performed a root cause analysis and determined the error to be a human error. The vendor installing the software failed to correctly configure the software. Prior to granting access, the software should have required that both the cyber security training and PRA prerequisites be satisfied. The issue lasted three days, from when SERC_URE1 granted the employee unescorted physical access until SERC_URE1 revoked the employee’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 granting access to Bulk Electric System Cyber Systems without appropriate training exposes the systems to inappropriate use. However, SERC_URE1 revoked the employee's access upon discovery; three days after SERC_URE1 granted access. The employee previously received the annual cyber security training approximately 16 months prior. The employee’s access was only physical no logical access was involved. In the three days that the employee had access, the employee accessed the SCADA control center twice, for a total of three minutes. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) revoked the employee’s access until the cyber security training was completed; 2) corrected the software program code to ensure cyber security training and PRA requirements are met prior to granting access; and 3) added the access management solution to the change management process to ensure adequate documentation is captured and detailed testing is completed prior to commissioning.
2016-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015677 | CIP-004-3a | R4. | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. SERC_URE1 failed to maintain lists of personnel with authorized unescorted physical access to Critical Cyber Assets (CCAs). The SERC_URE1 security team received a workflow ticket to provide physical access for two non-CIP locations for an existing contractor. The individual working the ticket inadvertently added access to substation control house Physical Security Perimeters (PSPs), instead of the substation yard as requested. This occurred during a transition to a new Physical Access Control System (PACS), while SERC_URE1 had both systems running in parallel operations. The individual completing the ticket selected a facility name in the old system when he or she should have selected a similar facility name in the new system. SERC_URE1 erroneously provided the individual unescorted physical access to the PSP and did not add the individual to the authorized access list. Approximately one month later, while reviewing access reports for any discrepancies, a newly implemented internal control, a SERC_URE1 compliance analyst discovered the physical access granted without the proper workflow ticket. SERC_URE1 initiated an investigation, and nine days after the discovery, SERC_URE1 completed its review and interviews and revoked the improper access. On three separate occasions over five days, a SERC_URE1 contractor granted three additional individuals unescorted physical access to several PSPs in error. All three individuals were part of a collective bargaining unit, and the SERC_URE1 contractor attempted to modify their badge access permissions to address a potential work stoppage. The contractor inadvertently added access on three separate occasions to all substation control houses instead of just the control houses at a single CIP substation. The two lists had similar names within the PACS system, and the contractor selected the wrong list while making each access change. Since SERC_URE1 granted these individuals access in error, it did not add these individuals to the authorized access list. Eight days after the first instance, a SERC_URE1 compliance analyst discovered all three instances while reviewing an access report generated as part of a newly implemented internal control. SERC_URE1 corrected all three access errors that same day. Human error was the root-cause in all four instances, in that individuals made incorrect selections when assigning access permissions. The issue lasted for approximately a month and a half, from when SERC_URE1 granted the first individual access in error and did not update the access list, through when SERC_URE1 revoked access for the last three individuals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to maintain lists of personnel with authorized unescorted physical access to CCAs could have given unauthorized personnel the opportunity to physically access CCAs and potentially damage, degrade, or obtain data that could be detrimental to SERC_URE1 operations or the BPS. However, the individuals given improper access remained in good standing with SERC_URE1, had valid and up-to-date personnel risk assessments, and were current on all required training. SERC_URE1 did not grant remote logical access to these individuals. SERC_URE1 reviewed badge access reports and found the individuals did not use or attempt to gain access to any PSP during the violation. The improper physical access permissions lasted 38 days for the first individual and between three and eight days for the remaining three individuals. No harm is known to have occurred. SERC considered SERC_URE1’ CIP-004 R4 compliance history in determining the disposition track. SERC determined that SERC_URE1’s CIP-004 R4 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE1: 1) provided training to affected staff to discuss the recent issues with incorrect access levels being added, and the need for precision; 2) modified naming conventions of access levels in the PACS to lessen confusion; 3) provided training to the access control group on the naming conventions; 4) added an additional monitor so that they can have the PACS, the security access request, and the recently acquired security management system up simultaneously, rather than having to keep one minimized; 5) developed a written procedure for processing of security access requests by the access control group; and 6) conducted training on the new access control group security access request processing procedure.
2016-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016015683 | CIP-003-3 | R6 | SPPRE_URE1 submitted a Self-log stating that, it had a minimal risk instance of noncompliance with CIP-003-3 R6 because SPPRE_URE1 personnel deployed certain software to numerous cyber assets that had not been approved per SPPRE_URE1’s change control process. Specifically, SPPRE_URE1 personnel were attempting to diagnose certain communications issues between two endpoint systems and a security management system. To understand the cause of these issues, SPPRE_URE1 personnel began preparations to deploy certain diagnostic software to gather logs and other necessary information. In preparation, the assigned SPPRE_URE1 technician began performing pre-deployment activities prior to seeking formal approval for the software change. During these preparations, however, the SPPRE_URE1 technician inadvertently used an automatic rather than manual installation process. As a result, the diagnostic software installation occurred immediately upon saving the work project on the security management system. All such installations are required to first be approved per SPPRE_URE1’s change control process. Additionally, because the task was created at the organizational level, the diagnostic tool went to numerous Critical Cyber Assets and non-Critical Cyber Assets instead of just the two endpoint systems. The root cause of this instance of noncompliance was lack of detailed instructions on how to properly deploy the diagnostic software at issue. In addition, SPPRE_URE1 did not provide adequate training to the SPPRE_URE1 technician tasked with deploying this particular diagnostic software. The duration of this instance of noncompliance was 1 day, from the date the diagnostic software was installed on the cyber assets until the date the software was removed from the cyber assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to adhere to change control processes presents a potential risk to the reliability of the BPS by providing the opportunity for the introduction of vulnerabilities to Critical Cyber Assets, which if exploited, could affect the availability of Critical Cyber Assets and/or lead to unauthorized access to Critical Cyber Assets. Notwithstanding, the software at issue is merely a diagnostic reporting tool, the purpose of which is to log and diagnose communication issues associated with the server. Because the software serves as a reporting tool, SPPRE_URE1 attested that it did not have any operational impact on the devices to which it was inadvertently deployed. Additionally, the diagnostic software was developed by and only relates to software from a trusted SPPRE_URE1 vendor. Moreover, SPPRE_URE1 was immediately aware of the unintentional software deployment and provided evidence that it removed the software from all impacted systems within 24 hours. No harm is known to have occurred. SPP RE considered SPPRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SPPRE_URE1: 1) removed the diagnostic software from all impacted systems one day after it was inadvertently deployed; 2) created a desk procedure that provides instructions on how to properly install the diagnostic software in question; and 3) trained the SPPRE_URE1 technician on the use and configuration of the diagnostic tool in SPPRE_URE1’s security management system.
2016-11-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015943 | CIP-007-3a | R6; R6.4 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R6. Specifically, TRE_URE1 failed to retain required system event logs for the minimum 90-day period specified in CIP-007-3a R6.4. TRE_URE1 replaced an existing server tasked with storing system event logs for three core switch devices with a new server. During the transition, however, TRE_URE1 personnel did not authorize the three switch devices on the new server. As such, while the three devices at issue continued to produce logs and send them to the new server, the new server did not actually store the logs. As a result, TRE_URE1 did not retain the necessary system event logs for 13 days until TRE_URE1 personnel provided the necessary authorizations for the three affected devices. The root cause of this noncompliance was an inadequate process to address the transition between servers tasked with storing system event logs. In particular, TRE_URE1’s change request and physical security change control documentation did not include a specific requirement to confirm the authorization of devices on the system event log storage server. TRE_URE1 had an issue with CIP-007-3a R6 for 13 days, from when the old logging server was turned off until TRE_URE1 personnel authorized the three devices at issue on the new system event logging server and began retaining logged information for those devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the issue was short, lasting only 13 days. Second, TRE_URE1 provided evidence that it retained logs for all other devices within the three affected devices’ respective Electronic Security Perimeters (ESPs). As such, although the new server did not retain system event logs for the three affected devices, TRE_URE1 did retain logs of all traffic passing through those devices for the duration of the issue. Third, no Cyber Security Incidents occurred during the duration of the logging issue. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) corrected the configuration of the new server to receive and store the logs for the three devices; 2) revised its change request and physical security change control documentation to require that a checkbox is selected to ensure TRE_URE1 verifies that the applicable server is updated/authorized when devices are configured; and 3) provided the revised procedure and information regarding the authorization process to relevant IT personnel. Texas RE has verified the completion of all mitigation activity.
2016-11-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015944 | CIP-007-3a | R5; R5.2.1; R5.3.3 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R5.3. In particular, TRE_URE1 stated that it failed to change the password at least annually for a single default account. Subsequently, Texas RE determined that TRE_URE1 also had an issue with CIP-007-3a R5.2.1 because TRE_URE1 did not disable the default account or change that default account’s password prior to putting the impacted system into service. A third-party vendor created a default account on a TRE_URE1 server to monitor certain fuel resupply facilities. Subsequently, TRE_URE1 transferred its operations to a new control center. As part of this transition, the server in question began functioning as TRE_URE1’s Physical Access Control System (PACS) with the default account enabled and the original vendor-installed password in place. However, because the default account was not identified or assigned to any TRE_URE1 users, TRE_URE1 did not detect the account until it performed a check on the various user accounts on the PACS server. Following the identification of the single default account at issue, TRE_URE1 disabled the account. Accordingly, TRE_URE1 did not change the vendor-installed password prior to placing the default account on the PACS server into service and also did not update the password for that single default account annually by retaining the vendor-installed password for 496 days. The root cause of this noncompliance was that TRE_URE1 lacked a sufficient process to detect default accounts installed by third parties on its system. In particular, TRE_URE1 relied solely on a manual process to detect such default accounts. TRE_URE1 had an issue with CIP-007-3a R5 for 496 days, from when the PACS server went into service with the default account enabled and the original password in place until TRE_URE1 disabled the single default account at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the software application in question was fully segregated from the PACS server’s security functions. Second, only employees granted authorized access to enter the Physical Security Perimeter in which the PACS was located could have accessed the PACS server, including the default account at issue here. Third, during the duration of the issue, no employee had authorized electronic access to the default account. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) disabled the applicable user account; 2) updated its process to identify when default accounts are created by implementing an automatic check to detect default accounts. TRE_URE1 previously had a manual process in place; 3) updated its process document to clarify that TRE_URE1 staff will oversee the entire process when a third party is hired to perform system changes; and 4) provided information regarding the new TRE_URE1 default account processes to affected TRE_URE1 personnel. Texas RE has verified the completion of all mitigation activity.
2016-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015945 | CIP-002-5.1 | R2. SR2.2 | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-5.1 R2. NPCC_URE1 failed to have its CIP senior manager or delegate approve its Bulk Electric System (BES) cyber system impact rating spreadsheets prior to the enforcement date of CIP-002-5.1. The noncompliance ended when the CIP senior manager signed off on the spreadsheets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 completed its review of its BES cyber system impact rating spreadsheets but failed to perform the administrative function of having its CIP senior manager's signature. The issue was discovered internally and corrected the day after. No harm is known to have occurred. NPCC considered NPCC_URE1's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, NPCC_URE1: 1. signed the BES asset summary by its senior CIP manager; and 2. created a work order in its work management system to have BES cyber systems impact rating spreadsheet information reviewed on an annual basis. NPCC has verified the completion of all mitigation activity.
2016-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015708 | CIP-006-3c | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. RFC_URE1’s Team Leader IT Services commissioned work on two NERC Physical Security Perimeters (PSPs) which were located two floors apart. Electricians were to pull fiber-optic data cables between two NERC PSPs. RFC_URE1 originally anticipated that only one PSP cabinet would have to be open at a time. Consequently, RFC_URE1 assigned access rights to both PSP cabinets to two security officers – one for second shift, and one for third shift – who could escort the electricians to either PSP cabinet. However, during the course of the work, it became clear the electricians would need to access both PSPs at the same time in order to complete the fiber termination and testing work. Accordingly, the second-shift security guard, who had access to both PSPs, arranged for another security officer to escort one of the electricians to the other PSP to complete the work, despite the fact that this officer did not have access rights to the PSP. As a result, for approximately 2-3/4 hours, one of the PSPs was guarded by a security officer who was not assigned access to that particular PSP. The PSP in question was secured and closed after the security officer at the central alarm station contacted the security services company’s Account Manager about the issue. The root cause of this noncompliance was the security officers’ failure to follow the established process for visitor/contractor access to PSPs. This contributing factor implicates the management practices of workforce management and asset and configuration management. This issue started when RFC_URE1 granted the electrician access to the PSP without a proper escort, and ended approximately 2-3/4 hours later, when RFC_URE1 secured and closed the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, RFC_URE1 identified and corrected the issue in less than 3 hours, demonstrating effective internal controls. Second, although the security guard escorting the electrician did not have assigned access to that particular PSP cabinet, he had a verified identity, a current personnel risk assessment, current security training, and had authorized unescorted physical access to non-NERC assets at the company. Third, the PSP cabinet at issue is located in a secured building owned and occupied by RFC_URE1 with controlled building and room access. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) clarified within its procedure for access control for facilities subject to regulatory standards that an escort is an individual who is authorized for unescorted access to that protected facility; 2) clarified the responsibilities for accepting or transferring escort duties for maintenance or construction work to be done within a protected facility including cabinets; 3) clarified procedures by revising any references to “host” in the Physical Security Plan and specify that an escort for a PSP must already be authorized for unescorted access to that PSP; 4) included clarification of an authorized escort in the Physical Security Plan and the security officers’ central alarm station post orders; and 5) reinforced the visitor control program including assigned PSP access.
2016-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015709 | CIP-006-3c | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. RFC_URE2’s Team Leader IT Services commissioned work on two NERC Physical Security Perimeters (PSPs) which were located two floors apart. Electricians were to pull fiber-optic data cables between two NERC PSPs. RFC_URE2 originally anticipated that only one PSP cabinet would have to be open at a time. Consequently, RFC_URE2 assigned access rights to both PSP cabinets to two security officers – one for second shift, and one for third shift – who could escort the electricians to either PSP cabinet. However, during the course of the work, it became clear the electricians would need to access both PSPs at the same time in order to complete the fiber termination and testing work. Accordingly, the second-shift security guard, who had access to both PSPs, arranged for another security officer to escort one of the electricians to the other PSP to complete the work, despite the fact that this officer did not have access rights to the PSP. As a result, for approximately 2-3/4 hours, one of the PSPs was guarded by a security officer who was not assigned access to that particular PSP. The PSP in question was secured and closed after the security officer at the central alarm station contacted the security services company’s Account Manager about the issue. The root cause of this noncompliance was the security officers’ failure to follow the established process for visitor/contractor access to PSPs. This contributing factor implicates the management practices of workforce management and asset and configuration management. This issue started when RFC_URE2 granted the electrician access to the PSP without a proper escort, and ended approximately 2-3/4 hours later, when RFC_URE2 secured and closed the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, RFC_URE2 identified and corrected the issue in less than 3 hours, demonstrating effective internal controls. Second, although the security guard escorting the electrician did not have assigned access to that particular PSP cabinet, he had a verified identity, a current personnel risk assessment, current security training, and had authorized unescorted physical access to non-NERC assets at the company. Third, the PSP cabinet at issue is located in a secured building owned and occupied by RFC_URE2 with controlled building and room access. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) clarified within its procedure for access control for facilities subject to regulatory standards that an escort is an individual who is authorized for unescorted access to that protected facility; 2) clarified the responsibilities for accepting or transferring escort duties for maintenance or construction work to be done within a protected facility including cabinets; 3) clarified procedures by revising any references to “host” in the Physical Security Plan and specify that an escort for a PSP must already be authorized for unescorted access to that PSP; 4) included clarification of an authorized escort in the Physical Security Plan and the security officers’ central alarm station post orders; and 5) reinforced the visitor control program including assigned PSP access.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015115 | CIP-005-3a | R2; R2.2 | SERC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a R2. SERC_URE1 enabled ports and services that are not required for operations or monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 performed an approved change on its SERC_URE1 and SERC_URE1 affiliate (affiliate) Energy Control Center (ECC) and Backup Control Center (BCC) firewalls. However, the firewall administrator inadvertently configured the firewalls to allow any port to any service through the firewalls. The administrator configured the firewalls to allow ingress and egress of the full range of ports and services for affiliate Critical Cyber Assets (CCAs) to SERC_URE1 CCAs. In addition, the administrator configured the firewall to allow other affiliate CCAs with full range egress of ports and services to SERC_URE1 CCAs. A few hours later, ECC staff performed a business verification for the approved change management ticket and discovered the incorrect firewall rules. The next day, the firewall administrator corrected the rules on the firewall management console, but due to extreme heat and weather conditions, the firewall administrator could not update the production firewalls. Two days after the discovery, SERC_URE1 updated the production firewall rules to restrict access as required. SERC_URE1 determined that human performance was the primary cause of noncompliance. SERC_URE1 followed its change management process for documentation and approval, but the administrator did not perform the change as documented and approved. The issue lasted for approximately two days, from when SERC_URE1 implemented the incorrect firewall rules, until SERC_URE1 modified the firewall rules. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to control or restrict electronic access to the ESPs could have led to harm to the BPS by increasing the likelihood that cyber intrusions could have occurred resulting in damage to various CCAs. However, SERC_URE1 performed a risk analysis and discovered that even though the administrator configured the firewall rules to allow the traffic to pass, the firewalls lacked the required network routing. Therefore, because there was no network routes defined in the firewalls network, traffic was unable to pass. The enabled firewall rules confined the traffic between specific CCAs not permitting entire subnets. In addition, the enabled range of communications was constrained between protected ESPs. Further, SERC_URE1 identified the issue through an internal control. SERC considered SERC_URE1’s CIP-005-3a R2 compliance history in determining the disposition track. SERC determined that SERC_URE1’s CIP-005-3a R2 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE1: 1) corrected the firewall policy in the firewall management console; 2) pushed the updated firewall policy to the SERC_URE1 ECC/BCC firewall clusters and the affiliate ECC/BCC firewall clusters; 3) conducted operator/manager consultation/coaching; 4) required the operator to attend classroom human performance training course; 5) had the operator review existing applicable processes/procedures; 6) revised existing procedures/processes; and 7) communicated the revised procedures/processes to personnel.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016015833 | CIP-007-3a | R5; R5.3 | SERC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R5.3. SERC_URE2 did not implement passwords on four Critical Cyber Assets (CCAs). In preparation for CIP Version 5, SERC_URE2 replaced four of its six network switches. Prior to deploying into the production environment, SERC_URE2 configured and tested the new switches in a test environment and did not observe issues with the existing cyber security controls. Four days later, a SERC_URE2 system administrator accessed one of the switches and noted that a password was not required. The system administrator initiated an immediate review of the facts and circumstances, and discovered that the SERC_URE2 personnel did not save the configuration settings to permanent memory. The configuration settings included a requirement for a complex password, but SERC_URE2 staff failed to save the configuration to permanent memory at the conclusion of the testing. The technical capabilities of the devices allow support staff to modify the running configuration, but one must save the changes to permanent memory prior to either powering the device off, or rebooting. If one fails to save the running configuration to permanent memory prior to power off or reboot the device will return to the last saved state. The root cause of this failure was a lack of specific instructions for how SERC_URE2 personnel should properly save the configuration settings for this type Cyber Asset. The issue lasted for approximately four days, from when SERC_URE2 moved four switches into the production environment without a complex password being required, until SERC_URE2 configured the devices to require a complex password. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure configure the network switches could lead to unauthorized personnel gaining access through the Electronic Security Perimeter (ESP) firewall access point and potentially manipulating other CCAs, data, or operations in order to create an adverse impact on the BPS or local operations. However, SERC_URE2 had the CCAs within an established ESP and physical security perimeter with logging and alerting enabled. The duration of this issue was limited to less than four days. SERC_URE2 reviewed the system security logs and SERC_URE2 found no issues. SERC considered SERC_URE2’s CIP-007-3a R5 compliance history in determining the disposition track of this instant issue. SERC determined that SERC_URE2's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE2: 1) configured the password settings and saved to permanent memory; 2) performed a manual log review for cyber security events; 3) modified existing change process of programming such devices to include manual confirmation of settings after one reboot of device before placing into production; and 4) provided awareness to staff on the modified change process.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016015897 | CIP-005-3a | R3; R3.2 | SERC_URE2 submitted a Self-Report stating that it had an issue of CIP-005-3a R3.2. SERC_URE2 did not effectively implement and document the process for monitoring and logging access at access points to the Electronic Security Perimeters (ESPs). In preparation for CIP Version 5, SERC_URE2 replaced the primary firewall and stand-by firewall for the primary control center (ECC) and back-up control center (BCC), respectively. During installation, SERC_URE2 configured the devices to forward the system security logs to the centralized log aggregation server. However, SERC_URE2 failed to configure the aggregation rules on the server, preventing the system from normalizing the firewall security logs. The normalization of the logs allows the logs to be reconciled against the established monitoring and alerting rules. The failure to have normalization rules prevented the system from properly assessing the stored logs and generating alarms, as needed. Three and a half months later, SERC_URE2 discovered the centralized log aggregation server did not assess the logs, and therefore, it did not generate alerts. SERC_URE2 immediately assessed all the stored logs for security events, with no findings. The assessment of the security logs for the BCC firewalls occurred 112 days after deployment to production, and the assessment of the security logs for the ECC occurred 104 days after deployment. The root-cause was a lack of specific detail in the procedure on how to set up the rules for this new type of Cyber Asset. The issue lasted for three and a half months, from when SERC_URE2 first deployed new firewalls into the production environment without configured log aggregation rules until SERC_URE2 discovered this issue and manually assessed the stored logs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to properly configure the application to assess and alert on the logs could have permitted a security event to go unnoticed for a longer than acceptable period. However, the manual review that SERC_URE2 conducted only went beyond the permitted ninety days by 14 days. SERC_URE2 performed a review of all security logs since the date of deployment. The firewalls were within a secured Physical Security Perimeter with monitoring and alerting enabled. SERC considered SERC_URE2’s CIP-005-3a R3 compliance history in determining the disposition track of this instant issue. SERC determined that SERC_URE2's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE2: 1) performed a manual review of the firewall security logs; 2) enhanced the change control process to include a check following the system change to verify that security controls have not been adversely affected; and 3) provided awareness to CIP personnel on the modified change management process.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016015972 | CIP-004-3a | R3; R3.2 | SERC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R3.2. SERC_URE2 did not update each personnel risk assessment (PRA) at least every seven years after the initial PRA. While SERC_URE2 was migrating its PRA workflow process into a new CIP Version 5 workflow management tool, it discovered an employee who was due to have the seven-year PRA renewal completed 32 days earlier. SERC_URE2 used an outlook calendar entry to remind staff every fourth quarter annually to identify those individuals with upcoming PRA renewal dates. Either the calendar entry expired or SERC_URE2 staff deleted it in error, resulting in a failure to conduct the PRA renewal review. SERC_URE2 conducted an extent-of-condition assessment and identified no additional issues. SERC_URE2 discovered the issue while migrating to a new automated workflow management tool. SERC_URE2’s failure to conduct the seven-year PRA renewal was due to weak internal controls. SERC_URE2 utilized a manual process, which was wholly dependent on a calendar reminder to trigger the PRA renewal. The issue lasted 32 days, from when the SERC_URE2 employee was due to have the seven-year PRA renewal conducted until SERC_URE2 discovered and removed all access rights pending the PRA renewal completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure to renew the PRA could have permitted an individual with disqualifying events to retain access and pose a risk to SERC_URE2 operations or BPS functionality. However, this single employee was a member of SERC_URE2 management who is now, and was prior to this occurrence, in good standing with SERC_URE2. The SERC_URE2 employee at issue had only physical access to the two SERC_URE2 control centers and no electronic access permissions. The seven-year PRA exceeded the renewal deadline by only 32 days. SERC considered SERC_URE2’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) removed authorized physical access on the discovery date; 2) conducted a review of PRA expiration dates of all personnel with authorized physical access; 3) added the PRA renewal review back into Outlook Calendar with no expiration date; and 4) configured a PRA dashboard in the software now being used for CIP compliance tracking. The dashboard graphically shows PRA currency and how many are nearing expiration.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2016016044 | CIP-005-3a | R1; R1.5 | SERC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3 R5.2.2 pursuant to CIP-005-3a R1.5. SERC_URE2 did not identify and approve all individuals with access to shared accounts on the CIP access point firewalls. While updating newly implemented firewalls into a new access tracking and management tool, SERC_URE2 discovered a single employee who had system administrator access to four CIP firewalls via the shared administrator account without approval. Five months earlier, during CIP Version 5 transition activities, SERC_URE2 deployed four new CIP firewalls and configured the systems for administrators to log in using individual domain-authenticated accounts. SERC_URE2 did not approve access to the shared administrator account for the individual that initially setup and configured the firewalls. SERC_URE2 had not formally approved the employee in question as an ESP firewall administrator, thus SERC_URE2 should not have granted the employee shared account access to the firewalls. The root cause of the issue was human performance. SERC_URE2 personnel failed to follow the CIP Version 3 manual change request process. SERC_URE2 was transitioning to CIP Version 5 processes, and change management staff did not think the existing CIP Version 3 processes applied to the firewall administrator’s access permissions. The issue lasted for approximately five months, from when SERC_URE2 first deployed new firewalls into the production environment granted unauthorized personnel with access to the shared administrator account, until SERC_URE2 approved the employee to have access to the CIP firewalls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to identify all individuals with access to shared accounts could have permitted undocumented or potentially unauthorized personnel to gain access to the access points to the Electronic Security Perimeters and made it impossible to know who was using shared accounts and for what purposes. However, the employee was in good standing with SERC_URE2 and was current on cyber security training and personnel risk assessment. SERC_URE2 had approved the employee for shared account access on CIP servers and workstations, and SERC_URE2 considered this employee the subject matter expert on the new CIP firewalls. SERC considered SERC_URE2’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) granted approval for the employee for the role of ESP Firewall Administrator, which includes access to the administrator shared account; 2) enhanced the change control process to review and implement logical access management for new or replaced assets; and 3) provided awareness to staff on the updated change control process.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2016015543 | CIP-004-3a | R3; R3.2 | SERC_URE3 submitted a Self-Report stating it had an issue of CIP-004-3a R3.2. SERC_URE3 identified an instance where it did not update an employee’s personnel risk assessment (PRA) at least every seven years. SERC_URE3 conducted an internal compliance assessment review and discovered it did not update an employee’s PRA within seven years of the last assessment. Approximately three and half months earlier, the employee’s PRA would have been seven years old and SERC_URE3 was required to update. However, SERC_URE3 did not identify the aging PRA and failed to take action. SERC_URE3 has manual procedures to conduct periodic reviews to determine PRAs that expire in the next twelve months, and the procedure requires the initiation of an update as necessary. However, SERC_URE3 staff did not follow the procedure and did not identify the aging PRA. Therefore, SERC_URE3 failed to identify the expired PRA and perform the required assessment update. SERC_URE3 determined the root cause to be human error. SERC_URE3 staff failed to follow the manual procedures to review the users with Critical Cyber Asset (CCA) access, with the date of the last PRA. SERC_URE3 performed an extent of condition and did not discover additional instances. The issue lasted approximately three and half months, from when SERC_URE3 did not perform the PRA update until SERC_URE3 revoked the individual's CCA access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE3’s failure to update PRAs of personnel with physical and/or electronic access elevates the risk of an internal threat. Personnel with such access could have become involved in criminal activity, which would impose hardships, or malevolent activities into the workplace environment. These personnel could cause physical and/or electronic damage to CCAs or Critical Assets thus affecting the BPS. However, SERC_URE3 conducts logging and monitoring of CCAs, as well as physical access to Critical Assets, 24 hour a day, seven days a week. In addition, the employee in question attended annual Cyber Security training and was authorized access. SERC_URE3 performed the updated PRA and it did not identify any issues or concerns. SERC considered SERC_URE3’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE3: 1) removed the employee’s CCA access; 2) performed a PRA update; 3) performed a thorough root cause evaluation; 4) updated the access management operational guide; and 5) provided training on the access management operational guide.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2016015845 | CIP-004-3a | R2; R2.1 | SERC_URE4 submitted a Self-Report stating that it had an issue of CIP-004-3a R2.1. SERC_URE4 failed to ensure that all personnel with access to Critical Cyber Assets (CCAs) had received proper training prior to granting such access. An individual from SERC_URE4 staff escorted a vendor representative into the primary control center to assist in the configuration of software while preparing for CIP Version 6 compliance. SERC_URE4 allowed the vendor to perform the necessary system configuration on the CCA for approximately 30 minutes. The SERC_URE4 escort observed the vendor’s actions the entire time. However, the vendor had not taken training prior to accessing the CCA. SERC_URE4 discovered the issue when another employee within the Physical Security Perimeter observed the vendor entering commands directly to the CCA. The root-cause was human performance. The SERC_URE4 escorting employee did not follow procedures requiring proper electronic access authorization of individuals. SERC_URE4 conducted an extent of condition review and did not discover additional issues. The issue lasted for approximately 30 minutes, from when SERC_URE4 provided the vendor electronic access to the single CCA until the approved escort took over the data entry while the vendor provided instructions only. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4 permitting an unapproved and unauthorized vendor to access a CCA directly could have resulted in unintended modifications, which could pose impacts to local operations or to the BPS. However, the vendor was only able to access a single CCA, a domain controller used to authenticate CCA users, and the duration of the access did not exceed 30 minutes. The vendor did not have direct access to CCAs that are used for SCADA control or monitoring. In addition, the escort, who was present the entire time, monitored all entries and commands. SERC considered SERC_URE4’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE4: 1) provided special training to individuals with electronic access to CCAs. The training covered the incident that occurred and why it was a violation. In addition, the training addressed what should have happened and what did happen once the violation was discovered; and 2) provided awareness to the employees of their responsibilities under this particular CIP standard and that CIP-004-3a does not permit supervised or "escorted" cyber access.
2016-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2016015632 | CIP-006-3c | R5 | SERC_URE5 submitted a Self-Report stating that it had an issue with CIP-005-3a R1.5. SERC_URE5 failed to maintain access control for a Physical Security Perimeter (PSP) dedicated to electronic access control and/or monitoring (EACM) Cyber Assets, which SERC_URE5 believed was required as a protective measure specified in CIP-006-3c R3. SERC later determined that this issue was more appropriately addressed under CIP-006-3c R5 because EACM Cyber Assets resided within an identified PSP, but SERC_URE5 failed to implement controls for monitoring physical access at all access points to the PSP 24 hours a day, 7 days a week. The security console that provides monitoring of the PSP access points received a power failure alarm for a PSP access point. Five minutes later, the security console received a low battery alarm for the same PSP access point. An hour and a half later, the security console received an alarm indicating that all power (primary and battery back-up) had been lost. The power failure resulted in the PSP door failing open for safety reasons, to allow any occupants who may have been inside to exit if needed. However, the alarms did not specify the door had been opened without authorization, they simply indicated power failures. Thus, SERC_URE5 could not identify unauthorized access attempts through the PSP door and would not know to immediately investigate if an unauthorized access attempt occurred. The guard issued a non-emergency repair ticket, instead of an emergency repair order. The security coordinator recognized the issue with the repair order, and changed it to an immediate dispatch. A repair technician arrived at the PSP access point and found the door unsecured. Almost eight hours after the issue began, the IT team initiated human observation, which continued until the repair technician completed the repair by replacing the door controller. SERC_URE5 reviewed the closed-circuit television (CCTV) footage and found that no access had occurred during the issue. The root-cause of the issue was a failure by SERC_URE5 to have configured action alerts associated with this type of equipment failure, which resulted in a failure to respond immediately. SERC_URE5 performed an extent-of-condition review and determined no other similar issues occurred. The issue lasted approximately eight hours, from when SERC_URE5 stopped monitoring the PSP door until SERC_URE5 began human observation to provide immediate review of unauthorized access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A loss of power at the PSP door left the door open, presenting the opportunity for unauthorized personnel to gain access to the control center EACM devices and damage or alter the devices, which could leave SERC_URE5 operators with significantly degraded data. However, SERC_URE5 monitored the PSP access point by a CCTV feed at the guard station and confirmed by reviewing the CCTV footage that no access had occurred through the door in question during the issue. In addition, the PSP contained EACM devices and did not contain any Critical Cyber Assets. Further, the PSP was located in a remote area within a secured building with corporate card reader access and 24 hours per day, seven days per week on site security guards, reducing the likelihood of unauthorized access. SERC_URE5 left the PSP access point unsecured for slightly less than eight hours. No harm is known is have occurred. SERC considered SERC_URE5’s CIP-006-3a R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE5: 1) posted personnel at the IT Firewall Cage to provide access control; 2) replaced the failed intelligent controller; 3) provided email communications to the analysts advising them to use the location communication loss steps outlined in the CIP-006 NERC compliance procedure to address device communication losses; 4) reviewed all PACS action messages for NERC PSPs to ensure that the appropriate steps and priority are outlined for response; 5) updated the action messages as necessary; 6) developed a procedure for managing action messages within the PACS; 7) revised the NERC CIP-006 compliance procedure to address device power and communication loss; and, 8) conducted training on the procedural changes.
2016-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015212 | CIP-007-3a | R1 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-007-3a R1 because an SPPRE_URE1 employee connected his corporate laptop to an Electronic Security Perimeter (ESP) without first testing the laptop as a “new Cyber Asset” to ensure it did not adversely affect existing cyber security controls. Specifically, a SPPRE_URE1 employee installed a new remote terminal unit (RTU) at a substation and connected it to the ESP. Transmission Control Protocol/Internet Protocol (TCP/IP) is the only available method to configure the RTU for network communication protocol associated with SPPRE_URE1’s SCADA system. As a result, the SPPRE_URE1 employee connected to the RTU switch, accessed the RTU via the RTU switch by using TCP/IP, and configured the RTU. The root cause of this instance of noncompliance was lack of training, as the employee did not realize that his laptop became an ESP Cyber Asset once he connected it to the RTU switch. The duration of this instance of noncompliance was less than one hour, which occurred on the date the laptop was connected to and disconnected from the RTU switch. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test the laptop that migrated from the corporate network to the substation ESP as a new Cyber Asset presented a risk to the BPS by providing the potential for malware to be introduced onto SPPRE_URE1’s ESP network, which potentially could have resulted in the loss of sensitive data, corruption of data, or manipulation of applications or data. SPPRE_URE1 attested to the following mitigating factors. This was an isolated incident, which lasted less than an hour. SPPRE_URE1’s ESP network is configured to prevent station-to-station communication; therefore, based on SPPRE_URE1 network rules, even had the laptop been infected, any potential compromise to Cyber Assets would have been isolated at the substation ESP where the laptop connected to the RTU switch. The laptop was never re-purposed, was under the control of vetted personnel while outside the subject ESPs, and SPPRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptop from being compromised. Additionally, the laptop used to configure the RTU utilizes a specific operating system. The only other computer in the substation that utilizes the specific operating system is the substation data repository (SDR) computer, which is used to monitor recorded events, i.e., switch opened/closed. Therefore, even had the laptop been infected, any potential risk of compromise most likely would have been limited to the SDR computer. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) removed the laptop from the substation ESP; 2) revised its procedure to include configuration of newer versions of RTUs; and 3) trained all affected personnel on the revised procedure. SPP RE has verified the completion of all mitigation activity.
2016-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015915 | CIP-006-3c | R2; R2.2 | TRE_URE1 submitted a self-log stating that it had an issue with CIP-007-3a R5. Texas RE subsequently determined that this instance of noncompliance pertains to CIP-006-3c R2 rather than CIP-007-3a R5 because the server at issue is a Cyber Asset that authorizes and/or logs access to a Physical Security Perimeter. Under this Standard, such Cyber Assets must satisfy the access authorization requirements set forth in CIP-007-3. As such, TRE_URE1 had an issue under CIP-006-3c R2.2 because TRE_URE1 did not limit access to the Cyber Asset in question solely to users with authorized access to it. Information Technology (IT) personnel identified an issue with a backup server which could have potentially resulted in a data loss. To address the issue, an IT administrator granted access to another member of the IT infrastructure group without following TRE_URE1’s required access authorization process for granting access to the applicable server account. The root cause of the issue was an inadequate system for obtaining access authorizations during emergency situations. Specifically, TRE_URE1 had no explicit process for granting access to the server in question during situations requiring immediate access. TRE_URE1 had an issue with CIP-006-3c R2 for two days, from when the IT infrastructure member obtained access to the single server at issue without the required access authorization approvals until TRE_URE1 granted the IT infrastructure member authorization to the server at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the IT infrastructure member had a current background check and completed all required NERC CIP training when the issue occurred. Second, TRE_URE1 stated that the IT infrastructure employee is a member of the appropriate infrastructure group requiring access to the server at issue. Third, TRE_URE1 detected the issue through a daily exception report and resolved the noncompliance within two days by granting access to the IT infrastructure member. Finally, the IT administrator responsible for initially providing unauthorized access was in fact authorized to grant such access to the single server at issue here, but did not follow TRE_URE1’s access authorization process for doing so. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) provided the IT infrastructure member with appropriate access authorization to the single server at issue; 2) added a message banner to the applicable server login screen indicating that new access accounts should not be created without an approved request in TRE_URE1’s electronic access request system; 3) created a process in TRE_URE1’s electronic access request system for requesting access to the root password manager application applicable to the server at issue; 4) created a process to address CIP Exceptional Circumstances under the new CIP version 5 Standards, including the applicability of CIP Exceptional Circumstances to access authorizations; and 5) provided video training that addresses the definition of a CIP Exceptional Circumstance. Texas RE has verified the completion of all mitigation activity.
2016-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016015919 | CIP-006-3c | R2; R2.2 | TRE_URE2 submitted a self-log stating that it had an issue with CIP-007-3a R5. Texas RE subsequently determined that this instance of noncompliance pertains to CIP-006-3c R2 rather than CIP-007-3a R5 because the server at issue is a Cyber Asset that authorizes and/or logs access to a Physical Security Perimeter. Under this Standard, such Cyber Assets must satisfy the access authorization requirements set forth in CIP-007-3. As such, TRE_URE2 had an issue under CIP-006-3c R2.2 because TRE_URE2 did not limit access to the Cyber Asset in question solely to users with authorized access to it. Information Technology (IT) personnel identified an issue with a backup server which could have potentially resulted in a data loss. To address the issue, an IT administrator granted access to another member of the IT infrastructure group without following TRE_URE2’s required access authorization process for granting access to the applicable server account. The root cause of the issue was an inadequate system for obtaining access authorizations during emergency situations. Specifically, TRE_URE2 had no explicit process for granting access to the server in question during situations requiring immediate access. TRE_URE2 had an issue with CIP-006-3c R2 for two days, from when the IT infrastructure member obtained access to the single server at issue without the required access authorization approvals until TRE_URE2 granted the IT infrastructure member authorization to the server at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the IT infrastructure member had a current background check and completed all required NERC CIP training when the issue occurred. Second, TRE_URE2 stated that the IT infrastructure employee is a member of the appropriate infrastructure group requiring access to the server at issue. Third, TRE_URE2 detected the issue through a daily exception report and resolved the noncompliance within two days by granting access to the IT infrastructure member. Finally, the IT administrator responsible for initially providing unauthorized access was in fact authorized to grant such access to the single server at issue here, but did not follow TRE_URE2’s access authorization process for doing so. No harm is known to have occurred. | To mitigate this issue, TRE_URE2: 1) provided the IT infrastructure member with appropriate access authorization to the single server at issue; 2) added a message banner to the applicable server login screen indicating that new access accounts should not be created without an approved request in TRE_URE2’s electronic access request system; 3) created a process in TRE_URE2’s electronic access request system for requesting access to the root password manager application applicable to the server at issue; 4) created a process to address CIP Exceptional Circumstances under the new CIP version 5 Standards, including the applicability of CIP Exceptional Circumstances to access authorizations; and 5) provided video training that addresses the definition of a CIP Exceptional Circumstance. Texas RE has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015599 | CIP-004-3a | R3 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R3. Specifically, WECC_URE1 reported that during WECC_URE1’s monthly access review process, WECC_URE1 identified two personnel who had unescorted physical access to a Physical Security Perimeter (PSP) without having a current Personnel Risk Assessment (PRA). WECC_URE1’s process for initiating the PRA renewal, and for disabling badge access, was a manual process which should be undertaken after a single manual notification or revocation notification had been received. The two individuals were sent email notifications to begin the PRA process, however the emails were not acted upon, and therefore completion of the PRA did not move forward. Additionally, access is not automatically revoked if the appropriate requirements are not met. WECC_URE1 remediated the issue by revoking access. This issue began when two WECC_URE1 personnel had access to a PSP without having a current PRA, and ended when WECC_URE1 removed their access to the PSP. The duration of the noncompliance was 17 days. The root cause was delay in time caused less than adequate actions. The two individuals who were sent email notifications to begin the PRA process did not recognize the emails and therefore they did not move forward with completing the PRAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance WECC_URE1 failed to update a PRA for two personnel who had unescorted physical access to one PSP at a control center containing SCADA devices, classified as Critical Cyber Assets. Failing to timely update and review a PRA could cause WECC_URE1 to miss changes in an individual’s criminal history, an element of potential risk for safety and security which could impact the Bulk Electric System. However, WECC_URE1 had compensating controls in place at the time the issue occurred. Specifically, the two personnel had completed CIP training and were approved to have access to the one PSP. Additionally, an initial PRA had been performed on the two individuals. WECC_URE1 verified that the two personnel had not accessed the PSP during the 17 days of noncompliance. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WECC_URE1 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue WECC_URE1: 1) implemented a preventative control to automatically expire the appropriate access if the PRA process is not satisfied by the PRA expiration date; 2) incorporated additional email notifications as part of the PRA process; and 3) updated PRA procedure to clarify roles and responsibilities. WECC verified completion of WECC_URE1's mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015325 | CIP-002-3 | R4 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-002-3 R4. Specifically, WECC_URE2 reported that during an internal review of WECC_URE2’s procedures that supported NERC compliance, it discovered that WECC_URE2 failed to document the required annual approval of the Risk-Based Assessment Methodology (RBAM) for one calendar. The last documented approval of the methodology was the previous year. The root cause of this issue was a misinterpretation of the “NERC Year” 15 month requirement as WECC_URE2 was preparing to transition to CIP Version 5. This issue began when WECC_URE2 failed to review its list of Critical Assets at least annually, and ended when WECC_URE2 declared its intent to transition to CIP Version 5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to document the required annual approval of its RBAM in accordance with CIP-002-3 R4. Failure to annually review and approve the RBAM could potentially result in an RBAM that may not accurately identify facilities, Critical Assets, or Critical Cyber Assets. If facilities and devices are not correctly identified, it could lead to insufficient CIP protections for the facilities and devices that control the entity's transmission load. If there are insufficient CIP protections, someone could potentially trip breakers or drop load. However, WECC_URE2 had reviewed and approved the null lists of Critical Assets, and Critical Cyber Assets. Additionally, there was no loss of any BES elements, and no Cyber Security Incidents occurred. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. WECC_URE2 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE2: 1) transitioned to CIP Version 5, which rendered its RBAM obsolete. WECC verified completion of WECC_URE2's mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016015721 | CIP-005-3a | R1 | WECC_URE3 submitted a Self-Report stating that it had an issue with CIP-005-3a R1. Specifically, WECC_URE3 reported that WECC_URE3 conducted a CIP-007-3 R4 test and installation, pursuant to its procedure. An EACM device was selected as the test asset during this procedure. This Electronic Access Control and Monitoring (EACM) device was located at a backup control center facility within the Physical Security Perimeter (PSP), but external to the Electronic Security Perimeter (ESP). Due to a mistaken configuration in the server, both the signature and engine updates in the evaluation group were installed onto the EACM device for testing. This was the only CIP EACM device that received the engine update. This issue had not previously occurred because this was the first time an engine update happened at the same time as the signature update. The root cause of this issue was a mistaken configuration in the server. Therefore, WECC_URE3 did not provide the protections of CIP-007-3 R1 when it failed to test an antivirus engine update before it installed a non-security related patch to an EACM device. After being released by the vendor, the patch was automatically downloaded, loaded to a WECC_URE3 server, and marked for evaluation. The issue started when WECC_URE3 implemented the update without performing the required testing and ended when the EACM device was rolled back to the previously tested and approved engine. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to test one significant change to an antivirus product before the implementation to an EACM device. Failure to test a significant change could allow potentially harmful software onto a device which controls logical access into an ESP containing WECC_URE3’s Critical Cyber Assets (CCAs). However, in this case, the patch was quickly removed from the device. The device was also part of a redundant pair, so if this device was not functional, the other device could control access into the ESP. Additionally, all CCAs inside the ESP continued to have full antivirus and malware protection for the duration of this issue. For these reasons, and because no harm is known to have occurred, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System. | To mitigate this issue, WECC_URE3: 1) rolled back the EACM device to the previously tested and approved engine; 2) changed the server configuration into separate containers for antivirus signatures and engines; and 3) revised procedures to test signatures on non-CIP protected assets. past tense activity. WECC has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2016015550 | CIP-004-3a | R3 | WECC_URE4 submitted a Self-Report stating it had a possible issue of noncompliance with CIP-004-3a R3. Specifically, WECC_URE4 reported it did not have updated Personnel Risk Assessments (PRAs) for two WECC_URE4 employees within the required period of seven years after the initial PRAs were conducted. In response to WECC Data Requests, and a telephone conference call, WECC_URE4 confirmed to WECC that the actual number of PRA’s that had expired was five. This issue was discovered during the quarterly review of WECC_URE4’s list of individuals with authorized cyber and authorized unescorted physical access to Cyber Assets. This issue began the day after the first PRA expired, and ended when the last PRA was updated, for a total of 150 days. The root cause of this issue was WECC_URE4’s less than adequate compliance process; due to insufficient documentation of processes for managing its PRA updates and the inexperience of WECC_URE4’s new HR personnel overseeing its PRA process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to update PRA’s for five employees/contractors with access to CCA devices, which could potentially result in an individual having an unknown criminal history since their previous PRA was performed. By failing to perform timely PRAs, WECC_URE4 could have permitted access to improperly vetted individuals with unknown malicious intentions. However, WECC_URE4’s Cyber Assets are protected according to the applicable NERC Standards and Requirements; which include monitoring and alerting of unauthorized physical and logical access attempts. The individuals in scope were in good standing with WECC_URE4; there were no changes in access rights between the time the PRAs expired and when they were updated; had completed NERC CIP training; and were approved to have CIP access. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. WECC_URE4 does not have previous violations of this Standard and requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE4: 1) Upgraded its identity and access management system with functionality that will automatically alert Human Resources 90 days before the expiration of a PRA. This control will serve as a double check to its yearly renewal list and a reminder to send the renewal request to the employee. The upgrade will also automatically initiate the process for revocation of access 15 days before the PRA expiration date if no action has been taken; 2) Modified its PRA renewal process by assigning and training other HR employees as backups for the PRA renewal process; and 3) Drafted and implemented a PRA work instruction document to train additional HR personnel on the PRA renewal process
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015015149 | CIP-004-3a | R4 | WECC_URE5 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R4. Specifically, WECC_URE5 reported that it failed to update its list of personnel with authorized electronic and/or physical access to Critical Cyber Assets (CCAs) within seven calendar days for three employees who retired. These three individuals, through automated means, had their user IDs and Identification Badges (front-end authentication) disabled/removed within 24 hours. However, because a separation code was missing from WECC_URE5's system, an automated notification was not sent to the task workers to remove these retirees from the backend systems, and therefore, work orders were not generated to update the list of personnel with access to CCAs. Subsequent to WECC_URE5’s original self-report submittal, WECC_URE5 self-reported a second possible issue of noncompliance with CIP-004-3a R4. Specifically, WECC_URE5 reported that it failed to remove unescorted physical access to PSPs within seven calendar days for one contractor who no longer required said access and failed to update its list of personnel with authorized electronic and/or unescorted physical access to CCAs. WECC_URE5’s security office received, through interoffice mail, an ID badge for a security officer that had unescorted physical access to PSPs. That same day, security called the vendor, to inquire as to the reason the ID badge had been relinquished. The vendor confirmed the officer had resigned. The first issue began when WECC_URE5 failed to update its list of personnel within a timely manner for three employees who retired from WECC_URE5; was discovered during the course of monitoring revocation statuses; and ended when WECC_URE5 completed the manual removal of CIP access for the three retires from all backend system. The second issue began when WECC_URE5 failed to update its list of personnel and remove CIP access within a timely manner for once contractor who no longer required access; was discovered when WECC_URE5 received the ID badge belonging to the contractor; and ended when WECC_URE5 disabled the badge. The root cause of the first issue was insufficient configuration and testing WECC_URE5's system prior to implementation. The system is not a CIP Asset. The root cause of the second issue was the vendor not alerting WECC_URE5's, within 24 hours, as stated in their service agreement, of a termination of one of its employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In both instances, WECC_URE5 failed to update its list of personnel with electronic and/or unescorted physical access to CCAs within seven days for individuals who no longer required such access. Failure to maintain a list of personnel with electronic and/or physical access to CCAs could allow unauthorized access to the CCAs to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the BES, thereby potentially negatively impacting the BES. However, WECC_URE5 implemented strong preventative controls. Specifically, WECC_URE5 had several layers of physical access controls in place to prevent unauthorized physical access to its CCAs. In addition, logging was enabled both for electronic and physical access, which would generate alerts in the case of inappropriate access attempts. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) updated its system by adding the missing retirement code; 2) tested the update prior to placing it into production; 3) met with its vendor to review the terms of their master service agreement; and 4) implemented a process for receiving a daily report form its vendor for all separations, even if it is a null list.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2015014902 | CIP-007-3a | R3 | WECC_URE6 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R3. WECC_URE6 reported that it did not assess security patches for applicability within 30 days of availability. Specifically, during an internal compliance review, WECC_URE6 discovered that between for approximately 4 years, WECC_URE6 should have assessed for applicability patches, of which about 2% were determined to be applicable security patches. The missed assessments ranged from 31 days to 69 days from the release of the security patch. This issue applies to assessing security patches, not applying them. The applicable security patches had subsequently been applied to the devices in scope. The root cause of this issue was WECC_URE6 personnel not prescriptively following 30-day reminders to assess available security patches. This issue began when the first available security patch was not assessed for applicability, and ended when WECC_URE6 completed its assessment of the available security patches. The maximum amount of time the security patches were not assessed was 69 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance WECC_URE6 failed to assess 2,082 patches for applicability, of which 40 were applicable security patches, within 30 days on applicable devices. Failure to promptly assess security patches for applicability could allow vulnerabilities on devices to remain unnoticed and unchecked for longer periods. This could allow the vulnerabilities to be exploited by malicious personnel, potentially compromising the Cyber Assets essential to the operation of Critical Assets. However, WECC_URE6 implemented preventive controls. The devices in scope were within both an electronic and physical security perimeter, reducing the attack vectors available to vulnerable cyber devices. The security patches were assessed within 69 days, thus limiting the duration of unknown exposure to the devices. WECC_URE6’s EMS network is segmented from its corporate environment, and it is not internet facing. Additionally, WECC_URE6 had implemented a firewall that performs both intrusion and anti-virus detection. Upon detection of a cyber security event, the firewall issues an email notification to EMS Support personnel. WECC_URE6 also implemented detective controls by deploying intrustion detection software that provided near real-time analysis of cyber security events involving the access points to the ESP. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WECC considered WECC_URE6 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE6: 1) developed and implemented a patch management oversight procedure used to verify that all security patches have been assessed for applicability and to identify deployment dates. 2) procured services from a 3rd party vendor that will provide EMS support personnel with a weekly report that contains all vulnerabilities that are applicable to EMS support Cyber Assets and additional details utilized in the evaluation and determination of applicability of each security patch. 3) WECC_URE6 changed its program to directly track and assess security patches only. WECC verified completion of WECC_URE6’s mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014014045 | CIP-007-3a | R4 | WECC_URE7 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-3a R4. Specifically, WECC_URE7 failed to file Technical Feasibility Exceptions (TFEs) for five devices that do not technically support Anti-Virus and malware prevention tools. WECC determined that this issue began when WECC_URE7 failed to submit the required TFEs and ended when WECC_URE7 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE7 failed to file Technical Feasibility Exceptions (TFEs) for five devices. This could potentially result in these devices having undocumented or insufficient compensating measures to address the lack of malware prevention tools. This could lead to an increased exposure of the devices to a virus or other malware that, once introduced, could spread to other devices within the ESP. However, WECC_URE7 implemented strong preventive controls to prevent the malware. Specifically, the devices in scope are naturally hardened and thus inherently resilient to virus and other malware. This drastically reduces the likelihood of malicious software being introduced into the production environment from one of the 5 devices in scope. No harm is known to have occurred. | To mitigate this issue, WECC_URE7 created and submitted the appropriate TFE documentation. WECC has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2015014675 | CIP-007-1 | R5 | WECC_URE8 submitted a Self-Certification stating that it was in violation of CIP-007-1 R3. In the Self-Certification, WECC_URE8 reported that it failed to maintain an audit trail of shared account use, specifically knowing who is accessing the shared account, as required by CIP-007 R5.2.3. The issue was discovered during a mock audit to prepare for WECC_URE8's audit. WECC_URE8 knew which device was being used, which shared account was being used, and what time it was being used, but did not know who was using the account. The WECC SME issued a data request to receive additional information. There were devices in the SCADA ESPs for which the audit trail was missing. WECC determined that WECC_URE8 is in violation of CIP-007 R5 for failing to maintain an audit trail of shared account use. The cause was a lack of understanding of compliance obligation. This issue started when the Standard became mandatory and enforceable for WECC_URE8 and ended on Mitigation Plan completion. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE8 failed to maintain an audit trail of shared account use for devices. These devices are located at four facilities and are in the ESP for the SCADA system. Failing to have an accurate audit trail of shared account use could lead to undetected unauthorized use of the shared accounts. Because WECC_URE8 was not maintaining an audit trail of shared account use, it might not have sufficient information to determine the cause unauthorized use and may not discover that a malicious person has entered its network and has access to the network. This could delay recovery from the issue and could potentially lead to other issues affecting the BES. WECC_URE8 implemented strong preventive controls to prevent the unauthorized use. Specifically, WECC_URE8 ensures that only those ports and services necessary for operations are enabled, disabling all other ports. This could limit the attack threshold that could be used by an attacker and prevent certain traffic from entering WECC_URE8's network. WECC_URE8 also uses antivirus and other anti-malware software that looks for known attack signatures and could prevent an attempted malware attack. WECC_URE8 also implemented strong detective controls to detect unauthorized use. Specifically, as mentioned above, WECC_URE8 only enables ports and services that are necessary for operations. For those ports that are enabled, WECC_URE8 tracks configuration changes to the SCADA system using automated software, which could allow untracked changes to be identified. WECC_URE8 also uses other tools to monitor system events related to cyber security. With this monitoring and alerting, WECC_URE8 could know if an unauthorized person is in its network. As further compensation, WECC_URE8 implemented good compensating controls. Specifically, WECC_URE8 was maintaining an audit trail of which shared account was used, on which device the account was used, and the time it was used, as well as a list of those with access to the shared accounts; the failure was that the audit trail did not contain information as to who was using the shared account each time one was used. With this information, incomplete as it is, if the above scenario occurred, WECC_URE8 could have a starting point in its investigation of what caused the issue (i.e., the list of people with access to the shared accounts), which could reduce the time it takes to discover that a malicious person is on WECC_URE8's network. WECC_URE8 also ensures that the password of each shared account is changed at least once a year. For an extended attack by a malicious person, more than one password may need to be captured to affect WECC_URE8's load, which may increase the likelihood of WECC_URE8 discovering an unauthorized person has access to its network. No harm is known to have occurred. | To mitigate this issue WECC_URE8 is transitioning to CIP v5 and the obligation to keep an audit trail of shared account use does not exist in CIP v5. WECC has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2015014927 | CIP-006-3c | R6 | WECC_URE8 submitted a Self-Report stating that it had an issue of noncompliance with CIP-006-3c R6. Specifically, WECC_URE8 failed to log sufficient information to uniquely identify individuals and the time of access for visitors, as required by CIP-006-3c R6. WECC_URE8 discovered gaps in the manual logs at five locations. Following further discussion, WECC determined that WECC_URE8 failed to log the escort name and the sign-out dates and times of visitors within Physical Security Perimeters (PSPs) for several locations, resulting in gaps in visitor logs. The root cause was a lack of awareness and training about the procedures to properly fill-out PSP manual logs for personnel responsible for escorting visitors into a PSP. This issue started when visitors first left a PSP and failed to adequately log the exit, and ended when WECC_URE8 completed its mitigation activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE8 failed to log sufficient information to uniquely identify individuals and the time of access for visitors. However, the manual logs were only used for individuals with unescorted access. Additionally, in many cases, sign-in information captured a name and date, with only the sign-out date missing. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE8 amended the procedures to include checking the logbooks for gaps and provided training through security awareness bulletins, employee meetings, and annual training requirements. WECC has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2015014928 | CIP-006-3c | R4 | WECC_URE8 submitted a Self-Report stating that it had an issue of noncompliance with CIP-006-3c R4. Specifically, WECC_URE8 failed to implement the operations and procedural controls to manage physical access at all access points to the Physical Security Perimeter (PSP), as required by CIP-006-3c R4. The WECC_URE8 security operations center (SOC) received a Physical Access Control System (PACS) forced-door alarm. WECC_URE8 investigated the issue further and discovered that the cleaning contractor at a substation acquired a hard key to the back-up control center (BUCC) and used to the key to gain access to the BUCC to clean. The cleaning contractor was not authorized for physical access to the BUCC. The contractor received the key from the previous cleaning contractor via the contracting officer. There were Critical Cyber Assets (CCAs) in the BUCC located at the substation. This issue started when a contactor entered a PSP using a hard key that was not issued to them, and ended when the hard key was retrieved from the contractor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE8 failed to implement the operations and procedural controls to manage physical access at all access points to the PSP. Failing to properly implement the physical access controls increases the risk that the CCAs and other devices within the PSP become compromised. However, the governing contract with the individual in scope has general provisions requiring a background check before work can begin. PACS also detected a forced-door alarm, triggering an immediate response, once the contractor entered the PSP. Additionally, the cyber assets within the Electronic Security Perimeter (ESP) at the BUCC are secured with CIP controls, including account/password management, security event monitoring, patching, malware prevention, change management, restricted ports/services, incident response procedures, and recovery procedures. Logins are required to access cyber assets within the ESP. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE8: 1) retrieved the access key that was used in error; 2) counseled the contract employee on procedures for CIP access; 3) re-keyed locks at all substations; and 4) trained all contractors on key procedures. WECC has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC2015015292 | CIP-004-3a | R4 | WECC_URE9 submitted a Self-Report stating that it was in violation of CIP 004 R4. Specifically, WECC_URE9 failed to revoke access to Critical Cyber Assets within seven calendar days for one individual who no longer required such access, as required by CIP 004 R4.2. The individual in scope had physical access to substations. WECC_URE9 did collect this individual’s badge on the day that the individual no longer needed access. The cause was a lack of training and understanding of roles and responsibilities in the suspend/terminate process. WECC determined that this violation began eight days after the individual no longer required such access and ended when WECC_URE9 revoked all access for the individual. | In this instance, WECC_URE9 failed to revoke access within seven days of one employee no longer needing access. This could result in an unauthorized person having access to restricted areas, increasing the risk of potential harm to the CCA. WECC_URE9 implemented strong preventative controls to prevent unauthorized access. Specifically, WECC_URE9 collected the individual’s badge. This would prevent the individual from gaining access to the CCA. WECC_URE9 also had good detective controls. Specifically, WECC_URE9 had physical and logical logging at its PSPs and CCA. Thus, if the individual tried to gain unauthorized logical access to CCAs, WECC_URE9 could have detected it and been able to take appropriate actions. WECC_URE9 did a review of its physical and logical logs and confirmed the employee never attempted to gain access to CCA. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the bulk power system. | To mitigate this issue, WECC_URE9: 1) Revoked access for the individual involved; and 2) Trained its supervisors and/or process owners to ensure the execution of the existing workflow is followed properly. WECC has verified the completion of all mitigation activity.
2016-09-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015545 | CIP-004-3a | R2; R2.1 | MRO_URE1 submitted a Self-Log stating that it had an issue of CIP-004-3a R2. Specifically, MRO_URE1 authorized access to an employee from a local distribution company to two substations prior to that employee having completed CIP training. The employee had completed a general "Security Awareness Training" that did not meet all required elements of MRO_URE1's Cyber Security training and awareness program. MRO_URE1 discovered this issue and immediately revoked that employee's access. This issue resulted from an upgrade to MRO_URE1's learning management system (LMS) that changed the display of the available courses which led the employee to incorrectly believe that he had taken the required training. Additionally, MRO_URE1's failure to verify that the appropriate training was conducted prior to granting access contributed to the issue. The issue began when the employee was granted access, and ended when MRO_URE1 revoked the access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is minimal as the employee did not actually access the two substations. Additionally, while the employee's training did not meet the requirements of the standard, the employee did receive some training on security related issues. Finally, the employee was a long term employee who had an up to date Personal Risk Assessment (PRA). No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-004-3a R2. | To mitigate this issue, MRO_URE1: 1) revoked the employee's access until the employee completed the required training; 2) performed an "Extent of Condition Analysis" to confirm that this was the only instance of noncompliance caused by confusion with the LMS system; 3) trained Physical Security staff to perform quality checks related to training course verification; and 4) MRO_URE1 combined its "General Security Practices" training course with its "CIP Cyber Security Awareness" training course. MRO verified that mitigating activities were complete.
2016-09-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015619 | CIP-004-3a | R3 | MRO_URE1 submitted a Self-Log stating that it had an issue of CIP-004-3a R3. Specifically, MRO_URE1 granted authorized access to an employee of a local distribution company (LDC) without updating a Personnel Risk Assessment (PRA) conducted in the past that had expired under the requirement of the Standard. MRO_URE1 suspended the employee's access after discovery. The cause of this issue was that the LDC employee had the same name as another LDC employee that had an updated PRA, and MRO_URE1 did not independently verify whether this LDC employee had a current PRA or not. The issue began when the employee was granted access, and ended approximately six weeks later when MRO_URE1 revoked the access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An employee that has an expired PRA is less of a risk than an employee who has never had a PRA conducted. Further, MRO_URE1 did an analysis and confirmed that this employee was the only one with this issue. Finally, MRO_URE1 was able to self-detect this noncompliance which is a strong indication of active internal controls. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-004-3a R3. | To mitigate this issue, MRO_URE1: 1) revoked the employee's access until the employee had an up to date PRA; 2) performed an "Extent of Condition Analysis" to confirm that this was the only instance of noncompliance caused by duplicate names; and 3) both the LDC and MRO_URE1 adopted a unique employee ID to their respective PRA programs that would prevent situation from reoccurring. MRO verified that mitigating activities were complete.
2016-09-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015547 | CIP-006-3c | R1 | MRO_URE1 submitted a Self-Log stating that it had an issue of CIP-006-3c R1. Specifically, on October 16, 2014, MRO_URE1 left a contract painter unattended for 21 minutes inside the Physical Security Perimeter (PSP). The contract painter was left alone, when the MRO_URE1 employee responsible for escorting him, left because the MRO_URE1 escort was double booked on his calendar. The issue ended when another MRO_URE1 employee observed the contract painter, called corporate security, and a stand-in escort was provided. The cause of this issue was human error as the MRO_URE1 escort showed inattention to scheduling detail and poor judgment in leaving the contract painter. The issue began when the MRO_URE1 escort left the painter alone, and ended 21 minutes later when a stand-in escort was secured. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contract painter was left unescorted for a brief period of time (21 minutes). Finally, the contract painter was painting in a conference room and was not working in either the control or server room. No harm is known to have occurred. MRO considered MRO_URE1's CIP-006-3c R1 compliance history in determining the disposition track. MRO_URE1’s relevant prior noncompliance with CIP-006-3c R1 includes CIP-006-1 R1.8. MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The prior noncompliance involved MRO_URE1's failure to change passwords. MRO determined that Compliance Exception treatment was still appropriate because the current issue was not caused by any failure to mitigate the prior noncompliance and because the current issue does not involve password issues. | To mitigate this issue, MRO_URE1: 1) provided a stand-in escort for the contract painter; and 2) reinforced the "Escorted Access" procedures with the employee that abandoned the escort. MRO verified that mitigating activities were complete.
2016-09-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2015015436 | CIP-004-3 | R4 | MRO_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3 R4. Specifically, MRO_URE2 reported that a retired user had not been removed from the CIP domain within seven days of the individual's retirement. The individual had physical and logical access rights. The physical access rights were promptly terminated, but the individual continued to have logical access rights. The cause of this issue was weak processes for reviewing user access rights. The issue began on when MRO_URE2 failed to remove access within seven (7) days, and ended when the user account was deleted from the CIP domain. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because the user was not authorized for remote access and had his physical access timely revoked, he would not have been able to use the unrevoked logical access. Additionally, the user retired and was not terminated for cause. Further, the user's account was locked out after 90 days when the password was not changed. Finally, MRO_URE2 performed a comprehensive review and determined that the noncompliance was limited to this user. No harm is known to have occurred. This is MRO_URE2's first issue of noncompliance with CIP-004-3 R4. | To mitigate this issue, MRO_URE2: 1) removed the user from the CIP domain; 2) reviewed all security logs on the CIP domain server to confirm the user had no unauthorized access; 3) performed a comprehensive review of all users to confirm that no similar noncompliance occurred; 4) updated its procedure for the quarterly review, including instructions that are designed to find errors between authorization and actual accounts; and 5) further updated its procedure in preparation for the transition to CIP Version 5.
2016-09-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2015015172 | CIP-004-3 | R4 | MRO_URE3 submitted a Self-Report stating that it had an issue with CIP-004-3 R4. Subsequently, MRO_URE3 submitted a Self-Report stating that it had a second issue with CIP-004-3 R4. In the first issue MRO_URE3 discovered during a quarterly review that an employee, who was approved for unescorted physical access within the Control Center's Physical Security Perimeter (PSP), was not on the Control Center's unescorted physical access list. This employee was the Communication Director and rarely came to the Control Center. For the second issue, while performing a quarterly review, MRO_URE3 discovered that the previous quarter's personnel list with access to Critical Cyber Assets was not reviewed by the CIP Senior Manager or delegate. The cause for the first issue was a lack of verification tools or procedures that would have more promptly identified the discrepancy between the approved list and the access list; the cause of the second issue was a lack of automated controls, such as reminders to complete the quarterly reviews. The first issue began when the employee's name was not added to the access list within seven days, and ended when the employee was added to the access list; the second issue began when the CIP Senior Manager or delegate failed to review the list in the first quarter and ended when the second quarter review was conducted. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the first issue, the employee was approved for physical access, but was not listed. Additionally, the risk was reduced because the noncompliance was limited to a single employee, who did not regularly work at the Control Center, and who did not have electronic access rights. Regarding the second issue, the duration of the noncompliance was relatively short (69 days) and MRO_URE3 was able to provide reasonable assurance that timely quarterly reviews were conducted in the preceding quarters. Additionally, MRO_URE3 conducted a comprehensive review and determined that no removals from an access list were missed due to the noncompliance. Finally, both issues were self-reported which is a strong indication of detective controls. No harm is known to have occurred. | To mitigate this issue, MRO_URE3: 1) added the employee to the Control Center's list for unescorted physical access to mitigate the first issue; 2) implemented a new enterprise wide access management program with access management and credential enforcement tools to prevent reoccurrence of the first issue; 3) conducted the second quarter review to mitigate the second issue; 4) conducted a thorough review to determine if any removals were missed due to the second issue; and 5) added and configured quarterly automated review reminders in its calendar program to provide escalations until the review is complete to prevent reoccurrence of the second issue.
2016-09-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015758 | CIP-002-3 | R4. | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-3 R4. The CIP senior manager or delegate did not sign the risk assessment and its results for one year. The plant engaged a third-party consultant to conduct a compliance assessment and best practices review of NERC Standards. Staff turnover at the plant contributed to the tasks not being completed in a timely manner. Over an 18-month period, NPCC_URE1 saw several senior staff members leave positions at the plant, including a plant manager and a compliance coordinator. The annual risk assessment process was not captured in the plant's maintenance management system, thus the assessment relied on people versus process to ensure its completion. The issue started the first day after the conclusion of NPCC_URE1's defined calendar year and ended when NPCC_URE1's CIP manager signed the risk assessment and results. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 is a small entity with less than 200 MW of generation. During a past audit, NPCC auditors reviewed NPCC_URE1’s use of its risk-based assessment methodology to its assets for the audit period. The methodology was applied and it was determined that the assets are not critical to reliable operation of the Bulk Electric System. The current risk assessment, prepared and signed as a result of the mitigation activity, found no new critical assets or Critical Cyber Assets. Throughout the duration of the noncompliance, the null list has remained unchanged. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1. Reviewed and signed the risk assessment; and 2. Developed a standing work order in their work management system. This will ensure the appropriate personnel are automatically notified to compete and sign the annual CIP risk assessment. NPCC has verified the completion of all mitigation activity.
2016-09-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015757 | CIP-002-3 | R2. | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-3 R2. NPCC_URE1 did not review their risk assessment for one year. The plant engaged a third-party consultant to conduct a compliance assessment and best practices review of NERC standards. Staff turnover at the plant contributed to the tasks not being completed in a timely manner. Over an 18-month period, NPCC_URE1 saw several senior staff members leave positions at the plant, including a plant manager and a compliance coordinator. The annual risk assessment process was not captured in the plants maintenance management system, thus the assessment relied on people versus process to ensure its completion. The issue started the first day after the conclusion of NPCC_URE1's defined calendar year and ended when NPCC_URE1 reviewed their risk assessment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 is a small entity with less than 200 MW of generation. During a past audit, NPCC auditors reviewed NPCC_URE1’s use of its risk-based assessment methodology to its assets for the audit period. The methodology was applied and it was determined that the assets are not critical to reliable operation of the BES. The current risk assessment, prepared and signed as a result of the mitigation activity, found no new critical assets or Critical Cyber Assets. Throughout the duration of the noncompliance, the null list has remained unchanged. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1. Reviewed and signed the risk assessment; and 2. Developed a standing work order in their work management system. This will ensure the appropriate personnel are automatically notified to compete and sign the annual CIP risk assessment. NPCC has verified the completion of all mitigation activity.
2016-09-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016016056 | CIP-004-3a | R4; R4.2. | NPCC_URE2 submitted a self-log stating that it had an issue with CIP-004-3a R4. An employee with authorized unescorted physical access rights to Critical Cyber Assets (CCAs) transferred departments. The issue started when the employee's physical access rights to CCAs should have been revoked and ended 11 days later when the employee's physical access rights to CCAs were revoked. The supervisor of the employee's past department should have called the security control center to ensure timely access revocation, but in this instance, he relied upon the automatic access revocation process that is initiated by job transfer paperwork. The job transfer paperwork was submitted after the transfer occurred and backdated the effective date. This late physical access revocation incident was discovered during a review of the automatic access revocation log file. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of access records confirmed that the employee did not access substations during the period in question. The employee had up-to-date CIP training and a personnel risk assessment. The employee has worked at NPCC_URE2 for several years and continues to work for NPCC_URE2. The employee's cyber access to CCAs at substations was revoked by changing passwords within the CIP-004-3a R4.2 seven calendar day requirement. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1. Revoked CIP access; 2. Provided a targeted communication to the Supervisor; and 3. Issued a communication to all employees regarding the NERC CIP access revocation process. NPCC has verified the completion of all mitigation activity.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016050 | CIP-004-2 | R4 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-004-2 R4. RFC_URE1 discovered that its system allowed users with a user id from the first domain to log onto the computers in the second domain via their first domain credentials. RFC_URE1 discovered this noncompliance during a meeting where an operator asked whether it was possible to log into a SCADA PC with a first domain user ID and password versus a second domain user account. One of RFC_URE1's IT security specialists checked and verified that this was possible, but only if the user was physically at the terminal (a Critical Cyber Asset (CCA)) for the second domain. The actual start date of the incident is unknown, as the original two-way trust between the first and second domains was in place prior to the effective date of the CIP standards. By default, on a machine, server, or desktop, the NT Authority\Authenticated Users group and NT Authority\Interactive group are installed in the local machine's User group. These two groups are domain system groups and membership in them cannot be controlled. All domain users are automatically placed into these groups. This allows anyone with an active domain account the ability to log onto any system as a User. These are non-privileged accounts that cannot make changes to the system. When a two-way trust is established between domains, the NT Authority\Authenticated Users group and NT\Authority Interactive group automatically includes active users from the trusted domain where a two-way transitive trust has been established. Because the secondary domain authenticates the user, the user is permitted to logon and is given non-privileged access just as users of the primary domain. Access Control Lists (ACLs) on the firewalls do not permit first domain access to map to CCAs on the Transmission SCADA network (TSN). The second domain can map files shares on the outbound side to a single IP address file share and a single site, but not to the whole first network and no external networks. No CIP Protected Information is stored in either of these locations. The root cause related to the pre-existing configuration prior to the CIP standards. Because the NT Authority\Authenticated Users group and NT\Authority Interactive group are both system groups, they cannot be enumerated with traditional or vendor tools. As a result, the first domain user ID’s would never have shown up on user permissions list for the second domain. Also, documentation does not mention these groups, nor indicate how they interact with a domain two-way trust. This issue started the date CIP-004 originally went into effect and ended when RFC_URE1 ended the default two-way trust between the first and second domains which will prevent future users with a user id from the first domain from logging onto the computers in the second domain via their first domain credentials. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, Users could not use credentials to remotely log into the second domain. Rather, in order for a user to access the second domain machines, the user would have to have physical access to a device in the second domain. And, throughout the duration of the incident, no individual had only physical access to the Physical Security Perimeter containing the second domain machines. All approved personnel had both physical and electronic access. As a result, someone with only first domain access would have had to be escorted into the Physical Security Perimeter and log onto a device without the escort's knowledge. Second, the users did not have any heightened access. The user could only sign into the machine with their first domain, and the user would not have been able to run high-level applications (involving SCADA, for example) from the workstation because second domain authentication was required. In addition, there are no other trusts established between the domains. RFC_URE1 approached the regional entities once it discovered this issue in order to effectively disseminate the message to the industry at large because RFC_URE1 was concerned that the vulnerability existed elsewhere without entities' knowledge. As a result, the likelihood of compromise to RFC_URE1's system as a result of this issue is minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 established a group policy on the second domain that restricts the users to the local machine's Users group to only first domain Users and CBA_Anonymous. To verify that this technical resolution worked as intended, users made access attempts after the group policy changes were enforced and replicated throughout the domain. Users attempting to logon with the first domain accounts were denied logon.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015984 | CIP-006-3c | R4 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-006-3c R4. As a result of construction related activities, a man-trap door under construction at RFC_URE2’s control center facility was propped opened and left unattended for a period of time. Specifically, this man-trap door was being installed between a Physical Security Perimeter (PSP) and a non-PSP area, whereby the inner door opened into the PSP area and the outer door opened outward into the non-PSP area. At the time of the incident, the man-trap door was not yet functional. Additional security controls (i.e., key card and PIN access) were being configured before the door could be fully activated and formally used as a PSP access point. Accordingly, the outer door facing the non-PSP area was locked with no way to gain entry from the non-PSP side, but an authorized individual could open the inner door from inside the PSP and exit through the outer door into the non-PSP. Note: The PSP area into which the man-trap opens does not hold any protected NERC CIP devices. In order to gain access to the secured PSP rooms in which NERC CIP devices reside, an individual would need to gain access to the appropriate floor and transgress several additional layers of protections (e.g., badge controlled doors, security alarms, video monitoring, security personnel, etc.) before he/she could enter the secure PSP rooms in which protected NERC CIP devices are located. On this day, 3 contractors needed access to this man-trap area in order to complete construction related activities. The contractors were appropriately logged into a PSP visitor log book upon arrival and were escorted to the outer door non-PSP area by an authorized security guard. Upon realizing that the outer door could not be opened, the authorized security guard rerouted himself and gained access to the PSP through another commissioned access point. The guard then proceeded through the PSP to the man-trap door, where he opened the inner door and propped open the outer door. At this point, the security guard escorted the 3 contractors through the man-trap and into the PSP to perform construction related activities. As a result of the door being opened, an alarm was generated and responded to by security console personnel, who cleared the alarm upon verifying the presence of authorized security personnel and the need for doorway access to facilitate construction activities. The contractors worked within the area for approximately 5 hours using the monitored man-trap doorway to enter and exit the PSP while completing their tasks. When their tasks were complete, the security guard escorted the contractors out of the PSP and properly logged them out of the PSP visitor log book. The security guard did not, however, properly secure the man-trap door as required by RFC_URE2 security procedures. Shortly after the first group of contractors left the man-trap area, another authorized security guard along with 3 additional contractors arrived. These additional contractors were onsite to clean up construction debris left behind by various construction activities taking place throughout the facility. These contractors had been properly logged into the general facility visitor log book upon arrival, but had not been logged into the PSP visitor log book, as it was not anticipated that they would be entering any PSP areas. Upon making their way to the particular area at issue, and because the man-trap doorway was open, it was not clear to the security guard that the room beyond the man-trap doorway was restricted to PSP access. As a result, the security guard escorted the contractors through the man-trap doorway and into the PSP not realizing this to be a secure area requiring PSP visitor logging. Nonetheless, the security guard remained present and monitored the contractors activities at all times. The contractors were in the area for approximately 80 minutes to clean up the debris left behind by the previous group. When they were finished, the security guard escorted the contractors out of the PSP through the man-trap door. Approximately 3.5 hours after the second group left the area, the contractor foreman discovered the open man-trap door and contacted the on-site security officer. The security officer immediately responded, investigated the issue, and secured the door. The root cause for this first issue is ineffective training because the first security guard did not properly secure the man-trap door when he left. Also as a result of construction related activities, a door in the lower level of RFC_URE2’s control center facility leading to the Pit (i.e., the “Pit door”) was inadvertently left open and unguarded for approximately 22 minutes. The Pit is an outdoor area within the secure gated confines of the control center facility, where large construction equipment can be lowered to the underground level of the facility from the outside and then retrieved by personnel on the inside. The Pit door that provides access to the Pit from inside the facility is located off of a hallway in the PSP. Note: The Pit serves a construction related function and is not a typical feature of the facility. On this day, an authorized security guard escorted a construction contractor from within the PSP to the Pit area to perform certain construction related activities. The security guard propped open the door allowing the contractor to exit the PSP hallway and step into the Pit area to perform his tasks while the security guard monitored his activities. After completing his tasks, the contractor re-entered the PSP hallway, and the security guard disengaged the door prop as they walked away from the area. The Pit door, however, did not close completely due to a functional failure in the door closing mechanism at the time of the incident. As a result, the door was left ajar and unattended for approximately 22 minutes before it was discovered by a System Operator, who immediately notified security personnel. In response, security personnel immediately secured the door and reported the incident to the appropriate supervisors for further investigation. The root cause for this second issue is also ineffective training because the security guard did not ensure that the door was properly secured when he left. The issues started when RFC_URE2 was required to comply with CIP-006-3c R4 and ended when RFC_URE2 completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE2’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described, certain aspects of these security protocols were not followed by the personnel involved, but were immediately reported upon their discovery. Specific to the RFC_URE2 control center, the risk harm assessment took into consideration the significant construction activities underway and the project-driven increase in the number of construction and security personnel at the facility as a result. In response to the unique circumstances created by the construction project, RFC_URE2 has hired a significant number of additional new security personnel and contractors, who have undergone requisite training, but are new to the RFC_URE2 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring), and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: Immediate Mitigation: In all instances, the PSP doors were closed and secured. RFC_URE2 supervisors took immediate steps to meet with the security guards involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances. As the security guards are contracted through a security vendor company, these issues were further taken up with the vendor management, who took disciplinary actions, up to and including the suspension of an employee, where determined appropriate. Additional Mitigation: RFC_URE2 has further implemented an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RFC_URE2’s security awareness program, security awareness communications focused on reiterating and reinforcing PSP access protocols company wide. As a more targeted measure, PSP access protocols will be covered in detail at upcoming NERC compliance meetings, including the monthly CIP SME meetings, effectively reinforcing awareness throughout all areas where access issues have arisen. Additionally, the Chief Compliance Officer and other management met with the construction project supervisor to discuss the issues and ways to prevent future occurrence. Additional meetings with the RFC_URE2 legal team and management are scheduled for continued PSP compliance awareness training. Finally, in addition to approaching the issue from an awareness perspective, RFC_URE2 is reviewing its work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training designed to specifically address the occasions when a PSP doorway must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015985 | CIP-006-3c | R4 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-006-3c R4. As a result of construction related activities, a man-trap door under construction at RFC_URE3’s control center facility was propped opened and left unattended for a period of time. Specifically, this man-trap door was being installed between a Physical Security Perimeter (PSP) and a non-PSP area, whereby the inner door opened into the PSP area and the outer door opened outward into the non-PSP area. At the time of the incident, the man-trap door was not yet functional. Additional security controls (i.e., key card and PIN access) were being configured before the door could be fully activated and formally used as a PSP access point. Accordingly, the outer door facing the non-PSP area was locked with no way to gain entry from the non-PSP side, but an authorized individual could open the inner door from inside the PSP and exit through the outer door into the non-PSP. Note: The PSP area into which the man-trap opens does not hold any protected NERC CIP devices. In order to gain access to the secured PSP rooms in which NERC CIP devices reside, an individual would need to gain access to the appropriate floor and transgress several additional layers of protections (e.g., badge controlled doors, security alarms, video monitoring, security personnel, etc.) before he/she could enter the secure PSP rooms in which protected NERC CIP devices are located. On this day, 3 contractors needed access to this man-trap area in order to complete construction related activities. The contractors were appropriately logged into a PSP visitor log book upon arrival and were escorted to the outer door non-PSP area by an authorized security guard. Upon realizing that the outer door could not be opened, the authorized security guard rerouted himself and gained access to the PSP through another commissioned access point. The guard then proceeded through the PSP to the man-trap door, where he opened the inner door and propped open the outer door. At this point, the security guard escorted the 3 contractors through the man-trap and into the PSP to perform construction related activities. As a result of the door being opened, an alarm was generated and responded to by security console personnel, who cleared the alarm upon verifying the presence of authorized security personnel and the need for doorway access to facilitate construction activities. The contractors worked within the area for approximately 5 hours using the monitored man-trap doorway to enter and exit the PSP while completing their tasks. When their tasks were complete, the security guard escorted the contractors out of the PSP and properly logged them out of the PSP visitor log book. The security guard did not, however, properly secure the man-trap door as required by RFC_URE3 security procedures. Shortly after the first group of contractors left the man-trap area, another authorized security guard along with 3 additional contractors arrived. These additional contractors were onsite to clean up construction debris left behind by various construction activities taking place throughout the facility. These contractors had been properly logged into the general facility visitor log book upon arrival, but had not been logged into the PSP visitor log book, as it was not anticipated that they would be entering any PSP areas. Upon making their way to the particular area at issue, and because the man-trap doorway was open, it was not clear to the security guard that the room beyond the man-trap doorway was restricted to PSP access. As a result, the security guard escorted the contractors through the man-trap doorway and into the PSP not realizing this to be a secure area requiring PSP visitor logging. Nonetheless, the security guard remained present and monitored the contractors activities at all times. The contractors were in the area for approximately 80 minutes to clean up the debris left behind by the previous group. When they were finished, the security guard escorted the contractors out of the PSP through the man-trap door. Approximately 3.5 hours after the second group left the area, the contractor foreman discovered the open man-trap door and contacted the on-site security officer. The security officer immediately responded, investigated the issue, and secured the door. The root cause for this first issue is ineffective training because the first security guard did not properly secure the man-trap door when he left. Also as a result of construction related activities, a door in the lower level of RFC_URE3’s control center facility leading to the Pit (i.e., the “Pit door”) was inadvertently left open and unguarded for approximately 22 minutes. The Pit is an outdoor area within the secure gated confines of the control center facility, where large construction equipment can be lowered to the underground level of the facility from the outside and then retrieved by personnel on the inside. The Pit door that provides access to the Pit from inside the facility is located off of a hallway in the PSP. Note: The Pit serves a construction related function and is not a typical feature of the facility. On this day, an authorized security guard escorted a construction contractor from within the PSP to the Pit area to perform certain construction related activities. The security guard propped open the door allowing the contractor to exit the PSP hallway and step into the Pit area to perform his tasks while the security guard monitored his activities. After completing his tasks, the contractor re-entered the PSP hallway, and the security guard disengaged the door prop as they walked away from the area. The Pit door, however, did not close completely due to a functional failure in the door closing mechanism at the time of the incident. As a result, the door was left ajar and unattended for approximately 22 minutes before it was discovered by a System Operator, who immediately notified security personnel. In response, security personnel immediately secured the door and reported the incident to the appropriate supervisors for further investigation. The root cause for this second issue is also ineffective training because the security guard did not ensure that the door was properly secured when he left. The issues started when RFC_URE3 was required to comply with CIP-006-3c R4 and ended when RFC_URE3 completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described, certain aspects of these security protocols were not followed by the personnel involved, but were immediately reported upon their discovery. Specific to the RFC_URE3 control center, the risk harm assessment took into consideration the significant construction activities underway and the project-driven increase in the number of construction and security personnel at the facility as a result. In response to the unique circumstances created by the construction project, RFC_URE3 has hired a significant number of additional new security personnel and contractors, who have undergone requisite training, but are new to the RFC_URE3 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring), and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: Immediate Mitigation: In all instances, the PSP doors were closed and secured. RFC_URE3 supervisors took immediate steps to meet with the security guards involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances. As the security guards are contracted through a security vendor company, these issues were further taken up with the vendor management, who took disciplinary actions, up to and including the suspension of an employee, where determined appropriate. Additional Mitigation: RFC_URE3 has further implemented an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RFC_URE3’s security awareness program, security awareness communications focused on reiterating and reinforcing PSP access protocols company wide. As a more targeted measure, PSP access protocols will be covered in detail at upcoming NERC compliance meetings, including the monthly CIP SME meetings, effectively reinforcing awareness throughout all areas where access issues have arisen. Additionally, the Chief Compliance Officer and other management met with the construction project supervisor to discuss the issues and ways to prevent future occurrence. Additional meetings with the RFC_URE3 legal team and management are scheduled for continued PSP compliance awareness training. Finally, in addition to approaching the issue from an awareness perspective, RFC_URE3 is reviewing its work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training designed to specifically address the occasions when a PSP doorway must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016015983 | CIP-003-3 | R6 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-003-3 R6. While conducting an annual password change review pursuant to newly implemented password change procedural controls, the RFC_URE4 substations area discovered 6 meters, identified as non-Critical Cyber Assets (nCCAs) that had not had their passwords changed since commissioning. This discovery triggered a comprehensive compliance review of these devices, and determined that the following errors occurred during device installation under the CIP v3 configuration management program, to which significant improvements have been made under CIP v5, as discussed further below: (1) The devices were appropriately identified as nCCAs and documented as such on the appropriate NERC CIP devices lists and Electronic Security Perimeter diagrams. These meters, however, include a separate serial connected display component from which the information that the meters collect can be read. On the NERC CIP device lists, the serial number for the display devices were documented in place of the serial number for the actual meters, thus resulting in the display device being misunderstood by personnel as being the actual meters in future activities. Note: These display devices do not have any accounts or passwords associated with them. They are simply read-only devices from which meter information is displayed. (2) The default passwords for the actual meters were changed on commissioning, but the changed passwords were not appropriately documented for future use. Accordingly, between the display devices being erroneously understood to be actual meters and no known passwords on file for the meters, there was a misunderstanding that these devices did not have passwords that needed to be changed annually. (3) Finally, while all other required security measures and controls were in place (e.g., ports and services baseline, tracking for purposes of security patching and firmware upgrade, etc.), these devices were not added to existing technical feasibility exceptions for their inability to support logging/alerting and anti-virus/malware prevention software. It is important to note that no configuration updates were made to the meters after initial installation. There have been no security patches or updates issued for these devices since being commissioned. Because the changed passwords were never documented and their associated passwords remained unknown, these devices therefore were never accessed. This noncompliance involves the management practice of asset and configuration management because RFC_URE1 did not have accurate records of the serial numbers for the display devices and actual meters. The root cause is poor verification because RFC_URE4 did not ensure that the documented serial numbers were accurate. This issue started when RFC_URE4 was required to comply with CIP-003-3 R6 and ended when RFC_URE4 completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While certain protections under the requirements were not fully implemented, the devices do not have command and control functionality and were determined to be non-critical to the reliability of the BPS. Moreover, these devices are housed in Physical Security Perimeter secured substation control houses to which only select personnel with requisite authorizations have access. Also, no configuration updates were ever made to the meters after initial installation. There have been no security patches or updates issued for these devices since commissioning. Lastly, because the changed passwords were never documented and remained unknown, these devices were never accessed. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: Immediate Mitigation: Upon identification of the issue, RFC_URE4 initiated password change forms for the metering devices. The device vendor was consulted to support the password change since the original changed passwords on these devices were unknown. Moreover, personnel now identified with electronic access to the Meters will be tracked in the user account management database for the purposes of tracking access to the associated user/system accounts. Additional Mitigation: As part of the CIP Version 5 transition, RFC_URE4 has developed a robust Configuration Management (CM) program pursuant to the new CIP Standards. The new CM program contains enhanced device commissioning processes that were developed based on lessons learned from industry best practices and RFC_URE4 past experiences. These device commissioning processes include standardized checklists and evidence collection touch-points for each applicable CIP requirement. Specific to addressing the issue presented herein, the device commissioning checklist includes particular line items to ensure that: (1) default passwords are changed, (2) TFEs are accounted for, and (3) associated evidence is collected and reviewed before the change control documentation can be closed out. The same standardized practice of specific checklist line items and evidence collection touchpoints is repeated for each CIP requirement that must be in place before a device can be commissioned into the production environment. All responsible personnel will be trained on the CIP Version 5 CM program prior to implementation.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016015986 | CIP-006-3c | R4 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-006-3c R4. As a result of construction related activities, a man-trap door under construction at RFC_URE4’s control center facility was propped opened and left unattended for a period of time. Specifically, this man-trap door was being installed between a Physical Security Perimeter (PSP) and a non-PSP area, whereby the inner door opened into the PSP area and the outer door opened outward into the non-PSP area. At the time of the incident, the man-trap door was not yet functional. Additional security controls (i.e., key card and PIN access) were being configured before the door could be fully activated and formally used as a PSP access point. Accordingly, the outer door facing the non-PSP area was locked with no way to gain entry from the non-PSP side, but an authorized individual could open the inner door from inside the PSP and exit through the outer door into the non-PSP. Note: The PSP area into which the man-trap opens does not hold any protected NERC CIP devices. In order to gain access to the secured PSP rooms in which NERC CIP devices reside, an individual would need to gain access to the appropriate floor and transgress several additional layers of protections (e.g., badge controlled doors, security alarms, video monitoring, security personnel, etc.) before he/she could enter the secure PSP rooms in which protected NERC CIP devices are located. On this day, 3 contractors needed access to this man-trap area in order to complete construction related activities. The contractors were appropriately logged into a PSP visitor log book upon arrival and were escorted to the outer door non-PSP area by an authorized security guard. Upon realizing that the outer door could not be opened, the authorized security guard rerouted himself and gained access to the PSP through another commissioned access point. The guard then proceeded through the PSP to the man-trap door, where he opened the inner door and propped open the outer door. At this point, the security guard escorted the 3 contractors through the man-trap and into the PSP to perform construction related activities. As a result of the door being opened, an alarm was generated and responded to by security console personnel, who cleared the alarm upon verifying the presence of authorized security personnel and the need for doorway access to facilitate construction activities. The contractors worked within the area for approximately 5 hours using the monitored man-trap doorway to enter and exit the PSP while completing their tasks. When their tasks were complete, the security guard escorted the contractors out of the PSP and properly logged them out of the PSP visitor log book. The security guard did not, however, properly secure the man-trap door as required by RFC_URE1 security procedures. Shortly after the first group of contractors left the man-trap area, another authorized security guard along with 3 additional contractors arrived. These additional contractors were onsite to clean up construction debris left behind by various construction activities taking place throughout the facility. These contractors had been properly logged into the general facility visitor log book upon arrival, but had not been logged into the PSP visitor log book, as it was not anticipated that they would be entering any PSP areas. Upon making their way to the particular area at issue, and because the man-trap doorway was open, it was not clear to the security guard that the room beyond the man-trap doorway was restricted to PSP access. As a result, the security guard escorted the contractors through the man-trap doorway and into the PSP not realizing this to be a secure area requiring PSP visitor logging. Nonetheless, the security guard remained present and monitored the contractors activities at all times. The contractors were in the area for approximately 80 minutes to clean up the debris left behind by the previous group. When they were finished, the security guard escorted the contractors out of the PSP through the man-trap door. Approximately 3.5 hours after the second group left the area, the contractor foreman discovered the open man-trap door and contacted the on-site security officer. The security officer immediately responded, investigated the issue, and secured the door. The root cause for this first issue is ineffective training because the first security guard did not properly secure the man-trap door when he left. Also as a result of construction related activities, a door in the lower level of RFC_URE4’s control center facility leading to the Pit (i.e., the “Pit door”) was inadvertently left open and unguarded for approximately 22 minutes. The Pit is an outdoor area within the secure gated confines of the control center facility, where large construction equipment can be lowered to the underground level of the facility from the outside and then retrieved by personnel on the inside. The Pit door that provides access to the Pit from inside the facility is located off of a hallway in the PSP. Note: The Pit serves a construction related function and is not a typical feature of the facility. On this day, an authorized security guard escorted a construction contractor from within the PSP to the Pit area to perform certain construction related activities. The security guard propped open the door allowing the contractor to exit the PSP hallway and step into the Pit area to perform his tasks while the security guard monitored his activities. After completing his tasks, the contractor re-entered the PSP hallway, and the security guard disengaged the door prop as they walked away from the area. The Pit door, however, did not close completely due to a functional failure in the door closing mechanism at the time of the incident. As a result, the door was left ajar and unattended for approximately 22 minutes before it was discovered by a System Operator, who immediately notified security personnel. In response, security personnel immediately secured the door and reported the incident to the appropriate supervisors for further investigation. The root cause for this second issue is also ineffective training because the security guard did not ensure that the door was properly secured when he left. The issues started when RFC_URE4 was required to comply with CIP-006-3c R4 and ended when RFC_URE4 completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE4’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described, certain aspects of these security protocols were not followed by the personnel involved, but were immediately reported upon their discovery. Specific to the RFC_URE4 control center, the risk harm assessment took into consideration the significant construction activities underway and the project-driven increase in the number of construction and security personnel at the facility as a result. In response to the unique circumstances created by the construction project,RFC_URE4 has hired a significant number of additional new security personnel and contractors, who have undergone requisite training, but are new to the RFC_URE4 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring), and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: Immediate Mitigation: In all instances, the PSP doors were closed and secured. RFC_URE4 supervisors took immediate steps to meet with the security guards involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances. As the security guards are contracted through a security vendor company, these issues were further taken up with the vendor management, who took disciplinary actions, up to and including the suspension of an employee, where determined appropriate. Additional Mitigation: RFC_URE4 has further implemented an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RFC_URE4’s security awareness program, security awareness communications focused on reiterating and reinforcing PSP access protocols company wide. As a more targeted measure, PSP access protocols will be covered in detail at upcoming NERC compliance meetings, including the monthly CIP SME meetings, effectively reinforcing awareness throughout all areas where access issues have arisen. Additionally, the Chief Compliance Officer and other management met with the construction project supervisor to discuss the issues and ways to prevent future occurrence. Additional meetings with the RFC_URE4 legal team and management are scheduled for continued PSP compliance awareness training. Finally, in addition to approaching the issue from an awareness perspective, RFC_URE4 is reviewing its work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training designed to specifically address the occasions when a PSP doorway must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015421 | CIP-003-3 | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. A contract security guard discovered that he had access to CIP Confidential Information through a shared folder. The contract security guard reported this access to his supervisor based upon the training he received on RFC_URE5’s information protection program. The security guard’s supervisor contacted the appropriate individuals to immediately restrict access to the folder. RFC_URE5 determined that while granting access to this shared folder to a new corporate security specialist, the responsible individual mistakenly changed the folder access to company-wide access. Upon further investigation, RFC_URE5 also discovered that CIP Confidential Information was inadvertently placed in other file locations without the requisite access controls. Specifically, RFC_URE5 discovered that CIP Confidential Information had been stored in files maintained by RFC_URE5’s IT group. The root cause of this noncompliance was the fact that RFC_URE5’s key control (i.e., requiring that CIP Confidential Information be secured in the relevant group’s file structure, which has strict access controls) was ineffective when CIP Confidential Information was placed in other file structures, such as the shared folder at issue, without the necessary access controls. RFC_URE5 has no way to physically or electronically prohibit the placement of CIP Confidential Information in folders outside of the designated, sure locations. Therefore, RFC_URE5 must rely on training to enforce that prohibition. This contributing factor relates to the management practices of information management, which focuses on protecting and managing information items, and workforce management, which focuses on managing employee permissions and access to assets. This issue started when RFC_URE5 inadvertently changed the access permissions on the shared folder and ended when RFC_URE5 moved all files containing CIP Confidential Information to the appropriate, protected locations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the nature of the CIP Confidential Information that was placed at risk was not sensitive enough to compromise any BPS systems. Second, those unauthorized individuals who had access to CIP Confidential Information through the IT folders were eligible for authorization based upon their job functions and the fact that they had completed NERC compliance training, but had not been granted access because they did not yet require it. ReliabilityFirst also notes that during the period of exposure, no unauthorized person actually accessed the CIP Confidential Information at issue. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) restricted access to files containing CIP Confidential Information to authorized users; 2) provided additional training and direction regarding restricted access and CIP Confidential Information to all CIP asset owners and all RFC_URE5 employees who participate in RFC_URE5’s cybersecurity working group; 3) verified that no CIP asset owner or other CIP authorized person maintains files in unrestricted spaces; 4) verified that all files containing CIP Confidential Information have been moved to the protected directory maintained by RFC_URE5 compliance group; and, 5) committed to perform quarterly certifications and spot checks to ensure that all CIP Confidential Information is maintained in the restricted access space.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016015540 | CIP-003-3 | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. During a monthly review of access privileges, RFC_URE5 discovered that one person was inadvertently granted access to a folder containing CIP Confidential Information. RFC_URE5 immediately terminated the access upon discovery. Upon further investigation, RFC_URE5 discovered that the unauthorized access was granted when the responsible individual granted access to an unauthorized person with a similar last name as the person who was intended to receive access. The root cause of this noncompliance was a human performance issue where the individual responsible for granting access rights selected the wrong person. This contributing factor relates to the management practices of information management, which focuses on protecting and managing information items, and workforce management, which focuses on managing employee permissions and access to assets. This issue started when RFC_URE5 inadvertently granted access to the wrong employee and ended when RFC_URE5 discovered the mistake and terminated access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this noncompliance was an isolated incident of human performance that is not indicative of a systemic problem. Second, the unauthorized employee was granted access only to account names and not the passwords associated with those accounts. Therefore, the unauthorized employee could not use this information to gain access to the BES Cyber System. Third, RFC_URE5 had existing detective controls in place (i.e., a monthly review of access privileges), which detected this access error. ReliabilityFirst also notes that the unauthorized person did not actually access the files containing CIP Confidential Information. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) terminated the unauthorized employee’s access; and 2) implemented an additional control where an alert is generated when an individual is added to one of the CIP Confidential folders. The alert is sent to key stakeholders in the compliance group, enabling them to immediately detect errors in the granting of access.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2016015553 | CIP-007-3a | R5; R5.3.3 | During a Compliance Audit conducted as per an existing multi-regional registered entity agreement, ReliabilityFirst determined that RFC_URE6 had an issue of CIP-007-3a R5.3.3. An RFC_URE6 employee began working on a Request for Information associated with an ongoing audit and discovered that two accounts did not have their password changed. Account #1 was used to access certain switches. The password on the account was last changed approximately twenty-one months earlier and was never used. It had a 12 character, randomly generated, complex password. This account was to be used for emergency purposes only. The account was disabled. Since the account has not been needed for emergency purposes, the account was deleted. Account #2 was used for network and certain backups. The password on the account was last changed approximately twenty-one months earlier and was used daily as part of the backup process by a backend service. It had a 12 character, randomly generated, complex password. The account was disabled. The backup process has been modified to use another account and therefore this account was deleted. The root cause of this noncompliance was inadequate internal controls to confirm and ensure all necessary passwords were being changed annually. Specifically, the process in place to manage passwords for shared accounts at the time of the noncompliance was a manual process with no specific guideline for generating account lists and to verify that all account passwords were changed as required. This contributing factor involves the management practices of verification, asset and configuration management, and information management. This issue started 15 months (per CIPv5) after Account #2 was last changed and ended when Account #2 was disabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, both accounts had 12 characters, randomly generated, complex passwords. Furthermore, these passwords were stored in encrypted, password protected databases. Second, access to the database for Account #1 was only known by 9 individuals, and access to the database for Account #2 was only known by 19 individuals. Third, RFC_URE6 had configured monitoring for all accounts to alert if an account has failed logon attempts or if the account was locked out. Fourth, the environments where these accounts reside are within NER CIP Electronic Security Perimeters (ESPs) and protected by firewall electronic access points, and associated access rulesets/policies. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) deleted both accounts; 2) completed a one-time comprehensive review on all NERC CIP assets to ensure passwords were changed: 3) added enhancements to System Manager (Compliance and Configuration application) to scan all CIP assets and provide alerts if passwords are approaching the end of the year and haven’t been changed. (i.) System Manager will automatically capture when a password was last changed (PswdLastSetTime’) and when a password was last used (LastLogonTime) as part of a daily scan done for all Windows assets. This information will be stored in the database. The system will also allow for manual entries of this same information to be added for non-Windows assets, which will also be stored in the database. It will be the responsibility of the Technologist to manually enter non-windows asset password information into the system, as defined in the Annual Password Change Guideline. This task to verify the process is being followed has been added to the annual Cyber Vulnerability Assessment (CVA) process. (ii.) Automated monthly reports will be run and sent to the Security Administrator to show if any passwords have not been changed within a set amount of time (to be determined) for all accounts on CIP assets. The information for Windows and non-windows assets will be included in the reports. The ‘to be determined’ time will allow time to complete an annual password change; 4) added a step to the annual CVA to verify all passwords have been changed. A report will be run from System Manager to confirm passwords have been changed on all assets for the current year. The list of assets will be determined during the physical walk down of the CVA and then this list will be compared to System Manger to ensure all assets are appropriately identified in the system; and 5) completed a comprehensive review to verify that this was an isolated case on all NERC CIP assets to ensure passwords were changed. No other issues were found.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016015478 | CIP-003-3 | R4 | RFC_URE8 submitted a Self-Report stating that it had an issue of CIP-003-3 R4. At the time of the noncompliance, RFC_URE8 was involved in a due diligence process for the potential sale of its assets to a prospective buyer. The prospective buyer executed Non-Disclosure Agreements (NDAs) and related confidentiality agreements, both at the organizational and individual level, with RFC_URE8 outlining the sharing of RFC_URE8 company information. The confidentiality agreements require that all information will be returned to RFC_URE8 or destroyed at the end of the sale process except if the prospective buyer is required by law to retain a copy of that information to comply with a law or a regulation. RFC_URE8, however, did not include provisions in the NDAs and confidentiality agreements concerning the accessibility of certain NERC CIP-related information as required in RFC_URE8’s CIP Information Policy. RFC_URE8 discovered that it had provided Critical Infrastructure Information (CII) to the prospective buyer without having the prospective buyer review and agree to RFC_URE8’s CIP Information Policy. The CIP Information Policy requires the recipient of the CII to not disclose or discuss the CII with anyone that had not reviewed and agreed to the CIP Information Policy. RFC_URE8 performed an investigation to determine what CII information it shared with the prospective buyer. During this investigation, RFC_URE8 identified that it had shared one document, a RFC_URE8 CIP Audit Report, with the prospective buyer that contained CII. After this discovery, RFC_URE8 reached out to the prospective buyer and identified all potential recipients of this CII and requested those recipients to review the RFC_URE7 CIP Information Policy and sign a disclosure where they would agree to follow RFC_URE8’s CIP Information Policy and not disclose the CII. This noncompliance involves the management practice of workforce management through ineffective training. The RFC_URE8 individuals responsible for executing the NDAs and confidentiality agreements with the prospective buyer were not properly trained on the fact that the confidentiality agreement needed to include a section where the prospective buyer reviewed and agreed to follow RFC_URE8’s CIP Information Policy. Therefore, ineffective training is the root cause of this noncompliance. This issue started when RFC_URE8 shared a document containing CII with the prospective buyer before the prospective buyer had agreed to follow RFC_URE8’s CIP Information Policy, and ended when RFC_URE8 secured attestations consistent with its CIP Information Policy from the individuals at the prospective buyer who received the CII. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individuals at the prospective buyer who received the CII were already under organizational and individual NDAs and confidentiality agreements to prevent further distribution or use of the CII. The CII that RFC_URE8 released to the prospective buyer is not representative of RFC_URE8’s current configuration, structure, or approach. There is little current value in the CII that RFC_URE8 released to the prospective buyer as none of the CII was “actionable” information that would have enabled an individual to compromise RFC_URE8’s networks. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) developed awareness and refresher posters that document how to correctly handle CII information and RFC_URE8 posted those posters in all facilities including the corporate office; 2) communicated with staff the importance of following its CIP Information Policy; 3) secured the relevant attestations consistent with its CIP Information Policy from those individuals working for the prospective buyer to whom the information was released; 4) evaluated the current CII process to ensure proper controls are in place for release of CII before that information is sent out; and 5) developed a training for all employees on procedural expectations.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016015479 | CIP-007-3a | R3 | RFC_URE8 submitted a Self-Report stating that it had an issue of CIP-007-3a R3. While reviewing the RFC_URE8 Monthly Security Patches workflow, the Director of Compliance discovered that RFC_URE8 had not reviewed and analyzed the applicability of some Windows patches within 30 days after the patches were released. RFC_URE8’s CM-3 Security Patch Management Procedure requires RFC_URE8 IT personnel to review and analyze all applicable security patches within 30 days of their availability. After the Director of Compliance discovered this issue, RFC_URE8 conducted an investigation and discovered that Windows Security patches were released and were downloaded two days later. The patches, however, were not reviewed by the RFC_URE8 IT Subject Matter Expert (SME) until thirty-six days later. The SME responsible for completing the review left the company and failed to complete the review before his departure. Following that SME’s departure, the workflow to review the patches remained open and unaddressed until the SME’s replacement addressed the patches. The patches were reviewed and analyzed six days late. This noncompliance involves the management practices of verification and workforce management. Verification is an issue because RFC_URE8 did not have an effective procedure in place to confirm that the responsible SME reviewed the patches on time. Workforce management is implicated because RFC_URE8 did not have an effective organizational structure in place to ensure that work was not delayed when an employee left the company. The lack of an effective verification procedure is the root cause of this noncompliance. This issue started when RFC_URE8 failed to review and analyze the applicability of the patches within 30 days of the patches being released, and ended when RFC_URE8 reviewed and analyzed the applicability of the overdue patches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE8 employs a layered “defense-in-depth” cybersecurity strategy. To do any damage that could come from not applying a Windows Security patch on time, an intruder would need to pass through RFC_URE8’s firewalls to gain access to the equipment within the Electronic Security Perimeter (ESP), which are enabled with only those ports and services needed for operation and are monitored through an intrusion detection system. An intruder would have to pass through these defenses to access the ESP and then have the proper credentials to access an account on the compromised device to trip the equipment. These additional protections make it unlikely that an intruder would be able to cause any damage from a patch that was reviewed six days late. RFC_URE8’s decision to apply the Windows Security patches at issue were not impacted by the six day delay in assessment. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) had the Director of Compliance add calendar reminders every third Tuesday (one week beyond Windows patch Tuesday) to ensure those responsible for performing the patch reviews have appropriately scheduled time for the review; 2) reinforced with all involved in the patch review and management process the obligations of the CIP Standards and RFC_URE8’s internal procedures; and 3) added changes to its workflow to alert the Director of Compliance and the Compliance team when the SME assigned to review patches has not timely performed the review. ReliabilityFirst has verified the completion of all mitigation activity.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2016015582 | CIP-004-3a | R4 | RFC_URE8 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. An RFC_URE8 employee voluntarily resigned. According to CIP-004-3a R4.2 and RFC_URE8’ Information Security Policy as well as RFC_URE8's Procedures, RFC_URE8 is required to remove an employee’s access to Critical Cyber Assets (CCAs) within seven days of his resignation if the employee was not terminated for cause. In this instance, the employee at issue voluntarily resigned. On the day the employee resigned, RFC_URE8 removed his corporate access privileges, which included retrieving his keycard and removing his electronic access to corporate assets. Two days later, RFC_URE8’s Director of Compliance sent an e-mail reminder advising all CIP Subject Matter Experts (SMEs) and program leadership that passwords for all CIP CCAs must be changed and all access lists updated by close of business five days later. The passwords for RFC_URE8 plant equipment and Windows device passwords were changed by close of business on the seventh day. A RFC_URE8 network engineer, however, did not complete the password changes on RFC_URE8 CIP network assets until the eighth day after the employee voluntarily resigned. These final password changes were made one day late because the RFC_URE8 network engineer forgot to complete the changes. This noncompliance involves the management practices of workforce management and verification. The network engineer was not effectively trained to follow the seven day access revocation period. RFC_URE8 did not have an effective check in place to make sure that it met the seven day access revocation period after an employee voluntarily resigned. Ineffective training and ineffective verification are the root causes of this noncompliance. This issue started when RFC_URE8 was required to remove the employee's access to CCAs, and ended when RFC_URE8 finished removing the employee's access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE8 removed the employee’s corporate access privileges, including his keycard, and electronic access to corporate assets on the same day he resigned. This removal meant that the employee could not access any CCAs unless he was physically onsite at the plant. The employee would be unable to access any CCAs onsite because RFC_URE8 removed his keycard on the day he resigned. Additionally, the employee was traveling overseas for the duration of the noncompliance meaning he would not have had the opportunity to physically access the CIP environment or any CCAs. The only access that was not removed within the seven day time frame was specific and generic account access to CCAs. Lastly, the employee’s complete access to CCAs was only removed one day late. No harm is known to have occurred. | To mitigate this issue, RFC_URE8: 1) changed all of the necessary passwords on CCAs; 2) revoked access to all generic or shared accounts on CCAs; 3) ensured that removal of CIP related access privileges is included in the Human Resources Department exit checklist; and 4) provided additional training regarding CIP process deadlines and the protocol for alerting management when the potential exists to miss required CIP commitments. ReliabilityFirst has verified the completion of all mitigation activity.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2016015581 | CIP-003-3 | R6 | RFC_URE9 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. Through an internal compliance review, RFC_URE9 IT staff discovered two cases where RFC_URE9 employees did not follow RFC_URE9’s change management process, which resulted in two instances of missed testing. The first issue involved a video card replacement. RFC_URE9 discovered during an internal review of System change management documentation that an employee installed a video card on a NERC workstation without following RFC_URE9’s change management process for the addition or removal of Critical Cyber Asset (CCA) hardware. That process provides controls and guidance to personnel supporting the System and directs employees on how to make modifications to the System by detailing all required tasks for review and approval, validation, and documentation. Per the process, hardware changes to CCAs require the issuance of a ticket, the use of an installation procedure, and collection of testing evidence before and after CCA hardware is added or removed. The ticket provides the documentation requirements for performing the change and includes fields for an installation plan and a test plan. RFC_URE9 staff performed a video card upgrade of a NERC workstation in order to support the use of four display monitors at the workstation. An RFC_URE9 employee shut down a NERC workstation for 15 minutes to replace the video card to allow the addition of two extra monitors. The employee installing the monitors failed to create a PCS ticket meaning there was no documentation of the installation or a test plan for approval of the ticket. The employee made the incorrect assumption that testing performed on three other workstations at the initial system commissioning four months earlier would serve as evidence of security control testing for the video card replacements on this fourth workstation where new drivers were installed. This assumption was incorrect because testing is required for hardware changes to each CCA and the work being performed was not covered by an existing PCS ticket. RFC_URE9 staff deployed an executable file into the production environment as a “simple” change that was not expected to impact the baseline configuration within the System. The executable file was a SCADA application that calculates real time unit performance. This file does not impact actual operations. RFC_URE9’s change management process has different requirements for executing “simple” changes to the calculation than for “complex” changes to the calculation. In this case, RFC_URE9 staff thought they were executing a “simple” change, but were actually executing a “complex” change that affected the baseline configuration for two SCADA servers and therefore did not follow the proper procedures for a “complex” change such as using a PCS ticket and performing testing of the change prior to deployment of the executable file. RFC_URE9 staff did follow the proper procedures for a “simple” change. RFC_URE9 updated the baseline configurations for the two SCADA servers following the deployment in the calculation approximately four months later. This noncompliance involves the management practices of work management through an unclear process and workforce management through ineffective training. The unclear process is the root cause. The change management process itself was unclear as the matrix categorized calculation changes as "complex" or "simple", with different procedures for each, without discrete criteria and context for making the correct determination of what constitutes a simple versus a complex change. The process also lacked specific guidance on how to conduct the testing. In addition to the unclear process, another contributing cause to this noncompliance was ineffective training because the RFC_URE9 employee performing the video card upgrade did not follow or fully understand RFC_URE9’s change management process. This issue started when RFC_URE9 incorrectly deployed an executable file into the production environment as a “simple” change rather than as a “complex” change and ended when RFC_URE9 finished rectifying both errors by returning the NERC workstation with the video card upgrade to service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the installation of the video card at the work station, no operator was using that workstation and the installation only took 15 minutes to complete. If an issue had occurred during the video card replacement, the operator would have been relocated to a spare workstation in the same Physical Security Perimeter (PSP). If all workstations within a single PSP failed, operators would relocate to a backup Control Center. For the executable file that was deployed without the proper testing, the file was a tool to assist RFC_URE9 dispatch personnel with real-time information about unit performance. The availability of this tool did not impact actual operations or RFC_URE9's ability to follow dispatch instructions. Lastly, the change in the baseline configuration to the two SCADA servers were made and did not have any impact because RFC_URE9 received no notice of server failure which would have occurred in the event of a server failure. No harm is known to have occurred. | To mitigate this issue, RFC_URE9: 1) retrained the employee that performed the video card replacement and the employee that deployed an executable file into the production environment as a “simple” change when it was actually a “complex” change on correctly following RFC_URE9’s change management process; and 2) RFC_URE9’s system Team and CIP Compliance Team also revised its change management process to include the change management matrix. This revised process was published on RFC_URE9’s website. RFC_URE9’s Director sent an email to management requesting approval to distribute the new revised process and sent out the announcement to all those affected by the revised process including the operations group and the compliance group on that same day. The revisions and the matrix were meant to provide more criteria for classifying changes based on impact level and for identifying required actions based on the type of change. The new process describes in detail how and when to complete a ticket and the multiple approvals required. These details include whether pre-change testing in a lower environment is required, whether the change qualifies as significant change, and what types of tickets are required to document the change. The new process makes it clearer to end users when to follow procedures for a simple change and when to follow procedures for a complex change. ReliabilityFirst has verified the completion of all mitigation activity.
2016-09-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015450 | CIP-007-3a | R2 | SERC_URE1 submitted a self-log stating that it had an issue of CIP-007-3a R2. SERC_URE1 failed to ensure that it enabled only those services required for normal and emergency operations. In the fourth quarter of the year, a SERC_URE1 service desk employee installed an approved and authorized operating system update on an energy management system (EMS) workstation within the primary control center. The installation process initiated an operating system service not previously authorized but required for installation. The service remained active at the conclusion of the installation process, but the service was not required for normal or emergency operations. SERC_URE1 used change scripts to test and confirm the existing baselines to the new running configurations on the Cyber Assets. Post-installation change scripts did not identify the additional service. SERC_URE1 returned the updated workstation, with the added service in place, to normal operations on the same day. Approximately one year later, SERC_URE1 conducted its required annual Cyber Vulnerability Assessment (CVA) and discovered the service running on the EMS workstation. After reviewing the CVA results,SERC_URE1 disabled the service and commenced an internal review into the facts and circumstances. SERC_URE1 learned that the change script it used after installing the system update had malfunctioned. The script properly collected the running data, but the compare function within the script failed to report differences between the baseline and the change. SERC_URE1 was unable to determine the reason why the install process did not disable the service upon completion or why its change script did not identify the enabled service after installation. The workstation involved was approximately 2% of the total Critical Cyber Assets (CCAs) in SERC_URE1’s CIP program. Thirty-six individual users had access to the workstation. SERC_URE1 had conducted the required CVA, using ports and services data prior to the service being enabled on the EMS workstation involved here. SERC_URE1 concluded that CVA later in the fourth quarter of the same year. Therefore, SERC_URE1 conducted the annual CVAs as required. SERC_URE1 conducted an extent-of-condition review through the following year's CVA and determined there were no other similar issues. To conduct the annual CVA, SERC_URE1 used different scanning tools than the malfunctioning script that failed to identify the added service. The malfunctioning script, a secondary failure in this issue, did not result in any similar occurrences. The cause of this issue was twofold. First, SERC_URE1’s installation process failed to disable a service upon completion of the installation. Second, a malfunctioning script used to compare the baseline of approved ports and services to the ports and services running on the Cyber Asset at issue did not report the added service and therefore SERC_URE1 took no action to disable it. The issue lasted from approximately one year, from when SERC_URE1 made a change and enabled a service not required for normal and emergency operations until SERC_URE1 disabled the service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to enable only those services required for normal and emergency operations left a single service enabled that was not properly documented, providing an attack vector to a CCA inside the ESP of which SERC_URE1 was unaware. However, SERC_URE1 secured its CCAs within an established Electronic Security Perimeter with ingress and egress deny-by-default firewall rules that required explicit access permissions and which would have denied access to the service in question. The workstation involved had up-to-date security patches, updated malware prevention software, and current anti-virus signatures installed. No harm is known to have occurred. | To mitigate this issue, SERC_URE1: 1) provided additional testing and fixes to the supplementary detective mechanism used to provide regular port and service audits on the machine; and 2) provided greater specificity in change control documentation to help initially detect additional services installed at the EMS workstations.
2016-09-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015015390 | CIP-006-3c | R1; R1.6 | SERC_URE2 submitted a Self-Report stating it had an issue with CIP-006-3c R1. SERC_URE2 did not follow the appropriate procedure and process for logging and continued escort of its visitors while inside the Physical Security Perimeters (PSPs). At 1:31 p.m., a contractor with authorized unescorted physical access to the computer room Physical Security Perimeter PSP permitted a visitor to enter the PSP without completing the visitor access log and without obtaining the necessary visitor badge as required by SERC_URE2’s procedures. In addition, the contractor who permitted the PSP access failed to continuously escort the visitor while within the PSP. The contractor permitted the visitor PSP access and left the visitor alone in the PSP for less than five minutes. At 1:33 p.m., the contractor was standing outside the PSP when an SERC_URE2 staff member questioned the location of the visitor. The contractor stated that the visitor was within the PSP unescorted, so the staff member and the contractor entered the PSP to retrieve the visitor. At 1:35 p.m., the contractor and visitor exited the PSP. SERC_URE2 discovered the issue by employee awareness and observation. The staff member observed the unescorted access and questioned the location of the visitor. The root cause was human performance. Specifically, the contractor in question failed to follow internal visitor processes. The issue lasted from 1:31 p.m., when the contractor and visitor entered the PSP and the contractor did not document the visitor, and ended on October 7, 2015 at 1:35 p.m., when the contractor escorted the visitor out of the PSP. While SERC was performing its assessment and determining the scope of the violation, SERC_URE2 submitted a scope expansion with the following additional issue. A SERC_URE2 operator observed, through the video surveillance, one of its employees escorting a visitor inside a substation PSP. At 11:26 a.m., the escort departed the PSP and went outside the building to receive a phone call, leaving the visitor unattended. At 11:28 a.m., the operator observed that the escort returned inside the PSP and resumed escorting the visitor. The approximate time of unescorted access was two minutes. The root cause was determined to be human performance. The employee did not follow the visitor control program procedures. SERC_URE2’s extent of condition concluded there were no further instances of similar issues. This issue lasted from 11:26 a.m., when the escort left the visitor unattended in the PSP, and ended at 11:28 a.m., when the escort returned and escorted the visitor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2 leaving the visitor unescorted within a PSP could lead to the visitor potentially causing physical damage to the control system functionality of SERC_URE2’s operations or the BPS. However, the Critical Cyber Assets within the PSPs require user names and passwords in order to gain access and have alarms to alert security personnel in the event of multiple failed log-on attempts. SERC_URE2 verified, that in both instances, the visitor was unescorted for less than five minutes and was immediately removed from the PSP once identified. No harm is known to have occurred. SERC considered SERC_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) removed the visitors from the PSPs; and 2) coached the escorts on visitor control requirements, and SERC_URE2 policies and procedures.
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015304 | CIP-004-3a | R3; R3.2 | SPPRE_URE1 submitted a Self-Report stating that it had an instance of noncompliance with CIP-004-3a R3.2 because it failed to update an employee’s Personnel Risk Assessment (PRA) within the required seven-year timeframe. SPPRE_URE1 discovered the issue of noncompliance during an internal audit of personnel PRA records. The root cause of this instance of noncompliance was human error. SPPRE_URE1 missed the seven-year PRA update because an incorrect seven-year renewal date had been entered during the manual transfer of PRA data to an access management database. This instance of noncompliance lasted nine months; it began the date the employee’s PRA was required to have been renewed and ended the date the employee’s access was revoked pending a completed PRA. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to timely update a PRA could cause SPPRE_URE1 to miss changes in an individual’s criminal history, an element of potential risk for safety and security. The risk to the reliability of the BPS was mitigated by protective measures in place at the time of the instance of noncompliance. The employee had a prior PRA and had the appropriate Critical Cyber Asset training. The employee was in good standing and the employee’s employment status had not changed over the course of the previous seven years. In addition, the Control Center, i.e. the employee’s work space, was staffed 24/7 by personnel in positions where attempted unauthorized access to Critical Cyber Assets would have been detected. SPPRE_URE1 discovered the instance of noncompliance as a result of implementing effective detective controls, the employee continues to be in good standing, and the PRA did not include any adverse findings. No harm is known to have occurred as a result of this instance of noncompliance. SPP RE determined that Compliance Exception treatment is appropriate. The instant noncompliance posed minimal risk to the reliability of the bulk power system. Furthermore, SPPRE_URE1 detected the instant noncompliance as a result of internal controls, self-reported and mitigated the noncompliance upon discovery. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1. revoked the employee’s access and conducted a PRA prior to restoring access; and 2. implemented a quarterly check of employee PRA records to ensure that the PRAs are renewed timely. SPP RE has verified the completion of all mitigation activity.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015258 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report stating that as a responsible entity, it had a possible issue of noncompliance with CIP-004-3a R4.2. Specifically, WECC_URE1 reported that they failed to revoke unescorted physical access for one individual within seven days of that access no longer being needed, as required by CIP-004-3a R4.2. This issue began the eighth day after unescorted physical access was no longer needed for an individual and was remediated when the substations access key was recovered. The root cause was determined to be the failure of WECC_URE1’s Human Resources department to follow established processes to alert physical security of the individual’s retirement from the company. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE1 failed to revoke unescorted physical access for one individual within seven days of that individual retiring; the individual had badge and key access to substation blockhouses. Failure to revoke access that is no longer needed could result in the misuse of Critical Cyber Assets at substations where this individual had access. However, the risk of malicious behavior was low as the individual in question had a current personnel risk assessment, CIP training, and retired from WECC_URE1 in good standing. WECC_URE1 reviewed their access logs which revealed no access attempts were made by said individual two months before he retired or any time after he retired Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue(s) WECC_URE1: 1) Process improvements as part of WECC_URE1’s CIP Version 5 transition activities; 2) Refined procedures, including WECC_URE1’s over-arching CIP-004 procedure; and 3) Supplementing current WECC_URE1 training program with a handbook to be used as a reference tool which defines how WECC_URE1 complies with each CIP Standard. WECC verified that WECC_URE1 completed mitigating activities.
2016-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015706 | CIP-004-3a | R3; R3.2 | During a Compliance Audit, NPCC determined that NPCC_URE1 had an issue of CIP-004-3a R3.2. Prior to the start of the On-site Audit, NPCC_URE1 reported to NPCC that in preparation for the audit, it had discovered one employee's personnel risk assessment (PRA) had not been renewed within the required seven-year period. In preparation for the audit, NPCC_URE1 discovered that the employee's PRA had lapsed. Upon discovery of the issue, the employee's control room access was immediately removed until the new PRA was completed. This issue started when the employee's PRA lapsed, and ended when the employee's access privileges were revoked, a period of 14 days. The root cause of this noncompliance was the use of quarterly reports in NPCC_URE1's system to track the expiration of PRAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the violation was short, as it was discovered that the employee's PRA had not been renewed only 14 days after the date when the PRA had lapsed. The employee's access was immediately revoked upon discovery of the missing PRA. During the 14 day period of the violation, the employee did not attempt to gain access to the control rooms. Upon successful completion of a new PRA, the employee's CIP access was reinstated. The new PRA showed no issues for the employee and the employee was, and remains in good standing with the NPCC_URE1. No harm is known to have occurred as a result of this issue of non-compliance. | To mitigate this issue, NPCC_URE1: 1) Immediately revoked CIP access for the employee upon discovery of the missing PRA, and reinstated the access only once a new PRA was performed; and 2) Updated its system to generate e-mail reminders to HR and each employee's manager at 90 days, 60 days, 30 days, and on the day of expiration of an employee's seven-year PRA. NPCC has verified the completion of all mitigation activity.
2016-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015707 | CIP-007-3a | R5; R5.1.1 | During a Compliance Audit, NPCC determined that NPCC_URE1 had an issue of CIP-007-3a R5.1.1. Prior to the start of the On-site Audit, NPCC_URE1 reported to NPCC that in preparation for the audit, it had discovered that local shared accounts had been created on CIP assets, specifically data storage switches, in order to allow vulnerability scans to be performed on the assets by NPCC_URE1 technical security. These accounts were created prior to receiving the necessary approval. Upon discovery, the accounts were properly approved. The root cause of this noncompliance was human error due to a misinterpretation of the change request ticket for creating the accounts that led a system administrator to believe that the accounts had already received the proper approval. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the violation was short, as the accounts only existed without approval for a period of nine days. The accounts resulted in receiving the proper approval as they were necessary for performing vulnerability scans on the CIP assets. The creation and use of the accounts posed minimal risk to the reliable operation of the BES. No incorrect or inappropriate access resulted from the creation of the accounts prior to their approval. The employee's with access to the accounts were credentialed members of NPCC_URE1's technical security team. No harm is known to have occurred as a result of this issue of non-compliance. | To mitigate this issue, NPCC_URE1: 1) Retired the existing manual process for approving access requests; and 2) Implemented a new authorization process for approving access requests and creating new accounts through its system. Under the new system, system administrators will not have the ability to approve new accounts or access requests until the approval has been received from the proper supervisor or manager. Once the approval is received, administrators can assign specific access roles to individuals based upon their official job duties. NPCC has verified the completion of all mitigation activity.
2016-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016015682 | CIP-007-3a | R5; R5.1.1. | NPCC_URE2 reported that it had an issue of CIP-007-3a R5. During the quarterly review of physical and system access authorizations, it was discovered that two new security guards did not have the required system access request authorizations for NPCC_URE2 facility's access control system. As part of the on boarding process, both security guards required physical and system access to the facility’s access control system. In accordance with NPCC_URE2’s internal procedures, this is accomplished by the submittal and approval of both Physical Access Request (PAR) and System Access Request (SAR) to the access control system. A security sergeant had recently been assigned the responsibility for this task and submitted PARs for both individuals; Physical access to required Physical Security Perimeters was implemented for security guard #1 and security guard #2 shortly after their employment. However, the security sergeant did not submit the required SARs for authorization to the access control system . As part of their job responsibilities, both new security guards were provided access to the shared account from the beginning of their employment. Therefore, both security guards gained system access to the access control system without the required access authorization since their dates of hire. Upon the identification of omission, the required SARs were submitted for both individual. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The two security guards had authorized physical access to the facility, valid personnel risk assessments, and the mandatory CIP Training certifications on file. They were also under the supervision of the on shift security sergeant. No harm is known to have occurred as a result of this issue of non-compliance. | To mitigate this issue, NPCC_URE2: 1. Identified the issue and submitted System Access Requests for the two security guards authorization to the facility Physical Access Control System’s security guard account. 2. Approved the two submitted System Access Requests for the security guards. 3. Reviewed the applicable NPCC_URE2 procedures and expectations associated with the onboarding of new security personnel with security staff involved in the incident. 4. Reviewed and updated the “onboarding of new security personnel” check list with the onboarding of new security personnel and reviewed with the security staff. NPCC has verified the completion of the mitigation activity.
2016-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015583 | CIP-006-3c | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. Two RFC_URE1 contractors (“Contractor A” and “Contractor B,” collectively “Contractors”) entered the Physical Security Perimeter (PSP) at RFC_URE1’s location to perform scheduled electrical maintenance. Both Contractors gained entrance to the PSP without being logged as visitors by RFC_URE1 even though neither of the Contractors had current authorized unescorted access privileges to the PSP. Additionally, the two Contractors were not continuously escorted while they were inside in the PSP. Contractor A previously had access rights to enter PSPs, but RFC_URE1 revoked his access rights following the expiration of Contractor A’s Personnel Risk Assessment (PRA). Ninety days, sixty days, and thirty days before Contractor A’s PRA was set to expire, RFC_URE1 notified Contractor A that his authorized unescorted access to NERC PSPs would be revoked if his PRA was not timely renewed. Contractor A did not submit the required forms to renew his access and RFC_URE1 properly revoked Contractor A’s access. After his PRA expired, Contractor A was not authorized to enter the PSP without first being logged in as a visitor and Contractor A required an authorized escort while inside a PSP. Contractor B also did not have authorized unescorted access privileges to the PSP. After RFC_URE1 removed Contractor A’s access, Contractor A completed the required PRA renewal form and submitted it the next day. Although that PRA renewal request was completed, re-authorization of unescorted access to the NERC PSP required a new access request to be submitted and approved through RFC_URE1’s Access Request System. Due to an administrative error by Contractor A’s manager, Contractor A’s new access request was not submitted or approved through RFC_URE1’s Access Request System. Contractor A incorrectly believed that his PRA renewal request submission reauthorized his access privileges to the PSP. Upon arriving at RFC_URE1’s location, Contractor A successfully scanned his ID at a non-NERC exterior door card reader and entered into the vestibule outside of the PSP with Contractor B. Contractor A’s ID scanned successfully because he had authorized access to enter into and be in the building, but did not have authorized unescorted access to the PSP. Contractor A then scanned his ID card at the NERC PSP card reader and received an audible alert sound. A RFC_URE1 employee near the badge reader (“RFC_URE1 Employee A”) assumed the NERC PSP card reader was malfunctioning and brought both Contractors A and B into the NERC PSP. RFC_URE1 Employee A then had Contractor A scan his ID badge on another card reader inside the NERC PSP to test his hypothesis that the previous NERC PSP card reader was malfunctioning. This test, however, was completed on a non-NERC PSP card reader, and Contractor A’s ID badge scanned successfully. Following this second scan, RFC_URE1 Employee A logged Contractor B as a visitor to the PSP and logged Contractor A as Contractor B’s escort. RFC_URE1 Employee A did not log Contractor A as a visitor. Contractor A should not have served as Contractor B’s escort because Contractor A’s access privileges were not yet reauthorized. After first entering the PSP, the Contractors had to go back to their work van to get more materials and exited the PSP. Upon returning and attempting to re-enter the PSP, an audible alert again sounded at the NERC PSP card reader when Contractor A scanned his ID badge. This time, another RFC_URE1 employee (“RFC_URE1 Employee B”) denied the Contractors’ entry because of the invalid badge scan until RFC_URE1 Employee B found the Contractors an authorized escort. RFC_URE1 Employee B then logged the Contractors into the visitor log book as visitors and provided an authorized escort later that day for the Contractors to resume their electrical maintenance work. This noncompliance involves the management practices of workforce management through ineffective training and external interdependencies. Ineffective training comes from RFC_URE1 Employee A not following RFC_URE1’s access provisioning process and visitor access policy by assuming the initial badge reader was not functioning, not logging the contractors as visitors, and allowing the Contractors into the PSP without an authorized escort. External interdependencies is involved because Contractor A’s manager did not take the required second step of requesting PSP access via RFC_URE1’s Access Request System to reactivate Contractor A’s unescorted access privileges after Contractor A’s PRA was updated and cleared. Contractor A also did not understand all of the steps that needed to be completed before his access rights were reinstated. Ineffective training is the root cause of the noncompliance. This issue started when RFC_URE1 failed to log in the Contractors as visitors to a PSP and failed to continuously escort the Contractors while the Contractors were inside the PSP and ended when RFC_URE1 properly logged in the Contractors as visitors and provided them an authorized escort inside the PSP later in the day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. At the time of the noncompliance, RFC_URE1 had completed a PRA renewal for Contractor A and Contractor A maintained a business need for access to the PSP at issue. RFC_URE1, however, had not finished its internal process to reissue Contractor A’s access at the time of the noncompliance. Contractor A also had previously provided electrical maintenance support at that PSP, was a trusted contractor, and his role did not change. Contractor A escorted Contractor B the entire time both Contractors were within the PSP. Additionally, both Contractors had limited ability to access any terminals within the PSP as they did not have credentials to access the energy management system. RFC_URE1 employs defense-in-depth security measures (e.g., automated alerts and continuous monitoring of the BPS) and internal controls that limited the risk of an unauthorized access event triggering any further events that could have impacted the BPS. Lastly, RFC_URE1 confirmed that there were no attempts to access the restricted computer terminals within the PSP on the date in question. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 Employee B followed RFC_URE1’s access policies and protocols and prevented the Contractors from entering the PSP until an authorized escort was available. RFC_URE1 Employee B also logged both the Contractors into the visitor log and had an authorized escort continuously escort the Contractors when they reentered the PSP to remediate the noncompliance. To prevent recurrence, RFC_URE1: 1) issued an email reminder to all employees and contractors at RFC_URE1’s location reinforcing training on NERC PSP access equipment and proper protocol for NERC PSP access. This email went to employees and contractors that utilize the PSP at issue; 2) met with Employee A to discuss the event and reinforce RFC_URE1’s policies and procedures for entry into a PSP; 3) reviewed and updated the PSP signage to ensure there is clear, concise, and effective signage for PSP entry requirements; 4) created and distributed a job aid to assist employees, contractors, and supervisors for navigating the PRA renewal process; 5) revised Control Room Access Control procedure and implemented changes to affected personnel in order to clarify the proper access procedures at the control room and how to respond to denied access attempts; 6) created a job aid for supervisors, which will provide guidance on how to acquire employee’s historical access entitlements to position the supervisor to be able to assist if access is lost and needs to be reinstated; 7) revised its mandatory NERC Cyber Security Training during the normal review cycle to address the use of the red card reader to control access to all PSPs and to address how individuals are supposed to respond to an alert sound at PSPs; and 8) revised and implemented NERC CIP PSP Physical Security Controls procedure to clarify the proper visitor access procedures at PSP entrances and how to respond to denied access attempts.
2016-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015539 | CIP-004-3a | R3 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R3. During its annual review of existing Personnel Risk Assessments (PRAs), RFC_URE2 discovered that 3 employees’ PRAs had expired the prior year. All three of the employees with expired PRAs are long-term employees who have all previously completed the PRA process. The root cause of this noncompliance was information silos between the Human Resources and Infrastructure Security groups that were inadvertently created when RFC_URE2 merged multiple Human Resource Departments. Over the past two years, RFC_URE2’s Human Resources department has merged the operations of RFC_URE2 and a number of generation businesses into a single business unit. As the HR departments were consolidated, PRA dates were inadvertently stored in different locations, causing confusion about when they needed to be renewed. This contributing factor implicates the management practices of information management and workforce management. This issue started when the first PRA expired, and ended when RFC_URE2 revoked access for the individuals with expired PRAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, RFC_URE2 discovered these expired PRAs during a regularly scheduled, annual review of PRAs. Second, RFC_URE2 immediately revoked unescorted physical access for all three employees with expired PRAs upon discovery of the noncompliance. Third, all of these employees were trusted employees, who had been employed for approximately eight years, had successfully passed PRAs in the past, and had good work records. Fourth, only one of the 3 employees with an expired PRA had access to BPS Cyber Assets which consisted of only telecommunication equipment between the Control Center and the substations. Accordingly, this employee had no ability to cause outages to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed the employees’ access to the secure areas; 2) obtained a comprehensive list of all employees and contractors with unescorted access to NERC/CIP compliant facilities, and has entered those dates into the employee record within the Access Control System. This will allow the Infrastructure Security team to maintain control of initiating the renewal process; and 3) recertified the three employees’ access into secure areas.
2016-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015487 | CIP-007-3a | R5 | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. SERC_URE1 did not ensure individuals access were consistent with the concept of "need to know" with respect to work functions performed. SERC_URE1’s account provisioning process requires two levels of approval prior to provisioning or granting access, the employee’s manager and the space access approver. SERC_URE1’s access services team granted electronic access for an employee to two physical access control systems without receiving the required approvals. The access services team received the first level of approval from the employee’s manager but granted access prior to receiving the second required approval from the space access approver. The second approval is a manual process that requires an email response for approval or rejection. Seventeen minutes later, the access services team received an email stating that the employee received access. The access services team performed an account creation review, discovered the error, and removed access one minute later. The root cause of the issue is human performance. The access services team did not follow the process and granted access prior to receiving the required approvals. The issue lasted approximately eighteen minutes, from when SERC_URE1 inadvertently granted the employee access through when SERC_URE1 removed the employee’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to follow documented access provisioning procedures could have led to unauthorized personnel to have access to Critical Cyber Assets, providing an opportunity to cause harm and introduce BPS instability. However, the issue was discovered through an internal control, the duration of the issue was 17 minutes, and SERC_URE1 had not notified the employee that access was granted. The following day, SERC_URE1 approved and granted the access to the employee. Further, the employee’s NERC CIP training and personnel risk assessment were up to date. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-007-3a R5 compliance history in determining the disposition track. SERC determined that SERC_URE1’s CIP-007-3a R5 compliance history should not serve as a basis for applying a penalty. . | To mitigate this issue, SERC_URE1: 1) immediately removed access; 2) coached the access services team on its human performance enhancement tool; and, 3) coached the access services team on the security and compliance implications of mistakenly granting unauthorized access.
2016-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015015265 | CIP-007-3a | R5 | During a Compliance Audit, SERC auditors determined that SERC_URE2 had an issue with CIP-007-3a R5.3.3. SERC, in conjunction with SERC_URE2, identified five-user accounts where SERC_URE2 failed to change the password annually. In response to an SERC audit data request, SERC_URE2 discovered that it had failed to change five-user accounts annually in its Active Directory (AD) domains. As part of the audit process, the SERC audit team requested user password aging information from SERC_URE2’s AD domains. SERC_URE2 generated a user account listing from the AD domains where the passwords were beyond 420 days since the last password change. SERC_URE2 identified three user accounts in one AD domain and two user accounts in another AD domain. However, one of the accounts was common to both domains, so the issue affected four user accounts. SERC determined that three of the accounts in question did not surpass the annual password change requirement. However, SERC_URE2 changed the other account in 2013 and it has a password age of 722 days. The SERC_URE2 CIP AD domains utilize an automated software application to manage password complexity and aging. The application resides on the corporate AD domain, and when a user changes their password on the corporate domain the application checks to determine whether the user has a corresponding account in the CIP AD domains. If applicable, the software updates the password in the CIP AD domains. SERC_URE2 conducted a root-cause evaluation and determined that software malfunction was the root-cause. SERC_URE2 discovered during a software upgrade that communications was severed between the corporate AD domain and the CIP AD domains. The communication failure prevented the software from performing the verification for applicable CIP AD domain users. SERC_URE2 determined the instant issue was due to a previously undiscovered system malfunction where password changes did not successfully migrate from the corporate AD domain to the CIP AD domains. The issue lasted approximately nine months, from when SERC_URE2 failed to annually change the password, through when SERC_URE2 changed the password. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2’s failure to annually change passwords could have provided an ill-intended adversary more time to identify active user account credentials and gain unauthorized access to the Critical Cyber Assets (CCAs). The CIP AD domain servers resided within an Electronic Security Perimeter (ESP) that had controls in place to monitor and detect malicious traffic. Additionally, SERC_URE2 monitors the CIP AD domain servers residing in a Physical Security Perimeter (PSP) 24 hours a day, seven days a week. The account holder in question underwent a Personnel Risk Assessments, appropriate training, and had a valid business needs for access to the CCA. The current issue affected .0014 % of SERC_URE2's user accounts. SERC_URE2 reviewed its ESP and PSP logs and discovered no instances of unauthorized access. SERC_URE2 also reviewed internal logs and determined that no abnormal conditions existed during this instant issue. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-007 R5 compliance history in determining the disposition track. SERC determined that SERC_URE2’s CIP-007 R5 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE2: 1) performed a root cause evaluation; 2) forced affected users to change passwords; 3) implemented a password policy to send alerts to the security operations team when a user account password age is over 340 days; 4) setup a scorecard report to email the security operations team’s mail box every day for any user account age that is over 340 days; 5) configured alerts for failed and pending transactions in the active directory domains; and, 6) implemented 180 day password expiration functionality for all accounts managed by the system.
2016-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2016015562 | CIP-005-1 | R1; R1.5 | During a Compliance Audit, SERC determined that SERC_URE3 had an issue with CIP-005-3a R1.5 specifically related to CIP-005-3a R2. SERC_URE3 did not properly identify and protect all Electronic Access Control and Monitoring systems (EACMs). SERC later determined that the issue extended back to CIP-005-1 R1. SERC auditors discovered that SERC_URE3 provides external remote access to its energy management system (EMS) for vendor support. The vendor support technician has a unique user identification, password, and a digital certificate that are required to gain access to the EMS. SERC_URE3’s remote access process requires the following: 1) authentication on the internet facing corporate firewall using digital certificates, 2) an onsite SERC_URE3 EMS operator physically configuring a switch through a remote terminal unit allowing the network connectivity to an intermediate system, 3) authentication to a local account on the intermediate system, 4) authentication through the established Electronic Security Perimeter (ESP) firewall from the intermediate system to the CCA, and 5) authentication at the CCA. SERC_URE3 did not classify or protect the internet-facing corporate firewall or the intermediate system as EACMs. The device performed initial authentication services by verifying authenticity using digital certificates. The cause of this issue was a misinterpretation by SERC_URE3. SERC_URE3 did not understand that external interactive access controls were required to be located at the access point(s) to the ESP. The issue lasted approximately six years, seven months from when the Standard became mandatory and enforceable, through Mitigation Plan completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE3’s failure to classify or protect an EACM could potentially allow unauthorized changes on an EACM that could allow a malicious attack on the BPS. In addition, if either the external facing firewall or the intermediate system were unusable, vendor support staff would not have CCA access during an emergency. However, the vendor’s access was limited to a single approved individual, with a current personnel risk assessment and had went through SERC_URE3’s cyber security training. The vendor support staff has unique credentials and digital certificates to ensure the integrity of the accessing party. SERC_URE3 also utilizes a mechanical switch within the secured area that an EMS operator activates; ensuring awareness of who, when and why access is initiated. SERC_URE3 limited access to one EMS server, and the process to gain access required four separate username and password combinations. No harm is known to have occurred. SERC considered SERC_URE3’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE3: 1) removed the intermediate system and eliminated external remote access to its EMS. To mitigate this issue, SERC_URE3 will complete the following mitigation activities by December 31, 2016: 1) update the network drawings; 2) update the internal compliance program to include a step to collaborate with a third-party for instances of differing interpretations; and, 3) provide awareness training to SERC_URE3 staff on the updated internal compliance program.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014956 | CIP-006-3c | R1; R 1.6.1 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had a minimal risk instance of noncompliance with CIP-006-3c R1.6.1 for not maintaining complete logs of visitors who accessed two of its Physical Security Perimeters (PSPs). Although SPPRE_URE1 had a documented and implemented physical security plan, for the duration of the violation, the exit times for five SPPRE_URE1 employee visitors, and the names of the escorts for three SPPRE_URE1 employee visitors, were not documented in the logbooks associated with SPPRE_URE1’s Primary and Backup Control Centers. The duration of the noncompliance was ten months, beginning the date of the first incomplete visitor log, and continuing through the date SPPRE_URE1 completed retraining of all affected personnel on its visitor control program. The root cause of the noncompliance was a combination of human error due to personnel not adhering to SPPRE_URE1’s visitor logging procedures and lack of effective internal controls, i.e., verification reviews, to ensure such procedures were being strictly followed. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-006 R1.6.1 has the potential to affect the reliable operation of the BPS by creating an opportunity for unauthorized personnel to physically access Critical Cyber Assets that affect the operation of the BPS. Nonetheless, SPPRE_URE1 was aware of all eight visitors who entered the Primary and Backup Control Centers, and all were SPPRE_URE1 employees. Additionally, SPPRE_URE1 attested that the three individuals who entered the Backup Control Center were escorted while inside the PSP, and that the noncompliance was not documenting the names of the escorts in the log. SPPRE_URE1 completed all sections of the logs except for the exit times for the five employee visitors and the names of the escorts for three employee visitors. No harm occurred as a result of the instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) reviewed visitor logs for each PSP; 2) revised its Physical Security Plan to include at least monthly reviews of the visitor logs for each PSP; 3) added additional signage near PSPs to remind visitors and employees of the logging requirement; and 4) retrained all affected personnel on its visitor control program, which included notice of the revisions to the Physical Security Plan. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014954 | CIP-007-3a | R6 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had a minimal risk instance of noncompliance with CIP-007-3a R6. SPPRE_URE1 did not fully implement automated tools or organizational process controls to monitor system events that are related to cyber security on two Structured Query Language (SQL) databases residing on two Cyber Assets within its Electronic Security Perimeter (ESP). Although SPPRE_URE1 was logging “unsuccessful logon” attempts associated with the two SQL databases, it was not logging “successful logons,” which are system events related to cyber security. The duration of the noncompliance was three years, beginning the earliest date of the audit scope, and continuing through the date SPPRE_URE1 enabled its SQL databases to log successful logons. The root cause of the noncompliance was a misinterpretation of the standard, specifically, the lack of a clear definition of the term “system events related to cyber security,” resulting in a determination by SPPRE_URE1 that “successful login” attempts are not included in the definition. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R6 has the potential to affect the reliable operation of the BPS by allowing Critical Cyber Assets to be compromised and other system cyber security events to occur without the Responsible Entity’s knowledge. Although “successful logons” were not logged for the two SQL databases, “unsuccessful logon” attempts and other potential suspicious activities were being logged. Additionally, the two SQL databases did not house operational information. The other Cyber Assets located inside SPPRE_URE1’s ESP were found to be compliant with CIP-007-3a R6. Moreover, all Cyber Assets within the ESP were protected by multiple layers of firewalls, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by a Security Information and Event Management system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assets inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1 enabled its two SQL databases to log successful logons. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014949 | CIP-005-3a | R1; R1.6 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had a minimal risk instance of noncompliance with CIP-005-3a R1.6 because it did not document two network switches as non-critical Cyber Assets residing within its Electronic Security Perimeter (ESP). SPPRE_URE1 updated its Master Cyber Asset/Critical Cyber Asset List to reflect the installation of the two network switches; however, they were incorrectly documented as access points to the ESP instead of non-critical Cyber Assets within the ESP. The duration of the instance of noncompliance was 3.3 years, beginning the earliest date of the audit scope, and continuing through the date the two network switches were documented as non-critical ESP Cyber Assets on the Master Cyber Asset/Critical Cyber Asset List. The root cause of the noncompliance was a combination of human error due to personnel mistakenly documenting the two network switches and lack of internal controls, i.e., verification review process, to ensure the Master Cyber Asset/Critical Cyber Asset List was accurate. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-005-3a R1.6 has the potential to affect the reliable operation of the BPS by providing the opportunity for cyber intrusions to occur on Critical Cyber Assets and/or other Cyber Assets that are located inside the ESP. However, this noncompliance is a documentation error. Notwithstanding that the two network switches had been incorrectly documented as access points and reside within SPPRE_URE1’s ESP, they were afforded all the required CIP protective measures to prevent unauthorized access. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) revised its Master Cyber Asset/Critical Cyber Asset List by reclassifying the two network switches as non-critical Cyber Assets within the ESP; 2) revised its process for updating the Master Cyber Asset/Critical Cyber Asset List by limiting individuals who are authorized to revise the list; and 3) developed and implemented a process for quarterly reviews of the Master Cyber Asset/Critical Cyber Asset list to verify that each asset is correctly identified and documented. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2016015666 | CIP-006-3c | R4 | SPPRE_URE2 submitted a self-log stating that it had a minimal risk instance of noncompliance with CIP-006-3c R4. SPPRE_URE2 utilizes a badge reader and a personal identification number (PIN) pad for employee access to its Physical Security Perimeters (PSPs). Three employees with authorized unescorted access attempted to access the PSP. Although the badge reader successfully read their badges, the PIN pad did not recognize their PINs. The three employees gained access to the PSP with the assistance of other employees who also had authorized unescorted physical access to the PSP. SPPRE_URE2’s badge readers control and log physical access into and out of the PSP, and send logs to SPPRE_URE2’s Physical Access Control System (PACS) to detect and alert when there is unauthorized access. The PACS is configured to detect each successful entry and corresponding exit from the PSP and generate an alert if there is a discrepancy, e.g., an employee’s badge used to exit the PSP was not used to enter the PSP. In all three instances, alerts were immediately generated when the employees swiped their badges and exited the PSP. SPPRE_URE2’s Physical Security personnel immediately investigated the alerts and subsequently reported the activity to SPPRE_URE2 compliance personnel. The duration of the noncompliance was one month, beginning the date of the first noncompliant entry into the PSP, and continuing through the date after the last instance of noncompliant entry to the PSP. The root cause of the noncompliance was human error due to personnel not adhering to SPPRE_URE2 physical access procedure. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All three employees were authorized with unescorted physical access to the PSP and all events associated with this instance of noncompliance were immediately detected and investigated by SPPRE_URE2 Physical Security personnel. No harm is known to have occurred. | To mitigate this instance of noncompliance, SPPRE_URE2: 1) counseled the three employees on the proper process to resolve problems with their PINs; and 2) sent an email reminder to all personnel with authorized unescorted physical access to a PSP to follow the established procedure for accessing a PSP, and included instructions for resolving invalid PIN problems. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014599 | CIP-006-3c | R2; R2.2 | SPPRE_URE3 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-006-3c R2.2. During an annual assessment, SPPRE_URE3 discovered that cameras used to stream live video from its Alternate Control Center (ACC) were connected to its Primary Control Center (PCC) via a non-access point switch instead of an access point firewall, therefore SPPRE_URE3 had not implemented the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s) as required by CIP-005-3 R2. SPP RE determined the duration of the issue of non-compliance was sixteen months, beginning the date the switch was put into service, and continuing through the date the cameras were routed through the access point firewall for the PACS ESP-like environment. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to route the cameras through an access point could lead to undetected network access. However, the risk posed by the noncompliance was mitigated because the switches were afforded sufficient protections. SPPRE_URE3’s network traffic had to be initiated across a SPPRE_URE3-owned and managed fiber connection from the video system before the cameras would provide data. Data from the cameras was protected by a site-to-site virtual private network tunnel and did not leave the PACSs ESP-like environment, which was protected by an access point firewall that allowed view-only access to streaming video. Furthermore, the switch was protected by Cyber Assets with anti-malware software. SPPRE_URE3’s Network Intrusion Detection System (NIDS) continuously monitored and alarmed for unauthorized access within its network. SPPRE_URE3 implemented applicable patches and installed anti-virus for all technically feasible Cyber Assets. Also, the switch was physically protected by strictly limiting access to authorized personnel. No harm is known to have occurred to any SPPRE_URE3 Cyber Asset as a result of the issue. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1. routed the cameras through the access point firewall for the PACS ESP-like environment. 2. added a process in its Change Management program for the Information Security Officer to review all pre- and post- change documentation related to network assets to confirm results and configurations. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015624 | CIP-005-3a | R1; R1.5 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R3.1 and R3.2. Texas RE subsequently determined that this instance of noncompliance pertains to CIP-005-3a R1.5 rather than CIP-007-3a R3. As required by CIP-005-3a R1.5, TRE_URE1 failed to afford the protective measures as specified in Standard CIP-007-3 R3 for Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). Specifically, TRE_URE1 failed to perform assessments and document the implementation of numerous patches within 30 days of release of availability for a single Cyber Asset used for remote access control for a TRE_URE1 ESP. TRE_URE1 replaced a single non-CCA server. Upon replacement, the new TRE_URE1 server began experiencing issues communicating with TRE_URE1’s automated patch server. Subsequently, TRE_URE1 resolved the non-CCA server’s communication issues. Additionally, TRE_URE1 reviewed the patching history for the single server in question and discovered that the patches had not actually been assessed. TRE_URE1 personnel then performed the missing assessments and installed the last applicable security patch on the single server at issue. The root cause of this issue was an ineffective installation of a single server, which resulted in communications issues between the server and the TRE_URE1 automated patching system. In addition, personnel turnover coupled with insufficient processes for transferring patch management responsibilities, tracking the performance of patch assessments, and verifying patch implementation contributed to the duration of the patch assessment issue. Specifically, the TRE_URE1 employee responsible for coordinating patch assessment and implementation activities transferred job responsibilities at the same time TRE_URE1 personnel reported the communications issues with the new server. Subsequently, TRE_URE1 also updated its patch management process such that additional TRE_URE1 personnel assumed that the patches for the server had previously been assessed and implemented. Texas RE determined the issue duration to be for approximately one year and seven months, from the 31st day after the earliest patch was available for the server in question until the last patch was successfully installed by TRE_URE1 on the server in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the loss of the single server at issue could result in TRE_URE1’s inability to remotely access certain devices, the server did not control any Critical Cyber Assets (CCAs) and was not essential to their reliable operation. Further, throughout the duration of the issue, the single server in question continued to function as designed. TRE_URE1 also properly assessed and documented the implementation of patches for the CCAs associated with the patching process at issue. In addition, the single server was not directly connected to any CCAs during the duration of the patching issues. Finally, TRE_URE1 has multiple layers of physical and electronic security that would prevent a possible intruder from exploiting any patching vulnerabilities, including user name, password, and two-factor authentication requirements to electronically access the server. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) resolved the communication issue between the single non-CCA server and the automated patching server; 2) installed all applicable security patches on the single non-CCA server at issue; 3) implemented a tool to independently verify the installation of any security patches installed by the automated patch server; 4) implemented a supplemental patch management control for patches and firmware updates by establishing an internal process for tracking patch sources for the availability of new patches; 5) added an additional staff member to the personnel group at issue to ensure there is a primary and backup patch management SME in the event of personnel turnover; and 6) trained new staff on required patch management responsibilities. Texas RE has verified the completion of all mitigation activity.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014665 | CIP-004-3 | R4 | WECC_URE1 submitted a Self-Certification stating that as a responsible entity it had a possible issue of noncompliance with CIP-004-3 R4. Specifically, WECC_URE1 reported that during its Reliability Standard Audit Worksheet preparation, and a subsequent evidence review, Energy Management System (EMS) support personnel identified that electronic access to Critical Cyber Assets (CCA) had not been revoked for one individual within seven calendar days of said access no longer being needed pursuant to CIP-004-3a R4.2. This one individual was part of WECC_URE1’s summer internship program and left voluntarily upon the completion of the internship. EMS Support personnel decided to perform a thorough investigation of enabled users within the EMS environment, at which time they identified six additional individuals whose electronic access was not removed in a timely manner. This issue began when WECC_URE1 failed to remove electronic access to CCAs for one individual within a timely manner, and ended when the electronic access to CCAs was revoked for the remaining six individuals who had electronic access when access was no longer needed. The root cause of this issue was one WECC_URE1 EMS support employee not following documented processes for revoking access to CIP assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to revoke electronic access to CCAs within a timely manner for seven individuals who no longer required such access. Failure to timely revoke access to CCAs for employee’s no longer needing access could allow said employees with malicious intent to cyber and/or physically access CCAs which could compromise the security of such assets essential to the operation of the BPS. However, the CCAs were afforded added protective measures by being located within both an Electronic and a Physical Security Perimeter. Physical access to the PSP had been revoked upon termination by Enterprise Security for all seven individuals, which would have prohibited unescorted physical access to the CCAs. Additionally, WECC_URE1 requires an RSA token and two-factor authentication for remote electronic access, which was not available to any of the seven individuals. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue(s) WECC_URE1: 1) added all requests for electronic access to CCAs to its existing tracking system, which already maintains a list of individuals having unescorted physical access to WECC_URE1’s PSPs; 2) individuals are required to request electronic access to the EMS using the tracking system; 3) the tracking system is also utilized by personnel to submit revocation requests upon employee terminations. Automated request are received by EMS support management for processing; 4) dedicated one employee to perform a secondary review of all employee terminations and initiate electronic access revocation in the tracking system, as needed; and 5) EMS support personnel have developed a CIP user access revocation checklist that will be utilized to ensure that no user accounts remain enabled upon employee termination. WECC verified completion of WECC_URE1’s mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015364 | CIP-004-3a | R2 | WECC_URE1 submitted a Self-Report stating that as a responsible entity it had a possible issue of noncompliance with CIP-004-3a R2. Specifically, WECC_URE1 reported that it failed to provide annual CIP training for two contactors who had unescorted physical access to Critical Cyber Assets (CCA). WECC_URE1 states that it has defined annual as within 15 months. For contractor one, WECC_URE1 discovered an issue as it was moving into production an update to its database report tool, used to flag individuals with almost due and overdue CIP training. For contractor two, WECC_URE1 discovered an issue as it was running reports generated by its database reporting tool. Contractor two did not appear on the original report because at that time contractor two’s CIP access was disabled. Subsequent to that, contractor two was provisioned unescorted physical access to CCAs without annual CIP training. This issue began when the annual CIP training should have been administered, and ended when unescorted physical access for both contractors to CCAs was disabled. The root cause of this issue was a progress or status of task not being adequately tracked due to incorrect programming of a database tool. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide annual CIP training to two contractors with unescorted physical access to CCAs. The failure to provide annual cyber security training for personnel having unescorted physical access to CCAs could lead to personnel being unaware of the policies, access controls, and procedures for CCAs which may then lead to cyber security oversights and cyber security incidents that could result in potential security compromise of the CCAs. Such incidents may then cause harm to CCAs essential to the operation of the BES, thereby potentially negatively impacting the BES. However, both contractors had prior CIP training, thus aware of policies, access controls, and procedures for CCAs, and current Personnel Risk Assessments. WECC_URE1 determined that contractor one had a single instance, and contractor two had no instance, of accessing a Physical Security Perimeter during the time they should have had annual CIP training. As soon as WECC_URE1 was aware of this issue of noncompliance, unescorted physical assess to CCAs was disabled, access list were updated, and in the case of contractor two, training was provided in a timely manner. WECC_URE1 determined that contractor one did not need unescorted physical access to CCAs so annual CIP training was not administered and access remained disabled. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. WECC notes that WECC_URE1 has identified and self-reported the issue described herein, does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. For these reasons, WECC considers WECC_URE1’s compliance history as a factor in its designation of this remediated issue as a CE. | To mitigate this issue(s) WECC_URE1: 1) completed an independent review of source data from its various systems. No additional instances of noncompliance were identified as a result of the review; and 2) implemented a new training system that automated training assignments and reassignments based upon a CIP flag that originates from its tracking system, and automated weekly generated reports to better track and manage training in order to demonstrate compliance. WECC verified completion of WECC_URE1’s mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015388 | CIP-006-3c | R2; R2.2 | WECC_URE2 submitted a Self-Report stating it had a possible issue of noncompliance with CIP-006-3c R2.2. Specifically, WECC_URE2 reported that its IT Security department discovered two Physical Access Control Systems (PACS) were missing logs for user account access activity. WECC_URE2 discovered the issue when there were missing syslogs for non-CIP devices due to an error that occurred during a non-CIP change. The missing logs were the result of an upgrade to the operating system; due to the nature of the upgrade, the log collector required reconfiguration in order to recognize the upgraded servers. However, the reconfiguration did not occur because the test plan did not include this step. WECC_URE2 reported it was able to recover and manually review the majority of the logs from the originating servers, however there were some gaps as these log files had started to overwrite during the investigation period. Therefore, under CIP-006-3c R2.2, WECC_URE2 did not afford the protective measures specified under CIP-007-3 R5.1.2. The root cause of the issue was a less than adequate test plan; WECC_URE2’s test plan should have included a reconfiguration step. This issue began when WECC_URE2 failed to maintain logs for user account access activity for two upgraded servers, and ended when WECC_URE2 confirmed the logs were being received by the log collector. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to maintain logs of user account access activity for PACS for a period of ten days. Failure to collect and review logs of account access on PACS devices could lead to unauthorized physical access to Electronic Security Perimeters (ESPs). In turn, unauthorized access could result in malicious activity on WECC_URE2’s Cyber Assets. However, WECC_URE2 implemented a number of compensating controls. Specifically, WECC_URE2’s PACS are physically secured and only authorized individuals have access. Its PACS are isolated from the internet, and internally with network segmentation, including firewalls which deny access by default. Also, remote access from the internet to the corporate network is only available by using two-factor authentication. Further, WECC_URE2’s primary monitoring of its BES Cyber System is performed in real-time at its command center, which is manned twenty four hours a day. No harm is known to have occurred. | To mitigate this issue, WECC_URE2: 1) Confirmed the logs were being received by the log collector. 2) Restored syslog reporting to all devices and modified its test plan to ensure syslog functionality. WECC verified completion of WECC_URE2’s mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016015482 | CIP-003-3 | R5; R5.2 | WECC_URE3 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-003-3 R5.2. Specifically, during WECC_URE3’s weekly CIP process owner meeting, a Subject Matter Expert inquired about its annual verification of access to Critical Infrastructure Protection Protected Information and whether the task notification was sent. WECC_URE3’s reliability compliance staff discovered that the recurring task did not dispatch; causing WECC_URE3 to not annually review its access privileges to protected information. The cause of this issue was due to an individual human error; an employee inadvertently set the recurring task incorrectly. The recurring task was set to automatically dispatch every 10 years, instead of once every year for the next 10 years. This issue began when WECC_URE3 failed to annually review access privileges to protected information and ended when WECC_URE3 completed a full review of its access privileges to protected information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, WECC_URE3 failed to annually review access privileges to protected information to confirm that access privileges were correct and corresponded with WECC_URE3’s needs and appropriate personnel roles and responsibilities. Such failure could have enabled an unauthorized person to access sensitive information, potentially exposing WECC_URE3’s Critical Cyber Assets essential to the operation of the BPS. However, although WECC_URE3’s review of access privileges was not reviewed in accordance with the timeframe in the Standard; WECC_URE3 did review two of its seven access list in preparation for CIP Version 5 transition. Further, upon discovery that the remaining five lists were not reviewed, WECC_URE3 performed a full review of the remaining access privilege lists and found there were no changes to its protected information access privileges as well. | To mitigate this issue, WECC_URE3: 1) Conducted a full review of its access privileges to protected information; and 2) Set the recurrence task pattern to semi-annual review for duration of 10 years WECC verified completion of WECC_URE3's mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2016015591 | CIP-004-3a | R2 | WECC_URE3 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-004-3a R2. Specifically, during a review of WECC_URE3’s procedures the compliance manager discovered its cyber security training program did not have evidence of an annual review. The cause of this issue was due to an individual human error; an employee inadvertently set the recurring task incorrectly. The recurring task was set to automatically dispatch every 10 years, instead of once every year for the next 10 years. This issue began when WECC_URE3 failed to annually review its cyber security training program, and ended when WECC_URE3 completed a review of its cyber security training program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, WECC_URE3 failed to annually review its cyber security training program. Such failure could result in personnel not being aware of new, existing, or modified policies, access controls, and procedures for its Critical Cyber Assets (CCAs). In turn, could lead to cyber security oversights and cyber security incidents resulting in security compromise of its CCAs. Such incidents may then cause harm to Critical Cyber Assets essential to the operation of the BPS. However, although the review of the cyber security training program was not reviewed in accordance with the timeframe in the Standard, WECC_URE3’s program had been under active review and revision during the third quarter in preparation of CIP Version 5 transition; documentation of such review was not captured. Further, after a full review of its cyber security training program WECC_URE3 found there were no notable changes to its program. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. | To mitigate this issue, WECC_URE3: 1) Conducted a full review of its cyber security training program; and 2) Set the recurrence task pattern to semi-annual review for duration of 10 years WECC verified completion of WECC_URE3's mitigating activities.
2016-07-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014014526 | CIP-006-3c | R1 | MRO_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. Specifically, a dispatch employee (still a trainee) escorted an unauthorized visitor through a door that was not intended for visitor access. The employee brought the visitor into the Physical Security Perimeter (PSP) of MRO_URE1's control center without logging the entry. The employee did this inadvertently and was unaware that visitors were supposed to go through another door. The issue was recognized immediately by other employees and the visitor was removed from the PSP. The cause of the noncompliance was inadequate training for the new employee. The issue began when the visitor entered the PSP, and ended approximately 30 seconds later when the visitor was removed from the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The visitor was only in the PSP for approximately 30 seconds. Additionally, the visitor was continuously escorted and was not able to observe any sensitive materials or displays. Finally, MRO_URE1 has an established visitor program that is well distributed as evidenced by the immediate recognition of the issue by the other employees. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-006-3c R1. | To mitigate this issue, MRO_URE1: 1) removed the visitor from the PSP; 2) counseled the employee on MRO_URE1's Physical Security Plan and building access procedures; and 3) reinforced the visitor access procedure during the annual compliance training for all employees and again during dispatcher training sessions.
2016-07-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015015418 | CIP-004-3a | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. During quarterly access reviews, RFC_URE1 identified three separate CIP-004 issues that involve duplicate access records, an inaccurate authorized access list, and a failure to timely revoke access to a Critical Cyber Asset (CCA). For the duplicate access records issue, RFC_URE1 identified an issue involving one employee that impacted the accuracy of its list of individuals with authorized physical access to a CCA. RFC_URE1 discovered that the individual in question was a contractor who transitioned to become a full-time employee of RFC_URE1. The individual, both in his contractor and employee roles, filled a trusted CIP position with a timely Personnel Risk Assessment (PRA), up-to-date CIP training, and a valid need for physical access to the CCA. When the individual transitioned to become a full time employee, he had a new record created which accurately identified the employee on the list of individuals with authorized physical access. However, the employee’s old record as a contractor was inadvertently maintained thus misidentifying him as a contractor with actual physical access. The individual appeared twice on RFC_URE1’s list of individuals with authorized physical access (as both contractor and an employee) causing some confusion as to the individual’s proper role and access. RFC_URE1 removed the individual’s entry as a contractor to ensure the accuracy of the list. For the inaccurate authorized access list issue, RFC_URE1 identified one instance where all users in a domain group that typically received access to CCAs were added to an authorized access list for a CCA where only a smaller portion of the group were actually granted access in this instance. As a result, for one quarter, additional users were incorrectly included on the authorized access list. RFC_URE1 discovered the error and removed the additional individuals from the authorization list. RFC_URE1 did not identify any instances where anyone that had been added to the authorized access list in error used that access. For the failure to timely remove access issue, RFC_URE1 identified one instance where an employee’s access to a CCA, had not been removed after the employee’s leave of absence. RFC_URE1’s procedure requires that an employee’s access to a CCA be removed if an employee’s leave is longer than two weeks. In this case, the employee took a medical leave of longer than two weeks and RFC_URE1 did not properly remove the employee’s access. When the employee returned from medical leave, the employee still had access even though that access should have been removed after the employee’s medical leave extended past two weeks. This noncompliance implicates the management practice of asset and configuration management and verification through an ineffective review process. RFC_URE1 determined that the manual processes for handling access records during the transition of a worker from contractor to employee status had insufficient quality checks and peer review steps. RFC_URE1’s overly complex manual process for maintaining access records contributed to the inaccurate authorized access list issue. The failure to remove access after a greater than two-week absence revealed a weak process for managing that type of leave. Ineffective training and an ineffective review process are root causes of this noncompliance. This issue started with the beginning of the CIP-004 issue involving failure to remove access when RFC_URE1 failed to remove the employee’s access that went on extended medical leave and ended the date RFC_URE1 finished resolving the CIP-004 issue involving an inaccurate authorized access list by removing access to CCAs for the additional users erroneously included on the list. This is the duration because all of the issues discussed above occurred during this time period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For all three of these issues, RFC_URE1 uses security event monitoring to monitor CIP accounts that would alert upon any suspicious or malicious activity. This security event monitoring system was never triggered during any of the three issues and that confirms that no improper access was attempted. RFC_URE1 also has controls in place to detect and reduce the likelihood of errors and to remediate issues shortly after they are discovered (including quarterly access reviews and the workflow and approval features). The effectiveness of these controls is evidenced by the fact that these issues were quickly identified. In addition, for the duplicate access issue, the risk was mitigated by the fact that the noncompliance was a duplicate documentation error concerning an individual with granted access and appropriate and updated security credentials. For the inaccurate authorized access list issue, the users in the domain group were trusted employees. For the failure to timely remove access issue, the employee on extended medical leave did not have access to the room that housed the CCA nor the ability to remotely access the application. This employee was also a trusted employee with a current PRA, background investigation, and CIP training. The employee was supporting the CCA during his transition to a new job role and would have retained his access for the necessary period to support the transition but for his extended leave of absence. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed electronic access for the individual who was on medical leave and no longer required access; 2) removed the employee’s physical access to the room housing the CCA; 3) completed a physical access removal ticket to clear the duplicate entry and ensure the accuracy of the status of the individual who transitioned from contractor status to full-time employee; 4) removed access for the members of the domain group in the inaccurate authorized access list issue who were granted access in error; 5) removed access for the two individuals in the inaccurate authorized access list issue and updated the appropriate documentation; 6) documented, reported, and provided feedback to performers on issues identified prior to implementation of a centralized access control program 7) developed a procedure, as part of RFC_URE1’s CIP V5 access control program, to ensure an associated access authorizer review group will be created for each Authorized Access List (for physical access and electronic access); 8) implemented a centralized access control program and mapped automated aspects to manual aspects under the prior program; and 9) ensured authorized access lists in scope of RFC_URE1’s CIP V5 program have been documented and aligned to an access authorizer review group during user acceptance testing. To mitigate this issue, RFC_URE1 will complete the following mitigation activities: 1) RFC_URE1 committed to document and report issues identified during the second quarter quality peer check process, including assessment of the improvements in access provisioning experienced through the new centralized tool. In order to minimize and prevent future occurrences of similar issues, as part of the RFC_URE1 CIP V5 implementation program, a project is being developed to improve and support access control and access governance across RFC_URE1. The project includes the design and implementation of a solution, which will centralize access management and governance processes and procedures. The solution will provide a number of centralized services including roles-based access control, user account life-cycle management, access certification (governance), password management, access requesting and approvals (authorization), and auditing and reporting functions. Many of the manual aspects of the current access program at RFC_URE1 will be centralized and automated in the new tool.
2016-07-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015283 | CIP-003-3 | R6 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. An operational technology employee copied an executable file used to migrate historical data to a non-critical Cyber Asset within an Electronic Security Perimeter. The executable file was tested in the test environment, but the employee did not adhere to RFC_URE2's formal change control process. Rather, the employee implemented the change in the production environment without first processing a Request for Change ticket. The root cause of this noncompliance was human error related to the employee’s failure to follow formal, documented procedures. This contributing factor relates to the management practice of workforce management, which focuses on, inter alia, providing training, education, and awareness to employees. The issue lasted approximately 1 day, from the date the employee implemented the change in the production environment until RFC_URE2 created a Request for Change ticket to document and approve the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE2's process for change control and configuration management is effective at preventing noncompliances of this nature. In the twelve months prior to this incident, RFC_URE2 generated 158 Request for Change tickets for CIP-related changes. This incident constitutes the only error during this time period, resulting in a 99.4% success rate. Second, RFC_URE2 promptly identified this noncompliance through its detective controls. Specifically, RFC_URE2 has implemented automatic scanning for files installed without proper adherence to the change control process. This detective control identified the issue and alerted appropriate personnel of the unauthorized executable file. Third, the cyber asset on which the executable file was installed is a historical system only with no control capability. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) counseled and trained the responsible employee on current procedures and related NERC CIP requirements; and 2) emphasized to staff the potential risk of human error possible when completing NERC CIP-related tasks.
2016-07-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015490 | CIP-007-3a | R3 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R3. After launching a new vulnerability management system, RFC_URE2 identified a patch that was not assessed within thirty days of availability. After this issue was identified, RFC_URE2 assessed the patch thirty-five days later. RFC_URE2 installed the patch on test assets following the assessment process. After RFC_URE2 verified that the patch had no adverse effect on the test assets, RFC_URE2 installed it on production assets. The root cause of this noncompliance was a configuration issue in RFC_URE2's system, which retrieves and organizes email notifications from vendors regarding patch releases. The system was using two folders to store emails related to security patches and mistakenly put this email notification in the wrong folder. This contributing factor relates to the management practice of asset and configuration management, which focuses on, inter alia, verifying the integrity of assets and configuration items, including performing assessments. This issue lasted approximately five days, from the date RFC_URE2 was required to assess the patch, until RFC_URE2 completed the assessment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the network traffic and analysis tool is used for troubleshooting only, and thus has no control capability. Second, RFC_URE2's new detective control, promptly identified this issue and notified the appropriate personnel. Third, even though the patch was assessed five days late, it was still tested and applied in the same timeframe that it would have been had it been assessed on time. No harm is known to have occurred. | To mitigate this issue, RFC_URE2 : 1) modified its system to consolidate patch notifications into a single email folder using an email rule to prevent this specific type of issue from occurring again; 2) implemented the system to track available patches associated with the majority of CIP related cyber assets that it scans (windows servers, workstations and many of the applications that reside on them), reducing the reliance on email for patch updates; and 3) updated the open patches report used by the system during the patch review process to change the color of the “Assessed Date” field to indicate that the window of time to assess a given patch is getting close or past due.
2016-07-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015282 | CIP-007-3a | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. While performing its Electronic Security Perimeter (ESP) Annual Review, RFC_URE2 identified an individual as having access to servers, without the corresponding access request ticket and approval. Said servers are non-critical Cyber Assets that reside within the ESP. The root cause of this noncompliance relates to the management practice of workforce management, which focuses on, inter alia, managing employee permissions and access to assets as well as employee training. Here, the responsible employee misunderstood an access request ticket that was submitted for this particular individual to give him access to the electric historian system. The responsible employee misunderstood the access request ticket and granted this individual access to both the electric and gas historian systems. This issue started on the date RFC_URE2 granted the individual access to the servers and ended on the date RFC_URE2 revoked this individual’s access to said servers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE2's process for reviewing ESP access is an effective preventative control. In the twelve months included in its ESP Annual Review, RFC_URE2 generated 582 CIP-related access request tickets. This incident constitutes the only error during this time period, resulting in a 99.8% success rate. Second, RFC_URE2 identified this noncompliance through its detective controls. Specifically, RFC_URE2 has implemented its ESP access review process to identify this type of noncompliance. This detective control identified the issue and alerted appropriate personnel. Third, the servers are non-critical cyber assets and operate a historical system with no control capability. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) revoked this individual’s access to the system; 2) counseled and trained the technician responsible for granting unauthorized access on current procedures and related NERC CIP requirements; and 3) emphasized to staff the potential risk of human error possible when completing NERC CIP-related tasks.
2016-07-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2016015494 | CIP-007-3a | R5 | SPPRE_URE1 submitted a Self-Report stating that it had two minimal risk instances of noncompliance with CIP-007-3a R5 because it did not implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. Instance No. 1 SPPRE_URE1 began transitioning its staff from SCADA system shared user accounts to individual user accounts. During this transition, its Dispatchers were allowed to share login sessions to ensure operational continuity. After the transition period ended, SPPRE_URE1 discovered that a new Dispatcher, who had a business need for electronic access to SPPRE_URE1’s SCADA system but had not yet been authorized for such access, had been sharing other Dispatchers’ individual SCADA user accounts to access the SCADA system during his work shifts. The duration of this noncompliance was five weeks; it began when the Dispatcher began sharing other Dispatchers’ SCADA user accounts and ended the date that the Dispatcher was granted authorized electronic access and obtained an individual SCADA user account. Instance No. 2 SPPRE_URE1 discovered that an Operations employee utilized other Operations employees’ individual SCADA user accounts during nine work shifts after his individual user account password had expired. The duration of this noncompliance lasted three weeks; it began when the Operations employee began utilizing other Operations employees’ SCADA user accounts and ended the date SPPRE_URE1 ensured that the Operations employee was accessing the SCADA system with the password for his individual SCADA user account. The root cause of both instances of noncompliance was a lack of training for Operations and Dispatch personnel to ensure they understood the required use of individually assigned SCADA accounts. Although SPPRE_URE1 had implemented a new policy requiring the use of individual SCADA accounts, SPPRE_URE1 did not provide specific training and formal policy reinforcement to Operations and Dispatch Staff on logging into/out of work stations using assigned individual SCADA accounts. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R5 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized access and possible misuse of Critical Cyber Assets (CCAs). Regarding the first instance of noncompliance, the new Dispatcher had a current PRA and cyber security training, had a business need for electronic access to the SCADA system, and was escorted within the Physical Security Perimeter by a Dispatcher with authorized electronic access and unescorted physical access. The new Dispatcher logged access each shift in an electronic log so that account access was documented and trackable. Regarding the second instance of noncompliance, the Operator is a long-time employee and was authorized for electronic access to the SCADA system and unescorted physical access to CCAs. SPPRE_URE1 timely detected, mitigated, and reported the instances of noncompliance. No actual harm occurred as a result of the noncompliance. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE1: 1) provided an individual account to the new Dispatcher; 2) provided refresher training to all Dispatchers; 3) issued a Dispatch Standing Order to Operations staff instructing them on the usage of individually assigned SCADA accounts; and 4) enabled a lock-out transparent screen saver feature on applicable staff workstations to enforce use of the individual SCADA accounts.
2016-07-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015015207 | CIP-005-3a | R1; R1.5 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had a minimal risk instance of noncompliance with CIP-005-3a R1.5 because it did not afford the protective measures specified in CIP-007-3a R5.3.3 to Cyber Assets used in the access control and/or monitoring of its Electronic Security Perimeter (ESP). CIP-007-3a R5.3.3 requires SPPRE_URE2, as part of its account management program, to change passwords at least annually on Cyber Assets within its ESP to minimize the risk of unauthorized system access. SPPRE_URE2 was unable to provide evidence of annual password changes for shared administrator accounts associated with its ESX virtual host servers, which are electronic access control and monitoring (EACM) devices located within SPPRE_URE2’s ESP. The duration of this instance of noncompliance lasted twenty-two months; from the day after the previous Compliance Audit, through the date SPPRE_URE2 provided documentation of password changes for the administrator accounts associated with the ESX virtual host servers. The root cause of this instance of noncompliance was a lack of internal controls to ensure full adherence to SPPRE_URE2’s Access Control Process. SPPRE_URE2’s Access Control Process covered shared passwords, required the passwords to be changed annually, and required documentation to demonstrate password changes. However, the process lacked a method to track and document password changes to the shared accounts. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R1.5 as it relates to CIP-007-3a R5.3.3 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized system access to devices located within an ESP. Notwithstanding, the ESX virtual host shared accounts were the only accounts affected by the noncompliance, and all other protective measures prescribed in R1.5 were afforded to the ESX virtual host servers. All Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE2’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE2 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) revised its Access Control Process to include: a. the utilization of a spreadsheet to track password changes for shared accounts, which will serve as documentation for password changes; and b. a review of password changes for shared accounts to be included in its quarterly access reviews; and 2) trained all affected personnel on the revisions to the Access Control Process. SPP RE has verified the completion of all mitigation activity.
2016-07-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015669 | CIP-003-3 | R6 | TRE_URE1 submitted a self-log stating that it had an issue with CIP-003-3 R6. Specifically, TRE_URE1 personnel deployed certain software that did not have an approved change control record to numerous Critical Cyber Assets (CCAs) and Non-Critical Cyber Assets (NCCAs) impacting the Texas RE region. TRE_URE1 personnel were attempting to diagnose certain communications issues between two endpoint systems and TRE_URE1's security management system. To understand the cause of these issues, TRE_URE1 personnel began preparations to deploy certain diagnostic software to gather logs and other necessary information. In preparation, the assigned TRE_URE1 technician began performing pre-deployment activities prior to seeking formal approval for the software change. During these preparations, however, the TRE_URE1 technician inadvertently used an automatic rather than manual installation process. As a result, the diagnostic software installation occurred immediately upon saving the work project on the security management system rather than following the formal approval process. Additionally, because the task was created at the organizational level, the diagnostic tool went to numerous CCAs and NCAAs instead of just the two endpoint systems. The root cause of this issue was that TRE_URE1 lacked detailed instructions on how to properly deploy the diagnostic software at issue. In addition, TRE_URE1 did not provide adequate training to the TRE_URE1 technician tasked with deploying this particular diagnostic software. TRE_URE1 had an issue with CIP-003-3 R6 for one day, from when TRE_URE1 personnel deployed the diagnostic software without formal change control documentation and approval until TRE_URE1 removed the diagnostic software from the impacted systems. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for several reasons. First, the software at issue is merely a diagnostic reporting tool. Because the software in question serves as a reporting tool, TRE_URE1 states that it would have no operational impact on the devices to which it was inadvertently deployed. Second, it was developed by and only relates to software from a trusted TRE_URE1 vendor. Finally, TRE_URE1 was immediately aware of the unintentional deployment and provided evidence that it removed the software from all impacted systems within 24 hours. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) removed the diagnostic software from all impacted systems one day after it was inadvertently deployed; 2) created and distributed a desk procedure that provides instructions on how to properly install the diagnostic software in question; and 3) trained the TRE_URE1 technician on the use and configuration of the diagnostic tool in TRE_URE1’s security management system.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014871 | CIP-006-3c | R1.1, R2.1, R1.6.2 | WECC_URE01 submitted a Self-Certification stating that it had a possible issue of noncompliance with CIP-006-3c R1.1, R1.2, and R1.6.2. Specifically, WECC_URE01 reported that it failed to ensure Critical Cyber Assets (CCAs) were within a completely enclosed (“six-wall”) border, failed to identify all Access Points (APs) to a Physical Security Perimeter (PSP), and failed to provide continuous escorted access to a visitor within the PSP, as described below. CIP-006-3c R1.1 issue - During a mock audit, a 2x4 foot opening in the Backup Control Center (BUCC) PSP was discovered. This opening had existed since the BUCC was commissioned. The hole was above the ceiling in the attic between the PSP and a manager’s office. The manager’s office was being monitored for access. CIP-006-3c R1.4 - two APs at a PSP were designated egress only emergency exits. Three APs at the BUCC were designated egress only emergency exits. The Physical Security Plan was updated within the 30 day window to identify the doors as non-access points. All of the doors had been programmed to deny access from the exterior; however, the hardware to allow access from the outside was not removed. WECC_URE01 received a report that the doors were being used to access the PSP since the date of their designation as egress only emergency exits. CIP-006-3c R1.6.2 - During two separate occasions, one of WECC_URE01’s operators escorted his son into a PSP, but failed to provide continuous escorting while in the PSP. Specifically, the operator left his son, while the operator finished filling out the visitor log. The other operators on duty could not account for the son’s whereabouts. During the investigation into this issue, another instance of not performing escorting responsibilities in accordance with WECC_URE01’s established program occurred was discovered. The CIP-006-3c R1.1 issue began when WECC_URE01 commissioned a new PSP with CCAs but failed to ensure the PSP had a completely enclosed (“six-wall”) border, and ended six days after WECC_URE01 discovered the PSP opening when WECC_URE01 installed a mesh barrier thus completely enclosing the PSP. The CIP-006-3c R1.2 the issue began when the APs in question where designated as egress only emergency exits, and ended 29 days after notice of the issue when the doors were designated as PSP APs and the Physical Security Plan was updated to reflect the change. The CIP-006-3c R1.6.2 issue began when the operator failed to provide continuous escorting of his son within a PSP, and ended on when WECC_URE01 provided training on its visitor management program. The root cause of this issue was human error in that WECC_URE01 personal failed to follow documented procedures for securing their PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE01 failed to ensure CCAs are enclosed within a completely enclosed (“six-wall”) border could lead to unauthorized access to, and use of, the CCAs within the PSP. WECC_URE01 implemented strong preventive controls. Specifically, the opening into the PSP is in the attic between the PSP and an adjoining room; the only access point into the attic is inside the PSP. Without direct access into the PSP, it would be difficult for someone to easily gain access to the attic. The adjoining room has a plaster ceiling with no openings to access the attic; someone could attempt to create a hole in the ceiling, and therefore access the attic, but that attempt could take time, allowing WECC_URE01 personnel more time to stop any such attack. WECC_URE01 also has personnel in the PSP 24x7 who could prevent the person from damaging any devices. WECC_URE01 implemented strong detective controls. Specifically, although the room adjoining the PSP is not part of the PSP, WECC_URE01 installed tools to monitor access to the room. If a malicious person were to gain access into the adjoining room and attempt to create a hole in the ceiling, WECC_URE01 could know that an unauthorized person is in the room and take appropriate action. WECC_URE01 also has personnel in the PSP 24x7 who could detect if someone attempted to enter the PSP from the ceiling. WECC_URE01 confirmed that only authorized access personnel entered the door associated with the card reader at the PSP Access Points during the time in question. All security controls and measures remained in place to monitor access for the doors following their designation as non-access points. This includes card reader door alarms, security guard site patrols, and investigations of potential unauthorized access into the SOC and BUCC PSP. WECC_URE01's CIP Senior Manager approved modifications to WECC_URE01's CIP-006-3c Physical Security Plan and associated PSP diagrams to reinstate the subject APs as defined "PSP APs" for both the SOC and BUCC. As part of the investigation WECC_URE01's personnel conducted an assessment to determine if any CCA's had been compromised or systems conditions had changed during the period of time the SOC operator’s son was left unescorted. WECC_URE01 operations staff reviewed the EMS logs for any abnormalities or lack of alarms responses that negatively impacted WECC_URE01's system. The results determined that there were no issues or impacts to the either systems. Additionally, because the escorting operator is assigned to WECC_URE01's a facility that only monitors and controls distribution services, WECC_URE01's BES equipment was not logically or physically affected. Based on this information, and because no harm is known to have occurred, these issues posed minimal risk to the reliability of the Bulk Power System. | To mitigate this issue, WECC_URE01: 1) completed mitigation of all three issues on when it installed a mesh barrier over the PSP opening. 2) WECC_URE01 provided refresher training to its personnel on visitor control practices, and designated the five access doors as PSP APs. 3) WECC_URE01 updated its change management process, specifically for changes to PSPs. Any change to a PSP needs to be approved and vetted prior to the change. The new form being used includes: requestor name, change justification, designated approving authority, and confirmation date of when the change was completed. 4) WECC_URE01 conducted additional refresher Physical Security Training to reinforce WECC_URE01's Visitor Pass Management responsibilities to the personnel who have physical access to WECC_URE01's CCA locations, 5) and WECC_URE01 conducted a system assessment to ensure WECC_URE01 CCAs and Transmission operations systems were not affected. WECC verified completion of WECC_URE01’s mitigating activities.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015072 | CIP-007-3a | R6 | WECC_URE01 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R6. Specifically, WECC_URE01 reported that it did not ensure that four devices were being monitored for system events related to cyber security. At the time of their installation, the devices were configured to monitor events at the device level, but these logs were not being sent and monitored by WECC_URE01’s system so logs were never reviewed. The issue was discovered when WECC_URE01 was preparing for a mock audit. This issue began when WECC_URE01 installed four devices within WECC_URE01’s Energy Management System (EMS), and ended when WECC_URE01’s system administrator configured its system to monitor the four devices for security events. The root cause of this issue was WECC_URE01's lack of a process to ensure new devices are monitored when being put into production | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE01 failed to monitor four FEP Terminal Servers for security events. Failing to monitor system events related to cyber security could allow for undetected malicious activity on the devices, which could disrupt the entity’s load and generation control. Although the devices were not connected to any field devices, they were still within the EMS Electronic Security Perimeter (ESP). However, the risk of an outside person compromising the devices is low as the devices were inside the ESP; behind a firewall with access controls designed to deny access by default. The entity also used an Intrusion Detection System (IDS) to monitor traffic into and out of the ESP and could have detected malicious activity designed to compromise the devices. Finally, the devices were connected to the EMS network, but were not fully implemented for use in the network. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. | To mitigate this issue, WECC_URE01: 1). WECC_URE01 configured the four devices to monitor for security events. 2). WECC_URE01 updated its change control process for new devices to receive proof from its Security Monitor Program that any new devices added to the EMS are monitoring upon commissioning. WECC verified completion of WECC_URE01’s mitigating activities.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015060 | CIP-007-3a | R3 | WECC_URE02 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R3. Specifically, WECC_URE02 reported that a WECC_URE02 employee conducted a review following an end-of-life announcement for an antivirus software product. During this review, the employee discovered that a patch for the antivirus software product had not been installed on certain Cyber Assets. The patch had previously been approved for installation. WECC_URE02 had a program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). In this instance, however, WECC_URE02 did not install the patch during its quarterly process. The devices in scope were located within designated PSPs. This issue began when WECC_URE02 failed to install an approved cyber security patch on the Cyber Assets, and ended when the approved cyber security patch was installed on the Cyber Assets in scope. The cause of this issue of noncompliance is WECC_URE02's failure to follow established documented procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE02 failed to implement its CIP-007 R3 Security Patch Management program by not installing an assessed and approved patch during its quarterly patch cycle. The patch was applicable to WECC_URE02’s anti-virus software and resolved a single security vulnerability which could potentially allow privilege escalation to an authenticated user. Failure to install applicable cyber security patches could allow potentially harmful software to remain on the devices in scope which could affect WECC_URE02’s ability to control generation. However, to take advantage of this vulnerability, an attacker would need existing access as an authenticated user. WECC_URE02 performs PRAs on, and provides training to, all individuals who are granted access to its CCAs as authenticated users. Privilege escalation would not provide additional access to WECC_URE02's EMS. The use of special privileges was logged on WECC_URE02's access control and monitoring devices. In addition, failed access attempts would be logged and alerted by WECC_URE02's access control and monitoring devices. WECC_URE02's firewalls were not vulnerable to this exploit, and would continue to monitor the ESP. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC_URE02 does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WECC_URE02: 1) implemented a new step in its patch evaluation procedure to identify an SME associated with each patch, which will be documented in its Security Patch Evaluation Log. 2) streamlined its Security Patch Evaluation log to more clearly delineate each patch evaluation window. 3) implemented a peer review of each security-related patch that has been approved for installation, to ensure that all applicable Cyber Assets have been patched and documented appropriately. The SME associated with each patch will sign-off on each of their patches in the Security Patch Evaluation Log to indicate successful completion of the peer review. WECC approved completion of WECC_URE02's mitigation plan.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015015240 | CIP-007-1 | R5 | WECC_URE03 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-1 R5. Specifically, WECC_URE03 reported that one of its administrators discovered that certain Critical Cyber Assets (CCAs), were not sending access attempt logs to its log center. WECC_URE03 determined that its procedure to configure devices to send access attempt logs to its center was not sufficient and WECC_URE03 lacked technical controls to prevent or detect this issue. This issue began for each device when it was deployed . Remediation was completed when all devices were configured to send access attempts logs to WECC_URE03’s log center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE03 failed to ensure that logs of sufficient detail to create a historical audit trail of user account access activity were being generated. Specifically, there are 25 devices in scope located in two PSPs and one ESP: 11 terminal services routers, 10 switches, and 4 routers. Failing to generate logs of sufficient detail to create historical audit trails of account use could lead to unauthorized access attempts and unauthorized use not being detected and handled accordingly. If malicious activity occurred on the devices, the entity may not be able to detect the activity or determine the origin of the activity. However, WECC_URE03 had several layers of controls to prevent this, including limiting ports and services on the devices to only those required, which could limit the possible attack surface. WECC_URE03 also used antivirus on its network which could detect any malicious software used in an attack. The devices were within an ESP and behind Access Points configured to only allow authorized traffic into the ESP. Physical access to the devices was also restricted to those with CIP training, current PRA, and approved access. These controls limit the likelihood a successful attack could occur and go undetected. | To mitigate this issue(s) WECC_URE03: 1) identified all CIP devices at the BCC with configurations which were not reporting user access activity and reconfigured those devices to forward failed and access logins to the log center server; 2) configured its servers with rules and policy test to automatically detect misconfigurations going forward; and 3) updated CIP-007-3 procedures to ensure that all new device types are configured in accordance CIP-007-3 R5.1.2, and tested prior to deployment into production. WECC verified completion of mitigation.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015015162 | CIP-002-3 | R2 | WECC_URE04 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-002-3 R2. Specifically, WECC_URE04 reported that during its annual review of its Critical Asset list, WECC_URE04 failed to update the list after a change. The scope of this possible issue of noncompliance is one Critical Asset. This issue began when WECC_URE04 added a new Critical Asset to its inventory of existing Critical Assets, and when WECC_URE04 added the Critical Asset to its Critical Asset list in accordance with CIP-002-3 R2. The cause of this issue of noncompliance was a lack of communication between WECC_URE04’s Compliance, and Transmission and Distribution departments relating to documented procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE04 failed to update its Critical Asset list, after a change, in a timely manner. Failing to update the Critical Asset list could lead to Critical Cyber Assets not being documented and protected, which could potentially result in negative impacts to the reliability of the Critical Asset. In this instance, the Critical Asset did not contain any Critical Cyber Assets and WECC_URE04’s Critical Asset list was updated as soon as the issue was discovered. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue(s) WECC_URE04: 1) will implement new processes and procedures as part of its CIP Version 5 transition which will help mitigate and prevent this issue from occurring again WECC verified that WECC_URE04 remediated this issue.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015015003 | CIP-003-3 | R5 | WECC_URE04 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-003-3 R5. Specifically, an outside legal consultant contracted to work for WECC_URE04 had access to an excel spreadsheet containing a list of CIP Cyber Asset device names and locations, classified by WECC_URE04 as Critical Cyber Asset (CCA) protected information, without approved authorization. WECC_URE04’s manager learned that WECC_URE04’s litigation counsel had collected emails from his inbox in order to determine their relevance to an ongoing non-NERC related litigation matter. Those emails were stored in a WECC_URE04 database that WECC_URE04 litigation counsel could access, including outside legal consultants. This issue began when the litigation attorney viewed the CIP Cyber Asset device names and location list, and ended when WECC_URE04’s personnel deleted the manager’s emails from the database. The cause of this issue of noncompliance was an oversight by WECC_URE04 to explicitly document, in its information protection policy, that WECC_URE04 litigation personnel should be authorized to have access to NERC CIP protected information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE04 failed to approve access to Critical Cyber Asset protected information for one litigator prior to that litigator accessing said information. Viewing this information, the lawyer could have intentionally or unintentionally shared (via email) the information with other third parties, who could potentially be malicious. A malicious person could attempt to attack WECC_URE04’s Energy Management System (EMS) and targeted the device names listed in the file at those locations. However, the risk of malicious harm occurring was low as the litigator had a legitimate reason to have access to the information and was reviewing the document to determine its relevance in a case. It is also unlikely that access to only device names and locations could be used to cause harm to WECC_URE04’s EMS. Additionally, WECC_URE04 had logical and physical controls (such as firewalls, Intrusion Detection System, antivirus, card readers, guards, etc.) to help prevent an attack on its Critical Cyber Assets within its EMS. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue WECC_URE04: 1) updated its NERC CIP Information protection program to include a section to address access for its Law Department and outside counsel; and 2) provided new online training covering NERC CIP Protected Information to over 5,500 personnel.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015015424 | CIP-003-3 | R6 | WECC_URE04 submitted a Self-Reported stating that it had a possible issue of noncompliance with CIP-003-3 R6. Specifically, WECC_URE04 reported that in the course of an internal review, WECC_URE04 discovered that a workstation identified as a Critical Cyber Asset (CCA), had been removed from the Electronic Security Perimeter (ESP) and decommissioned without an approved Request for Change (RFC) form. The proposed change to the workstation was originally documented in an RFC which was subsequently cancelled as it was believed the workstation was already covered in a different RFC. The end result was that the workstation was not covered by an RFC as required by the WECC_URE04 procedure. This issue began when WECC_URE04 decommissioned and removed the workstation from within the ESP without documenting the change, and ended when WECC_URE04 completed formal documentation of the change and reported the change to its compliance office, in accordance with WECC_URE04’s procedure. The cause of this issue was that accuracy /effectiveness of a change was not verified or validated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE04 failed to implement supporting configuration management activities to identity, control, and document changes to hardware and software components of Critical Cyber Assets as required by CIP 003-3 R6. Per the WECC_URE04’s Change Management Procedure, a device was removed from the ESP without a valid Request for Change (RFC) to support the change. Failure to implement established change control and configuration management processes could potentially allow adding or modifying hardware and software component changes that could be harmful to Critical Cyber Assets essential to the operation of the BES, thereby introducing or exposing potential security vulnerabilities to the Critical Cyber Assets within the ESP. However, WECC_URE04 had an established Change Management Procedure in place which included processes for completing an RFC, and in fact did complete the RFC, which was inadvertently deleted. Additionally, WECC_URE04, as a practice, performed internal reviews of changes to CCAs, which discovered this issue and remediated quickly. Based on this information and because no harm is known to have occurred, this issues posed minimal risk to the reliability of the BPS. | To mitigate this issue WECC_URE04 implemented an asset auto-discovery tool. The tool created a baseline of what existed on the devices in the ESP and will monitor and detect changes to the baseline. Changes to the baseline are investigated and corrected as appropriate.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015493 | CIP-005-3a | R2; R2.2 | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a R2. As part of the preparation for CIP Version 5 standards, NPCC_URE1 installed a tool for identifying open ports and services on critical cyber assts. This software replaces the manual processes that were previously used to meet the open ports and services requirements of CIP Version 3, specifically CIP-005-3a and CIP-007-3a, by identifying and detecting open ports. After the installation of the software was completed, it detected open ports and services that were not properly disabled by the manual processes previously used. The software detected several ESP access points, specifically ports and services on several terminal servers. The servers are used by URE1 to collect serial data from substation remote terminal units (RTUs) and encapsulate the data for use by the Supervisory Control and Data Acquisition (SCADA) energy management system (EMS). The duration of the issue was six years. The root cause of this issue was NPCC_URE1 using an incorrect command to close the ports and services. Since the implementation of the port scanning tool, NPCC_URE1 discovered that the previous command did not actually close the ports and services, rather it removed the entry from the service table list without actually disabling it. Since the ports and services were removed from the service table list but not actually disabled, NPCC_URE1 was unable to detect them as open without the use of a port scanning tool. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The terminal servers are isolated from the corporate data network and internet behind multiple layers of firewall. The devices have a lack of external routable connectivity, therefore a physical connection to the device would be necessary to access any of the open ports and services. For the unnecessarily open ports and services in question to have been compromised, a physical breach at the substation would have been necessary. If such access had occurred, any malware installed on the device would have been detected by the defense software, and antivirus servers within the control center would have flagged and alarmed for unauthorized malware. NPCC_URE1 has IT staff on hand at all times to address such alarms. No physical breach incidents were reported during the time period of the issue. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Disabled all ports and services not required for normal and/or emergency operations on the servers; 2) The NPCC_URE1 CIP team met with NPCC_URE1's corporate security technical specialists to review the network configuration, the security measures in place, and the impact of the open ports and services; and 3) Updated the procedure that includes the commands for disabling ports and services on the servers to include the correct command. NPCC has verified the completion of all mitigation activity.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015605 | CIP-005-3a | R4; R4.2 | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a, R4.2. Since the port scanning tool detected that NPCC_URE1 had unnecessarily opened ports and services on several terminal servers, it was also determined that NPCC_URE1's annual Cyber Vulnerability Assessments (CVAs) for four years were insufficient because they had not detected that the ports and services that were not needed were actually open. The root cause of this issue was the use of an incorrect command to disable the unneeded ports and services. NPCC_URE1 had used a command that only removed the ports and services from the service table list without actually disabling them. When the vendor that NPCC_URE1 hired to complete their CVAs during the four-year period compared the list of open ports and services on the service table list against a baseline spreadsheet, it showed only the necessary ports and services as open, even though all of the ports and services were open. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The terminal servers are isolated from the corporate data network and internet behind multiple layers of firewall. The devices have a lack of external routable connectivity, therefore a physical connection to the device would be necessary to access any of the open ports and services. For the unnecessarily open ports and services in question to have been compromised, a physical breach at the substation would have been necessary. If such access had occurred, any malware installed on the device would have been detected by defense software, and antivirus servers within the control center would have flagged and alarmed for unauthorized malware. NPCC_URE1 has IT staff on hand at all times to address such alarms. No physical breach incidents were reported during the time period of the issue. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Disabled all ports and services not required for normal and/or emergency operations on the servers; 2) Will use the automated port scanning tool in the future to identify open ports and services and will use the tool as part of the CVA process; and 3) The NPCC_URE1 CIP team met with NPCC_URE1's corporate security technical specialists to review the network configuration, the security measures in place, and the impact of the open ports and services. NPCC has verified the completion of all mitigation activity.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015607 | CIP-007-3a | R1; R1.1; R1.2; R1.3 | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R1. Since the port scanning tool detected that NPCC_URE1 had one unnecessarily opened port and service on each of two control system servers, it was also determined that NPCC_URE1's testing during commissioning of the two servers was insufficient. During NPCC_URE1's Supervisory Control and Data Acquisition (SCADA) system upgrade, two servers that had previously been running an older SCADA system version were reused with the newer version. A port on the servers was required to be open for the previous version, but was not required to be open for the newer version. The port therefore should have been disabled during commissioning of the new servers, however it remained open on each of the servers. Testing during installation of the new SCADA version on the servers did not detect that the port was left open when it should have been closed in the new version. When NPCC_URE1 implemented the port scanning tool and ran it on the servers, it was determined that the port was open when it should have been closed. The duration of the issue was for two years. The root cause of this issue was the use of the previous version baseline spreadsheet for ports and services during security controls testing rather than an updated version baseline. Since the applicable port was required to be open in the previous version it showed up as open on the baseline spreadsheet. When the running ports and services were compared against the baseline during security controls testing, the port was left open due to it being required for the older version. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The control system servers are located within the physical security perimeter (PSP) and electronic security perimeter (ESP) of NPCC_URE1's control centers, and are isolated from the corporate date network and internet behind multiple layers of firewall. Electronic access to the servers through the ports that were open is blocked at the network firewall. For the server's ports and services in question to have been compromised, a physical breach at the control center, or an electronic breach of the two factor remote access controls would have been necessary. A physical breach of the control center would have generated alerts that would have made corporate security aware of the breach in order to respond immediately. If an electronic breach of the two factor remote access controls had occurred, defense software and firewall alerting within the control center would have alarmed and notified support personnel of the compromise. No physical breaches of the control center, nor electronic breaches of the two-factor remote access controls occurred during the time period of the issue. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Disabled the port and service not required for normal and/or emergency operations on each of the two servers at the control center; 2) The NPCC_URE1 CIP team met with NPCC_URE1's corporate security technical specialists to review the network configuration, the security measures in place, and the impact of the open ports and services; and 3) Will use the automated port scanning tool in the future to identify open ports and services on all CCAs. NPCC has verified the completion of all mitigation activity.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015608 | CIP-007-3a | R2; R2.1; R2.2 | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R2. During NPCC_URE1's Supervisory Control and Data Acquisition (SCADA) system upgrade, two servers that had previously been running an older SCADA system version were reused with the newer version. A port on the servers was required to be open for the previous version, but was not required to be open for the newer version. The port therefore should have been disabled during commissioning of the new servers, however it remained open on each of the servers. When NPCC_URE1 implemented the port scanning tool and ran it on the servers, it was determined that the port was open when it should have been closed. The duration of the issue was for two years. The root cause of this issue was the use of the previous version baseline spreadsheet for ports and services during security controls testing rather than an updated version baseline. Since the applicable port was required to be open in the previous version it showed up as open on the baseline spreadsheet. When the running ports and services were compared against the baseline during security controls testing, the port was left open due to it being required for the older version. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The control system servers are located within the physical security perimeter (PSP) and electronic security perimeter (ESP) of NPCC_URE1's control centers, and are isolated from the corporate date network and internet behind multiple layers of firewall. Electronic access to the servers through the ports that were open is blocked at the network firewall. For the server's ports and services in question to have been compromised, a physical breach at the control center, or an electronic breach of the two factor remote access controls would have been necessary. A physical breach of the control center would have generated alerts that would have made corporate security aware of the breach in order to respond immediately. If an electronic breach of the two factor remote access controls had occurred, defense software and firewall alerting within the control center would have alarmed and notified support personnel of the compromise. No physical breaches of the control center, nor electronic breaches of the two-factor remote access controls occurred during the time period of the issue. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Disabled the port and service not required for normal and/or emergency operations on each of the two servers at the control center; 2) The NPCC_URE1 CIP team met with NPCC_URE11's corporate security technical specialists to review the network configuration, the security measures in place, and the impact of the open ports and services; and 3) Will use the automated port scanning tool in the future to identify open ports and services on all CCAs. NPCC has verified the completion of all mitigation activity.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015609 | CIP-007-3a | R8; R8.2 | NPCC_URE1 submitted a Self-Report stating that they had an issue of CIP-007-3a, R8.2. Since the port scanning tool detected that NPCC_URE1 had one unnecessarily opened port and service on each of two control system servers, it was also determined that NPCC_URE1's annual Cyber Vulnerability Assessments (CVAs) for two years were insufficient because they had not detected the open ports and services that should have been closed. The root cause of this issue was the use of a baseline spreadsheet for ports and services required for normal and/or emergency operations from an older version of the Supervisory Control and Data Acquisition (SCADA) system on the servers. The established baseline spreadsheets from the previous version of the SCADA system required the port to be open, however when NPCC_URE1 upgraded to a newer version, the port was not required anymore and should have been closed. When the vendors NPCC_URE1 hired to complete their CVAs compared the open ports and services against the baseline spreadsheets, the showed up as properly open since the spreadsheet was using the previous version of the system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The control system servers are located within the physical security perimeter (PSP) and electronic security perimeter (ESP) of NPCC_URE1's control centers, and are isolated from the corporate date network and internet behind multiple layers of firewall. Electronic access to the servers through the ports that were open is blocked at the network firewall. For the server's ports and services in question to have been compromised, a physical breach at the control center, or an electronic breach of the two factor remote access controls would have been necessary. A physical breach of the control center would have generated alerts that would have made corporate security aware of the breach in order to respond immediately. If an electronic breach of the two factor remote access controls had occurred, defense software and firewall alerting within the control center would have alarmed and notified support personnel of the compromise. No physical breaches of the control center, nor electronic breaches of the two-factor remote access controls occurred during the time period of the issue. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Disabled the port and service not required for normal and/or emergency operations on each of the two servers at the control center; 2) The NPCC_URE1 CIP team met with NPCC_URE1's corporate security technical specialists to review the network configuration, the security measures in place, and the impact of the open ports and services; and 3) Will use the automated port scanning tool in the future to identify open ports and services on all CCAs and will use the tool as part of the CVA process. NPCC has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014823 | CIP-007-3a | R5 | RFC_URE1 submitted a Self-Certification stating that it had an issue of CIP-007-3a R5. RFC_URE1 failed to log their regular use of three Critical Cyber Assets (CCAs) that have shared accounts. During RFC_URE1's CIP-007-3a Self-Certification review, RFC_URE1 identified that its staff was failing to regularly log their use of three CCAs that have shared accounts. The manual logging was put in place for all three CCAs with shared accounts to provide an audit trail and to show compliance for those individuals who accessed the CCAs per CIP-007-3a R5.1.2 and CIP-007-3a R5.1.3. The Standard requires that individuals log every time they use these CCAs that have shared accounts and RFC_URE1's manual logging, if followed properly, would show compliance. The logs for these CCAs, however, were only sporadically filled out. For the Transmission Control Room PC specifically, the operators were not logging when they would use the Transmission Control Room to monitor normal operations. The operators, however, would log any abnormal operations such as switching or password changes. CIP-007-3a R5.1.2 says the Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days and CIP-007-3a R5.1.3 requires RFC_URE1 to review those user accounts at least annually to verify access privileges are being followed in accordance with CIP-003-3 R5, CIP-004-3 R4. This noncompliance concerned the management practice of implementation because RFC_URE1 did not effectively implement its process to have RFC_URE1 staff regularly log their use of the CCAs at issue. RFC_URE1 also did not verify that the logging process had been effectively implemented and that all relevant RFC_URE1 staff were following the process. The root cause was weak implementation and ineffective training. The operators were not effectively trained as they did not understand that they needed to log every time they used one of the shared accounts. The duration of this noncompliance is from the date RFC_URE1 first failed to log its use of CCAs with shared accounts, to the date RFC_URE1 finished retraining those personnel with access to CCAs on the proper logging procedure for accessing those CCAs. | ReliabilityFirst determined that the subject noncompliance posed a minimal risk to the reliability of the bulk power system based on the following factors. All individuals with access to the Physical Security Perimeters (PSPs) and CCAs have gone through the access authorization process prior to being placed on the access matrix. An individual must be on the access matrix in order to gain access to the CCAs. RFC_URE1 performs quarterly reviews to ensure that the access matrix is current and correct. RFC_URE1 restricts access to the passwords to the CCAs to individuals that need to access the specific CCA. Individuals logging onto the CCAs can be identified forensically through RFC_URE1 card readers and cameras. Lastly, this Standard and Requirement does not exist in CIP V5, which minimizes the risk posed by this noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) reviewed all access attempts on the three CCAs at issue; 2) reviewed the access matrix for those CCAs in that PSP to ensure that only the personnel who were supposed to have access had access; 3) retrained those personnel with access to the CCAs with shared accounts on the proper logging procedure for accessing those CCAs with shared accounts. RFC_URE1 has a procedure that details how personnel are supposed to log in when accessing those CCAs and RFC_URE1 reinforced that procedure with the relevant personnel as part of the retraining; and 4) reviewed and confirmed that the personnel are properly logging their access every time they access one of the shared accounts on the CCAs. RFC_URE1 presented 90 days of logs for the CCAs from the time period in question that showed that personnel were logging their use of the CCAs. In terms of preventing future recurrence, this Standard and Requirement does not exist in CIP V5. Nevertheless, RFC_URE1 is committed to ensuring the security of its bulk power system Cyber Assets by being compliant with CIP V5. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014724 | CIP-003-1 | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue with CIP-003-1 R4. RFC_URE2 failed to properly identify, classify, and protect information associated with Critical Cyber Assets (CCAs) in accordance with RFC_URE2’s Information Protection Program. RFC_URE2 discovered testing and configuration data containing CIP Confidential Information stored in four different places within the System: (1) the Asset Management module, (2) the Change Management module, (3) the Issue Management module; and, (4) the Problem Management module. Although RFC_URE2 performed the requisite quarterly access entitlement reviews of the System’s Asset Management module, these reviews did not include a check to ensure that the individuals on the access list had a “need to know” the information, as required by RFC_URE2’s Information Protection Program. Additionally, RFC_URE2 determined that it did not perform any quarterly access entitlement reviews of the System’s Change Management module, Issue Management module, and Problem Management modules, as required by RFC_URE2’s Information Protection Program. The root cause of this noncompliance was human error related to the management practice areas of information management and verification. This noncompliance involves information management because RFC_URE2 failed to adequately vet employees who had access to all of its sensitive information. This noncompliance involves verification because RFC_URE2 failed to ensure that it performed its quarterly access entitlement reviews in accordance with the requirements of its Information Protection Program. The duration of this noncompliance is from the date RFC_URE2 was required to comply with CIP-003-1 R4, to the date by which RFC_URE2 added the Asset Management, Change Management, Issues Management, and Problem Management modules to its Information Protection Program and ensured that they are subject to quarterly information protection entitlement reviews. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, RFC_URE2’s failure to perform the requisite access entitlement reviews for the Change Management, Issue Management, and the Problem Management modules, resulted in only three missed user accounts because almost all user accounts were covered by the review RFC_URE2 performed on the Asset Management module. Second, those three missed user accounts included: (1) a test account created by the System’s administrator; (2) an account for an employee who has been with RFC_URE2 for approximately 7 years; and, (3) an account for a contractor who has worked with RFC_URE2 for approximately 5 years. Furthermore, both the employee and contractor had received annual CIP certification training as required by CIP-004 and had proper Personnel Risk Assessments in place. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) performed all necessary quarterly entitlement reviews; 2) added the Asset Management, Change Management, Issues Management, and Problem Management modules to its Information Protection Program and ensure that they are subject to quarterly information protection entitlement reviews; 3) expanded the distribution of its survey regarding potential new locations of CIP Confidential Information to include all of RFC_URE2's Information Technology management (previously this survey was provided only to known CIP Confidential Information Owners). RFC_URE2 also changed its Information Protection Program to require a quarterly review of this survey (previously RFC_URE2 performed an annual review of the survey); 4) replaced the entire platform for the Remedy Ticket System with a new platform to improve access management; and, 5) ensured that all CIP Confidential Information located on the platform is added to the Information Protection Program and the list of quarterly entitled reviews.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014725 | CIP-003-1 | R5 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-1 R5. RFC_URE2 determined that it did not annually review access privileges for three user accounts in the System’s Change Management module, Issue Management module, and Problem Management modules. The root cause of this noncompliance was human error related to the management practice areas of information management and verification. This noncompliance involves information management because RFC_URE2 was unaware of where it stored all of its sensitive information. This noncompliance involves verification because RFC_URE2 failed to ensure that it performed its quarterly access entitlement reviews in accordance with the requirements of its Information Protection Program. The duration of this noncompliance is from the date on RFC_URE2 was required to comply with CIP-003-1 R5, to the date by which RFC_URE2 added the Asset Management, Change Management, Issues Management, and Problem Management modules to its Information Protection Program and ensured that they are included in the quarterly information protection entitlement reviews. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, RFC_URE2’s failure to perform the requisite access entitlement reviews for the Change Management, Issue Management, and the Problem Management modules, resulted in only three missed user accounts because almost all user accounts were covered by the review RFC_URE2 performed on the Asset Management module. Second, those three missed user accounts included: (1) a test account created by the System’s administrator; (2) an account for an employee who has been with RFC_URE2 for approximately 7 years; and, (3) an account for a contractor who has worked with RFC_URE2 for approximately 5 years. Furthermore, both the employee and contractor had received annual CIP certification training as required by CIP-004 and had proper Personnel Risk Assessments in place. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) performed all necessary quarterly entitlement reviews; 2) added the Asset Management, Change Management, Issues Management, and Problem Management modules to its Information Protection Program and ensure that they are subject to quarterly information protection entitlement reviews; 3) expanded the distribution of its survey regarding potential new locations of CIP Confidential Information to include all of RFC_URE2's Information Technology management (previously this survey was provided only to known CIP Confidential Information Owners). RFC_URE2 also changed its Information Protection Program to require a quarterly review of this survey (previously RFC_URE2 performed an annual review of the survey); 4) replaced the entire platform for the Remedy Ticket System with a new platform to improve access management; and 5) ensured that all CIP Confidential Information located on the platform is added to the Information Protection Program and the list of quarterly entitled reviews.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015372 | CIP-007-3a | R3 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R3. RFC_URE3 assessed an applicable patch within thirty days of its release, but did not timely document that assessment. More specifically, a vendor released a security patch applicable to RFC_URE3. Twenty-four days later, RFC_URE3 assessed the patch and scheduled the patch to be deployed and thereafter deployed the patch without delay. RFC_URE3 had documentation of its assessment in the form of meeting minutes and an email, but did not document the assessment in RFC_URE3’s SharePoint site, as required by its procedures, until 116 days after the vendor released the patch (86 days late). A root cause was that, due to human error and lack of verification controls, RFC_URE3’s employee did not enter the patch in RFC_URE3’s tracking tool, which contributed to RFC_URE3 not creating the required documentation for the assessment. RFC_URE3’s mitigation includes adding verification controls for patch applicability documentation to reduce the likelihood of this type of human error recurring. The issue started on the date by which RFC_URE3 was required to document the assessment, and ended on the date RFC_URE3 formally documented its assessment of the security patch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was a documentation issue because RFC_URE3 timely assessed the security patch and, without delay, implemented the patch. RFC_URE3 merely failed to formally document the assessment, although it had informal documentation in the form of meeting minutes and an email. Additionally, RFC_URE3 self-identified the noncompliance and then immediately documented its assessment. Accordingly, the noncompliance posed only minimal risk to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) documented the patch as required by RFC_URE3’s patch assessment process; 2) counseled the responsible Patch Analysts on the requirements of the documented patch assessment process, including the importance of following procedure and the impact of non-compliance; 3) determined whether the patch was evaluated for applicability within thirty days of availability; 4) evaluated new controls and reviewed the apparent cause of human error and discussed new controls to address the noncompliance; 5) developed a quality check control to verify that the outcome of patch analysis meetings are entered into RFC_URE3’s SharePoint site as required by the process, including frequency of verification, parties involved, and artifacts as proof of completion; and 6) implemented new control steps identified in the plan developed in the previous milestone by updating its current process and notifying and training staff on the change.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015374 | CIP-007-3a | R9 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R9. This noncompliance involves two instances. First, RFC_URE3 deployed two cyber assets into production. During the preparation for deployment, RFC_URE3 discovered that a newer version of software on the cyber assets necessitated a modification of a line command in the test procedures, and RFC_URE3 thus executed the updated line command. However, due to this change, CIP-007-3 R9 requires RFC_URE3 to update the test procedures within thirty calendar days. RFC_URE3 did not update the documentation until 67 days later. RFC_URE3 discovered the issue as a result of routine discussions during its Information Technology department’s staff meeting. Second, RFC_URE3 identified that a vendor implemented changes to the command structure of network load balancer assets. Due to this change, CIP-007-3 R9 requires RFC_URE3 to update the test procedures documentation within thirty calendar days. RFC_URE3 executed the updated command several times before identifying the documentation error during a system upgrade over two years later. RFC_URE3 updated the documentation shortly after identifying the issue. ReliabilityFirst determined that a root cause related to lack of verification controls to ensure that changes to the system were implemented pursuant to RFC_URE3’s processes, which required that documentation be updated to reflect current test procedures. The first instance started on the date RFC_URE3 should have updated its test procedure, and ended on the date RFC_URE3 updated its test procedure. The second instance started on the date RFC_URE3 should have updated its test procedure, and ended on the date RFC_URE3 updated its test procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This was a documentation issue because although the documentation was not updated, RFC_URE3 executed the correct, updated tests on the assets at issue. Accordingly, the noncompliance posed only minimal risk to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) updated its test procedures; 2) evaluated its Change Management Ticketing System and associated process for improvement; 3) retrained and counseled the employees on documentation updates; and 4) implemented process improvements and technical modifications.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015396 | CIP-004-3a | R3 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-004-3a R3. RFC_URE4 failed to update expired personnel risk assessments (PRAs) for ten employees. RFC_URE4 uses a Physical Access Control System (PACS) to monitor and control access for entry points to NERC CIP Physical Security Perimeters (PSPs). Individuals are granted unescorted physical access to individual PSPs through a process approved by senior management. RFC_URE4 conducts a PRA pursuant to that process prior to granting employees unescorted physical access. RFC_URE4’s policy is to update each PRA at least every seven years after the initial PRA was conducted or for cause. During RFC_URE4’s quarterly access entitlement review, RFC_URE4 identified several anomalies in PRA dates for some of its employees. RFC_URE4 further investigated the anomalies and determined that ten employees had PRA dates that were greater than seven years old. CIP-004-3a R3 requires and RFC_URE4’s policy is to perform PRAs on employees once every seven years. For those ten employees, RFC_URE4 had begun the process to update their PRAs, but did not complete the process. The process was not completed because of an administrator error. The administrator error occurred when the administrator did not revoke the access privileges for the ten employees that had expired PRAs. The administrator was notified that the ten PRAs for these employees were about to expire and needed to be updated, but the administrator did not update their PRAs on time. Therefore, those ten employees’ PRAs were expired and overdue. RFC_URE4 revoked unescorted physical access privileges to PSPs for the ten employees with expired PRAs and began the process to re-initiate PRAs for the impacted employees. This noncompliance involves the management practice of verification and implementation. RFC_URE4 did not have an effective process or control in place to make sure that employees’ PRAs were renewed before they expired. RFC_URE4 also did not effectively implement a process or control that would revoke unescorted physical access privileges for an employee when that employee’s PRA expired. The root cause is a lack of effectively implemented processes and controls. The duration of this noncompliance is from the date the first of the ten employees’ PRAs expired, to the date RFC_URE4 revoked unescorted physical access privileges to PSPs for the ten employees with expired PRAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE4 not having current PRAs for these ten employees could reduce RFC_URE4’s ability to protect against individuals with malicious intent. The risk is minimal here because the ten employees with expired PRAs all had previously completed a PRA with no disqualifying issues identified. RFC_URE4 has continuously employed all ten employees involved in this noncompliance. Additionally, seven of the ten employees that retained access to PSPs did not utilize that access and did not enter NERC-protected space. Three of the ten employees that retained access to PSPs did utilize that access to physically enter NERC-protected space. None of the ten employees with expired PRAs had cyber access to the bulk power system cyber systems. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) initiated revocation of unescorted physical access privileges for the ten employees with expired PRAs; 2) conducted reinforcement training on the importance of renewing employees’ PRAs on time and revoking access of those employees with expired PRAs with the relevant employees; 3) implemented a monthly internal control to review upcoming PRA expirations; and 4) implemented an automated process for revocation where a person’s NERC CIP access is automatically revoked upon the expiration of the individual’s PRA. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015397 | CIP-004-3a | R2 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-004-3a R2. RFC_URE4 discovered that two of RFC_URE4’s system administrators’ NERC CIP training had expired two months prior to RFC_URE4 revoking the system administrators’ access. RFC_URE4 identified that two system administrators’ NERC CIP training had expired two months earlier. This violation was identified as part of an internal control improvement where RFC_URE4 centralized NERC CIP Training across its departments and RFC_URE4 began requesting validation of training expirations from all departments on a monthly basis. After discovering that administrators’ NERC CIP training had expired, RFC_URE4 took appropriate steps to remove the administrators’ access and to retrain the administrators. On the same day RFC_URE4 provided the training to the two system administrators, RFC_URE4 reinstated the system administrators’ access. This noncompliance involves the management practice of verification and implementation. This noncompliance occurred because the system administrators were transferred to positions where NERC CIP tasks and qualifications, such as a personnel risk assessment (PRA) and NERC CIP Training, were not transferred to the new positions in the central repository system. RFC_URE4 lacked proper processes and procedures to ensure a seamless transition of employee tasks and qualifications when an employee is transferred. The root cause is a failure to implement proper processes and procedures. The duration of this noncompliance is from the date RFC_URE4 was required to have removed the access of the two system administrators with expired NERC CIP Training, to the date RFC_URE4 removed the two system administrators’ access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The system administrators only have access to systems not associated with providing control functions for the bulk power system. The systems providing control functions continued to operate as expected for the two months when the system administrators should not have had access. The two system administrators were experienced system administrators that previously had valid NERC CIP training and PRA and only missed their refresher training due to an oversight where their NERC CIP tasks/qualifications were not transferred in the central repository system. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) initiated revocation of access privileges for the two system administrators; 2) had the two RFC_URE4 system administrators complete their NERC CIP annual training; 3) implemented a monthly internal control to review upcoming training expirations; and 4) implemented an automated process for revocation where a person’s NERC CIP access is revoked upon the expiration of their annual NERC CIP training. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015014716 | CIP-007-3a | R2 | ReliabilityFirst determined that RFC_URE5 had an issue of CIP-007-3a R2 as a result of a Compliance Audit. During its Cyber Vulnerability Assessment, RFC_URE5 discovered that it did not implement its documented process to ensure that only those ports and services required for normal and emergency operations were enabled. Specifically, RFC_URE5 enabled a port on multiple switches that reside within the Electronic Security Perimeter (ESP). However, said port was not listed in the baseline of enabled ports for the switches and was not required for normal and emergency operations. Therefore, RFC_URE5 failed to ensure that only those ports and services required for normal and emergency operations were enabled. The root cause of the noncompliance was that RFC_URE5 did not follow its test procedures correctly to discover the open ports because the testing process was not clearly communicated to the individuals responsible for testing. Also, the procedure was written in such a way that the individuals implementing it misinterpreted it. Thus, RFC_URE5’s verification controls failed because they were not clearly written or communicated and thus were not effective in this instance. This issue started on the date the ports became enabled and ended on the date RFC_URE5 disabled the applicable ports. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE5’s failure to implement its documented process to ensure that only those ports and services required for normal and emergency operations are enabled could create an opportunity for unauthorized access through an open communication channel. However, this risk was mitigated by the following factors. The devices are protected by RFC_URE5’s layered security approach, including a Physical Security Perimeter and ESP. The ESP and associated firewall and router rule sets are a compensating measure to restrict electronic access to these devices. This measure ensures that only authorized IP addresses and ports are permitted through the firewall and rejects any communication not documented as a necessary part of normal or emergency operations. In addition, IT Security Operations deploys network-based intrusion prevention and/or detection devices. These devices report to the centralized management console server and are monitored. Also, RFC_URE5 would have received an alert if any unauthorized electronic access attempts were made. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 disabled the enabled port and updated its applicable testing procedure to clarify the steps to take when comparing existing open ports against the device type baseline. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014344 | CIP-007-3a | R5 | RFC_URE5 submitted a Self-Report stating that it had an issue with CIP-007-3a R5. RFC_URE5 failed to ensure that an individual who had access permission on a shared account was consistent with the concept of “need to know” with respect to work functions performed. Specifically, a provisioner granted access to a restricted password list to the wrong user for approximately 15 hours. The wrong user was never notified that he obtained access. After discovering the issue the next morning via an automated process, access was promptly revoked. The password list was for all RFC_URE5 substation Critical Cyber Assets (CCAs) that have passwords. The root cause of the noncompliance was human error. More specifically, the provisioner completed another request prior to the request at issue, and, because he was momentarily distracted by a call or message, inadvertently left the window open from the prior request on his screen while working on the request at issue, which resulted in him entering the information for the request at issue into the prior request. This issue started when access permission was granted to the wrong user and ended when access permission was revoked from that user. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE5 quickly discovered the noncompliance through an automated process and immediately remedied the noncompliance. Second, the wrong user was unaware that he was granted access to the password list, thus reducing the likelihood that he would try to use the access. Third, the wrong user could not have accessed the CCAs because the he did not have physical or remote electronic access to CCAs. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) developed a list of NERC CIP Access Provisioners’ FAQ’s and Answers that can be used as training for provisioners; and 2) delivered the NERC CIP Access Provisioners’ FAQ’s and Answers as training to provisioners in IT. Also, in the Self-Report, RFC_URE5 noted that it removed the access from the wrong user upon identifying the issue. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015286 | CIP-006-3c | R1; R1.4 | SERC_URE1 submitted a Self-Report stating it had an issue with CIP-006-3c R1.4. SERC_URE1 stated that a janitorial contractor escorted a visitor into a Physical Security Perimeter (PSP) when the contractor had no authority to be an escort. A janitorial contractor escorted a visitor into the PSP without authorization. The janitorial contractor had authorized unescorted access to the PSP. However, SERC_URE1 had not authorized the contractor to perform escort duties. The visitor, who was the janitorial contractor’s employer, properly completed the PSP visitor logbook, and the janitorial contractor continuously escorted the visitor. Upon review of the visitor logbook, SERC_URE1 confirmed that the visitor was inside the PSP for approximately seven minutes. SERC_URE1 submitted a Self-Report expansion of scope stating that it had an issue with CIP-006-3c R1.4. Another contractor escorted a visitor into a PSP without authorization. SERC_URE1 had not authorized the contractor to perform escort duties. However, the contractor allowed escorted access for approximately 44 minutes. The visitor properly completed the PSP visitor logbook and the contractor continuously escorted the visitor. SERC_URE1 discovered the issues during a monthly internal review of the PSP visitor access logs. SERC_URE1 determined that the root cause was human error. The contractors failed to follow documented processes and procedures. The first issue lasted approximately four minutes from when the janitorial contractor, who was not an authorized escort, escorted the visitor into the PSP until the visitor departed the PSP. The second issue lasted approximately 44 minutes from when the contractor, who was not an authorized escort, escorted a visitor within a PSP until the contractor and visitor departed the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to follow its documented visitor pass management program may allow malicious actors to enter into a PSP and impose physical and/or electronic damage to its Critical Assets and/or Critical Cyber Assets. However, the contractors were trained, had Personnel Risk Assessments, and were authorized to access the PSPs. SERC_URE1 has PSP logging and monitoring deployed at all PSP access points. SERC_URE1 conducted monthly visitor logbook reviews to detect potential violations of access. The visitors in both instances completed the SERC_URE1 visitor logbook, as required. SERC considered SERC_URE1’s CIP-006 R1 compliance history in determining the disposition track. SERC_URE1’s prior CIP-006 R1 compliance history is unrelated to the instant issue. SERC_URE1 has no prior history of violating CIP-006-3c R1.4 that is relevant to this issue. SERC determined that SERC_URE1’s CIP-006 R1 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE1: 1) performed human error reviews with the contractors to review the incident and reiterate to the contractors that their actions violated SERC_URE1 procedures and must not reoccur; and, 2) required the contractors supervisors conduct one-on-one personnel reviews with each of its contractors that had SERC_URE1 CIP site access focusing on incident lessons-learned, how the issues occurred, and how the issues can be prevented. In addition, the focus was on specific CIP sites to which each contractor has authorized access, the contractor’s access level and the access limitations, and clear direction on who to contact if any questions may arise associated with their CIP access.
2016-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015015297 | CIP-006-3c | R4 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-006-3c R4. SERC_URE2 failed to implement the operational controls to manage physical access to all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. SERC_URE2 was performing an hourly security check of the physical access points and found a door that opened without requiring a badge and utilizing the deployed two-factor keypad. Upon discovery, the employee notified the security command center and SERC_URE2 instituted alternative procedures to continuously monitor the access point. In addition, in accordance with the Physical Security Plan, SERC_URE2 submitted an emergency work order for repairs for the local badge reader approximately 53 minutes later on the same day. The security system vendor arrived approximately three and a half hours after discovery and made repairs to the access point. The staff onsite continued to monitor the door, and the corporate operational security team verified the badge reader was operating as designed three days later. The root cause of the issue was hardware failure. The issue lasted approximately 17 days, from the date of the last documented door test, until SERC_URE2 deployed continuous monitoring on the unsecured access point. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to implement operational controls to manage physical access may lead to unauthorized personnel gaining access to Critical Cyber Assets. However, the perimeter in question was within a secure facility controlled by badge readers and all interior facility doors were secure. In addition, the facility was within a secure perimeter protected by a fence that required restricted card access to enter. SERC_URE2 monitored the door in question with closed circuit television monitoring, and upon discovery, SERC_URE2 staff continuously monitored the access point. In addition, SERC_URE2 staffs the protected area in question 24 hours a day, seven days a week with operational employees. SERC_URE2 reviewed the video and only authorized personnel accessed the door during the outage. SERC considered SERC_URE2 and its affiliates’ CIP-006-3c R4 compliance history in determining the disposition track. SERC determined that SERC_URE2 and its affiliates’ compliance history is unrelated to the instant issue and should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE2: 1) secured the door and continuously monitored the access point via live feed via the closed circuit television; and, 2) submitted an emergency request to repair the hardware.
2016-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015015357 | CIP-006-3c | R2; R2.2 | SERC_URE3 submitted a Self-Report stating that it had an issue with CIP-006-3c R2.2. SERC_URE3 failed to retain all logs specified in CIP-007 R6 for ninety calendar days for the physical access control systems (PACS), as required by CIP-006-3c R2.2. The log retention software for SERC_URE3 PACS servers utilizes an agent on each of the four PACS servers to cache event logs and conduct reviews for any configured cyber security events. Every four hours, the system collects and migrates the cached events to the PACS log retention repository. The repository maintains the event logs for a minimum of ninety days. This is the SERC_URE3 primary log retention process to meet CIP-007-3a R6 log retention requirements pursuant to CIP-006-3c R2.2. As a back up to this process, SERC_URE3 configure its PACS agent to save the event logs locally for up to eight days. The PACS database server experienced a system failure attributed to a software issue. Three days later, SERC_URE3 resolved the database server issue and returned to normal operations. Because the repair occurred within the eight-day period for the back-up process to retain cyber event security logs, SERC_URE3 did not conduct additional investigations or reviews. Over two months later, while preparing for a third party compliance review, SERC_URE3 discovered that the log retention process had failed for the three days, and logs for a period of 61 to 65 hours were not available. SERC_URE3 initiated contact with the logging application vendor regarding why the secondary back-up process failed to function as expected. The vendor could not identify the root cause or replicate the issue. The root-cause of this issue was a technology failure in the automated log retention tool for PACS, as well as a failure of the secondary tool. One vendor provides both log retention options, and there is no alerting to SERC_URE3 upon failure to transfer and retain logs. The issue lasted three days, from when the PACS server database failed and the PACS log retention process stopped working on both the primary and back up, through when SERC_URE3 restored the server database to normal operations and the primary log retention process resumed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to retain cyber security event logs for a full ninety days could have hindered a forensics investigation had a cyber-security event occurred. However, the logs that SERC_URE3 did not retain were a small portion, less than three days’ worth, of the collected logs. SERC_URE3 secures the PACS within established Physical Security Perimeters (PSP) and Electronic Security Perimeters (ESP) with monitoring and alerting enabled. SERC_URE3 maintains the access logs to the ESP and PSP, which would have assisted during a forensic investigation. In addition, the PACS servers require two-factor authentication with a jump host, so a forensic review could have leveraged the jump host logs if needed. SERC considered SERC_URE3’s CIP-006 R1.8 compliance history in determining the disposition track. SERC considered SERC_URE3’s CIP-006-3c R2.2 compliance history in determining the disposition track. SERC determined that SERC_URE3’s CIP-006 R1.8 and R2.2 compliance history should not serve as a basis for applying a penalty. None of the prior instances involved logging on the PACS but were applicable to other tentacle requirements. SERC considered SERC_URE3’s CIP-007 R6 compliance history in determining the disposition track. SERC determined that SERC_URE3’s CIP-007 R6 compliance history should not serve as a basis for applying a penalty. The first prior noncompliance did not involve log retention issues, but was a failure to log for some substation CCAs due to technical limitations, and SERC_URE3 failed to file the required Technical Feasibility Exception. The second prior noncompliance did not involve log retention, but was a failure to enable logging on some CCAs within the EMS environment. Neither of the CIP-007-1 R6 issues included mitigation steps that should have eliminated or addressed the potential opportunity to fail regarding logging for PACS. | To mitigate this issue, SERC_URE3: 1) resolved the technical issue and restored the server to full functionality; 2) worked with the vendor to troubleshoot failure of the secondary control (up to 8 day agent caching); and 3) reviewed the vendor’s recommendations and implemented the appropriate corrective actions.
2016-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014781 | CIP-005-3a | R1; R1.5 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-005-3a R1.5 for not providing the protective measure specified in CIP-005-3a R3.2. CIP-005-3a R3.2 requires SPPRE_URE1’s security monitoring processes to “detect and alert for attempts at or actual unauthorized accesses” to Cyber Assets used in the access control and/or monitoring of SPPRE_URE1’s Electronic Security Perimeter (ESP). SPPRE_URE1 discovered a large batch of electronic files had locked up its logging and collection server associated with non-Critical Cyber Assets located within the Electronic Security Perimeter (ESP). Believing that the server lock-up was caused by non-CIP related temporary report files, SPPRE_URE1 personnel deleted the electronic files and reset the logging and collection system to solve the problem. SPPRE_URE1 later discovered that the deleted files were access logs associated with thirteen non-Critical Cyber Assets located within its ESP. As a result, had there been electronic attempts at or actual unauthorized accesses to one or more of the affected non-Critical Cyber Assets, an alert would not have been generated by the logging and collection server for SPPRE_URE1 to investigate. The duration of this instance of noncompliance was from the earliest date electronic access logs from the non-Critical Cyber Assets were deleted from the logging and collection server, through the latest date that such access logs were deleted from the logging and collection server. The root cause of this instance of noncompliance was human error due to personnel not recognizing the electronic files as access logs for non-Critical Cyber Assets within SPPRE_URE1’s ESP before deleting them. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R1.5 has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur without the Registered Entity’s knowledge. Notwithstanding, only non-Critical Cyber Assets were affected, as SPPRE_URE1 utilizes a separate logging and alerting tool for monitoring Critical Cyber Assets within its ESP. Except for CIP-005-3a R3.2, all other protective measures specified in CIP-005-3a R1.5 had been afforded. The unavailability of the electronic access logs was limited to one month. SPPRE_URE1’s Cyber Assets were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. SPPRE_URE1 timely identified, self-reported, and mitigated this instance of noncompliance. No actual harm is known to have occurred as a result of the noncompliance. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. Although this is a repeat of CIP-005 R1, the underlying conduct of the two instances was different. The prior violation involved SPPRE_URE1’s failure to (i) identify and document all access point to its ESP (R1); (ii) identify all non-Critical Cyber Assets within its ESP (R1.4); (iii) identify and document some EACM servers on SPPRE_URE1’s Master Asset List (R1.5); and (iv) timely document the installation of a data communication device between two control center ESPs on its network diagram (R1.6), none of which related to security monitoring and alerting. Additionally, the instant noncompliance only pertains to R1.5, and does not involve a failure of identifying or documenting an EACM server. Regarding the other prior violation, it involved a different CIP-005 requirement, which is unrelated to security monitoring and alerting. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) reset the logging and collection system, which caused the logging and collection server to again have monitoring and logging capabilities for the affected non-Critical Cyber Assets; 2) verified that logs have been saved and available since resetting the logging and collection system; 3) met with affected security status monitoring support personnel and identified the root cause of the noncompliance, i.e., inadvertently clearing the electronic access logs, and advised all such personnel that they must prioritize log retention during any future troubleshooting of the logging and collection system; and 4) implemented alerting configurations to the logging and collection system to generate alerts for failure of the system, i.e., system lock-up or interruption of the system. SPP RE has verified the completion of all mitigation activity.
2016-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015401 | CIP-006-3c | R1; R1.6.2 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-006-3c R1.6.2 for failing to continuously escort a contractor within the Physical Security Perimeter (PSP). Specifically, a SPPRE_URE1 employee, who had authorized unescorted physical access to SPPRE_URE1’s PSP, escorted the contractor to a room inside the PSP where the contractor was required to work. Shortly thereafter, the employee walked into an adjacent room to assist the contractor in pulling a cable through an adjoining wall, thereby leaving the contractor unattended for a few minutes. The duration of this instance of noncompliance was less than a single day. The root cause of the noncompliance was inadequate training. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-006-3c R1.4 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized access and possible misuse of Critical Cyber Assets (CCAs). Nonetheless, for the duration of the noncompliance, the contractor remained inside the room he was working, which was monitored by video surveillance 24/7. Another employee with authorized PSP access noticed the contractor inside the PSP without an escort, summoned another employee to stay with the contractor, and immediately reported the issue to Physical Security. The PSP is completely within a Federal complex with additional layers of security and access control. The offending employee had a current personnel risk assessment and cyber security training. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1 retrained affected personnel on its visitor program for visitors needing continuous escorted access within the PSP.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015177 | CIP-003-3 | R5 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-003-3 R5. Specifically, WECC_URE1 reported that in the process of reviewing access to its Compliance Repository, it discovered one employee, who no longer worked at WECC_URE1, still had read-only access to CIP Protected Information. This issue began when WECC_URE1’s quarterly review should have identified and corrected the oversight, and ended approximately 2 years later, when WECC_URE1 disabled the employee’s access. The root cause of this issue was a process oversight. All of the necessary paperwork was filled out, but not all steps to remove access were complete and there was not a peer review. | In this instance, WECC_URE1 failed to revoke read-only access to CIP Protected Information for a former employee. Such failure could have enabled an unauthorized person to access protected information, and could have compromised devices on the WECC_URE1’s network. However, WECC_URE1 timely revoked the individual’s logical and unescorted physical access to CIP Assets, making access to protected information unlikely. Additionally, the employee left WECC_URE1 in good standing, providing WECC_URE1 with reasonable assurance that this individual would not likely attempt to harm WECC_URE1 or disseminate protected information. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. | To mitigate this issue, WECC_URE1: 1) revised its procedures to incorporate a peer review to confirm access changes are fully completed. WECC verified that WECC_URE1 completed mitigating activities.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014703 | CIP-007-1 | R2 | WECC_URE1 submitted a Self-Certification stating that it had a possible issue of noncompliance with CIP-007-3a R2. Specifically, WECC_URE1 reported that WECC_URE1 implemented a process improvement effort to verify their list of authorized ports and services on protected assets. As part of this effort, WECC_URE1 used an alternate command to generate its list of enabled ports during its 2014 Cyber Vulnerability Assessment. As a result of the alternate command, WECC_URE1 discovered that it had failed to list one port on its authorized ports and services list for one Electronic Security Perimeter (ESP) switch. The switch functioned as an access switch for Energy Management System Front End Processors and provided communication within the Electronic Security Perimeter. This issue began when WECC_URE1 was required to demonstrate compliance with this Standard, and ended when WECC_URE1 added the port in question to its list of authorized ports and services. The root cause of this issue failure to implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to identify one port on its baseline of approved ports, which was required to be enabled, on one switch within WECC_URE1’s ESP. Failure to identify all enabled ports and services could allow unknown and/or unmonitored ports and services on the ESP. In this case, the switch provided communication within the ESP; had a port been enabled when it should not have been, this could have allowed unnoticed access to the switch. If the switch were compromised and taken offline, internal communication to WECC_URE1’s Supervisory Control and Data Acquisition (SCADA) system could have been interrupted. However, WECC_URE1 had network security controls that analyze traffic for threats affecting ports and required a secured port to manage the switch. Additionally, WECC_URE1’s ESP firewall configuration blocked unsolicited traffic from passing into the networks segregated by the ESPs. The system is located within a secured Physical Security Perimeter, and only a limited number of individuals, all of whom have received Cyber Security training and have an approved Personnel Risk Assessment on file, have access to the Physical Security Perimeter. The systems are also located on an isolated network with no direct access to WECC_URE1’s corporate network, or the Internet. All traffic to the network passed through secured Access Points. Further, throughout the duration of this issue, WECC_URE1 had anti-malware software installed and operating, and all applicable security patches had been assessed and installed, or were scheduled for installation. For this reason, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. | To mitigate this issue, WECC_URE1: 1) determined, in accordance with its procedure, that the port was required for management during normal and emergency operations while the switch is in use within the ESP; 2) confirmed the scope of the issue was limited to the device in question; and 3) removed the device from the ESP in an effort to standardize and simplify the network. WECC verified that WECC_URE1 completed mitigating activities.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015176 | CIP-007-3a | R3 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R3. Specifically, WECC_URE1 reported that WECC_URE1 failed to assess a security patch that was made available to the public by its vendor. WECC_URE1 used calendar reminders for patch review. The WECC_URE1 SME performing the review missed the calendar reminder to perform the assessment within 30 calendar days for the availability of the patch. This issue began 31 calendar days after the security patch was made available, and ended when WECC_URE1 assessed the security patch for applicability. The root cause of this issue is human error. WECC_URE1 uses Outlook reminders, and the SME missed the reminder to the patch review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to assess a security patch for applicability within 30 calendar days of availability. This could have left the two devices open to attacks targeting the vulnerabilities the patch would have fixed. However, WECC_URE1 uses antivirus software at a network level designed to prevent malicious code from affecting devices on the network. The two devices are located in the ESP. The ESP is a protected network isolated from untrusted networks such as the Internet. Electronic access to the ESP is controlled, logged, and monitored. WECC_URE1 ensures all traffic going into the ESP passes through firewalls with access rules designed to prevent an attacker from gaining access to the ESP. Employees with physical and electronic access to devices within the ESP have up-to-date personnel risk assessments on file and have attended cyber security training. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. | To mitigate this issue, WECC_URE1: 1) assessed the patch for applicability; 2.) set up tasks to send automatic reminders to review available patches every two and half weeks; 3) established additional reminders to escalate the review if a review is not completed by the due date; and 4) listed compliance personnel as backups to review the patches and ensure the assessment is performed within the necessary timeframe when SMEs are unavailable. WECC verified that WECC_URE1 completed mitigating activities.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015057 | CIP-007-3a | R4.2 | WECC_URE2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R4. Specifically, WECC_URE2 reported that it did not regularly update anti-virus signatures on servers for several months. Updates did occur during this time, but not regularly on these specific servers. WECC_URE2 identified the issue in while conducting an inventory of all Critical Cyber Assets (CCAs) and Non-Critical Cyber Assets (NCCAs) in the Electronic Security Perimeter (ESP). This inventory identified the servers in the Energy Management System environment that had out-of-date anti-virus and anti-malware signatures installed; several of the servers also needed other anti-virus and anti-malware products to be updated before current anti-virus and anti-malware signatures could be installed. All the affected servers are classified as NCCA within the ESP. This issue began when WECC_URE2 failed to update its anti-virus signatures on the devices within the ESP, and ended when anti-virus updates, including bringing signatures, engines, and agents to current standards were completed. The root cause of this issue was a failure on the part of WECC_URE2 staff to follow processes, and a lack of clarity regarding roles and responsibilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to update its anti-virus signatures on servers classified as NCCA in its EMS environment for several months in accordance with its CIP-007-3a R4 process. Failure to update anti-virus signature on any cyber assets within the ESP could lead to malware propagating from these servers and attempting to spread to other devices within the ESP, which could result in a disruption of the normal operation of the CCAs and thus the EMS. The malware could have also introduced a vector for attack or entrance into the ESP for further attacks and harm to CCAs in the EMS. However, in this case, the ESP firewalls restricted network access, and all other devices within the ESP had anti-virus protection, thus limiting malware exposure, and other traffic from outside the ESP. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the bulk power system. | To mitigate this issue, WECC_URE2: 1) retired several of the servers; 2) for other servers, instituted automatic updating; 3) for one server, deployed application whitelisting, allowing only the applications required for the server to perform its intended function to run, thus minimizing the likelihood of the execution of malware; 4) updated its anti-virus and anti-malware procedure to include clear designation of roles and responsibilities, process steps, and controls to ensure updates are performed regularly, and that evidence is collected to demonstrate compliance. For servers updated automatically, reports will be generated and reviewed daily to ensure that the latest updates have been applied. For servers updated manually, reports will be generated and reviewed at least every 30 days; and 5) for new servers, up-to-date anti-virus and anti-malware will be verified prior to being put into service, as part of implementation processes for all new devices. WECC verified the completion of all mitigation activity.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015566 | CIP-002-3 | R4 | MRO_URE1 submitted a Self-Report stating it had an issue of CIP-002-3 R4. Specifically, MRO_URE1 did not have the senior manager or delegate sign and date the approval of the risk-based assessment methodology (RBAM), the null list of Critical Assets (CAs), or the null list of Critical Cyber Assets (CCAs), for the year of 2014. The cause of this issue was MRO_URE1's reliance on institutional staff knowledge and initiative to complete these requirements. MRO_URE1 did not have adequate internal controls related to CIP-002-3 R4 compliance and a staff transition caused MRO_URE1 to miss the 2014 annual approval. The issue began when MRO_URE1 failed to conduct the annual approval, and to have the senior manager or delegate sign the RBAM and its null lists of CAs and CCAs, and ended when the senior manager signed and dated the approval of MRO_URE1's RBAM, its null list of CAs, and its null list of CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE1 did not have any CAs or associated CCAs, and the scope of the issue is limited to MRO_URE1's failure to have a senior manager or delegate approve MRO_URE1's RBAM, and sign MRO_URE1's null list of CAs and CCAs. The risk is further reduced because MRO previously audited MRO_URE1 with CIP-002-3 in scope, and MRO did not detect any noncompliance associated with MRO_URE1's determination that it did not have any CAs or CCAs. No harm is known to have occurred. This is MRO_URE1's first instance of noncompliance with CIP-002-3 R4. | To mitigate this issue, MRO_URE1: 1) performed the 2015 Annual Approval of its RBAM, and the null list of its CAs, and the null list of its CCAs; and 2) set up automated work flow processes to automatically alert staff when a CIP-002-3 due date is approaching. MRO_URE1 stated that mitigating activities were completed.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2015015039 | CIP-002-3 | R4 | MRO_URE2 submitted a Self-Report stating that it had an issue of CIP-002-3 R4. Specifically, MRO_URE2 did not have the senior manager or delegate sign and date the approval of the risk-based assessment methodology, the null list of Critical Assets (CAs), or the null list of Critical Cyber Assets (CCAs). The cause of this issue was, MRO_URE2's failure as a relatively new registered entity, to understand the full scope of its responsibilities under the CIP standards. The issue began when the standard became applicable to MRO_URE2 and ended when the senior manager signed and dated the approval of MRO_URE2's risk-based assessment methodology, its null list of CAs, and its null list of CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE2 did not have any CAs or associated CCAs, and the scope of the issue is limited to MRO_URE2's failure to have a senior manager or delegate approve MRO_URE2's risk-based methodology, and sign MRO_URE2's null list of CAs and CCAs. The risk is further reduced because MRO_URE2 is a lower voltage generator with no transmission assets. Moreover, in determining this issue was appropriate for compliance exception treatment, MRO considered the relatively brief duration of this issue, and the fact that MRO_URE2 detected, self-reported, and promptly mitigated this issue. Finally, MRO_URE2 will not have any medium or high impact facilities under CIP Version 5. No harm is known to have occurred. This is MRO_URE2's first instance of noncompliance with CIP-002-3 R4. | To mitigate this issue, MRO_URE2: 1) designated an individual to be the senior manager; 2) had the senior manager sign and approve MRO_URE2's risk-based assessment methodology, a null list of CAs, and a null list of CCAs; 3) updated the CIP-002-5.1 process to demonstrate readiness with the CIP V5 transition; and 4) set reminders in the senior manager's calendar and its computerized maintenance management system to serve as a reminder for upcoming deadlines. MRO_URE2 stated that mitigating activities were completed.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2015015038 | CIP-003-3 | R2 | MRO_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R2. Specifically, MRO_URE2 did not designate an individual to be the senior manager. The cause of this issue was, MRO_URE2's failure as a relatively new registered entity, to understand the full scope of its responsibilities under the CIP standards. The issue began when the standard became applicable to MRO_URE2 and ended when MRO_URE2 designated an individual to be its senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE2's noncompliance is limited to failing to designate an individual to be the senior manager. This issue did not expose MRO_URE2 to any significant risk from adversaries as MRO_URE2 does not have any Critical Assets or associated Critical Cyber Assets. The risk is further reduced because MRO_URE2 is a lower voltage generator with no transmission assets. Moreover, in determining this issue was appropriate for compliance exception treatment, MRO considered the fact that MRO_URE2 detected, self-reported, and promptly mitigated this issue. Finally, MRO_URE2 will not have any medium or high impact facilities under CIP Version 5. No harm is known to have occurred. This is MRO_URE2's first instance of noncompliance with CIP-003-3 R2. | To mitigate this issue, MRO_URE2 designated an individual to be its senior manager. MRO_URE2 stated that mitigating activities were completed.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2016015555 | CIP-004-3a | R3 | MRO_URE3 submitted a Self-Report stating that it had an issue of CIP-004-3a R3. A maintenance contractor, who had unescorted physical access to Control Centers, did not have a current personnel risk assessment (PRA). This occurred due to a data entry error when MRO_URE3 personnel were entering the original date of the contractor’s PRA into MRO_URE3’s database. The original PRA was conducted in March 2008, but was incorrectly entered as March 2013. The cause of the violation was human error. MRO_URE3 has automated controls in place to ensure that PRAs are kept current, but this violation occurred because an employee made a typographical error during the data entry process. This violation began when the initial PRA became more than 7 years old, and ended when MRO_URE3 discovered the noncompliance and revoked the contractor’s access privileges. | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While verifying the background of individuals with access to CCAs is an essential CIP requirement, the risk was reduced in this case due to a number of factors. MRO_URE3 has strong internal controls regarding compliance with this standard including a database that tracks PRAs. Additionally, MRO_URE3 detected this noncompliance and self-reported the issue which is a result of conducting regular reviews. Further, the duration of the noncompliance was relatively brief (4 months). Finally, this contractor was well known to MRO_URE3 and had provided services to MRO_URE3 for years without incident. No harm is known to have occurred. MRO_URE3 has no relevant history of noncompliance with CIP-004-3a R3. | To mitigate this issue, MRO_URE3 deactivated the contractor's physical access rights until MRO_URE3 could conduct an updated PRA. MRO_URE3 stated that mitigating activities were completed.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO2016015617 | CIP-014-1 | R1 | MRO_URE4 submitted a Self-Report stating that it had an issue of CIP-014-1 R1. Specifically, MRO_URE4 omitted a future substation, that was planned to be in service within 24 months, from its initial risk assessment of its Transmission stations and Transmission substations. The cause of this issue was MRO_URE4's failure to consider facilities that were planned, but not in service, in its initial risk assessment. This issue started when the Standard became mandatory for MRO_URE4, and ended when MRO_URE4 updated its risk assessment to include the future substation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to include future facilities in an internal risk assessment may reduce a registered entity's ability to provide adequate physical security to a critical facility when it comes online. However, in this case, the risk was minimal. MRO_URE4 determined that the future substation would not meet the criteria for a critical substation under the Standard's rational. This determination was confirmed by MRO_URE4's independent third party reviewer when the third party reviewed MRO_URE4's updated assessment per CIP-014-2 R2. Further, in determining that this issue qualified for Compliance Exception treatment, MRO considered the fact that MRO_URE4 self-reported this issue and the issue had a very short duration (less than one week). No harm is known to have occurred. This is MRO_URE4's first issue with CIP-014-1 R1. | To mitigate this issue, MRO_URE4 assessed the future substation under its CIP-014-2 R1 methodology. MRO verified that mitigating activities were completed.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015643 | CIP-007-3a | R3.1 | RF_URE1 submitted a self-log stating that it had an issue of CIP-007-3a R3.1. RF_URE1 IT failed to perform an assessment of two patches within 30 days of release by the vendor. During a meeting, the Subject Matter Expert (SME) responsible for assessment of these patches was not available. RF_URE1 recognized the two patches were not assessed while preparing for the meeting. The SME completed the assessment for both patches the next day and determined that only patch 2 was applicable to a single RF_URE1 firewall appliance. The patch assessment performed was 46 days after release of Patch 1, and 32 days after release of Patch 2, thereby failing to meet the 30 day requirement. The root cause was a lack of an effective procedure to make sure that all patches are assessed within 30 days of their release even if the assigned SME for a given set of patches misses some patches in his or her initial assessment. This issue started when RF_URE1 did not assess the first released patch within 30 days of its release, and ended when RF_URE1 completed the patch assessment for both patches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF_URE1 IT had already mitigated the security vulnerability addressed by the patch when initially identified by the vendor the previous year. RF_URE1 IT identified the missed patch assessment during the following monthly patch assessment cycle. RF_URE1 IT assessed the applicable patch within 32 days of being released by the vendor and RF_URE1 IT assessed the other vendor released patches within the required 30-day period during the timeframe of this potential violation. There are several internal controls in place to detect or prevent violation occurrence, including: • RF_URE1 IT has a team to manage the patch process • RF_URE1 IT conducts monthly patch assessment meetings to provide oversight and facilitation for RF_URE1 IT SMEs to assess and track released patches • RF_URE1 IT maintains a spreadsheet to track released patches and the results of the patch assessments • RF_URE1 IT SMEs are assigned asset types for which they are responsible to perform monthly patch assessments Although these controls were not effective in this instance, they are part of the RF_URE1 IT patch management process. In this case, the RF_URE1 IT SME failed to identify the full set of patches for every assigned asset type and was subsequently unable to attend the meeting at which he could have been reminded of the missed assessments. The RF_URE1 IT SME did perform the needed patch assessment when preparing for the next meeting the following month. No harm is known to have occurred. | To mitigate this issue, RF_URE1: 1) performed and documented the patch assessments; 2) enhanced the patch tracking spreadsheet to facilitate a more complete review of assessments during the monthly meeting, including the addition of asset types to the spreadsheet; and 3) revised the procedure to require the IT Network Supervisor, in addition to the process manager, to perform a review of the monthly patch assessment report to ensure all assessment activities are completed.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015644 | CIP-007-3a | R3.1 | RF_URE2 submitted a self-log stating that it had an issue of CIP-007-3a R3.1. RF_URE2 determined that RF_URE2 IT failed to perform an assessment of two patches within 30 days of release by the vendor. During a meeting, the Subject Matter Expert (SME) responsible for assessment of these patches was not available. RF_URE1 recognized the two patches were not assessed while preparing for the meeting. The SME completed the assessment for both patches the next day and determined that only patch 2 was applicable to a single RF_URE1 firewall appliance. The patch assessment performed was 46 days after release of Patch 1, and 32 days after release of Patch 2, thereby failing to meet the 30 day requirement. The root cause of this violation was that the team did not have an adequate mechanism in place to verify that patches for all asset types had been reviewed monthly. This issue started when RF_URE2 did not assess the first released patch within 30 days of its release, and ended when RF_URE2 completed the patch assessment for both patches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm to the reliability of the Bulk Electric System that could have occurred during the situation was minor to none. Of the two patches that were not assessed, only one was applicable to a RF_URE2 asset; RF_URE2 IT had already implemented mitigation steps for the vulnerability related to that patch. The patch was an update to a bulletin posted the previous year. The applicable patch that was assessed late was identified and assessed within 32 days of release (only 2 days after the requirement). This is within the compliance window under CIP-007 Version 5. RF_URE2 considered the harm level was unlikely to be realized for the following reasons: • The vulnerability addressed by the applicable patch was previously mitigated the previous year after the vendor released a security bulletin. The patch is a permanent fix to address the vulnerability. Because RF_URE2 implemented mitigations the previous year, RF_URE2 was not vulnerable to this security risk at the time of patch release. RF_URE2 has the several internal controls in place to detect or prevent violation occurrence, including: • RF_URE2 IT has a team to manage the patch process • RF_URE2 IT conducts monthly patch assessment meetings to provide oversight and facilitation for RF_URE2 IT SMEs to assess and track released patches • RF_URE2 IT maintains a spreadsheet to track released patches and the results of the patch assessments • RF_URE2 IT SMEs are assigned asset types for which they are responsible to perform monthly patch assessments Although these controls were not effective in this instance, they are part of the RF_URE2 IT patch management process. In this case, the RF_URE2 IT SME failed to identify the full set of patches for every assigned asset type and was subsequently unable to attend the meeting at which he could have been reminded of the missed assessments. No harm is known to have occurred. | To mitigate this issue, RF_URE2: 1) performed and documented the patch assessments; 2) enhanced the patch tracking spreadsheet to facilitate a more complete review of assessments during the monthly meeting, including the addition of asset types to the spreadsheet; and 3) revised the procedure to require the IT Network Supervisor, in addition to the process manager, to perform a review of the monthly patch assessment report to ensure all assessment activities are completed.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015646 | CIP-007-3a | R5.2.1 | RF_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R5.2.1. Having completed a compliance investigation, RF_URE3 determined a possible violation had occurred involving CIP-007-3a R5.2.1 as applied to the renaming of factory default accounts. While reviewing a list of CIP device accounts for purposes of assessing annual password changes, a compliance representative noticed an account with a username that appeared to be associated with a factory default account setting. A Subject Matter Expert (SME) was consulted, and determined that the account in question was in fact a default account that was enabled on two devices, without the default username being changed during device commissioning. The default passwords for both accounts, however, were changed upon device commissioning and annually thereafter. As discussed in the mitigation activities, the default account usernames were changed immediately upon identifying the issue. Upon investigating the root cause of the issue, a gap was identified in the configuration procedure in effect at the time of commissioning. The procedure in effect at that time addressed the configuration requirements for a previous generation of the remote terminal unit (RTU) for which default account usernames could not be changed. Specifically, this procedure called for the password associated with required enabled default accounts to be changed at commissioning, but due to the lack of device capability, the procedure did not speak to the renaming of the default username. Subsequently, the RTUs were replaced with different RTUs which do allow for default usernames to be changed. At commissioning, however, the configuration procedure had not been amended to account for the renaming of the replacement default accounts and was followed by personnel to configure the two devices at issue, which resulted in the passwords for the enabled default accounts being changed but not the usernames. Thereafter, when device commissioning was completed, the configuration procedure was subsequently updated to explicitly state that the username associated with enabled default accounts on the replacement RTUs must also be changed, but the configuration of the devices at issue was not revisited after the update was made. The root cause was a gap in the configuration procedure at the time of commissioning that did not address the need to change the default username during device commissioning. This issue started when the default username was not changed during device commissioning, and ended when RF_URE3 finished changing the default usernames at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the default usernames had not been changed, the passwords associated with the default accounts were changed at commissioning and annually thereafter. Knowledge of the passwords and therefore access to these accounts was limited to a controlled number of substation personnel granted authorized electronic access on the basis of business need, valid personnel risk assessment (PRA) and completion of requisite training. No harm is known to have occurred. | To mitigate this issue, RF_URE3: 1) immediately initiated a change control to change the default account usernames; 2) reviewed the account tracking list to ensure that no other default account usernames exist. No additional enabled default accounts were found to still have their default username in use; and 3) implemented significant enhancements to its configuration management program as part of the CIP Version 5 transition. Specifically, RF_URE3 developed comprehensive device commissioning processes with checklists to provide clear direction with regard to each activity that must be adequately completed and documented prior to commissioning a device into production. Of the many required commissioning activities, the configuration management interactive user account setup process will include line items to identify all default/shared/generic accounts, disable the accounts that are determined not to be necessary, and only enable those accounts that are required for device operations. For those default/shared/generic accounts that must be enabled, the process will further specify that the default username must be changed as operationally acceptable and device capabilities permit. Moreover, the process will require that the default password must be also changed as device capabilities permit. To verify that these activities have been completed correctly, RF_URE3’s CIP Version 5 program incorporates a number of quality control check points, where independent reviews and approvals will be performed before an activity can be considered complete. All responsible personnel were trained on the CIP Version 5 configuration management program prior to implementation.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015647 | CIP-006-3c | R4 | RF_URE3 submitted a self-log stating that it had an issue of CIP-006-3c R4. As a result of construction related activities, a loading dock door at RF_URE3’s control center facility was opened by authorized personnel, but inadvertently left unattended for approx. 1 minute during a scheduled delivery. This door leads to a Physical Security Perimeter (PSP) hallway, and is badge controlled to limit access to only personnel with authorized unescorted physical access. Moreover, beyond this hallway, several additional layers of protections are in place (e.g., badge controlled doors, security alarms, video monitoring, etc.) before an individual can gain access to the secure PSP rooms in which Cyber Assets reside. On this day, the loading dock door was initially opened by authorized personnel to facilitate the delivery of construction supplies. However, upon propping the door open, the authorized personnel walked away from the area, during which time a mover entered and exited the PSP hallway area (right off the loading dock doorway) with the first set of delivery boxes. The mover had not been logged in as a visitor nor was an authorized escort present at the time. Nonetheless, security personnel responded immediately to the open door alarm, and within 15 seconds of the mover’s initial entry, an authorized guard arrived at the loading dock door. The security guard remained at the scene and monitored the open door until the mover completed the rest of the delivery. A video recording of the incident was reviewed and shows that the mover did not gain access beyond the PSP hallway area (right off the loading dock doorway), the delivery was completed in less than 10 minutes, and the door was closed securely by the security guard upon completion. The root cause was ineffective training because the authorized personnel walked away from the area after propping open a loading dock door instead of staying by the opened loading dock door until delivery was completed. This issue started when the loading dock door was propped open and a mover entered the PSP hallway area without being logged in as a visitor and without an authorized escort, and ended on when a security guard closed the loading dock door securely and when the mover finished his job and left the PSP hallway area while a security guard was present. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF_URE3’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described above, certain aspects of these security protocols were not followed by the personnel involved, but were immediately reported upon discovery. Specific to the instances involving the RF_URE3 control center, the risk harm assessment took into consideration significant construction activities underway and the project driven increase in the number of visitors at the facility as a result. In response to these unique circumstances, RF_URE3 has hired a significant number of new security personnel and contractors, who have undergone requisite training, but are new to the RF_URE3 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring) and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RF_URE3: 1) closed and secured the PSP doors; 2) Supervisors took immediate steps to meet with the individuals involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances; 3) held larger team meetings to reiterate PSP access protocols with all responsible personnel. To mitigate this issue, RF_URE3 will complete the following mitigation activities: 1) RF_URE3 is undertaking an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RF_URE3’s security awareness program, security awareness communications will be focused on reiterating and reinforcing PSP access protocols company wide; 2) as a more targeting measure, PSP access protocols will be added to the agenda and covered in detail at upcoming monthly NERC compliance team meetings, including the monthly CIP subject matter expert meetings, effectively reinforcing awareness throughout all areas where access issues have arisen; and 3) in addition to approaching the issue from an awareness perspective, RF_URE3 will be reviewing existing work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training for when PSP doorways must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate. The process to review existing work processes and procedures to identify opportunities for enhancement is a lengthy endeavor because RF_URE3 is reviewing all relevant existing work processes and procedures and looking for any areas of improvement. This broad scope explains the long mitigation duration.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016015648 | CIP-006-3c | R4 | RF_URE4 submitted a self-log stating that it had an issue of CIP-006-3c R4. As a result of construction related activities, a door on the roof of RF_URE4’s control center facility was inadvertently left unlocked for approx. 27 minutes. The control center roof is approx. 30 feet above ground with no means of access from outside the building. The roof door at issue leads to a stairway that terminates in the Physical Security Perimeter (PSP) area. Accordingly, the door has been secured as an exit door only, and cannot be opened from the outside. Moreover, beyond the stairway, several additional layers of protections are in place (e.g., badge controlled doors, security alarms, video monitoring) before an individual can gain access to the appropriate floor and then the secure PSP rooms in which Cyber Assets reside. On this day, an authorized security guard escorted a group of contractors onto the roof to perform certain construction related activities. All of the contractors were appropriately logged as visitors. Moreover, the escorting security guard remained on the roof to monitor the contractors for the duration of their work activities. Given that the roof door is an exit only door and cannot be opened from the outside, the security guard kept the door propped open slightly, so as to ensure that he and the contractors would not get locked on the roof. An open door alarm was received, responded to, and explained by the security guard’s need to escort and monitor the contractors on the roof. Upon completion of the work activities for that day, the security guard escorted the contractors off the roof and in doing so pulled the door behind him as he walked down the stairs, but the door’s interior dead bolt was extended which stopped the door from closing completely. Approx. 27 minutes later, a security console operator noticed that the open door alarm had not yet been cleared despite completion of the roof work, and immediately secured the door upon investigating the situation. A video recording of the incident was reviewed and shows that no one (other than the authorized security console operator) approached the unsecured door during this timeframe. The root cause was ineffective training because the security guard walked away from the roof door without ensuring that the roof door had closed securely and properly. This issue started when the security guard left the roof door open after he escorted the contractors off the roof, and ended 27 minutes later when a security console operator noticed the open door alarm and securely closed the roof door. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF_URE4’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described above, certain aspects of these security protocols were not followed by the personnel involved, but immediately reported upon discovery. Specific to the instances involving the RF_URE4 control center, the risk harm assessment took into consideration significant construction activities underway and the project driven increase in the number of visitors at the facility as a result. In response to these unique circumstances, RF_URE4 has hired a significant number of new security personnel and contractors, who have undergone requisite training, but are new to the RF_URE4 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring) and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RF_URE4: 1) closed and secured the PSP doors; 2) Supervisors took immediate steps to meet with the individuals involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances; 3) held larger team meetings to reiterate PSP access protocols with all responsible personnel. To mitigate this issue, RF_URE4 will complete the following mitigation activities: 1) RF_URE4 is undertaking an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RF_URE4’s security awareness program, security awareness communications will be focused on reiterating and reinforcing PSP access protocols company wide; 2) as a more targeting measure, PSP access protocols will be added to the agenda and covered in detail at upcoming monthly NERC compliance team meetings, including the monthly CIP subject matter expert meetings, effectively reinforcing awareness throughout all areas where access issues have arisen; and 3) in addition to approaching the issue from an awareness perspective, RF_URE4 will be reviewing existing work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training for when PSP doorways must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate. The process to review existing work processes and procedures to identify opportunities for enhancement is a lengthy endeavor because RF_URE4 is reviewing all relevant existing work processes and procedures and looking for any areas of improvement. This broad scope explains the long mitigation duration.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2016015650 | CIP-006-3c | R4 | RF_URE5 submitted a self-log stating that it had an issue of CIP-006-3c R4. An electric maintenance crew was dispatched to a RF_URE5 substation to assist in the installation of a tie-line from a 230kV line to a switch. Upon clearing security and arriving at the substation yard, crew members were asked to carry boxes of equipment from their work vehicles into the control house Physical Security Perimeter (PSP). Prior to the crew’s arrival, authorized personnel were already onsite, and had appropriately badged/logged into, and opened the control house door. With authorized personnel inside the control house, the control house door was propped open in order to facilitate the work already underway between the control house and the switch yard. However, when the subsequent crew members arrived, carrying needed equipment, 4 of the crew members entered the control house PSP without badging/logging in at the control house door. Of the 4 crew members at issue, 3 were authorized for unescorted physical access and 1 was not. All 4 crew members had valid personnel risk assessments and requisite training on file. In all instances, the crew members were present in the PSP for less than 1 minute to deliver the equipment and then exited, and authorized personnel were in the PSP monitoring their activities the entire time. A video recording of the incident was reviewed and shows that the crew members did not re-enter the PSP after the delivery was complete. The door to the control house was closed securely by the remaining authorized personnel upon completion of the days’ work activities. The root cause was ineffective training because the 4 crew members entered the control house PSP without badging or being logged in contrary to RF_URE5's procedure. This issue started when the door to the control house was propped open and 4 of the crew members entered the control house PSP without badging/logging in at the control house door, and ended when the 4 crew members left the control house PSP and the door to the control house was securely closed by the remaining authorized personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF_URE5’s Physical Security Plan requires that access points to PSPs be secured and monitored at all times. Moreover, the Plan also requires that authorized personnel and visitors be appropriately logged prior to PSP entry. In the instances described above, certain aspects of these security protocols were not followed by the personnel involved, but immediately reported upon discovery. Specific to the instances involving the RF_URE5 control center, the risk harm assessment took into consideration significant construction activities underway and the project driven increase in the number of visitors at the facility as a result. In response to these unique circumstances, RF_URE5 has hired a significant number of new security personnel and contractors, who have undergone requisite training, but are new to the RF_URE5 facilities and PSP access protocols. Nonetheless, thorough review and investigation of each incident determined that no Cyber Assets (critical or otherwise) were accessed or compromised by unauthorized individuals. While certain individuals failed to follow all of the established security protocols, effective additional controls were in place to protect against unauthorized access (e.g., badge controlled secure PSP rooms, alarms, video surveillance, and onsite security and authorized personnel monitoring) and ensure immediate issue identification and correction. No harm is known to have occurred. | To mitigate this issue, RF_URE5: 1) closed and secured the PSP doors; 2) Supervisors took immediate steps to meet with the individuals involved, make them clearly aware of their incorrect actions, and reinforce the correct protocols to be exercised under all circumstances; 3) held larger team meetings to reiterate PSP access protocols with all responsible personnel. To mitigate this issue, RF_URE5 will complete the following mitigation activities: 1) RF_URE5 is undertaking an aggressive personnel awareness campaign to reinforce the PSP access requirements. As part of RF_URE5’s security awareness program, security awareness communications will be focused on reiterating and reinforcing PSP access protocols company wide; 2) as a more targeting measure, PSP access protocols will be added to the agenda and covered in detail at upcoming monthly NERC compliance team meetings, including the monthly CIP subject matter expert meetings, effectively reinforcing awareness throughout all areas where access issues have arisen; and 3) in addition to approaching the issue from an awareness perspective, RF_URE5 will be reviewing existing work processes and procedures to identify opportunities where enhancement can be made to further support personnel compliance with the PSP access protocols and minimize instances of human performance errors. Such enhancements may include, but are not limited to: (i) adding PSP access protocols as a standing topic covered during regularly reoccurring personnel safety briefings and functional area team meetings, (ii) formalizing guidelines and training for when PSP doorways must be propped open to facilitate work activities; and/or (iii) instituting processes to quickly escalate PSP access errors to senior management for disciplinary action as determined appropriate. The process to review existing work processes and procedures to identify opportunities for enhancement is a lengthy endeavor because RF_URE5 is reviewing all relevant existing work processes and procedures and looking for any areas of improvement. This broad scope explains the long mitigation duration.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2016015673 | CIP-004-3a | R4.2 | RF_URE6 submitted a self-log stating that it had an issue of CIP-004-3a R4.2. Incident 1: Physical access was not revoked for a transferred employee. The employee transferred and Security Operation Center (SOC) was notified to revoke physical access seven days later. During a quarterly review, it was discovered that physical access was not revoked and SOC was notified the next day to complete revocation. It is not known why SOC did not revoke the employee's physical access. SOC was notified six days after the transfer; and an additional email was sent the next day. The supervisor of the transferred employee involved in the incident was on sick leave at the time, which contributed to some of the delay. The SOC reviewed the physical security access logs for the employee for the relevant timeframe and no use of the badge was discovered. Incident 2: Cyber access was not revoked for an employee who resigned to work for a contractor. The employee resigned and her supervisor submitted a request to remove cyber access fourteen days later. SOC was contacted twelve days later to remove physical access based on Human Resources notification; however, cyber access was not mentioned. It was determined that cyber access revocation was being processed. The NERC CIP Compliance representative verified that the employee's cyber access was being processed for revocation based upon a system review. The supervisor waited two weeks to submit the termination revoke request. It is not known why the supervisor waited two weeks to submit the request. Once the supervisor submitted the request, it was sent back to him for approval, which caused some delay. The organization followed the correct procedures. Also when the employee resigned, her supervisor collected her secure token, computer, and badge so there was no mechanism by which the employee could gain electronic or physical access. Incident 3: An electrician was terminated for cause. Human Resources notification of the for-cause termination was received the same day and emergency revokes were entered for all CIP access. The next day, one of the 2 revokes of electronic CIP access was completed. Three days later the second revoke of electronic CIP access was completed. The employee was terminated on a Friday, which also happened to be a holiday weekend. The employee that would have done a cursory follow-up was off. However, the employee's secure token was removed as well as physical access within the required time period. As such, there was no mechanism by which the employee could gain electronic or physical access. The employee still had Cyber Security CIP Substation access, which he would not have been able to use since he did not have physical access or his secure token. This issue started the date by which access should have been revoked in incident one, and ended the date access was revoked in incident three. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Incident 1: The issue posed a minimal risk to bulk power system reliability based on the following factor. The individual (who transferred to a new role) at issue is a trusted resource who continues to maintain other CIP accesses. Incidents 2 and 3: These issues posed a minimal risk to bulk power system reliability based on the following factors. The individuals' gateway access was revoked, and as a result, there was no mechanism by which the individuals could have gained electronic or physical access. Accordingly, this reduces the risk of compromise. It should also be noted that because the gateway access was revoked, the second and third incidents would not be considered violations under CIP Version 5. In addition, new software was installed as part of the CIP v5 conversion that will prevent future errors of this type. The software requires the gaining manager to enter the effective date where previous access will no longer be required. As a result, the likelihood of compromise to RF_URE6's system as a result of this issue is minimal. No harm is known to have occurred. | To mitigate this issue, RF_URE6: Incident 1: 1) revoked access. Incident 2: 1) revoked access; 2) collected the employee's secure token, computer and badge when the employee resigned, so there was no mechanism by which the employee could gain electronic or physical access; and 3) conducted refresher training with the supervisor. Incident 3: 1) issued a Human Resources notification of the for-cause termination and emergency revokes were entered for all CIP access; 2) completed one of the 2 revokes of electronic CIP access 1 day later; 3) completed the second revoke of electronic CIP access 3 days later; and 4) removed the employee's secure token, as well as physical access within the required time period. General: 1) installed new software as part of the CIP v5 conversion that will prevent future errors of this type. The software requires the gaining manager to enter the date where previous access will no longer be required. On that date, the access from the old position will be revoked. The software also auto revokes access if the manager does not enter a date after 7 days. RF_URE6 policy for transfers assumes a minimum of 7 days of access is needed to allow for a transition of job responsibilities between roles.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015015375 | CIP-004-3a | R4 | RF_URE7 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. While performing a review of user access rights, the IT Manager identified three users who should have had their energy management system (EMS) Operator workstation login access rights changed from full access and read-only access to just read-only access. The IT Manager discovered that the relevant removal requests were created through the Service Request Management (SRM) process. These requests were submitted because some of the tasks performed by these three individuals had been removed from their job and reassigned to other personnel with full EMS access. On the same day, these requests triggered three “work tasks” to be created in the SRM process and assigned to IT Security. However, the requests were not completed in a timely manner because the on-call person failed to recognize that the work tasks were assigned to him, despite having received an email notification for each of the three requests. During this particular person’s normal response to security incidents or requests, he regularly views tasks in the Incident Management queue within the system, but never uses the Service Request queue. The root cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the IT Security employee failed to properly utilize the company’s automated tools designed to prevent this type of noncompliance. The duration of this noncompliance is from the date RF_URE7 was required to modify these three employees’ access rights, to the date RF_URE7 actually completed the modifications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk of any of these three individuals causing any harm was very low because they all (a) are still employed by the company; (b) had undergone Personnel Risk Assessments and cyber security training in accordance with CIP Standards; and, (c) still have unescorted physical access rights due to the nature of their work. Second, this noncompliance is not indicative of a systemic issue at the company because (a) the company identified the noncompliance through its own internal review; and, (b) the company’s automated notification tool within the SRM process worked as designed, but was not used properly by the employee. | To mitigate this issue, RF_URE7: 1) referred the employee’s failure to properly utilize the company’s automated tools and failure to follow the company’s documented procedures to the employee’s manager for appropriate disciplinary action; and 2) enhanced the SRM process related to NERC CIP access revocations as follows: (i) including a note in the service request description indicating that if the requester thinks access should have been revoked prior to the current date, the requester should enter the current date and time and immediately contact the Manager of NERC/CIP Compliance via the cell phone number provided; (ii) changing the requested delivery date filed to allow entry of a time as well as a date and to allow entry of the current and any future date; (iii) changing the first supervisor approval for revocation requests to a notification because a very large percentage of revocation requests come from the supervisors in the first place. Thus, there is no need for them to approve the request they submitted. This notification will give supervisors an opportunity to question or override in appropriate circumstances; (iv) implementing a report which runs at 6:00 am daily to identify any revocation requests in queue for completion that day or any of the next 7 days to help ensure appropriate prioritization of requests; and (v) implementing a report which runs 4 times per day to identify any revocation request in queue for completion that day, which has not yet been completed. Alerts for this report will be sent to an increasingly wider audience to ensure escalation and completion of any such request.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2015015376 | CIP-004-3a | R4 | RF_URE8 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. While performing a review of user access rights, the IT Manager identified three users who should have had their energy management system (EMS) Operator workstation login access rights changed from full access and read-only access to just read-only access. The IT Manager discovered that the relevant removal requests were created through the Service Request Management (SRM) process. These requests were submitted because some of the tasks performed by these three individuals had been removed from their job and reassigned to other personnel with full EMS access. On the same day, these requests triggered three “work tasks” to be created in the SRM process and assigned to IT Security. However, the requests were not completed in a timely manner because the on-call person failed to recognize that the work tasks were assigned to him, despite having received an email notification for each of the three requests. During this particular person’s normal response to security incidents or requests, he regularly views tasks in the Incident Management queue within the system, but never uses the Service Request queue. The root cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the IT Security employee failed to properly utilize the company’s automated tools designed to prevent this type of noncompliance. The duration of this noncompliance is from the date RF_URE8 was required to modify these three employees’ access rights, to the date RF_URE8 actually completed the modifications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the risk of any of these three individuals causing any harm was very low because they all (a) are still employed by the company; (b) had undergone Personnel Risk Assessments and cyber security training in accordance with CIP Standards; and, (c) still have unescorted physical access rights due to the nature of their work. Second, this noncompliance is not indicative of a systemic issue at the company because (a) the company identified the noncompliance through its own internal review; and, (b) the company’s automated notification tool within the SRM process worked as designed, but was not used properly by the employee. | To mitigate this issue, RF_URE8: 1) referred the employee’s failure to properly utilize the company’s automated tools and failure to follow the company’s documented procedures to the employee’s manager for appropriate disciplinary action; and 2) enhanced the SRM process related to NERC CIP access revocations as follows: (i) including a note in the service request description indicating that if the requester thinks access should have been revoked prior to the current date, the requester should enter the current date and time and immediately contact the Manager of NERC/CIP Compliance via the cell phone number provided; (ii) changing the requested delivery date filed to allow entry of a time as well as a date and to allow entry of the current and any future date; (iii) changing the first supervisor approval for revocation requests to a notification because a very large percentage of revocation requests come from the supervisors in the first place. Thus, there is no need for them to approve the request they submitted. This notification will give supervisors an opportunity to question or override in appropriate circumstances; (iv) implementing a report which runs at 6:00 am daily to identify any revocation requests in queue for completion that day or any of the next 7 days to help ensure appropriate prioritization of requests; and (v) implementing a report which runs 4 times per day to identify any revocation request in queue for completion that day, which has not yet been completed. Alerts for this report will be sent to an increasingly wider audience to ensure escalation and completion of any such request.
2016-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015204 | CIP-007-3a | R5; R5.2.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had a minimal risk instance of noncompliance with CIP-007-3a R5.2.2. Specifically, SPPRE_URE1 granted employees access to shared database accounts but did not identify them on its Master Access List. The duration of this instance of noncompliance was approximately 35 months. The root cause of this instance of noncompliance was human error due to personnel not recognizing the database accounts as shared user accounts and thus subject to CIP-007-3a R5.2.2. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R5 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized system access. Notwithstanding, all individuals were authorized to have access to the shared Oracle database accounts based on their business needs. SPPRE_URE1 did not believe that the database accounts were shared accounts because they were neither intended nor used for interactive access, i.e., not used by a user but an application or service. The database accounts were the only shared accounts affected by the noncompliance and they had no external connectivity to devices outside the ESP network. All Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including user and security group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) identified all individuals with access to the shared database accounts and updated its Master Access List; 2) revised its Access Control Process to ensure that database accounts that are shared and could be used for interactive access are provided the security controls prescribed in CIP-007-3a R5; and 3) trained all affected personnel on the revisions to the Access Control Process. SPP RE has verified the completion of all mitigation activity.
2016-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015205 | CIP-007-3a | R8; R8.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had a minimal risk instance of noncompliance with CIP-007-3a R8.3. Specifically, SPPRE_URE1 did not include shared database accounts in its cyber vulnerability assessments (CVAs). The duration of this instance of noncompliance was approximately 36 months. The root cause of this instance of noncompliance was human error due to personnel not recognizing the database accounts as shared user accounts and thus required to be included in CVAs. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R8 has the potential to affect the reliability of the BPS by providing the opportunity for Cyber Assets within the Electronic Security Perimeter (ESP) to be exposed to unidentified vulnerabilities. The database accounts were the only shared accounts not included in the CVAs and they had no external connectivity to devices outside the ESP network. All Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including user and security group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) updated its Master Assess List to include the shared database accounts to ensure they will be included in future CVAs; and 2) alerted all affected personnel that the shared database accounts have been added to the Master Access List and are required to be included in future CVAs. SPP RE has verified the completion of all mitigation activity.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015658 | CIP-006-3c | R1.6 | WECC_URE1 submitted a self-log stating that it had an issue of CIP-006-3c R1.6.2. An WECC_URE1 failed to provide continuous escorted access for one visitor within a PSP for a period of two (2) minutes and 17 seconds. The root cause of this issue is the less than adequate training to one individual on escort procedures. Specifically, WECC_URE1 reported that WECC_URE1 Cyber Security analyst performed a Cyber Vulnerability Assessment (CVA) scan in a PSP. The analyst contacted another WECC_URE1 employee to come watch the area for a few minutes while they used the restroom. The employee scanned their badge to log their entry to the PSP but did not have approved physical access at that time; however, the enclosure was already open when they scanned their badge. Per a review of the recorded video, the employee momentarily opened and looked into the PSP cabinet while the analyst was still in the room and briefly walked around the area and then sat to read materials until the analyst returned. WECC_URE1’s security discovered the issue when they received an alarm when the employee scanned their badge at the PSP. Security reviewed the trace history of the DNA logs and camera footage to better understand the situation and then notified the analyst that the employee was denied access to the enclosure. The issue started when the WECC_URE1 analyst left the WECC_URE1 employee in the PSP without escorted access and the issue ended when the analyst returned to the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. No harm is known to have occurred. Having been granted unescorted physical access to PSP, the employee could have attempted to access devices. Per recorded video, the employee only opened the PSP to look in briefly while being escorted by the analyst and never modified any devices in the analyst’s absence. Further, malicious intent would have been difficult to achieve considering the limited time the employee was left alone with the PSP. The employee acts as the analyst’s backup for Physical Access Control System (PACS) administration and maintains multiple PSP access rights at the company, including electronic access to the entire PACS environment. The employee also maintains physical access to the room where the PSP is located, as well as all other card access points. The employee had a personnel risk assessment (PRA) and completed CIP training. Further, WECC_URE1’s security discovered and responded to the issue when they received an alarm. | To mitigate this issue, WECC_URE1: 1) WECC_URE1 reviewed of access for all personnel with assigned responsibilities was conducted to ensure the needed access is provisioned. The review identified the need to grant the employee access to all enclosures as part of their duties as the back-up PACS administrator. The access request was submitted. The request was approved. 2) WECC_URE1’s cyber security manager reviewed the process for escorting visitors at a PSP with the analyst. The manager discussed the need to validate access via direct log in or contacting security to validate existing access before allowing access.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015519 | CIP-004-3a | R4 | NPCC_URE1 submitted a self-log stating that it had an issue of CIP-004-3a R4. An employee with authorized unescorted physical access rights to critical cyber assets transferred departments and no longer required such physical access to critical cyber assets in their new role. The employee's physical access rights to critical cyber assets were revoked 10 days after the access rights should have been removed. The root cause was a delay in the receipt of a letter between the union represented employee and NPCC_URE1's labor representative. The automatic physical access revocation process was delayed due to the delayed employee transfer processing. Managers and supervisors are also expected to call the security center to ensure timely access revocation, but in this instance, the manager of the department was new to the position and was not aware of the requirement to call the security center to revoke access. This late access revocation incident was discovered during a review of the automatic access revocation log file. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of access records confirmed that the employee did not access substations during the period of the violation. The employee had up-to-date CIP training and a personnel risk assessment. The employee has worked for NPCC_URE1 since 2000 and continues to work for NPCC_URE1. The employee did not have electronic access to any CCAs. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1. Provided a targeted communication to the new manager of the department. 2. Issue a communication to all employees regarding the NERC CIP access revocation process. 3. The job change request form will be revised to have the new department supervisor/manager verify with the old department supervisor/manager if the employee has NERC CIP access. NPCC has verified the completion of all mitigation activity.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016015614 | CIP-004-3a | R4; SR4.1 | NPCC_URE2 submitted a self-log stating that it had an issue of CIP-004-3a R4.1. Following a review of its list of individuals with unescorted physical access to physical security perimeters, NPCC_URE2's security services became aware that an individual on that list no longer had a business reason for such access. Consequently, the individual's credentials were first deactivated then, three days later, purged entirely from the access list, which resides on the physical access control system. An investigation established that the person had transferred six months earlier to an affiliate company and surrendered his physical access credential to his supervisor. The supervisor did secure the credentials but failed to return them to security and to submit an electronic ticket to remove the person from the physical access control system. The root cause of this violation was a failure to follow the established procedure to submit an electronic ticket for removing the person's name from the list and to return the credentials to security services. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm of this instance of noncompliance is minimal because this represents an issue of administrative non-compliance. The individual's access was effectively revoked on the day of his transfer since his credentials were in his supervisor's possession, and not accessible to anyone else. A subsequent review of access logs indicates that the credentials were not used to gain access to physical security perimeters. Also, the employee had up-to-date CIP training and a satisfactory personnel risk assessment. The employee could not gain access to a perimeter without forcing a door, which would have resulted in a forced door alarm. The supervisor's office is located in a building requiring electronic badge access and has security guards at its entrance. The NERC CIP cyber assets in the substation have security controls to prevent and detect malicious and unauthorized use. These controls include methods to deter and detect malicious code, event logging, and password protection. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1. Deactivated the individual in the physical access control system. 2. Reviewed the use of the access credentials 3. Counselled the supervisor on: - the importance of following procedure, - the use of the proper form to report when an employee transfers, and - the requirement to return the credential to security services. NPCC has verified the completion of all mitigation activity.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016015615 | CIP-006-3c | R1; SR1.5 | NPCC_URE2 submitted a self-log stating that it had an issue of CIP-006-3c R1.5. A manager was erroneously granted unescorted physical access to a specific physical security, which contains the SCADA servers for the control room. The error was identified by security services during a review of individual authorization records, which occurs periodically in order to validate the list of individuals with various levels of access authorization in the physical access control system. Access was erroneously granted for a duration of 18 days. The root cause of this violation was a failure to allocate authorization access that is consistent with the approved level of authorization. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The manager, who is a long-term employee, had up-to-date CIP training and a satisfactory personnel risk assessment. In this incident, the manager was erroneously granted authorization to the perimeter containing the servers associated with the SCADA control system. However, the SCADA servers have additional layers of protection to prevent unauthorized use and to detect unauthorized use. These controls include password protection and the network is contained within an ESP having malware detection, configuration management, audit trails and event logging. If a malicious act to degrade the operation of the servers is attempted, there is a high probability that it would be detected. In addition, the PSP itself is located in an office building with security guards and electronic badging. Although the manager had been erroneously authorized for unescorted physical access to the above physical security perimeter, a review of access logs indicates that the credential was never actually used to gain access to it. The violation was identified by a review process whose frequncy of implementation exceeds the NERC CIP-required quarterly and annual reviews. In conclusion, the duration of the non-compliance was very short (18 days) and administrative in nature. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1. Deactivated the individual's credentials in the physical access control system. 2. Reviewed the use of the access credentials 3. Reviewed with the manager responsible for having implemented access authorization in the physical access control system the importance of verification of credentials by ensuring that the access granted matches the access approved. NPCC has verified the completion of all mitigation activity.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014961 | CIP-006-3c | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. RFC_URE1 identified two noncompliances with RFC_URE1’s visitor control program. First, a RFC_URE1 employee without unescorted access privileges was inadvertently issued the wrong type of access badge by RFC_URE1 Security and was allowed to access a RFC_URE1 Physical Security Perimeter (PSP) without continuous escorted access. The RFC_URE1 employee previously had authorized unescorted access privileges to the PSP; however, those access privileges were revoked due to the employee’s internal reassignment to a different department. When the RFC_URE1 employee accessed the PSP the employee was considered a visitor under RFC_URE1’s visitor control program, and was required to obtain a restricted visitor badge and be continuously accompanied by an escort while within the PSP. The RFC_URE1 Security Officer near the PSP did not verify the RFC_URE1 employee’s CIP access with the Security Operations Center and issued the employee a temporary non-visitor badge, which is reserved for employees with authorized unescorted access. Five days later, this issue was discovered and the employee was issued the proper badge and was continuously escorted within the PSP. Second, a RFC_URE1 employee did not follow the proper procedures to gain entry to a PSP. Although the employee had a valid business need, attending a training class, he did not have authorized unescorted access to this PSP and required a restricted visitor badge. The employee failed to register with RFC_URE1 Security to obtain a restricted visitor badge and, instead, mistakenly attempted to gain escorted access to the PSP by swiping his permanent Company ID badge against the PSP card reader. Due to an undiscovered hardware malfunction, the card reader was not registering all attempted entries and thus did not alert the Security Operations Center when the incorrect badge was used. The Security Operation Center was alerted, however, when the employee attempted to badge out of the PSP with his authorized escort. Upon receiving notice of the alarm from the Security Operations Center, RFC_URE1 Security immediately enforced the visitor access program by registering the employee as a visitor and providing him with the proper restricted visitor badge. The employee was otherwise continuously escorted while inside the PSP, as required by RFC_URE1’s visitor access program. These noncompliances concern the management practices of workforce management and verification and involve ineffective training. Workforce management and ineffective training are implicated in the first noncompliance because the RFC_URE1 Security Officer did not follow RFC_URE1’s protocol in granting the employee access to the PSP and in the second noncompliance because the RFC_URE1 employee did not follow the proper procedures to gain entry to a PSP. Verification is implicated in the first noncompliance because RFC_URE1 security did not verify that the RFC_URE1 employee was issued the proper access badge and in the second noncompliance because RFC_URE1 did not have an effective process in place to ensure that the PSP card reader was properly functioning. The root causes are ineffective training, the lack of a verification process, and the malfunctioning card reader. The duration of these noncompliances is from the date a RFC_URE1 employee without authorized unescorted access privileges accessed a RFC_URE1 PSP without continuous escorted access, to the date RFC_URE1 completed registering the involved employees with RFC_URE1 Security as visitors without authorized unescorted access, issued the correct restricted visitor badges, and repaired the malfunctioning card reader. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RFC_URE1 maintains 24 hour video surveillance of all of its PSP entry points. In both instances, the personnel at issue were NERC CIP authorized RFC_URE1 employees who had valid business needs to enter the PSPs and posed no security risks. For the first incident, the employee had authorized unescorted access to the PSP until the day prior to the incident. This employee had his access removed because of the employee’s internal reassignment to a different department. For the second incident, the employee was continuously escorted while inside the PSP. Lastly, RFC_URE1 followed its visitor access program upon the discovery of both of these incidents and followed up with several communications, such as emails, bulletins, and additional signs, to reinforce their physical security program. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) immediately enforced its visitor access program, appropriately registered the employees with RFC_URE1 Security, and issued the correct restricted visitor badges; 2) registered the employee in the second incident as a visitor, provided him with the proper restricted visitor badge, and repaired the malfunctioning card reader to ensure that it captures all attempted PSP entries; 3) reinforced its CIP access control procedures through additional training initiatives and direct communication to affected personnel and e-mailed all RFC_URE1 PSP access holders a copy of the RFC_URE1 Electric Operations Buildings (EOBs) and CIP Area Physical Access Procedure to reinforce awareness of the proper physical access procedures; 4) e-mailed an updated security bulletin to all RFC_URE1 personnel and all RFC_URE1 PSP access holders. The bulletin instructed personnel to read and understand the RFC_URE1 EOB and CIP Areas Physical Access Procedure and included a photo of a PSP card reader, a PDF copy of the RFC_URE1 security bulletin summarizing physical security reminders, and a copy of the PSP escort responsibilities handout; 5) retrained all relevant security guard personnel on its visitor badge procedures; 6) created additional instructional signs for use at all PSP entries to draw attention to and to further emphasize PSP Access Procedures; and 7) developed a training presentation to reinforce RFC_URE1’s CIP PSP guidelines and procedures. The training presentation was launched as a mandatory course for all RFC_URE1 employees and all RFC_URE1 PSP access holders. ReliabilityFirst has verified the completion of all mitigation activity.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015007 | CIP-006-3c | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. Two different RFC_URE2 employees failed to follow proper procedures for entering Physical Security Perimeters (PSPs) and escorting visitors. A RFC_URE2 employee, Employee A, triggered a force entry alarm while exiting a designated NERC PSP. After the alarm sounded, RFC_URE2 reviewed the video feed of and access logs for the PSP and the video showed a male employee exiting the PSP without badging out. Exiting the PSP without badging out caused the alarm to sound. Video footage also showed that Employee A entered the PSP with two other individuals. One of the other two individuals was another RFC_URE2 employee, Employee B, and the second individual was a contractor, Contractor A, onsite to repair hardware within the PSP. The PSP logged a valid attempt to enter for Employee B, which permitted the three individuals, Employee A, Employee B, and Contractor A, to enter the PSP. After completing its review of the event, RFC_URE2 determined that Contractor A signed into the general building security log and Employee B appropriately escorted Contractor A into and out of the PSP but failed to ensure that Contractor A was properly logged as a visitor into the PSP. Employee A did not use his access badge to gain entry to the PSP and tailgated behind Employee B. Employees A and B both should have badged into the PSP. The noncompliance stems from the fact that Employee B did not prevent Employee A from tailgating into the PSP, Employee B did not ensure that Contractor A was properly logged as a visitor into the PSP by signing into the NERC CIP Visitor Logbook, and Employee A attempted to exit the PSP without badging out. Both Employee A and Employee B had current and valid access to the PSP and had been requested to escort Contractor A into the PSP by a RFC_URE2 IT Manager. This noncompliance concerned the management practices of workforce management and verification. Poor workforce management and ineffective training are both implicated as Employee A and Employee B did not follow RFC_URE2’s procedures for entering and exiting PSPs and for escorting a contractor into a PSP. Verification is also implicated because Employee B did not verify that Contractor A completed an entry in the correct logbook when he entered the PSP. Contractor A only signed into the building security logbook and not the NERC CIP Visitor Logbook. The two logbooks were placed next to one another and not clearly marked to show a difference between the two logbooks. The root causes are ineffective training and the lack of a verification process. The duration of this noncompliance is from the date Employee A tailgated in and Contractor A did not sign into the NERC CIP Visitor Logbook, to the date RFC_URE2 responded to the force entry alarm and signed Contractor A into the NERC CIP Visitor Logbook. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Employees A and B had valid unescorted access rights to the PSP in question and had current Personnel Risk Assessments (PRAs) and NERC CIP awareness certification training. Employee B appropriately escorted Contractor A into and out of the PSP, remained with Contractor A the entire time he was inside the PSP, and escorted Contractor A out of the PSP. Contractor A also signed the building security log when entering the building, which recorded his entry, and Contractor A was authorized to be in the PSP to repair hardware within the PSP. Lastly, RFC_URE2 has force entry alarms active inside the PSP and live security video of activity within the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) responded to the force entry alarm, addressed Employees A and B, and ensured that Contractor A was properly logged in and escorted; 2) discussed the responsibilities related to tailgating and visitor escorting with the two employees involved in the issue in one-on-one meetings with their manager; 3) conducted a stand down meeting with the RFC_URE2 client services team whose employees were involved in the incident. The meeting included reinforcement of the need to follow proper procedures for entering PSPs and escorting visitors; 4) reminded the client services team of the importance of following proper procedures for entering PSPs and escorting visitors during a staff meeting; 5) worked to develop and distribute a message to all individuals with access to PSPs to reinforce the need to comply with access policies; 6) relocated the NERC CIP Visitor Logbook inside the PSP and clearly marked each sign-in page and the exterior of the logbook to indicate that the logbook is for NERC logging; 7) moved the NERC CIP Visitor Logbook for that PSP to shelves installed inside the PSP to make it clear that the NERC CIP Visitor Logbook is different from the building security logbook. The building security logbook is stored outside the PSP; and 8) created and posted a sign on the inside of the PSP to indicate the need to specifically sign visitors into the NERC CIP Visitor Logbook. ReliabilityFirst has verified the completion of all mitigation activity.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015234 | CIP-006-3c | R1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. A RFC_URE3 employee with authorized unescorted access rights to the Physical Security Perimeter (PSP) at RFC_URE3’s Back-Up Control Room provided access to a contractor to replace a printer cartridge in the PSP. The RFC_URE3 employee, however, failed to escort the contractor during the time the contractor was replacing the printer cartridge inside the PSP. RFC_URE3’s access control procedure and CIP-006-3c R1 require the RFC_URE3 employee to continuously escort the contractor while the contractor is inside the PSP. The contractor’s visit was properly logged into the PSP’s visitor log book for both the contractor’s entry and exit. Although logged properly, the contractor did not have authorized unescorted access and a badge to properly exit the PSP on his own. When the contractor exited the PSP by himself, an alarm sounded and sent an automatic notification to the Security Operations Center. Upon triggering the alarm, the contractor secured the PSP door and notified the RFC_URE3 employee that was supposed to be escorting him, that RFC_URE3 employee also contacted the Security Operations Center to inform them of the alarm event. RFC_URE3 Security, as directed by the Security Operations Center, investigated the alarm event and determined that the contractor’s attempted exit from the PSP caused the alarm. The contractor attempted to exit the PSP without his escort because the RFC_URE3 employee failed to continuously escort the contractor while inside the PSP. RFC_URE3 Security also confirmed that the RFC_URE3 employee had the appropriate NERC CIP credentials, an up-to-date PRA, and was authorized to access the PSP during this noncompliance. This noncompliance concerned the management practice of workforce management. Workforce management is implicated because the RFC_URE3 employee did not understand that he needed to continuously escort the contractor while the contractor was inside the PSP. The root cause is ineffective training because the RFC_URE3 employee did not fully understand RFC_URE3’s PSP visitor program. The duration of this noncompliance is from the date the contractor was left unescorted inside the PSP, to the date RFC_URE3 Security secured the PSP door and met up with the unescorted contractor after the contractor left the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The PSP houses a Back-Up Control Room that was not activated at any time while the contractor was inside the PSP. Additionally, the computer terminals within the PSP were not logged in, thereby preventing an unauthorized user such as the contractor from potentially accessing the Emergency Management System (EMS). RFC_URE3 evaluated the computer logs to confirm that there was no unauthorized or denied-access attempts on the computer terminals within the PSP during the event. RFC_URE3 also continuously monitors its PSPs. The RFC_URE3 employee in question had the appropriate NERC CIP credentials, an up-to-date PRA, was authorized to access the PSP, and properly logged the contractor into the PSP’s visitor log book on entry and exit. The RFC_URE3 employee only left the contractor unescorted in the PSP for a few minutes. Lastly, the contractor was a known and trusted contractor. RFC_URE3 Security immediately discussed the issue with the employee involved in the incident and RFC_URE3 reinforced their PSP access procedures and sent a message to reinforce the need to comply with those PSP access procedures. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) had a communication delivered to RFC_URE3 Operations Leadership to provide the details of the incident to all RFC_URE3 Operations Control Center (OCC) Shift Managers and to inform the managers of the investigation into the incident; 2) sent communication to OCC Shift Managers alerting them of the event and cautioning them around the protocols associated with accessing the PSP; 3) reviewed and reinforced with OCC PSP access holders the protocols associated with escorting and logging visitors to PSP areas - this included retraining the employee involved in the noncompliance; and 4) developed and distributed a message to all individuals with access to PSPs to reinforce the need to comply with RFC_URE3 CIP tailgating and visitor access compliance expectations. The purpose of this message was to reinforce the physical access policies across RFC_URE3. ReliabilityFirst has verified the completion of all mitigation activity.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014579 | CIP-003-3 | R6 | RFC_URE4 submitted a Self-Report stating that it had an instance of noncompliance with CIP-003-3 R6. RFC_URE4 failed to follow its change control and configuration management process for replacing Critical Cyber Asset (CCA) hardware components. This process requires emergency changes to CCA hardware components to be requested, tested, and approved within three days of implementation. However, here, RFC_URE4 did not request, test, or approve an emergency change until 210 days after implementation. As background, RFC_URE4’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE4 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE4 Headquarters. RFC_URE4’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE4 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE4 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. The loss of power to RFC_URE4’s centralized monitoring system caused a CIP server component to fail, prompting a repair. The repair was considered an emergency change, but the employee making the change did not submit a unique change request relating to the repair. Thus, RFC_URE4 failed to document the emergency change within three days of implementation, which is required by RFC_URE4’s change management process. The root cause of the issue was human error in neglecting to document the change. The duration of this noncompliance was from three days after the change was implemented and thus required to be documented, through the day the change control and management process was implemented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE4’s failure to follow its change control process for 210 days could have resulted in RFC_URE4 implementing a change that would make its system vulnerable, thus potentially allowing unauthorized access to CCAs. However, this risk was mitigated by the following factors. First, RFC_URE4 employs a defense-in-depth approach for continuous cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, McAfee host intrusion prevention and antivirus was operational. Third, two-factor authentication to access network devices was functioning. Fourth, firewall and other malicious software prevention tools were operational. Finally, this noncompliance concerned a repair rather than entry of a new system into RFC_URE4’s environment, thus reducing the likelihood that the change would cause significant vulnerabilities. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) conducted a data center migration. To do this, RFC_URE4 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE4 Headquarters infrastructure. To do this, RFC_URE4 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE4 underground electrical network systems. To do this, RFC_URE4 assessed RFC_URE4’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE4 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE4 took the following actions. To address business function availability prior to moving the data center, RFC_URE4 placed a second generator on standby at RFC_URE4 Headquarters and performed switchgear refurbishment. RFC_URE4 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE4 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014014308 | CIP-005-3a | R3 | RFC_URE4 submitted a Self-Report stating that it had an instance of noncompliance with CIP-005-3a R3. As background, RFC_URE4’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE4 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE4 Headquarters. RFC_URE4’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE4 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE4 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. The power outage at RFC_URE4’s Data Center resulted in the loss of power to RFC_URE4’s Cyber Assets that log security events and its systems used to monitor security events and alert support personnel of those security events. Without access to these Cyber Assets, RFC_URE4 could not implement its electronic or manual processes for monitoring and logging access at access points to all Electronic Security Perimeters (ESPs) as required by CIP-005-3a R3. The duration of this noncompliance was approximately 15 hours, when RFC_URE4 was unable to monitor and log access at access points to its ESPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE4’s failure to monitor and log access at ESP access points for 15 hours could have potentially resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets without RFC_URE4’s knowledge. However, the risk to the reliability of the BPS was reduced by the following factors. First, RFC_URE4 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, two-factor authentication to access network devices was functioning. Third, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) conducted a data center migration. To do this, RFC_URE4 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE4 Headquarters infrastructure. To do this, RFC_URE4 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE4 underground electrical network systems. To do this, RFC_URE4 assessed RFC_URE4’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE4 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE4 took the following actions. To address business function availability prior to moving the data center, RFC_URE4 placed a second generator on standby at RFC_URE4 Headquarters and performed switchgear refurbishment. RFC_URE4 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE4 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014319 | CIP-005-3a | R3 | RFC_URE5 submitted a Self-Report stating that it had an instance of noncompliance with CIP-005-3a R3. As background, RFC_URE5’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE5 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE5 Headquarters. RFC_URE5’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE5 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE5 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. The power outage at RFC_URE5’s Data Center resulted in the loss of power to RFC_URE5’s Cyber Assets that log security events and its systems used to monitor security events and alert support personnel of those security events. Without access to these Cyber Assets, RFC_URE5 could not implement its electronic or manual processes for monitoring and logging access at access points to all Electronic Security Perimeters (ESPs) as required by CIP-005-3a R3. The duration of this noncompliance was approximately 15 hours, when RFC_URE5 was unable to monitor and log access at access points to its ESPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE5’s failure to monitor and log access at ESP access points for 15 hours could have potentially resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets without RFC_URE5’s knowledge. However, the risk to the reliability of the BPS was reduced by the following factors. First, RFC_URE5 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, two-factor authentication to access network devices was functioning. Third, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) conducted a data center migration. To do this, RFC_URE5 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE5 Headquarters infrastructure. To do this, RFC_URE5 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE5 underground electrical network systems. To do this, RFC_URE5 assessed RFC_URE5’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE5 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE5 took the following actions. To address business function availability prior to moving the data center, RFC_URE5 placed a second generator on standby at RFC_URE5 Headquarters and performed switchgear refurbishment. RFC_URE5 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE5 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014014311 | CIP-006-3c | R1 | RFC_URE4 submitted a Self-Report stating that it had an instance of noncompliance with CIP-006-3c R1. As background, RFC_URE4’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE4 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE4 Headquarters. RFC_URE4’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE4 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE4 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. During the power outage at RFC_URE4 Headquarters, individuals were entering and exiting the Data Center Physical Security Perimeter (PSP) in order to determine the extent of the issue and to try to return it to an operational state. However, the automatic log was not documenting the entry and exit of RFC_URE4 personnel and visitors. Security guards began guarding the doors to the Data Center and attempted to ensure that all personnel signed the logs, but, because of the circumstances, many of the logs had insufficient information such as the time the individuals entered and exited the PSP. As a result, RFC_URE4 did not have logs to document entry and exit of RFC_URE4 personnel and visitors into the Data Center PSP for approximately eight hours. The duration of this noncompliance was approximately eight hours during the time RFC_URE4 did not comply with CIP-006-3c R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance could have potentially resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets without RFC_URE4’s knowledge. However, this risk was mitigated by the following factors. Upon losing power to the Data Center, RFC_URE4’s physical security personnel prohibited most individuals from entering RFC_URE4 Headquarters. For example, many employees attempted to enter the building, but RFC_URE4 informed them of the situation and told them not to return to work and that they could go home. Largely, only personnel who were working to remediate the outage were able to gain access to RFC_URE4 Headquarters. In addition, when individuals (e.g., vendors) arrived who required access to the Data Center, RFC_URE4’s security guards called the person responsible for the visitor and that person escorted the visitor to the necessary location. As a result, the likelihood of unauthorized personnel entering the Data Center was low. RFC_URE4 posted security guards at the entrance to the Data Center to keep manual logs of individuals’ entry and exit. In addition, during this time, an authorized physical security individual required personnel who were already in the Data Center to sign the logs. Although the logs do not include all of the required information, they contain as much information as RFC_URE4 thought practical and possible under the circumstances. In addition, while the potential for compromise existed, during the time period when RFC_URE4 was not capturing logs, the power was out to RFC_URE4 Headquarters such that the machines that could be electronically compromised were inoperable, thus reducing the risk that a physical compromise would have caused a reliability issue. Accordingly, for these reasons, the noncompliance posed minimal risk to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) conducted a data center migration. To do this, RFC_URE4 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE4 Headquarters infrastructure. To do this, RFC_URE4 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE4 underground electrical network systems. To do this, RFC_URE4 assessed RFC_URE4’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE4 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE4 took the following actions. To address business function availability prior to moving the data center, RFC_URE4 placed a second generator on standby at RFC_URE4 Headquarters and performed switchgear refurbishment. RFC_URE4 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE4 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014320 | CIP-006-3c | R1 | RFC_URE5 submitted a Self-Report stating that it had an instance of noncompliance with CIP-006-3c R1. As background, RFC_URE5’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE5 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE5 Headquarters. RFC_URE5’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE5 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE5 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. During the power outage at RFC_URE5 Headquarters, individuals were entering and exiting the Data Center Physical Security Perimeter (PSP) in order to determine the extent of the issue and to try to return it to an operational state. However, the automatic log was not documenting the entry and exit of RFC_URE5 personnel and visitors. Security guards began guarding the doors to the Data Center and attempted to ensure that all personnel signed the logs, but, because of the circumstances, many of the logs had insufficient information such as the time the individuals entered and exited the PSP. As a result, RFC_URE5 did not have logs to document entry and exit of RFC_URE5 personnel and visitors into the Data Center PSP for approximately eight hours. The duration of this noncompliance was approximately eight hours during the time RFC_URE5 did not comply with CIP-006-3c R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance could have potentially resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets without RFC_URE5’s knowledge. However, this risk was mitigated by the following factors. Upon losing power to the Data Center, RFC_URE5’s physical security personnel prohibited most individuals from entering RFC_URE5 Headquarters. For example, many employees attempted to enter the building, but RFC_URE5 informed them of the situation and told them not to return to work and that they could go home. Largely, only personnel who were working to remediate the outage were able to gain access to RFC_URE5 Headquarters. In addition, when individuals (e.g., vendors) arrived who required access to the Data Center, RFC_URE5’s security guards called the person responsible for the visitor and that person escorted the visitor to the necessary location. As a result, the likelihood of unauthorized personnel entering the Data Center was low. RFC_URE5 posted security guards at the entrance to the Data Center to keep manual logs of individuals’ entry and exit. In addition, during this time, an authorized physical security individual required personnel who were already in the Data Center to sign the logs. Although the logs do not include all of the required information, they contain as much information as RFC_URE5 thought practical and possible under the circumstances. In addition, while the potential for compromise existed, during the time period when RFC_URE5 was not capturing logs, the power was out to RFC_URE5 Headquarters such that the machines that could be electronically compromised were inoperable, thus reducing the risk that a physical compromise would have caused a reliability issue. Accordingly, for these reasons, the noncompliance posed minimal risk posed to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) conducted a data center migration. To do this, RFC_URE5 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE5 Headquarters infrastructure. To do this, RFC_URE5 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE5 underground electrical network systems. To do this, RFC_URE5 assessed RFC_URE5’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE5 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE5 took the following actions. To address business function availability prior to moving the data center, RFC_URE5 placed a second generator on standby at RFC_URE5 Headquarters and performed switchgear refurbishment. RFC_URE5 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE5 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014014333 | CIP-006-3c | R5 | RFC_URE4 submitted a Self-Report stating that it had an instance of noncompliance with CIP-006-3c R5. As background, RFC_URE4’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE4 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE4 Headquarters. RFC_URE4’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE4 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE4 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. As a result of the loss of power at RFC_URE4 Headquarters, RFC_URE4 lost the ability to monitor all physical access points to its Physical Security Perimeter (PSP) in real time as required by CIP-006-3c R5. More specifically, RFC_URE4’s Security Operations Center (SOC) could not connect to the monitoring servers located at the Data Center. SOC personnel evacuated RFC_URE4 Headquarters and traveled to the disaster recovery center. The SOC recovered the ability to monitor sites in real time. After the SOC came back online, security personnel took the following actions to investigate whether unauthorized physical access attempts occurred: (a) reviewed all unmanned PSPs and discovered no signs of forced entry and (b) reviewed communication logs for the backup system for every site and determined that no alarms occurred that required dispatch during the outage window. The duration of this noncompliance was approximately four and a half hours, during the time RFC_URE4 could not monitor physical access points to the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE4’s failure to monitor and log access at PSP access points for four and a half hours could have potentially resulted in an intruder gaining access to Critical Cyber Assets (CCAs) and Critical Assets and compromise the Bulk Electric System. However, this risk was mitigated by the following factors. First, RFC_URE4 did not lose electronic logging capability for its physical access controls systems, so RFC_URE4 was able to review electronic logs of its remote sites after it regained power. As a result, RFC_URE4 did not lose the data that would have been monitored, but rather only lost the capability to monitor it real time. Second, after the event RFC_URE4 immediately dispatched security personnel to each CIP site to determine whether there were signs of forced entry, and RFC_URE4 discovered none. Third, local alarms and strobe lights remained functional during the outage. Lastly, RFC_URE4 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) conducted a data center migration. To do this, RFC_URE4 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE4 Headquarters infrastructure. To do this, RFC_URE4 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE4 underground electrical network systems. To do this, RFC_URE4 assessed RFC_URE4’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE4 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE4 took the following actions. To address business function availability prior to moving the data center, RFC_URE4 placed a second generator on standby at RFC_URE4 Headquarters and performed switchgear refurbishment. RFC_URE4 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE4 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014334 | CIP-006-3c | R5 | RFC_URE5 submitted a Self-Report stating that it had an instance of noncompliance with CIP-006-3c R5. As background, RFC_URE5’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE5 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE5 Headquarters. RFC_URE5’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE5 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE5 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. As a result of the loss of power at RFC_URE5 Headquarters, RFC_URE5 lost the ability to monitor all physical access points to its Physical Security Perimeter (PSP) in real time as required by CIP-006-3c R5. More specifically, RFC_URE5’s Security Operations Center (SOC) could not connect to the monitoring servers located at the Data Center. SOC personnel evacuated RFC_URE5 Headquarters and traveled to the disaster recovery center. The SOC recovered the ability to monitor sites in real time. After the SOC came back online, security personnel took the following actions to investigate whether unauthorized physical access attempts occurred: (a) reviewed all unmanned PSPs and discovered no signs of forced entry and (b) reviewed communication logs for the backup system for every site and determined that no alarms occurred that required dispatch during the outage window. The duration of this noncompliance was approximately four and a half hours, during the time RFC_URE5 could not monitor physical access points to the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE5’s failure to monitor and log access at PSP access points for four and a half hours could have potentially resulted in an intruder gaining access to Critical Cyber Assets (CCAs) and Critical Assets and compromise the Bulk Electric System. However, this risk was mitigated by the following factors. First, RFC_URE5 did not lose electronic logging capability for its physical access controls systems, so RFC_URE5 was able to review electronic logs of its remote sites after it regained power. As a result, RFC_URE5 did not lose the data that would have been monitored, but rather only lost the capability to monitor it real time. Second, after the event RFC_URE5 immediately dispatched security personnel to each CIP site to determine whether there were signs of forced entry, and RFC_URE5 discovered none. Third, local alarms and strobe lights remained functional during the outage. Lastly, RFC_URE5 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) conducted a data center migration. To do this, RFC_URE5 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE5 Headquarters infrastructure. To do this, RFC_URE5 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE5 underground electrical network systems. To do this, RFC_URE5 assessed RFC_URE5’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE5 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE5 took the following actions. To address business function availability prior to moving the data center, RFC_URE5 placed a second generator on standby at RFC_URE5 Headquarters and performed switchgear refurbishment. RFC_URE5 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE5 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014014312 | CIP-007-3a | R6 | RFC_URE4 submitted a Self-Report stating that it had an instance of noncompliance with CIP-007-3a R6. As background, RFC_URE4’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE4 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE4 Headquarters. RFC_URE4’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE4 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE4 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. The power outage at RFC_URE4’s Data Center resulted in the loss of power to RFC_URE4’s Cyber Assets that log security events and its systems used to monitor security events and alert support personnel of those security events. Without access to these Cyber Assets, RFC_URE4 could not implement its automated tools or organizational process controls to monitor system events related to cyber security that may have occurred during that time period as required by CIP-007-3a R6. In addition, since RFC_URE4 did not have the logs, it could not review the logs for system events related to cybersecurity and maintain records of reviewing the logs as required by CIP-007 R6.5. The duration of this noncompliance was approximately 15 hours, when RFC_URE4 was unable to monitor and log system events related to cyber security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE4’s failure to monitor and log system events for 15 hours could have potentially resulted in an intruder gaining electronic access to Critical Cyber Assets and Critical Assets without RFC_URE4’s knowledge. However, this risk was mitigated by the following factors. First, RFC_URE4 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, McAfee host intrusion prevention and antivirus was operational. Third, two-factor authentication to access security zones such as Electronic Security Perimeters was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) conducted a data center migration. To do this, RFC_URE4 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE4 Headquarters infrastructure. To do this, RFC_URE4 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE4 underground electrical network systems. To do this, RFC_URE4 assessed RFC_URE4’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE4 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE4 took the following actions. To address business function availability prior to moving the data center, RFC_URE4 placed a second generator on standby at RFC_URE4 Headquarters and performed switchgear refurbishment. RFC_URE4 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE4 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014321 | CIP-007-3a | R6 | RFC_URE5 submitted a Self-Report stating that it had an instance of noncompliance with CIP-007-3a R6. As background, RFC_URE5’s headquarters experienced a loss of power to its data center (the Data Center). Underground explosions in the city caused a distribution network interruption. RFC_URE5 determined that these explosions were caused by the age and type of insulation for the underground secondary cables. A long duration, high impedance phase-to-phase fault in ducts caused pyrolysis of insulation, releasing hot hydrocarbon gases that ignited in the manholes. As a result of the underground explosions, utility service was cut to RFC_URE5 Headquarters. RFC_URE5’s backup generator failed to start, and manual attempts to start the backup generator initially failed. The Uninterruptible Power Supply batteries to the Data Center were drained before the generator was successfully started. In responding to the power outage, RFC_URE5 experienced challenges with notification, communication, and coordination of response and recovery efforts. The root causes that RFC_URE5 identified were that business continuity plans were not updated and/or practiced frequently enough, there was no mass notification method capable of notifying the enterprise, and there was a lack of integrated incident response framework. The power outage at RFC_URE5’s Data Center resulted in the loss of power to RFC_URE5’s Cyber Assets that log security events and its systems used to monitor security events and alert support personnel of those security events. Without access to these Cyber Assets, RFC_URE5 could not implement its automated tools or organizational process controls to monitor system events related to cyber security that may have occurred during that time period as required by CIP-007-3a R6. In addition, since RFC_URE5 did not have the logs, it could not review the logs for system events related to cybersecurity and maintain records of reviewing the logs as required by CIP-007 R6.5. The duration of this noncompliance was approximately 15 hours, when RFC_URE5 was unable to monitor and log system events related to cyber security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE5’s failure to monitor and log system events for 15 hours could have potentially resulted in an intruder gaining electronic access to Critical Cyber Assets and Critical Assets without RFC_URE5’s knowledge. However, this risk was mitigated by the following factors. First, RFC_URE5 employs a defense-in-depth approach for twenty-four hours a day, seven days a week cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, McAfee host intrusion prevention and antivirus was operational. Third, two-factor authentication to access security zones such as Electronic Security Perimeters was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) conducted a data center migration. To do this, RFC_URE5 implemented near and long-term solutions to mitigate data center availability risks, construct a new data center and associated IT components (e.g., servers, storage, and networking), and perform detailed data center move planning; 2) improved the RFC_URE5 Headquarters infrastructure. To do this, RFC_URE5 assessed the current building infrastructure, hardened existing electrical infrastructure, and reduced business operation risk prior to the data center migration; 3) improved the RFC_URE5 underground electrical network systems. To do this, RFC_URE5 assessed RFC_URE5’s underground electrical network systems across its footprint and prioritized risks and performed repairs or installed new components; and 4) improved its organizational response. To do this, RFC_URE5 identified corporate objectives for the business continuity program, performed a business impact analysis, and implemented an emergency mass notification and incident command system. To mitigate risk in the short-term, RFC_URE5 took the following actions. To address business function availability prior to moving the data center, RFC_URE5 placed a second generator on standby at RFC_URE5 Headquarters and performed switchgear refurbishment. RFC_URE5 also increased the frequency of turbine generator testing, updated generator training for operators, provided 24x7 coverage of the emergency generators and switchgear maintenance, and added additional staff members to support these activities along with operator training. In addition, RFC_URE5 performed circuit improvements including ensuring the generators can feed the UPS bypass circuits and remediating the switchgear feeding the building.
2016-04-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014133 | CIP-004-3a | R4 | SERC sent SERC_URE1 a notice of a Compliance Audit. SERC_URE1 and its affiliate submitted Self-Reports stating that it had an issue with CIP-004-3a R4. On three occasions, SERC_URE1 or its affiliated mistakenly granted individuals incorrect and unauthorized physical access to CCAs, and then identified and removed the mistaken access the following day. The first instance occurred when a former employee returned to SERC_URE1. The employee had previously had authorized physical access to one Physical Security Perimeter (PSP). When SERC_URE1 issued the employee a new badge upon his return to SERC_URE1, SERC_URE1 inadvertently granted him access to the PSP he previously had access to even though such access was not required or authorized. This error occurred because SERC_URE1 had not fully removed the employee’s prior access rights from its access control system, despite its prior termination of badge access as required, which resulted in the automatic granting of the prior access rights even though such access rights were no longer required or authorized. The next day, SERC_URE1 reviewed its daily anomaly report, found that the employee had access to a PSP that contained eight CCAs without the required authorization, and immediately removed the employee’s access rights to the PSP in question. The anomaly report is an internal control in which SERC_URE1 verifies access granted based on the access that was approved. The root cause for this issue was that SERC_URE1 failed to complete the request to revoke the individual’s access privileges in the access control system approximately 5 months prior, resulting in the restoration of the prior access rights when creating a new access badge. The second instance occurred when a SERC_URE1affiliate's physical access control administrator was granting authorized access to one employee for three PSP access points in the employee’s local office. At the same time, the administrator was granting general non-CIP access to second employee working in a second office. While programming the access, the administrator inadvertently granted access to the three PSP access points in the first office to the second employee. The second employee had not been authorized for access to CCAs, received cyber security training, or undergone a personnel risk assessment meeting the requirements of CIP-004 R3. The next day, the SERC_UR1 affiliate discovered the issue while reviewing its daily anomaly report to confirm that it appropriately granted access privileges. The SERC_UR1 affiliate found that the first employee had not received the correct access permissions and that the second employee had inadvertently received physical access rights to three PSP access points in the first office. The SERC_UR1 affiliate removed the second employee’s physical access to the PSP access points in the first office approximately 18 hours after the administrator inadvertently granted the access. The SERC_UR1 affiliate verified that the second employee did not access, nor attempt to access, any PSP access points during the issue. The root cause of the issue was a human performance failure, caused in part because the administrator had both employee records opened at the same time and inadvertently programmed physical access to the second employee. The third instance occurred when SERC_URE1’s badging office received and processed a request for an employee to gain physical access to four PSPs. The employee had a valid personnel risk assessment and had attended the required cyber security training. The SERC_URE1 badging office inadvertently granted the employee access to a fifth PSP that was not included in the approved request. The next day, SERC_URE1 discovered the issue while reviewing its daily anomaly report to confirm access privileges were appropriately assigned, discovered that the employee had been incorrectly granted physical access rights to the fifth PSP, and took immediate action to revoke the incorrect physical access rights. SERC_URE1 reported that human error was the primary cause of the failure. SERC_URE1 mitigated each instance within one day of identifying the mistaken granting of physical access to the PSP by removing the respective individual's access to the PSP in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 and its affiliate’s mistaken granting of physical access rights to CCAs that were incorrect and unauthorized could have resulted in unauthorized individuals gaining physical access to CCAs. However, in each instance, SERC_URE1 and its affiliate’s internal controls in the form of the daily anomaly report identified the mistaken granting of physical access within one day, allowing SERC_URE1 and its affiliate to take immediate action to revoke the mistaken physical access before harm could occur. In all three instances, SERC_URE1 and its affiliate reviewed the physical access logs and confirmed that none of the individuals attempted to or gained access to the PSPs to which they mistaken received access rights. For the first and third instances, the employees involved were up-to-date on cyber security training and had completed a personnel risk assessment. For the second instance, the SERC_URE affiliate performed an extent of condition analysis and determined that there were no other instances of CIP access being granted to an employee that was not authorized. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-004 R4 compliance history in determining the disposition track. SERC determined that SERC_URE1's compliance history should not serve as a basis for applying a penalty. Three prior issues were instances where SERC_URE1 failed to revoke employees’ access within the required seven day window. One prior issue is closely related to the instant issue. The mitigating activities implemented for the prior issue were instrumental in identifying the instant issue. For the first issue in a prior instance, two individuals who did not have physical access were on the access list. For the second issue, an individual maintained access that was no longer required. However, SERC_URE1’s internal review of access rights identified the issue 11 days later. For another prior issue, a security officer resigned but was not terminated in the SERC_URE1 system. The officer retained authorized unescorted physical access to three ESPs and retained possession of the access badge. SERC also considered the issues one day duration and the fact that SERC_URE1’s internal controls led to its discovery when determining that the issue was appropriate for compliance exception treatment. | To mitigate this issue, SERC_URE1: 1) removed physical access privileges for the individuals in question; 2) initiated an interim process to email the badging office for suspensions or terminations; 3) programmed a script within the Physical Access Control Systems (PACS) to remove any NERC CIP Access privileges from a suspended or deleted person record; and 4) documented the technical and procedural controls regarding the daily “deleted” script for the PACS.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014783 | CIP-005-3a | R3; R3.2 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-005-3a R3.2. SPPRE_URE1 discovered that a large batch of electronic files had locked up its logging and collection server associated with non-Critical Cyber Assets located within the Electronic Security Perimeter (ESP). Believing that the server lock-up was caused by non-CIP related temporary report files, SPPRE_URE1 personnel deleted the electronic files and reset the logging and collection system to solve the problem. SPPRE_URE1 later discovered that the deleted files were access logs associated with thirteen non-Critical Cyber Assets located within its ESP. As a result, had there been electronic attempts at or actual unauthorized accesses to one or more of the affected non-Critical Cyber Assets, an alert would not have been generated by the logging and collection server forSPPRE_URE1 to investigate. The duration of this instance of noncompliance was from the earliest date electronic access logs from the non-Critical Cyber Assets were deleted from the logging and collection server, through the latest date that such access logs were deleted from the logging and collection server. The root cause of this instance of noncompliance was human error due to personnel not recognizing the electronic files as access logs for non-Critical Cyber Assets within SPPRE_URE1’s ESP before deleting them. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R1.5 has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur without the Registered Entity’s knowledge. Notwithstanding, only non-Critical Cyber Assets were affected, as SPPRE_URE1 utilizes a separate logging and alerting tool for monitoring Critical Cyber Assets within its ESP. The unavailability of the electronic access logs was limited to one month. SPPRE_URE1’s Cyber Assets were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. SPPRE_URE1 timely identified, self-reported, and mitigated this instance of noncompliance. No actual harm is known to have occurred as a result of the noncompliance. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment. SPPRE_URE1's prior noncompliance involved different CIP-005 requirements, which are unrelated to security monitoring and logging processes. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) reset the logging and collection system, which caused the logging and collection server to again have monitoring and logging capabilities for the affected non-Critical Cyber Assets; 2) verified that logs have been saved and available since resetting the logging and collection system; 3) met with affected security status monitoring support personnel and identified the root cause of the noncompliance, i.e., inadvertently clearing the electronic access logs, and advised all such personnel that they must prioritize log retention during any future troubleshooting of the logging and collection system; and 4) implemented alerting configurations to the logging and collection system to generate alerts for failure of the system, i.e., system lock-up or interruption of the system. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014782 | CIP-005-3a | R5; R5.3 | SPPRE_URE1 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-005-3a R5.3. SPPRE_URE1 discovered that a large batch of electronic files had locked up its logging and collection server associated with non-Critical Cyber Assets located within the Electronic Security Perimeter (ESP). Believing that the server lock-up was caused by non-CIP related temporary report files, SPPRE_URE1 personnel deleted the electronic files and reset the logging and collection system to solve the problem. SPPRE_URE1 later discovered that the deleted files were access logs associated with non-Critical Cyber Assets located within its ESP. Because the electronic access logs were deleted from the logging and collection server, SPPRE_URE1 did not retain the electronic access logs for such assets for at least ninety calendar days. The duration of this instance of noncompliance was from the earliest date electronic access logs from the non-Critical Cyber Assets were deleted from the logging and collection server, through the latest date that such access logs were deleted from the logging and collection server. The root cause of this instance of noncompliance was human error due to personnel not recognizing the electronic files as access logs to non-Critical Cyber Assets within SPPRE_URE1’s ESP before deleting them. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R5.3 has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur without the Registered Entity’s knowledge. Notwithstanding, only non-Critical Cyber Assets were affected, as SPPRE_URE1 utilizes a separate logging and alerting tool for monitoring Critical Cyber Assets within its ESP. The unavailability of the electronic access logs was limited to one month. SPPRE_URE1’s Cyber Assets were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. Had a cyber security event occurred, SPPRE_URE1 most likely would have had access to the individual host device logs for use in forensics analysis. SPPRE_URE1 timely identified, self-reported, and mitigated this instance of noncompliance. No actual harm occurred as a result of the noncompliance. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment. SPPRE_URE1's prior noncompliance involved different CIP-005 requirements, which are unrelated to security monitoring and logging processes. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) reset the logging and collection system, which caused the logging and collection server to again have monitoring and logging capabilities for the affected non-Critical Cyber Assets; 2) verified that logs have been saved and available since resetting the logging and collection system; 3) met with affected security status monitoring support personnel and identified the root cause of the noncompliance, i.e., inadvertently clearing the electronic access logs, and advised all such personnel that they must prioritize log retention during any future troubleshooting of the logging and collection system; and 4) implemented alerting configurations to the logging and collection system to generate alerts for failure of the system, i.e., system lock-up or interruption of the system. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014784 | CIP-007-3a | R6; R6.4; R6.5 | SPPRE_URE1 discovered that a large batch of electronic files had locked up its logging and collection server associated with non-Critical Cyber Assets located within SPPRE_URE1’s Electronic Security Perimeter (ESP). Believing that the server lock-up was caused by non-CIP related temporary report files, SPPRE_URE1 personnel deleted the electronic files and reset the logging and collection system to solve the problem. SPPRE_URE1 later discovered that the deleted files were access logs associated with thirteen non-Critical Cyber Assets located within its ESP. Because the electronic access logs were deleted from the logging and collection server, SPPRE_URE1 would not have been able to “review” (R6.5) or “retain” system event logs for ninety calendar days” (R6.4) had there been a cyber security system event associated with one or more of the affected non-Critical Cyber Assets located within SPPRE_URE1’s ESP. The duration of these instances of noncompliance was from the earliest date electronic access logs from the non-Critical Cyber Assets were deleted from the logging and collection server, through the latest date that such access logs were deleted from the logging and collection server. The root cause of these instances of noncompliance was human error due to personnel not recognizing the electronic files were access logs to non-Critical Cyber Assets within SPPRE_URE1’s ESP before deleting them. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R6 has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets and other system events that are related to cyber security to occur without the Registered Entity’s knowledge. Notwithstanding, only non-Critical Cyber Assets were affected, as SPPRE_URE1 utilizes a separate logging and alerting tool for monitoring Critical Cyber Assets. The unavailability of the electronic access logs for the non-Critical Cyber Assets was limited to one month. All Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. Had a cyber security event occurred, SPPRE_URE1 most likely would have had access to the individual host device logs for use in forensics analysis. SPPRE_URE1 timely identified, self-reported, and mitigated these instances of noncompliance. No actual harm occurred as a result of the noncompliance. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issues are appropriate for Compliance Exception treatment. SPPRE_URE1's prior noncompliance involved different CIP-007 requirements, which are unrelated to security monitoring and logging processes. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE1: 1) reset the logging and collection system, which caused the logging and collection server to again have monitoring and logging capabilities for the affected non-Critical Cyber Assets; 2) verified that electronic access logs of the affected non-Critical Cyber Assets have been saved and available since the reset for the logging and collection system; 3) met with affected security status monitoring support personnel and identified the root cause of the noncompliance, i.e., inadvertently clearing the electronic access logs, and advised all such personnel that they must prioritize log retention during any future troubleshooting of the logging and collection system; and 4) implemented alerting configurations to the logging and collection system to generate alerts for failure of the system, i.e., system lock-up or interruption of the system. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014785 | CIP-006-3c | R2; R2.2 | SPPRE_URE1 submitted a Self-Report stating that it had minimal risk instances of noncompliance with CIP-006-3c R2.2 for not affording the protective measures specified in CIP-007-3a R6.4 and R6.5 to its Physical Access Control System (PACS). CIP-007-3a R6.4 and R6.5, as applied to CIP-006-3c R2.2, requires SPPRE_URE1 to “review logs” (R6.5) of PACS devices, “exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers,” associated with cyber security system events, and “retain all [such] logs . . . for ninety calendar days” (R6.4). SPPRE_URE1’s physical access control system (PACS) controls and monitors physical access to its PSP per CIP-006-3c R2. The PACS server sends electronic access logs of each individual PACS device to a logging and collection server. The logging and collection server monitors and issues alerts for cyber security system events associated with its PACS devices per CIP-007-3a R6. SPPRE_URE1 discovered that a large batch of electronic files had locked up the logging and collection server. Believing that the server lock-up was caused by non-CIP related temporary report files, SPPRE_URE1 personnel deleted the electronic files and reset the logging and collection system, to solve the problem. SPPRE_URE1 later discovered that some of the deleted electronic files were electronic access logs associated with its PACS devices. Because the electronic access logs from the PACS devices were deleted from the logging and collection server, SPPRE_URE1 would have been unable to review (R6.5) or retain such logs for ninety calendar days (R6.4), had there been a cyber security system event associated with one or more PACS device. The duration of these instances of noncompliance was from the earliest date electronic access logs from PACS devices were deleted from the logging and collection server, through the latest date that such access logs were deleted from the logging and collection server. The root cause of these instances of noncompliance was human error due to personnel not recognizing the electronic files were PACS access logs before deleting them. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-006-3c R2.2 has the potential to affect the reliability of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur without the Registered Entity’s knowledge. Notwithstanding, only non-Critical Cyber Assets were affected, as SPPRE_URE1 utilizes a separate logging and alerting tool for monitoring Critical Cyber Assets. The noncompliance did not affect the monitoring, alerting, or logging capabilities of cyber security system events to SPPRE_URE1’s Physical Security Perimeter. Except for CIP-007-3a R6.4 and R6.5, all other protective measures specified in CIP-006-3c R2.2 had been afforded. The unavailability of the electronic access logs for the PACS devices was limited to one month. All Cyber Assets within the ESP were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. SPPRE_URE1 timely identified, self-reported, and mitigated these instances of noncompliance. No actual harm is known to have occurred as a result of the noncompliance. SPP RE considered SPPRE_URE1’s compliance history and determined that the instant compliance issues are appropriate for Compliance Exception treatment. SPPRE_URE1's prior noncompliance involved different R2.2 protective requirements, which are unrelated to security monitoring and logging processes. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE1: 1) reset the logging and collection system, which caused the logging and collection server to again have monitoring, alerting, and logging capabilities of PACS devices; 2) verified that PACS access logs have been saved and available since the reset of the logging and collection system; 3) met with affected security status monitoring support personnel and identified the root cause of the noncompliance, i.e., inadvertently clearing PACS access logs, and advised all such personnel that they must prioritize log retention during any future troubleshooting of the logging and collection system; and 4) implemented alerting configurations to the logging and collection system to generate alerts for failure of the system, i.e., system lock-up or interruption of the system. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014014287 | CIP-007-3a | R1; R1.1; R1.3 | During a Compliance Audit SPP RE determined that SPPRE_URE2 had two minimal risk instances of noncompliance with CIP-007-3a R1.1. SPPRE_URE2 did not adhere to its security testing procedures for two significant changes applied to two existing Cyber Assets located within SPPRE_URE2’s Electronic Security Perimeter (ESP). Specifically, after the significant changes had been implemented, SPPRE_URE2 neither compared the open ports and services of such assets to its ports and services baseline nor conducted a default account review of the assets to ensure the account settings were correct as required by its security testing procedures. As a result, SPPRE_URE2 was unable to ensure that the significant changes to the PDS and data historian server did not adversely affect the production system or its operation. The duration of these instances of noncompliance was from the date the first significant change was implemented, through the date SPPRE_URE2 completed its mitigation. The root cause of these instances of noncompliance was SPPRE_URE2 personnel not adhering to its security testing procedures. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity for the installation of new Cyber Assets and significant changes to existing Cyber Assets within the ESP to adversely affect existing cyber security controls. Absent these isolated incidents, SPPRE_URE2 conducted compliant security testing for all significant changes to Cyber Assets located within its ESP. The assets are both protected by a firewall specifically configured to only allow traffic using specific protocols to enter the network, which prevents unsolicited traffic from passing into the ESP. SPPRE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets within the ESP are limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. SPP RE considered SPPRE_URE2’s compliance history and determined that the instant compliance issues are appropriate for Compliance Exception treatment. SPPRE_URE2's prior noncompliance involved involved different CIP-007 Requirements and they are unrelated to testing of significant changes to Cyber Assets within the ESP. Although the instant noncompliance is a repeat of CIP-007 R1.3, the underlying conduct of the prior and instant noncompliance is different. | To mitigate these instances of noncompliance, SPPRE_URE2: 1) developed a security controls testing form, which is to be completed and attached to each CIP significant change ticket, to ensure that such changes to not adversely affect existing cyber security controls; and 2) added a review task to all CIP significant change tickets requiring the CIP coordinator to review such tickets to ensure adherence to SPPRE_URE2’s security testing procedures prior to the tickets being closed. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2014013918 | CIP-007-3a | R5; R5.1.1 | SPPRE_URE3 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-007-3a R5.1.1. An employee (user) followed SPPRE_URE3’s account management process and requested approval of electronic access to certain Cyber Assets located within an SPPRE_URE3 Electronic Security Perimeter (ESP). Following approval of the access request by the designated personnel, the user sent the approved access request to the IT personnel responsible for activating electronic access approvals. However, the user had mistakenly requested an inappropriate level of electronic access based on his job responsibilities. The designated IT personnel realized that the user needed less restrictive access rights based on his job title and preemptively activated the appropriate level of access rights without first obtaining approval for that level of access rights from appropriate personnel per SPPRE_URE3’s account management process The duration of this noncompliance is from the date the user received unapproved electronic access, to the date SPPRE_URE3 approved the user’s proper electronic access. The root cause of this instance of noncompliance was human error due to personnel not adhering to SPPRE_URE3’s account management process. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-3a R5 has the potential to affect the reliable operation of the BPS by providing the opportunity for unauthorized system access. Although the actions taken by IT personnel to preemptively activate the employee access at the correct access level were not approved by the appropriated personnel prior to activation , the employee was ultimately approved for the less restrictive access rights originally provisioned by IT personnel. The unapproved access was discovered the next morning through a daily, detective control that compares provisioned access against approved access, and the employee’s access was revoked. The correct level of electronic access was approved within 48 hours. In addition, SPPRE_URE3 reviewed system logs and determined that the employee did not access any systems while he had unapproved access. SPPRE_URE3 promptly discovered, mitigated, and self-reported the noncompliance. No harm occurred as a result of the noncompliance. SPP RE considered SPPRE_URE3’s compliance history and determined that the instant issue was appropriate for CE treatment because SPPRE_URE3 has no relevant prior violations. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE3: 1) revoked the activated electronic access and submitted a new request for the correct access; 2) activated the approved correct access once the approvals were complete; and 3) counseled all affected IT personnel responsible for activating approved electronic accesses on SPPRE_URE3’s account management approval process. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015015411 | CIP-004-3a | R4; R4.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4.2. Specifically, TRE_URE1 failed to revoke physical access to Critical Cyber Assets (CCAs) within seven calendar days for seven employees who no longer required such access. For four of the TRE_URE1 employees in question, the root cause of the physical access revocation issue was an insufficient internal process for such revocations. In particular, TRE_URE1’s access revocation process called for its Human Resources (HR) department to initiate the access revocation process for certain employee transfers within the company when there were changes to that employee’s assigned work position number. In the current circumstances, however, the four TRE_URE1 employees in question were reassigned to other positions within the company without any corresponding changes to their respective work position numbers. Accordingly, the HR department did not recognize the need to request physical access revocation for these employees. For the remaining three TRE_URE1 employees, the root cause of the issue was human performance error. In particular, TRE_URE1 Compliance personnel failed to follow existing access control procedures for revoking physical access. Texas RE determined the issue duration to be more than one year and four months, from the day after TRE_URE1 should have revoked the employee’s access to CCAs in the first instance until TRE_URE1 revoked access for all seven employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All seven employees remained employed at TRE_URE1 throughout the duration of the issue. Further, only three of these employees actually entered a PSP at any time. None of these three employees had access to CCAs at the time they were in the PSP. Moreover, with the exception of one instance lasting one minute, the three employees were either continuously escorted or were performing tasks related to their transition and, therefore, required access. In addition, TRE_URE1 employs a layered defensive approach, including physical and electronic controls to protect and monitor CCAs within the PSP. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) revoked physical access for all seven employees; 2) modified existing TRE_URE1 access revocation processes to eliminate the connection between work position numbers and the revocation of access rights by shifting the responsibility for initiating the access revocation process for transferring employees from HR to the employee’s current manager; and 3) completed access management system training for Compliance personnel. Texas RE has verified the completion of all mitigation activity.
2016-03-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015040 | CIP-007-1 | R2; 2.1 | MRO_URE1 submitted a self-log stating that it had an issue with CIP-007-1 R2. Specifically, MRO_URE1 identified three Transmission Control Protocol (TCP) ports that were enabled on 20 Critical Cyber Assets (CCAs) and one non-critical cyber asset within its Electronic Security Perimeter (ESP) that were not included in its port documentation. MRO_URE1 identified this concern while conducting its annual cyber vulnerability assessment. MRO_URE1 relied upon its energy management system (EMS) vendor's documentation to identify and confirm its ports. However, the EMS vendor's documentation was incorrect and did not include all required and enabled ports. Following this discovery, MRO_URE1 confirmed with its vendor that the undocumented ports are necessary for maintenance operation of the equipment. The vendor released a Service Bulletin addressing the need to document these ports required for normal operation. This issue began when the EMS was placed into production and continued until MRO_URE1 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the three TCP ports were undocumented and unapproved, they were required to be enabled for normal operations. The affected devices were never directly accessible from the internet, and were protected by a layered security system which includes: location within a locked Physical Security Perimeter (PSP); alarming of interruptions of the physical Ethernet connections; logging and monitoring of the access to the Ethernet interface; location within an ESP protected by firewalls and Intrusion Detection Systems; and antivirus scanning. No harm is known to have occurred. This is MRO_URE1's first issue with CIP-007-1 R2. | To mitigate this issue, MRO_URE1: 1) disconnected the network from the equipment to ensure the Ethernet port is no longer utilized on the equipment; and 2) performed testing and evaluation to determine that the vendor configuration can be modified to support an alternative configuration; and 3) implemented an alternate local serial console port on the equipment to perform the required function.
2016-03-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2015015041 | CIP-007-3a | R2; 2.1 | MRO_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a, R2. Specifically, MRO_URE2 identified five unapproved Transmission Control Protocol (TCP)/Internet Protocol (IP) ports that were enabled on 15 Critical Cyber Assets (CCAs) that were not included in its port documentation. MRO_URE2 relied upon its energy management system (EMS) vendor's documentation to identify and confirm its ports. However, the EMS vendor's documentation was incorrect and did not include all required and enabled ports. MRO_URE2 learned of this issue with its EMS vendor during an industry forum, and performed an independent network mapper (nmap) scan on its devices and identified that it had enabled ports that were not documented. The vendor released a Service Bulletin addressing the need to document these ports required for normal operation. Upon identifying the affected ports, MRO_URE2 confirmed that the undocumented and unapproved ports were required to be enabled for normal operations. The issue began when the devices were placed into production, and continued until MRO_URE2 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the five TCP/IP ports were undocumented and unapproved, they were required to be enabled for normal operations. MRO_URE2 confirmed that the devices were never directly accessible to the internet and are protected by a layered security system which included: requiring physical access within an established Physical Security Perimeter (PSP); using local system password authentication; and changing default passwords upon commissioning. No harm is known to have occurred. This is MRO_URE2's first issue with CIP-007-3a R2. | To mitigate this issue, MRO_URE2: 1) performed an independent nmap scan on its devices; 2) added the five TCP/IP ports to existing cyber asset baseline definition; and; 3) updated its cyber asset commissioning procedure to include language to assess all active server interfaces to identify listening ports and services.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015500 | CIP-003-3 | R6 | RFC_URE1 submitted a self-log stating that it had an issue of CIP-003-3 R6. RFC_URE1 IT Technical staff was alerted by routine monitoring to a traffic anomaly. The monitoring tool detected a signature pattern anomaly. RFC_URE1 IT Technician investigated the alert and discovered software was installed on NERC CIP assets without going through the change control process. RFC_URE1 IT failed to follow its change control process when installing software on six NERC CIP assets. The NERC CIP assets included five Electronic Access Control and Monitoring (EACMS) and one Physical Access Control Systems (PACS) asset. The first five changes were initially identified by RFC_URE1's security monitoring within 24 hours of the software being installed. Security events are reviewed and reconciled to confirm that changes are authorized via RFC_URE1’s change control process. However, these installation activities were reconciled to incorrect change requests and the reconciliations were closed. The last EACMS was identified during investigation after the initial finding. Security monitoring identified the software installation for this device; however, the reconciliation was not completed before it was identified during this investigation. The root cause was ineffective training. The RFC_URE1 IT employees responsible for installing the software at issue on the six NERC CIP assets did not understand how to effectively follow RFC_URE1's change control process for installing software. The duration of this noncompliance is from the date RFC_URE1 first installed software on a NERC CIP asset without following its change control process to, the date RFC_URE1 retroactively completed the change control process for the six NERC CIP assets at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 IT performed testing, including a vulnerability scan, of the software prior to installation. The software was installed in the corporate non-NERC environment without any concerns. Only five EACMS assets and one PACS asset were updated without proper change control. The lack of knowledge of the change control process was not widespread. While certain new individuals did not understand the process, other RFC_URE1 IT employees who more frequently perform changes to NERC CIP assets understand and effectively implement the change control process. Of the RFC_URE1 IT priority incidents that RFC_URE1 addressed year to date, none resulted from a lack of change control or unauthorized changes. The cybersecurity testing was successfully completed 77 days after the software was deployed on the first NERC CIP asset. The cybersecurity testing found no risks and the software operated without issues during this time. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 completed the following mitigating activities: 1) retroactively completed the change control process for all six affected NERC CIP assets. Infrastructure Change Requests for these changes were created and completed; 2) completed Cybersecurity testing on associated development assets; 3) immediately held a stand down meeting with RFC_URE1 IT individuals with known involvement to review the incident; 4) counseled the individuals who did not follow the change control process to enforce expectations that formal Change Management is required for all NERC CIP changes; 5) revised their onboarding process to require new employees to complete training course, "RFC_URE1 IT Change Management;" 6) reduced the number of persons with access to Access Control System NERC assets; 7) conducted meetings with the individuals involved in the security reconciliation process for NERC CIP changes to reinforce the expectations that security alerts be reconciled accurately and in a timely manner; and 8) revised the security reconciliation process to require that the Support Team initiate a ticket to track reconciliation instead of the current email process.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015501 | CIP-007-3a | R1 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-007-3a R1. RFC_URE2 IT Transmission Management System (TMS) personnel discovered, that it had an issue of CIP-007-3 R1 because cybersecurity testing was not performed. RFC_URE2 IT personnel discovered five patches from the previous patch cycle were deployed in the production environment, but were not cybersecurity tested. Cybersecurity testing was conducted and documented in preparation for a regularly scheduled patch cycle. Following the completion of cybersecurity testing, patches were installed on production workstations. While preparing for the next patch cycle, IT support personnel noticed five patches in the NERC patch environment waiting to be installed into the test environment. At the beginning of a patch cycle, there should be no patches waiting for installation. After investigation, IT support personnel determined that the five patches in question were from the prior patch cycle. These patches were not installed from the NERC patch environment into the test environment when cybersecurity testing was performed in the prior patch cycle. Therefore, these five patches were not cybersecurity tested prior to installation in the production environment. 60 consoles were affected. The root cause of this violation was a data sync failure within the system responsible for delivering patches. The sync failure occurred when the patching tool ran out of hard drive space. RFC_URE2 IT may have identified the missing patches through the cybersecurity testing tool; however, the vulnerability scanning tool was not appropriately configured to identify the missing patches during cybersecurity testing. The issue occurred because of two failures in tools and an inadequate detection making control that is used for patching these specific devices. The duration of this noncompliance is from the date RFC_URE2 first installed a patch in the production environment without performing the necessary cybersecurity testing to the date RFC_URE2 conducted cybersecurity testing for the five missing patches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm to the reliability of the Bulk Electric System (BES) that could have occurred during the situation was minor to none. The patches are deployed to production consoles individually. If the patch caused operational problems on one device, the patch deployment would be discontinued until the operational problems were resolved. The TMS is supported by multiple redundant consoles. If the patching caused operational problems on one console, other consoles would support reliable operation of the BES. The consoles provide information to operations personnel and are also redundant. RFC_URE2 considered the harm level was unlikely to be realized for the following reasons: • Patching on these workstations is performed machine-by-machine. If deployment of patch would have caused immediate impact to the operations of the system, patching would have stopped immediately. • RFC_URE2 IT conducted cybersecurity testing for the patches after deployment and determined that there were no unexplained/unexpected results or changes identified that may affect cybersecurity controls. • The vendor performs a functional test of these patches before deployment and no issues were identified. RFC_URE2 has several internal controls in place to detect or prevent violation occurrence, including: • RFC_URE2 IT utilizes work group procedures for managing the patch release process. • RFC_URE2 IT has a strong compliance culture that includes a questioning attitude. The potential violation was found as a result of this questioning attitude. • RFC_URE2 IT uses a vulnerability scanning tool for cybersecurity testing that can help identify vulnerabilities associated with missing patches. RFC_URE2 IT uses this tool to perform cybersecurity testing. Although these controls were not effective in this instance, they are part of the RFC_URE2 IT patch management process that successfully manages most monthly patching cycles. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) conducted cybersecurity testing for the five missing patches (installed/data collected) and analyzed the data. There were no unexplained/unexpected results or changes identified that may affect cybersecurity controls; 2) updated the patch management job aid to add two new verification actions. The first action verifies that adequate hard drive space is available before beginning the synchronization process to collect the patches. The second action is performed after the sync process to verify that the required patches have been downloaded to the patch server; 3) revised the alert level for current monitoring activities on the patch tool to ensure sync issues are identified and addressed in real time; and 4) applied a Group Policy to update the configuration settings of the consoles based upon additional configuration settings provided by the vulnerability scanning tool vendor to identify the missing patches.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015503 | CIP-003-3 | R6 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-003-3 R6. RFC_URE2 determined that it had an issue of CIP-003-3 R6 because the change control process was not followed. RFC_URE2 IT personnel failed to follow its change control process when installing software on six NERC CIP assets. The NERC CIP assets included five Electronic Access Control and Monitoring (EACMS) and one Physical Access Control Systems (PACS) asset. The first five changes were initially identified by RFC_URE2's security monitoring within 24 hours of the software being installed. Security events are reviewed and reconciled to confirm that changes are authorized via RFC_URE2’s change control process. However, these installation activities were reconciled to incorrect change requests and the reconciliations were closed. RFC_URE2 IT Technical staff was alerted by routine monitoring to a traffic anomaly. The monitoring tool detected a signature pattern anomaly. IT Technical staff investigated the alert and discovered software was installed on NERC CIP assets without going through the change control process. The last EACMS was identified during investigation after the initial finding. Security monitoring identified the software installation for this device; however, the reconciliation was not completed before it was identified during this investigation. The root cause of this violation was lack of knowledge by IT personnel of the change control process. The IT individual who performed the software installation on the EACMS servers did not think a change request was required for this particular job because it required no outage or system reboot. This fundamental lack of knowledge presents a high risk that a different violation could have occurred during this timeframe. The duration of this noncompliance is from the date RFC_URE2 first installed software on a NERC CIP asset without following its change control process to, the date RFC_URE2 retroactively completed the change control process for the six NERC CIP assets at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm to the reliability of the Bulk Electric System that could have occurred during the situation was minor to none. Although the software was installed without proper change control, RFC_URE2 IT performed software testing as part of project implementation prior to installing the software in the corporate non-NERC environment without any concerns. RFC_URE2 IT performed a vulnerability scan as part of the software installation testing. The scan identified no active vulnerabilities associated with the software client. The software was installed on numerous physical servers prior to the first installation on a NERC CIP asset. In addition, only five EACMS assets and one PACS asset were involved. No harm is known to have occurred. RFC_URE2 considered the harm level was unlikely to be realized for the following reasons: • RFC_URE2 IT performed testing of the software including a vulnerability scan prior to installation. The vulnerability scan is part of RFC_URE2’s cybersecurity testing and was performed prior to initial deployment in the corporate environment. • The backup software in question had been previously installed in the corporate environment and performed without any concerns. • There were only five EACMS assets and one PACS asset involved; other NERC EACMS and PACS devices did not receive the new backup software during this phase of deployment. • The new backup software was not installed on any NERC Critical Cyber Assets. RFC_URE2 has the several internal controls in place to detect or prevent violation occurrence, including: • IT has documented change control procedures in effect. • IT has change control training for all IT personnel that will be performing change control tasks. • IT uses security monitoring to detect changes to cyber assets with manual change reconciliation of the logged changes to the change requests in the system. • IT performs security monitoring. Although these controls were in place, the preventative controls were not followed effectively in this instance. One monitoring tool identified the changes within 24 hours of the software installation. The alert generated by the security monitoring tool, requires review and reconciliation of the changes to change requests. However, during manual reconciliation, IT reconciled the software installations to incorrect change requests and the reconciliation was closed without identifying the issue. IT monitoring identified the software installation; however, detection occurred more than eight weeks after the first installation. | To mitigate this issue, RFC_URE2: 1) retroactively completed the change control process. Infrastructure Change Requests (ICR) for these changes were created and completed. Cybersecurity testing was completed on associated development assets; 2) held a stand down meeting with IT individuals with known involvement to review the incident; 3) counseled the individuals who did not follow the change control process to enforce expectations that formal Change Control is required for all NERC CIP changes; 4) revised their onboarding process to require new employees to complete training course IT Change Management; 5) reduced the number of persons with access to Access Control System NERC assets; 6) conducted meetings with the individuals involved in the security reconciliation process for NERC CIP changes to reinforce the expectations that security alerts be reconciled accurately and in a timely manner; and 7) revised the security reconciliation process to require that the Support Team initiate a ticket to track reconciliation instead of the current email process.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015015168 | CIP-005-1 | R2; R2.5.1 | During a Compliance Audit, SERC determined that SERC_URE3 had an issue with CIP-005-3a R2.5.1. SERC_URE3 failed to identify and describe its processes for requesting access to all electronic access points to the Electronic Security Perimeter (ESP). SERC_URE3 had a procedure that summarized the overarching process for how remote electronic access is approved, including the requirement that that IT manager and the CIP senior manager review all access requests prior to approving such requests. However, SERC_URE3’s procedure failed to describe the process for how an individual would request electronic access to the ESP. The root cause of this issue was SERC_URE3’s failure in its user access procedure to address the specific requirement requiring the entity to identify and describe the process for requesting electronic access to the ESP. This issue lased from when the Standard became mandatory and enforceable through Mitigation Plan completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3’s failure to have a documented process citing how an individual would request electronic access to the ESP could have left managers or supervisors unaware how to make or respond to such requests, potentially delaying access being granted or causing access to be granted when not actually required. However, SERC_URE3 had existing documentation that required the IT manager and the CIP senior manager to review all access requests and make a determination as to the individual’s need for and appropriateness of the access prior to approving such access. SERC_URE3 did not grant electronic access to electronic access points to the ESP in error during the issue. No harm is known to have occurred. SERC considered SERC_URE3’s CIP-005 R2 compliance history in determining the disposition track. SERC determined that SERC_URE3’s CIP-005 R2 compliance history should not serve as a basis for applying a penalty. The prior violation involved the failure to use a deny by default model for firewall traffic and the failure to allow only ports and services that are required for normal and emergency operations at all access points to the ESP. The Mitigation Plan for the prior violation would not have prevented the instant issue, which involved a failure to document the process for how individuals should request electronic access to the ESP. | To mitigate this issue, SERC_URE3: 1) revised the version five document to address how access is requested; 2) created a workflow diagram to illustrate how access is requested and approved; and 3) trained personnel on the procedural changes.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015014967 | CIP-005-3a | R2 | During a Compliance Audit , SERC determined that SERC_URE4 had an issue with CIP-005-3a R2.5.3. SERC_URE4 failed to complete the access review process and update the Critical Cyber Asset (CCA) access list within seven calendar days of any change as required. SERC_URE4 granted an individual modified access rights to Electronic Access Control and Monitoring (EACM) Cyber Assets. SERC_URE4’s access list indicated that SERC_URE4 granted the individual, but did not indicate when SERC_URE4 updated the list with this change. SERC_URE4 failed to provide evidence that it updated the list with this access modification within seven days as required. The list SERC_URE4 provided was dated for two and a half months later. However, SERC_URE4 did not provide a revision table or workflows for the list or other evidence that SERC_URE4 updated the list within seven days of the change. The root cause of this issue was some confusion internally of SERC_URE4 personnel in transitioning to compliance with Version 5 of the Standard. When SERC_URE4 personnel transferred information from a Version 3 list to a Version 5 list, they failed to record all required information. The issue lasted for approximately two months from the eighth day after SERC_URE4 changed the individual’s access rights, through when SERC_URE4 reviewed and signed-off on the CCA access list as accurate. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE4’s failure to document when it updated the access list with specific electronic or physical access rights within seven days of a change could prevent SERC_URE4 personnel from taking appropriate actions to remove access rights in a timely manner or quickly identifying incorrect access rights. However, this issue lasted less than 90 days and was limited to a single individual who was and remained in good standing with SERC_URE4, had taken the required cyber security training, and had a valid personnel risk assessment. Although SERC_URE4 could not demonstrate that it updated the list within seven days of the change, the access list indicated SERC_URE4 granted the individual access on a certain date and included a list review date. No harm is known to have occurred. SERC considered SERC_URE4’s CIP-005 R2 compliance history and determined there were no relevant instances of noncompliance. SERC considered SERC_URE4’s CIP-004 R4 compliance history in determining the disposition track. SERC determined that SERC_URE4’s CIP-004 R4 compliance history should not serve as a basis for applying a penalty. Two of the prior issues were mitigated more than three years prior to the instant issue and thus SERC did not consider them to be relevant to the instant issue. The other issues involved, respectively, a failure to document the individuals with physical access to CCAs at a single location and a failure to revoke individuals’ access to CCAs within seven days of those individuals no longer needing such access. The instant issue involved a failure by SERC_URE4 to document when it updated its CCA list with an authorized change in access rights for a single individual. The prior mitigating activities would not have prevented the instant issue. | To mitigate this issue, SERC_URE4: 1) retired the CIP Version 3 access list upon approval of the CIP Version 5 access list. This new list was developed as part of SERC_URE4's implementation for CIP Version 5 standards, and is attached as evidence; 2) revised the user account electronic access form to include a checkbox for update to the Cyber Access list spreadsheet; and 3) communicated/trained staff of the form modification during a CIP Version 5 meeting.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015014969 | CIP-007-3a | R5; R5.3.3 | During a Compliance Audit, SERC determined that SERC_URE4 had an issue with CIP-007-3a R5. SERC_URE4 failed to change passwords on eight service accounts at least annually. SERC_URE4 created eight service accounts within its energy management system (EMS) application, and since that time SERC_URE4 did not change the account passwords annually. These accounts provided the ability for applications to communicate and authenticate prior to sharing data in a mixed operating system environment. Using a random password generator, SERC_URE4 created the eight passwords to be 20 characters in length and consist of uppercase, lowercase, numeric, and special characters. Additionally, SERC_URE4 had the ability to change the service account passwords involved annually or more frequently based on risk. SERC_URE4 interpreted the CIP-007 R5.3 password requirements to apply only to accounts that involved “user activity” as stated in CIP-007 R5. However, the requirement to annually change passwords apply to system accounts as well. Although SERC_URE4 created these accounts as machine-to-machine accounts, they were default accounts that enabled the EMS to operate as designed and anticipated. The root cause of this issue was that SERC_URE4 misinterpreted which accounts the CIP-007 R5.3 password requirements applied to. This issue lasted approximately three years, from one day after SERC_URE4 should have changed the passwords annually, until mitigation completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4’s failure to change passwords for over three years could give malicious individuals an extended period to discover and misuse the passwords in ways that could be detrimental to the reliability of the BPS. However, the passwords used exceeded the complexity requirements and would be difficult to guess or crack. The machine-to-machine nature of the service accounts minimized the number of SERC_URE4 system administrators who knew or had sufficient access to learn the specific passwords. SERC_URE4 had layered defense-in-depth, including overall network topology that used layered firewalls outside of the ESP, policies that prohibited interactive sessions through the ESP access points and limited other forms of traffic, and limited external connectivity. SERC considered SERC_URE4’s CIP-007-3a R5 compliance history in determining the disposition track. SERC determined that SERC_URE4’s compliance history should not serve as a basis for applying a penalty. For the prior issue, SERC_URE4 failed to generate logs of sufficient detail to provide audit trails of individual user account access, review Critical Cyber Asset (CCA) user accounts to verify access privileges were correct, identify all individuals with access to CCA shared passwords, have a policy for use of shared accounts, and change passwords on CCAs on an annual basis and failed to submit a request for a Technical Feasibility Exception (TFE) when it was unable to technically enforce the password complexity requirement. In the instant issue, SERC_URE4 misinterpreted what accounts needed to meet the password requirements specified in CIP-007-3a R5.3 and failed to change passwords on eight machine-to-machine service accounts at least annually. The prior mitigating activities would not have prevented the instant issue. | To mitigate this issue, SERC_URE4 will complete the following mitigation activity by July 1, 2016: 1) transition to CIP Version 5.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015014 | CIP-006-3c | R2; R2.2 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R2.2. SERC_URE1 failed to provide physical access control system (PACS) servers the protective measures specified in CIP-003-3 R6 by failing to review malware protection updates prior to implementing them as required by its change control and configuration management program. SERC_URE1’s change control and configuration management program under CIP-003-3 R6 applied to the PACS as well as Critical Cyber Assets (CCAs). SERC_URE1 also maintained a procedure for change control applicable to all malware prevention software used within the CIP program, including PACS and CCAs. Both procedures required a work order and approval(s) prior to implementing changes to a production environment. A newly assigned malware protection administrator took over the program and modified the malware management console for PACS to make it more aligned with the maintenance environment. This unapproved change caused SERC_URE1 to deploy malware updates to PACS servers without conducting the proper review and subsequent testing and getting approvals required by its change management control program. SERC_URE1 improperly deployed the malware updates to 88.89% of its PACS servers, including two non-active failover PACS servers and three non-production test servers. The following day, the SERC_URE1 PACS application team identified the undocumented change to the PACS servers while reviewing a weekly report generated for all malware protection versions, to ensure they were all on the same patch level. SERC_URE1 identified a delta from the previous report and forwarded the information to the malware protection team to be investigated. The root-cause of this issue was two pronged: (1) a human performance error occurred when a newly assigned malware protection administrator failed to follow the established change control processes; and (2) operational deficiencies existed, such as a lack of sufficient details in procedures and a lack of technical controls. This issue lasted nine days, when the SERC_URE1 malware protection administrator made configuration changes that allowed updates to PACS servers without proper review as required by SERC_URE1’s change control and configuration management program, until SERC_URE1 fully tested the change after implementing it and found no impacts to existing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1’s failure to test for existing security control impacts before deploying changes could have caused the PACS system to fail. However, SERC_URE1 discovered this issue quickly, within one day, due to internal controls. SERC_URE1 completed mitigation within nine days of discovering this issue. The PACS door controllers provided access control and logging and would have remained operational if the PACS servers had failed. Prior to this issue, SERC_URE1 had tested the changes on non-CIP corporate systems with the same type of servers and found no adverse impacts. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-006 R1.8, CIP-006 R2, and CIP-003 R6 compliance history in determining the disposition track. SERC_URE1 had no compliance history involving CIP-006 R2. In the first CIP-006 R1.8 issue, SERC_URE1 failed to properly test changes to PACS. However, SERC_URE1 completed mitigating this violation more than three year prior to the instant issue. In the second CIP-006 R1.8 issue, SERC_URE1 failed to secure dial-up access to the PACS as required by CIP-005-1 R2.3 and failed to consider PACS door controllers in the CIP program as required by CIP-006-1 R2. SERC_URE1’s underlying conduct in the prior issue was different from the instant issue. In the third CIP-006 R1.8 issue, SERC_URE1 failed to follow a change management procedure for PACS, which is similar to this instant issue. However, in the prior issue, SERC_URE1 failed to follow its existing change management program for changes being made to the PACS devices. In this instant issue, a new administrator took over the program and made changes to the malware management console for PACS to make it more align with the ‘maintenance’ environment, resulting in malware updates being triggered to the PACS servers. SERC_URE1 found the issue within one day due to a strong internal control and fixed the issue quickly. SERC determined SERC_URE1’s compliance history with CIP-006 R1.8 should not serve as a basis for applying a penalty. In SERC_URE’s prior CIP-003 R6, SERC_URE1 failed to follow its internal change control management process when updating malware prevention software on 86 CCA workstations. However, in the instant issue, SERC_URE1 failed to follow the process when updating PACS. SERC determined SERC_URE1’s compliance history with CIP-003 R6 should not serve as a basis for applying a penalty. | To mitigate this issue, SERC_URE1: 1) disciplined the malware protection administrator for inadvertently configuring the change, failure to follow established change control process and procedures, and not assessing the impact of the intended change; 2) evaluated and developed an action plan to complete server malware protection system technical controls implementation; 3) improved malware protection operational procedure(s); 4) provided procedural change training to the malware protection team; 5) implemented the malware system technical controls implementation action plan; and 6) developed recurring training for the malware protection team.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015264 | CIP-004-3a | R4 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. SERC_URE1 failed to maintain its list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. SERC_URE1 transferred an employee out of a substation area, where the individual had CIP substation physical access permission, into a different department that did not require CIP access rights. On the same day, SERC_URE1 properly revoked the employee’s access permission by removing access from the employee’s permanent access profile and updated the appropriate list. Nineteen days later, before creating a new permanent access profile based on access needed for the employee’s new position, SERC_URE1 created a temporary access profile using the employee’s original permanent profile, which included CIP physical access permissions. Thus, SERC_URE1 improperly gave the employee temporary physical access permissions to CCAs without updating the access list. A week later, during an ad-hoc internal assessment of physical access permissions, SERC_URE1 found the employee at issue had physical access to the Physical Security Perimeters (PSPs), but did not have an authorization form within the access request system for such access. SERC_URE1 investigated the circumstances and cause of the discrepancy, and, the next day, SERC_URE1 determined that the employee did not need access to the CIP substation and immediately revoked the employee’s access rights. The following month, SERC_URE1 conducted a more expansive extent-of-condition investigation for all badge holders with temporary profiles available and found no additional instances of this type of occurrence. SERC_URE1 conducted a detailed clean-up of the temporary access profiles, in order to prevent recurrence. The root-cause of this issue was SERC_URE1 personnel lacked awareness that the CIP permissions on an individual’s temporary profile would continue to include the individual’s original access rights and would not automatically reflect changes made to the individual’s permanent access profile. This issue lasted for seven days, from when SERC_URE1 granted temporary access, which inadvertently included original physical CIP access permissions, until SERC_URE1 removed physical access for CIP sites from the employee’s profile. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to update the access list within seven days of a change in access rights could have given unauthorized personnel the opportunity to physically access CCAs and potentially damage, degrade, or obtain data that could be detrimental to SERC_URE1 operations or the BPS. However, the employee at issue remained in good standing with SERC_URE1, had an up-to-date personnel risk assessment, and was current on required training. SERC_URE1 granted the individual improper physical access to areas containing CCAs, not remote access. After discovering the issue, SERC_URE1 conducted a badge access analysis and found the employee did not use or attempt to gain access to any CIP PSP during the relevant time period. The employee at issue no longer possessed a brass key for the substation gates, preventing the employee from accessing the substation yard that contained the PSP boundary where the badge reader at issue was located. The improper access only lasted eight days. SERC_URE1 made a timely discovery of this issue due to an effective internal control. SERC considered SERC_URE1’s CIP-004 R4 compliance history in determining the disposition track. SERC determined that SERC_URE1's compliance history should not serve as a basis for applying a penalty. For three of the prior issues, SERC_URE1 failed to revoke authorized access within seven days. In the last issue, SERC_URE1 failed to update the access list within seven days of a change in access rights. Here, the issue has a different and unique root cause because SERC_URE1 used a temporary user profile in error. | To mitigate this issue, SERC_URE1: 1) removed temporary physical access to substations; 2) conducted a meeting with leadership to discuss corrective actions; 3) provided direction to security personnel to delete access from permanent and temporary profiles of cardholders in the PACS, if necessary; 4) reviewed temporary access profiles and updated as necessary; 5) updated and implemented facility process to utilize the standard security access request process and restricted security personnel's ability to modify cardkey access rights; and 6) conducted training with facility security on the security access process.
2016-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015015298 | CIP-004-3a | R4; R4.1; R4.2 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. SERC_URE2 failed to maintain list(s) of personnel with authorized cyber access to Critical Cyber Assets (CCAs), including their specific electronic access rights to CCAs. SERC_URE2 promoted an employee who had both approved unescorted physical access and remote access to multiple CCAs and Critical Infrastructure Protection (CIP) secured facilities. Due to the promotion, SERC_URE2 created a work order to have the employee’s remote access revoked. However, SERC_URE2 leadership continued discussing the need for this employee to potentially provide continued support for his or her prior role. The individual responsible for managing access revocations knew about the ongoing discussions and held the revocation work order pending a final management decision. Eight days later, SERC_URE2 management decided to permit revocation of the promoted employee’s remote access. The individual responsible for access revocations processed the work order and revoked remote access capabilities for the promoted employee and SERC_URE2 updated the list accordingly. SERC_URE2 failed to revoke access within seven days of personnel no longer requiring such access as required by CIP-004-3a R4.2. SERC_URE2 not only revoked the promoted employee’s remote access permissions, but also revoked the promoted employee’s additional access permissions, leaving the employee without the ability to access the system. However, SERC_URE2 did not process a work order to remove the additional access permissions and did not update the access list accordingly. Approximately nine weeks later, SERC_URE2 discovered this issue during an ad-hoc internal review, prior to the required quarterly review, and fixed the discrepancy by updating the list the same day. SERC_URE2 failed to update the access list within seven days of a change in access rights as required by CIP-004-3a R4.1. The root-cause of both issues was the individual responsible for managing access revocations failed to follow the proper processes. This issue lasted approximately nine weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue involved everyone that would require knowledge of the promoted employee’s status and access permissions, reducing the chance that the individual would retain access beyond required access. The employee remained with SERC_URE2 and had a current personnel risk assessment and the required cyber security training. The list discrepancy lasted 70 days, and the promoted employee had no access during that time. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-004-3a R4 compliance history in determining the disposition track. SERC determined that SERC_URE2's compliance history should not serve as a basis for applying a penalty. In the first issue, SERC_URE2 failed to update the access list for 51 days after the retirement of a customer’s employee. SERC_URE2 provided the individual read-only access and the customer failed to provide SERC_URE2 notification when the individual retired. The underlying conduct in this prior noncompliance is different from the instant issue. Further, SERC_URE2 completed mitigating activities almost three years prior to the instant issue. In the second issue, SERC_URE2 failed to revoke access to a single device upon a job transfer. Both prior occurrences were individual incidents involving a single individual and do not show a systemic issue occurring. | To mitigate this issue, SERC_URE2: 1) updated the system information repository to reflect the employee’s actual security status; 2) started using the CIP access management portal to manage job transitions and CIP role removals. For transitions and re-assignments, the responsible personnel enters a calendar date that determines when a role removal request will be generated. As this calendar date approaches, CIP access management portal will send out automated notifications to remind supervisors, information resource managers, and the CIP access management portal administrator to review the job transition and determine if an extension of access is needed; 3) created a document describing the purpose and functionality of the CIP access management portal, including step-by-step procedures on using CIP access management portal for role removals and transitions; 4) developed computer based training modules; 5) made the CIP access management portal training available; and 6) sent notification to personnel who were the primary target audience of the training.
2016-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015015395 | CIP-004-3a | R3; R3.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R3.2. Specifically, TRE_URE1 failed to perform a personnel risk assessment (PRA) reevaluation for an employee with physical and electronic access to Critical Cyber Assets (CCAs) within seven years of the initial personnel risk assessment. The PRA for a single TRE_URE1 employee expired while that employee continued to possess electronic and physical access to certain TRE_URE1 CCAs. Three days after the employee’s PRA expired, the employee in question returned to work from an extended leave of absence and entered a TRE_URE1 Physical Security Perimeter (PSP). Two days later, TRE_URE1 compliance personnel discovered during a review of annual training records that the employee had returned to work with an expired PRA. Upon discovering the issue, TRE_URE1 promptly revoked the employee’s physical and electronic access rights. The root cause of the issue was that TRE_URE1 did not possess adequate procedures for identifying expiring PRAs and correspondingly revoking access rights when appropriate. Specifically, the employee in question had previously been on an extended leave of absence and did not recognize that his PRA had expired prior to his returning to work. Texas RE determined the issue duration to be five days, from when the employee’s PRA expired until TRE_URE1 terminated the employee’s physical and cyber access rights. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The TRE_URE1 employee was a long-term employee who had previously held a valid PRA. Further, the employee only retained physical and electronic access rights for five days after his PRA expired. Following revoking his access rights, TRE_URE1 conducted a new PRA review and subsequently re-approved the employee’s electronic and physical access rights based on the new PRA’s successful completion. In addition, during the five-day period in which the single TRE_URE1 employee’s PRA had expired, the employee did not electronically access any CCAs. Moreover, although the employee did physically access a TRE_URE1 PSP, TRE_URE1 employs a layered defensive approach, including physical and electronic controls to protect and monitor CCAs within the PSP. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) immediately revoked the employee’s physical and electronic access to CCAs upon discovery; 2) performed a new PRA that was successfully completed shortly after the issue occurred; 3) conducted additional training on the TRE_URE1 access management system and process; 4) updated its access control program and access control procedures to clarify specific roles and responsibilities; and 5) modified its access management software to ensure electronic and physical access is automatically revoked seven days before expiration of a PRA. Texas RE has verified the completion of all mitigation activity.
2016-02-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015042 | CIP-007-3a | R2 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R2 because it did not ensure that all enabled ports required for normal operations were documented. MRO_URE1 utilized a system to track ports that are being utilized by Critical Cyber Assets (CCAs). During the implementation of the port-tracking system to create the baseline, MRO_URE1 manually entered the ports that would be active on its CCAs. To do so, MRO_URE1 relied upon the vendor's documentation to identify what ports were active. But, a vendor's documentation did not identify all ports that would be utilized. The vendor's documentation did not list four active ports and MRO_URE1 had used these four devices to support the vendors product. MRO_URE1 discovered this issued during its annual vulnerability assessment when it discovered four ports on four CCAs that were enabled that were not listed on the baseline. MRO_URE1 knew these ports were required to be active, and had previously documented these ports as being active in its previous the port-tracking system. The cause of this noncompliance was MRO_URE1's reliance upon a vendor's documentation in populating the active ports during the implementation of the port-tracking system. The instance of noncompliance began on the date Tripwire was implemented, and ended when MRO_URE1 updated the port-tracking system. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The noncompliance was limited to only four ports on four devices, and those ports were required for the normal operation of the devices. Further, MRO_URE1 knew that these ports were active and had previously documented these ports. Finally, the duration of the issue was brief, the issue was self-identified by MRO_URE1, and MRO_URE1 promptly mitigated and self-reported the issue once it was identified. This is MRO_URE1's first issue with CIP-007-3a R2. | To mitigate this issue, MRO_URE1: 1) contacted the vendor to determine why these four ports were not documented in the vendor's documentation resulting in the vendor updating its documentation to include these four ports; 2) updated the port-tracking system's Whitelist (baseline) to include the four ports; 3) setup a monthly review reminder of the Electronic Security Perimeter (ESP) Ports and Services document in AutoEDMS that will remind MRO_URE1 staff to check vendor documentation for any updated ports and services; and 4) setup an email alert for when ports and services test fail in the port-tracking system, this message will notfiy MRO_URE1 when there is any unauthorized port or service on a File System or Network Device. MRO_URE1 stated that mitigating activities were complete as of August 14, 2014.
2016-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015415 | CIP-004-3a | R4. | NPCC_URE1 had an issue of CIP-004-3a R4. During the quarterly review of physical access, NPCC_URE1 determined that a CIP Access Review was not conducted for an employee transferred from NPCC_URE1 Operations to NPCC_URE1’s Planning department. This resulted in the employee retaining access to control rooms. After discovery, the CIP access review for this employee was conducted, and it was determined that the employee does not require Control Room access in his new role. NPCC_URE1 revoked control room access a few months after. The cause of the violation was that Technical Security missed the e-mail notification of the transfer, which resulted in the access review not being conducted at the time of the transfer. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The transferred individual has remained a trusted NPCC_URE1 employee and still has a satisfactory Personnel Risk Assessment and Cyber Security Training. The employee also did not access or attempt to access a Control Room during the period in question. | To mitigate this issue, NPCC_URE1: 1) updated the employee’s access rights to reflect his new role. 2) improved workflow for managing employee transfers. Human Resources and Technical Security have an enhanced process for managing the CIP access review at the time of a transfer to supplement the current e-mail notifications, and transfers will not be finalized until after a CIP access review has been conducted.
2016-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015413 | CIP-007-3a | R6. | NPCC_URE1 had an issue of CIP-007-3a R6. Several NPCC_URE1 Critical Cyber Assets (CCAs) were not fully configured to log centrally to the NPCC_URE1’s Security Information and Event Management (SIEM) system when they were put in production. Almost all access to the CCAs in scope for this issue was logged to the SIEM. However, a few local user accounts, which are infrequently utilized were not logging properly. Activity occurring on the local accounts was logged; however, the logs were not sent to the NPCC_URE1’s SIEM and therefore, no active monitoring and alerting of access through these accounts was available. With respect to the cause, during the on-boarding process for new Cyber Assets, the Cyber Asset must be configured to send security event logs to the SIEM, and the SIEM must be configured to accept those logs. In this case, the Cyber Assets were configured to send logs to the SIEM, but the SIEM was not configured to accept the logs. Thus, the SIEM did not receive the logs for several months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Most access to the CCAs in question was logged through NPCC_URE1’s SIEM; this issue only affected a small number of local accounts. The systems are highly protected via physical and electronic security controls which meet CIP requirements. Bulk Power System reliability does not depend on the functionality of the affected devices – They are used for the markets only. The passwords for the local accounts are also highly protected using a password safe. A compromised enclosure would not provide interactive access to the servers. The affected servers are logged for availability through NPCC_URE1’s SIEM. An interruption in availability of these devices would have been detected in real time. In order to access the account, a user must either be within the PSP and directly access it or by obtaining access to the ESP and then additionally, authenticate to the device. The account's password is not a default password. | To mitigate this issue, NPCC_URE1: 1) fully configured the SIEM to accept the logs being forwarded from the Cyber Assets listed herein. The local logs were reviewed for the period in which the logging issue arose; no unusual activity was detected. 2) developed a process for periodically checking on an ongoing basis that all applicable CIP Cyber Assets are logging to the SIEM. 3) developed enhanced procedures to ensure tracking and timely mitigation of potential compliance issues.
2016-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015015353 | CIP-002-3 | R4. | NPCC_URE2 had an issue of CIP-002-3 R4. During their review of compliance documentation, NPCC_URE2 discovered they did not annually approve their risk based assessment methodology (RBAM), the list of Critical Assets (CAs), and the list of Critical Cyber Assets (CCAs). The root cause was failing to properly document the Senior Manager upon original designation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE2 had a documented RBAM and a null CA and CCA list for the prior years. | To mitigate this issue, NPCC_URE2: 1) approved the impact assessment methodology and list of CAs and CCAs 2) formalized a procedure for documenting an impact assessment methodology to use to identify NPCC_URE2's CA and CCAs. This procedure will be reviewed annually by NPCC_URE2's management.
2016-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015015339 | CIP-003-3 | R2. | NPCC_URE2 had an issue of CIP-003-3 R2. NPCC_URE2 did not document a senior manager with overall responsibility and authority for implementation of the CIP standards. The root cause was failing to properly document the Senior Manager upon original designation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE2 had a senior manager with overall responsibility and authority for implementation of the CIP standards but failed to document the individual. NPCC_URE2 does not have Critical Assets or Critical Cyber Assets. | To mitigate this issue, NPCC_URE2: 1) appointed and documented a senior manager 2) implemented a procedure requiring annual review of the senior manager designation. NPCC_URE2 management is also aware of the requirement to document any changes to the CIP Senior Manager within 30 days of the effective date.
2016-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015015337 | CIP-007-3a | R6. | NPCC_URE3 had an issue of CIP-007-3a R6. During a check, NPCC_URE3 discovered that it could not locate documentation associated with a review of logs for security events several cyber assets. During the investigation, the former managers with the responsibility for documenting the review were contacted and provided attestations that they reviewed the logs per their policy. However these managers could not direct NPCC_URE3 to the location of the sign-off sheet. NPCC_URE3 believes the sign-off sheet was maintained on the laptop computers, which were erased when the managers left employment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Real time alerting and monitoring was still enabled. All real time logs are reviewed, however, the documentation for reviewing all logs was not documented. The logs associated with the Critical Cyber Assets, Physical Access Control Systems, and those Cyber Assets within an Electronic Security perimeter reviewed by others than IT were reviewed and documentation is on-hand. Real time alerts were configured to be issued for three failed login attempts in a time period, certain firewall events, detected malicious code (AV), and failure of the log server to generate a daily report. In addition the AV report was generated by a separate server and being reviewed. These alerts would be responded to in real-time when received. Therefore, cyber assets essential to the operation of the Bulk electric System were being monitored and if a security event alert occurred then it would be captured and reviewed by a subject matter expert. | To mitigate this issue, NPCC_URE3: 1) completed reviews of logs 2) prevent future occurrences by using an electronic spreadsheet stored on their network system to prevent documentation from being lost
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015015096 | CIP-006-3c | R1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. During a phone upgrade, the authorized escort for two visitors left the two visitors unescorted inside of a Physical Security Perimeter (PSP) for approximately seven and a half minutes. The escort and the visitors were inside of a LAN room and RFC_URE1 treats the entire LAN room, where the visitors were left unescorted, as a PSP. The noncompliance was identified by another RFC_URE1 employee who noticed that the authorized escort had left visitors unescorted inside of the PSP and that RFC_URE1 employee immediately notified the authorized escort of the issue. This noncompliance concerns the management practice of workforce management because RFC_URE1 did not effectively train its escort on escorting procedures for visitors inside a PSP. The root cause is ineffective training. The duration of this noncompliance is approximately seven and a half minutes, from the date and time the authorized escort left the two visitors unescorted inside of a RFC_URE1 PSP to the time the authorized escort rejoined the visitors inside the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The visitors that were left unescorted within the PSP had no access to any Critical Cyber Assets (CCAs) at any time because the CCAs in that PSP were secured in a locked cabinet during the entire time the visitors were within the PSP. The Energy Management System (EMS) system located within the PSP is inside of a locked cabinet. The visitors did not attempt to and did not access any CCAs while in the PSP. Additionally, the visitors were only left unescorted within the PSP for a short amount of time: seven and a half minutes. The second RFC_URE1 employee’s quick awareness that the visitors were improperly left unescorted is the type of security awareness that ReliabilityFirst hopes all of its entities display. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) retrained the escort on visitor program and escorting requirements; 2) distributed to all relevant personnel and all support personnel on the floor where the issue occurred, awareness training outlining physical security, visitor program, and escorting requirements for personnel with authorized unescorted access to the PSP; and 3) distributed to all personnel with authorized unescorted access to the PSP, awareness training outlining physical security, visitor program, and escorting requirements.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014799 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. RFC_URE2 discovered it had potential compliance issues related to the quarterly access reviews of the list of personnel who have unescorted physical access to the Physical Security Perimeter (PSP) at one of their facilities. RFC_URE2 performs these quarterly access reviews to satisfy CIP-004-3a R4.1. Specifically, RFC_URE2 failed to perform its first and second quarterly access reviews for unescorted physical access to the PSP at that facility. RFC_URE2 failed to perform these two quarterly access reviews because the personnel responsible for performing these reviews were reassigned to a different department and the responsibility to perform the reviews was not effectively reassigned to new personnel. RFC_URE2 logged approximately 1,337 individual permission changes, access grants and revocations, for approximately 579 active users at the facility. RFC_URE2 granted electronic access to individuals at a level different than was authorized or to individuals without authorization and proper access credentials 21 times. RFC_URE2 also discovered two instances where access provisions or accounts for individuals were not wholly removed within 7 days after an individual no longer required access. The PSP at the facility was decommissioned. This noncompliance concerns the management practices of workforce management and verification. The root cause of missing the quarterly access reviews was lack of project ownership after the personnel responsible for performing the quarterly access reviews for the PSP at the facility were reassigned to a different department. Workforce management is implicated because no one at RFC_URE2 took steps to ensure that the task of performing the quarterly access reviews was effectively reassigned after the personnel previously responsible were reassigned to a different department. The root cause of the access issues was uncorrected human errors made during the granting and revoking of electronic access to Critical Cyber Assets (CCAs). Verification is implicated because RFC_URE2 did not have effective policies and procedures in place to verify that individuals were granted the proper level of electronic access. The duration of this noncompliance is from the first day that a quarterly access review was not timely performed for the calendar year, to the date RFC_URE2 finished correcting each instance of unauthorized electronic access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All personnel implicated in both issues had valid prior personnel risk assessments, current training, and were trusted employees that have been with RFC_URE2 for at least five years. Additionally, the personnel involved all were supposed to have some form of electronic access, the noncompliance arises from certain personnel having access at a higher level than was authorized, personnel receiving access without the proper access credentials, and two individual’s access not being wholly removed within 7 days after the individual no longer required access. The facility is contained within a larger substation complex surrounded by a physical boundary with access controls. Lastly, through a robust network of monitoring and detective controls, RFC_URE2 would be able to immediately detect any malicious actions on the Bulk Electric System taken by the individuals with unauthorized electronic access. No inappropriate activity was identified during the course of the noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE2 will complete the following mitigation activities: 1) confirm Physical Access Reviews for each PSP are assigned to a group or multiple individuals and will reinforce task responsibilities for performing physical access reviews. RFC_URE2 did not re-perform the first and second quarterly access reviews for the facility because that facility was decommissioned; 2) document, report, and provide feedback to performers on issues identified during the 1st and 2nd Quarter quality peer check process; 3) document, report, and provide feedback to performers on issues identified during the 3rd Quarter quality peer check process' 4) document, report, and provide feedback to performers on issues identified during the 4th Quarter quality peer check process; 5) develop a procedure, as part of RFC_URE2's CIP V5 access control program, to ensure an associated access authorizer review group will be created for each authorized access list (physical access and electronic access); 6) ensure authorized access lists in scope of RFC_URE2’s CIP V5 program have been documented and aligned to an access authorizer review group during user acceptance testing; 7) implement a centralized access control program and map automated aspects to manual aspects under the prior program; 8) document and report issues identified during the 2nd Quarter quality peer check process, including assessment of the improvements in access provisioning experienced through the new centralized tool.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015014939 | CIP-003-3 | R6 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. RFC_URE3 did not follow its change control or configuration management procedures in accordance with CIP-003-3 R6 during an emergency replacement of two terminal servers. RFC_URE3 did not follow proper change control and configuration management procedures when replacing two failed terminal servers. The terminal server replacements were deemed emergencies and expedited to ensure the reliability of communications, control, and monitoring to Remote Terminal Units (RTUs). RFC_URE3 did not discover that it did not perform security controls’ testing under CIP-007-3 R1 and did not apply the configuration to detect and alert upon attempts of unauthorized access per CIP-005-3a R3 on the emergency replacement of these two terminal servers until it performed an internal compliance review. This noncompliance concerns the management practices of verification and workforce management. Verification is implicated because the terminal servers were allowed to be installed without verifying that the servers had been installed properly. An IT analyst did not understand how to replace the two terminal servers while following RFC_URE3’s change control and configuration management processes and procedures. Workforce management is implicated because the IT analyst was not properly trained on how to install the terminal servers in compliance with CIP-003-3 R6. The root cause was ineffective training. The duration of this noncompliance is from the date RFC_URE3 replaced the two terminal servers without following proper change control and configuration management, to the date RFC_URE3 executed the required change control ticket that documented the replacement of the two terminal servers, the baseline configuration of the terminal servers, the security controls testing of the terminal servers, and the configuration of security event monitoring. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance only implicated two of RFC_URE3’s terminal servers. When the two terminal servers at issue were installed, RFC_URE3 changed the default passwords on the terminal servers and RFC_URE3 had monitoring controls in place to alert the appropriate CIP asset owners when multiple failed logon attempts are made on NERC CIP assets such as the two terminal servers. Additionally, for an unauthorized intruder to have exploited the terminal servers, the intruder would have needed to infiltrate several layers of firewalls and pass 2-factor authentication to reach the segregated and isolated Electronic Security Perimeter, or obtain unescorted physical access to a protected Physical Security Perimeter before the intruder could gain access to the devices at issue. Lastly, during the period of noncompliance, there were no unauthorized access attempts on any of the terminal servers on RFC_URE3’s system. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) conducted an operational stand down that briefed the team about the compliance impact of the lack of change control for the emergency replacement of a device in the Emergency Management Systems (EMS) environment; 2) verified the terminal servers in production against the Master Asset List information and verified the logging configuration for each of them; 3) distributed guidance on change control to the RFC_URE3 EMS staff; 4) conducted two meetings to share lessons learned with appropriate personnel; 5) conducted change control training and reviewed production change control procedures; and 6) developed a job aid that connects the RFC_URE3 procedures to the NERC CIP Version 3 Standards and distributed the job aid to RFC_URE3 EMS staff.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015260 | CIP-005-3a | R1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-005-3a R1. RFC_URE3 identified a group of devices that perform access control and monitoring to three access points on RFC_URE3’s Electronic Security Perimeters (ESPs) that are not properly classified as Electronic Access Control and Monitoring Systems (EACMS). Although protected by a number of physical and electronic security access and monitoring controls, the devices have not been afforded all of the protective measures due EACMS under CIP-005-3a R1.5. During an internal review of the configuration of the connections between RFC_URE3’s Primary and Backup Energy Management System (PEMS and BEMS), which are located within ESPs, and RFC_URE3’s environments, which are located outside of ESPs, RFC_URE3 discovered that the EACMS were unclassified. While outside the ESPs, the environments are secured within two Physical Security Perimeters (PSPs) and are subject to a number of physical and electronic access controls. The devices that should have been classified as EACMS are domain controllers and servers that are authenticating access for a limited number of workstations located within the two PSPs. The domain controller and severs are located outside of the ESPs. The domain controllers and serves at issue provide a layer of access control and monitoring and are protected by other redundant physical and electronic access controls. This noncompliance concerned the management practice of asset and configuration management because RFC_URE3 employees did not have a complete understanding of the makeup of its Emergency Management Systems design and the devices within that system. Asset and configuration management is implicated because RFC_URE3 did not maintain an accurate list of all of its EACMS devices. RFC_URE3 did not identify the domain controllers and servers as EACMS devices. The root cause was poor asset management. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-005-3a R1, to the date RFC_URE3 brought all devices at issue into full compliance with CIP-005-3a R1.5 by reclassifying the devices as EACMS and providing the devices with all appropriate protections. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 maintained a strong process for verifying and updating the anti-virus and the malware prevention signatures in place for these devices. Due to the security configuration and controls in place for these devices, there was a minimal threat from remote user access as the environments are segregated by local controls from the RFC_URE3 Data Network and sit behind multiple layers of segmented networks that are separated by firewalls. In order for a user to access the environments remotely, they must pass through multiple layers of security including obtaining an authorized and encrypted VPN connection and two-factor authentication. For a potential insider threat, RFC_URE3 has strong physical and electronic security controls in place including housing the devices within PSPs which require a valid Personnel Risk Assessment (PRA) to gain authorized unescorted access to the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 will complete the following mitigation activities: 1) RFC_URE3 committed to close the logging and monitoring gaps for the devices at issue in order to demonstrate full compliance with CIP-005-3a R1.5; 2) RFC_URE3 committed to create a job aid to document the process of the joint daily communication meetings that occur with RFC_URE3’s Operations and IT teams for EMS system changes; 3) RFC_URE3 committed to conduct a comprehensive internal review for CIP-005-3a R1.5 controls to ensure there are no other devices associated with RFC_URE3’s ESPs that need to be reclassified as EACMS; and 4) RFC_URE3 committed to conduct a quality assurance review to confirm that all CIP-005-3a R1.5 gaps have been mitigated.
2016-02-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014855 | CIP-004-3a | R4. (R4.1., R4.2.) | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4.1 and R4.2. SERC_URE1 failed to maintain its list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). During a quarterly access list review, SERC_URE1 discovered two instances where the access list was not updated within seven days of a change in employment status. Both employees voluntarily left the company, and on the date of their release, the responsible manager collected the access badges from each employee, eliminating their ability to gain access to any SERC_URE1 site, and specifically the CIP protected Physical Security Perimeters (PSPs). For one employee, SERC_URE1 failed to update the access list for 37 days after the individual should have been removed. For the second employee, SERC_URE1 failed to update the access list for 38 days after the individual should have been removed. In these two instances, the manager failed to properly follow the established SERC_URE1 procedure and follow through in getting the list update made. SERC_URE1 cited lack of manager training as the root cause of these two instances. During an extent of condition review, SERC_URE1 also found three employees that did not have their physical access to CCAs properly revoked within seven days of a role change. The two managers for the three involved employees failed to follow the established SERC_URE1 procedure for access list maintenance and review and properly complete the required internal paperwork to revoke access and update the access list to PSPs. SERC_URE1 determined that access for one of the employees was no longer required but SERC_URE1 failed to update the list for approximately seven months. SERC_URE1 determined that access for the other two employees was no longer required but SERC_URE1 failed to update the list for approximately eight and nine months, respectively. SERC_URE1 cited the root-cause of these three instances as a failure to properly follow the internal SERC_URE1 procedures. The manager of the first employee failed to properly complete a change form and check the box to indicate physical access to the CCAs should be revoked. The manager of the remaining two employees failed to follow the established procedure in the correct sequence, preventing the revocation of access and the necessary list updates from occurring. No logical or remote access to the CCAs was held by any of the involved employees. SERC_URE1 identified this condition internally, through its condition reporting process. This issue lasted from seven days after the first instance where SERC_URE1 failed to properly revoke access and update its access list until 10 months later when SERC_URE1 revoked access and updated the access list for the last employee. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to revoke three of the five employee’s access to CCAs, and update the access list, once access was no longer required could permit employees to mistakenly or through malicious intent access and modify or corrupt CCAs and potentially impact the energy management system or the BPS. Further, SERC_URE1’s failure to maintain an updated access list would hinder its ability to know who had actual access to CCAs and impact its ability to correct for employment changes if they arise. However, all employees involved in this issue were in good standing with SERC_URE1. All involved employees had received proper training and background checks, and were authorized for unescorted physical access to CCAs. All five issues revolved around physical access to CCAs, and did not involve remote or cyber access to CCAs. For two of the five instances at issue, the badge that permitted access was collected at the time of the employee’s release, eliminating these employees ability to return and gain access. Finally, none of the employees involved used or attempted to use their access permissions after the access was deemed no longer required. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined there were no relevant instances of noncompliance. SERC considered an affiliate's CIP-004 R4 compliance history in determining the disposition track. The original issue and the subsequent Mitigation efforts were distinctly different, and as such, this older issue was not considered as an aggravating factor for the current issue. | To mitigate this issue, SERC_URE1: 1) completed access revocation and list update for all incidents included in the self report; 2) performed an extent of condition review to identify and correct any additional incidences for which this condition exists; 3) provided targeted coaching to affected managers to mitigate potential reoccurrence; 4) reviewed the transmission procedure addressing personnel change/transfers and identified and initiated revisions necessary to prevent recurrence; 5) developed lessons learned document and share with applicable managers and supervisors who have personnel with CCA access; 6) reviewed its personnel change policy, and Personnel Change Checklist form and identified and implemented revisions necessary to prevent recurrence; 7) developed CCA Access Revocation Computer Based Training to specifically address aspects of access revocation related to this violation, including identification of training audience and assignment of training; and 8) evaluated the process to assign CCA access revocation training to a manager at the time of initial request for CCA access.
2016-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014280 | CIP-004-3 | R4; R4.1, R4.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had three instances of noncompliance with CIP-004-3a R4.1 and one instance of noncompliance with CIP-004-3a R4.2. CIP-004-R4.1 Instance Number One: SPPRE_URE1 did not conduct quarterly reviews of its list of personnel with electronic access to Critical Cyber Assets from for three years. The duration of this instance of noncompliance was approximately 43 months. The root cause of this instance of noncompliance was a combination of human error due to personnel not following SPPRE_URE1’s access management program and lack of effective user access management controls for ensuring that quarterly reviews were conducted. CIP-004-R4.1 Instance Number Two: An SPPRE_URE1 employee was granted electronic access to an additional workstation console; however the Critical Cyber Asset access list was not updated until ten (10) days after the access was granted. The duration of this instance of noncompliance was approximately two (2) days. The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s procedure for updating the Critical Cyber Asset access list. CIP-004-R4.1 Instance Number Three: An SPPRE_URE1 employee voluntarily terminated his employment with SPPRE_URE1; however, the Critical Cyber Asset access list was not updated until seventeen (17) months after the voluntary termination. The duration of this instance of noncompliance was approximately seventeen (17) months. The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s procedure for updating the Critical Cyber Asset access list. CIP-004-R4.2 Instance Number Four: An SPPRE_URE1 employee voluntarily terminated his employment with SPPRE_URE1. On that same date, SPPRE_URE1 collected the former employee’s badge and revoked his physical access rights to Critical Cyber Assets. Although SPPRE_URE1 attested that it also revoked the former employee’s electronic access to such assets, SPPRE_URE1 was unable to provide evidence of the revocation. The duration of this instance of noncompliance was approximately seventeen months The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s access management program for revoking electronic access rights. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-004 R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for personnel who should no longer have access to Critical Cyber Assets, with potential access to Critical Cyber Assets. Regarding Instance Number Two, the employee had existing electronic access rights to other Critical Cyber Assets. SPPRE_URE1 properly approved the employee’s electronic access rights to the additional workstation console, and the update to the electronic access list to reflect the change in such access rights was untimely by only two days. The instance of noncompliance was merely a documentation error. Regarding Instances Number Three and Four, the former employee voluntarily terminated his employment with SPPRE_URE1. On the same date of his termination, SPPRE_URE1 collected his badge and revoked his physical access to all Critical Cyber Assets. Therefore, the former employee was incapable of gaining physical access to Critical Cyber Assets inside the badge restricted areas. At the time of his termination, the former employee did not have any electronic access capabilities, remote or otherwise, to access Critical Cyber Assets from outside SPPRE_URE1’s badge restricted areas. The instance of noncompliance was merely a documentation error. Regarding Instance Number One, once mitigated, the Critical Cyber Asset access list remained unchanged except for the removal of the former employee’s electronic access rights. For all instances of noncompliance, no actual harm occurred. | To mitigate these instances of noncompliance, SPPRE_URE1: 1) reviewed its Critical Cyber Asset list, updated the list, and added future reviews of the list to its CIP Compliance Calendar (Instances Numbers 1-4); and 2) implemented a new document management system to help ensure that all needed evidence to show compliance with CIP-004 will be maintained (Instances Numbers 1-4). SPP RE has verified the completion of all mitigation activity.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014692 | CIP-005-3a | R2 | WECC_URE1 submitted a Self-Certification stating that it had an issue of CIP-005-3a R2. Specifically, during a third-party review of WECC_URE1’s compliance with CIP-005-3a, WECC_URE1 discovered that certain individuals in WECC_URE1’s electric Distribution Dispatch department may have external interactive cyber access (EIA) to WECC_URE1’s Electronic Security Perimeter (ESP). WECC_URE1 determined there were multiple individuals with the described EIA. Additionally, WECC_URE1 determined that each of these individual’s work stations did not have two-factor authentication. Therefore the work stations did not have the required strong procedural or technical controls at the access points, as required by CIP-005-3a R2.4. WECC SMEs reviewed the Self-Certification documentation and conducted interviews with WECC_URE1 compliance staff. The SME confirmed that WECC_URE1 failed to implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party for individuals where external interactive access into the ESP had been enabled. WECC determined that WECC_URE1 failed to implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party for individuals where external interactive access into the ESP had been enabled. Enforcement also determined that the compliance exception started when the employees in WECC_URE1’s Distribution Dispatch department received access to the SCADA system, impacting only non-bulk power system (BPS) assets on WECC_URE1’s distribution system. The cause of the issue was overlooking the external interactive cyber access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Failing to implement and maintain strong procedural or technical controls at the access points to ensure authenticity of the accessing party, could allow for unauthorized access to the ESP. In this case, WECC_URE1 personnel from inside the company had external interactive access. This access could not be used to send commands to BPS assets. Only non-BPS assets could be affected by this access from WECC_URE1 personnel. As a compensating measure, WECC_URE1 implemented a defense-in-depth architecture of physical and logical Cyber Security controls, including physical security mechanisms with guards, special locks, CCTV, and logical perimeter. WECC_URE1 also implemented internal Cyber Security controls, including firewalls, vulnerability scanning tools, Intrusion Detection Systems and a Security Incident and Events Management (SIEM) system. WECC_URE1 implemented preventative and detective controls by training the staff in the Control Centers to monitor the activities of employees entering the Control Center, including the individuals who had access to the Physical Security Perimeters (PSPs). WECC_URE1 had appropriate protections in place for employees entering and exiting the PSPs, and the majority of these individuals’ functions were limited. WECC_URE1 also implemented compensating controls by limiting the access of these employees to read-only with the distribution dispatchers also having permission to close line-breaks. Training staff on monitoring the systems should also detect and correct any malicious activity. | To mitigate this issue, WECC_URE1: 1) built and deployed Intermediate Systems that will be EACM assets; 2) tested the proof of concept for the secondary authentication factor; 3) updated the security controls procedures to include the dual-factor requirement for EIA assets; and 4) trained users and IT staff on the additional EIA requirements. To mitigate this issue, WECC_URE1 will completed the following mitigating activities: 1) will deploy dual factor authentication on all EIA assets.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014879 | CIP-007-3a | R5; R5.2.3 | WECC_URE2 submitted a Self-Certification stating that it had an issue of CIP-007-3a R5. WECC_URE2 failed to maintain an audit trail of shared account use for multiple devices. A WECC SME reviewed the Self-Report/Self-Certification and discussed the possible noncompliance with WECC_URE2. The SME determined that for WECC_URE2’s shared accounts, it was maintaining an audit trail of which account was being used, on which device the account was being used, and at what time the account was used, but failued to include who was using the account each time. WECC determined that WECC_URE2’s failure to have a policy for managing the use of shared accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes is a noncompliance of CIP-007-3a R5.2.3. WECC determined that this compliance exception began when it was required to demonstrate compliance with the Standard and was completed when the mitigating activities were completed. Under CIP V5, the Standards will no longer require entities to maintain audit trails of any kind for accounts, and this Requirement will no longer be included in the CIP Standards. WECC considered that this Standard will no longer be required in CIP V5 in the designation of this issue for compliance exception treatment. Additionally, WECC_URE2 submitted a Self-Report citing possible noncompliance with CIP-007-3a R5, which was given Violation ID# WECC2015014613. WECC_URE2 then identified the identical possible noncompliance in its annual Self-Certification, given Violation ID# WECC2015014879. Because Violation ID# WECC2015014613 was submitted during the Self-Certification period, and because it was duplicative of Violation ID# WECC2015014879, WECC dismissed Violation ID# WECC2015014613. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to maintain an audit trail of shared account use for multiple devices. These devices are located at multiple facilities and are located within the Electronic Security Perimeter (ESP) for the SCADA system. Failing to have an accurate audit trail of shared account use could allow undetected unauthorized use of the shared accounts. If a malicious individual were able to gain access to WECC_URE2’s network through shared accounts, that individual could potentially discover vulnerability on the SCADA network and launch a malware attack to capture user credentials. Such credentials could then be used to log on to any one of the devices in scope, which control WECC_URE2's transmission lines. These devices could then be used to trip or otherwise affect load. However, WECC_URE2 implemented preventive and detective controls. As a preventive control, WECC_URE2 ensures only those ports and services necessary for operations are enabled, thereby limiting traffic into WECC_URE2’s network. Also, WECC_URE2 uses antivirus and other anti-malware software that looks for known attack signatures to prevent malware attacks. As a detective control, WECC_URE2 continuously monitors devices on the SCADA network, which would detect and alert attempts to change device configurations, which would alert WECC_URE2 to unauthorized network access. For these reasons, WECC determined this compliance exception poses minimal risk to the reliability of the BES. | To mitigate this issue, WECC_URE2 began transitioning to CIP version 5. WECC determined that WECC_URE2 was not required to submit a formal mitigation plan to address this compliance exception because WECC_URE2 is transitioning to CIP V5, and because this Reliability Standard Requirement is no longer required in CIP V5.
2016-01-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015274 | CIP-007-3a | R8. | NPCC_URE1 did not fully complete a Cyber Vulnerability Assessment (CVA). NPCC_URE1 began the ports and services assessment and review of controls for default accounts but did not finish until the following year. Final documentation of the action plan was completed the year after. NPCC_URE1 completed their prior year's CVA. The primary cause of the potential violation is that substantial IT infrastructure work was being completed during the year to support NPCC_URE1’s move to its new control center. Many assets on the Critical Cyber Assets (CCA) List were being replaced. This resulted in a decision to delay scanning until the environment became more stable. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Scanning prematurely would have resulted in many assets being scanned just before their retirement and many new assets not being scanned for the CVA. NPCC_URE1's "defense in depth" network architecture and cyber security program are designed to mitigate potential security risks. Efforts taken to harden CIP assets prior to deployment through the NPCC_URE1's controlled Request for Change Process consistently result in a low number of issues found for ports and services during these assessments. No harm is known to have occurred. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NPCC_URE1: 1) completed their CVA NPCC has verified the completion of all mitigation activities.
2016-01-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015275 | CIP-005-3a | R4. | NPCC_URE1 did not fully complete a Cyber Vulnerability Assessment (CVA). The NPCC_URE1 performed all scans and firewall rule reviews but did not perform an analysis of those scan results until the following year. NPCC_URE1 did not perform a review to verify that only ports and services required for operations at access points are enabled and a review of controls for default accounts, passwords, and network management community strings. The primary cause of the potential violation is that substantial IT infrastructure work was being completed to support NPCC_URE1’s move to its new control center. Many assets on the Critical Cyber Asset (CCA) List were being replaced. This resulted in a decision to delay scanning until the environment became more stable. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Scanning prematurely would have resulted in many assets being scanned just before their retirement and many new assets not being scanned for the CVA. NPCC_URE1's "defense in depth" network architecture and cyber security program are designed to mitigate potential security risks. Efforts taken to harden CIP assets prior to deployment through the NPCC_URE1's controlled Request for Change Process consistently result in a low number of issues found for ports and services during these assessments. No harm is known to have occurred. They had firewalls in place and there were no security incidents detected. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NPCC_URE1: 1) completed their CVA NPCC has verified the completion of all mitigation activities.
2016-01-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015015371 | CIP-004-3a | R4. | An employee with authorized cyber and authorized unescorted physical access transferred departments. The employee no longer required such access to critical cyber assets in their new role. The employee's cyber and physical access rights to critical cyber assets were revoked several days after the effective date of the transfer. The automatic physical and cyber access revocation process was delayed due to the delayed employee transfer processing by the Services Delivery Center. Managers and Supervisors are also expected to call the Security Control Center to ensure timely access revocation, but in this instance, the Control Room did not remember to call the Security Control Center. This late access revocation incident was discovered during a review of the automatic access revocation log file. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of access records confirmed that the employee did not access any critical cyber assets during the period at issue. The employee had up-to-date CIP training and a Personnel Risk Assessment . The employee is a long standing employee continues to work for NPCC_URE2 in another department. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) revoked the employee's cyber and physical access rights to critical cyber assets; 2) provided a targeted communication to all access approvers and access requestors regarding the NERC CIP access revocation process; 3) issued a communication to all employees regarding the NERC CIP access revocation process; and 4) provided awareness training on the process for handling changes to job transfer paperwork. NPCC has verified the completion of all mitigation activites
2016-01-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014288 | CIP-007-3a | R2; R2.1, R2.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had minimal risk instances of noncompliance with CIP-007-3a R2.1 and R2.2. Although SPPRE_URE1 had a documented ports and services process in place, a small number of ports and services associated with Cyber Assets located within SPPRE_URE1’s Electronic Security Perimeter (ESP) had been enabled but were not included in SPPRE_URE1’s documented ports and services baseline. Additionally, two services associated with SPPRE_URE1’s production development server (PDS) had been enabled but not included on the ports and services baseline. Furthermore, a port range for an individual service associated with the PDS had not been clearly defined within the baseline. Thus, SPPRE_URE1 was unable to ensure that only those ports and services required for normal and emergency operations associated with the four network switches and PDS had been enabled per CIP-007-3a R2.1. Because the enabled ports and services identified in R2.1 were not included in SPPRE_URE1’s documented ports and services baseline, SPPRE_URE1 was unable to ensure that other ports and services, including those used for testing purposes, had been disabled prior to production of the four network switches and PDS inside the ESP per R2.2. The duration of these instances of noncompliance was approximately 42 months. The root cause of this instance of noncompliance was a lack of internal controls to ensure full adherence to CIP-007-3a R2, specifically, a lack of comprehensive change control and security testing procedures for the review of pre and post changes to ensure that all open ports and services required for normal and emergency operations is included in its documented ports and services baseline. | These issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-3 R2 has the potential to affect the reliable operation of the BPS by providing the opportunity for infiltration of unauthorized network traffic into the ESP through ports and services that are not necessary for normal or emergency operations, but nevertheless remain enabled. Nonetheless, all enabled ports and services associated with noncompliance are required for normal and emergency operations. Thus, actual harm neither occurred nor could have occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) developed and implemented enhanced change control and security testing measures, which requires reviews of pre and post changes to applicable devices to verify that security controls testing and baseline maintenance has occurred; and 2) conducted a ports and services baseline review and documentation, which includes all enabled ports and services required for normal or emergency operations. SPP RE has verified the completion of all mitigation activity.
2016-01-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014187 | CIP-003-3 | R5 | SPPRE_URE1 submitted a Self-Report stating that it had three minimal risk instances of noncompliance with CIP-003-3 R5 because the authorization process of SPPRE_URE1’s documented and implemented Access Control Procedure for Critical Cyber Asset Information (CCAI) was not followed when SPPRE_URE1 and vendor personnel were granted access to CCAI. CIP-003-3 R5 – Instance Number One SPPRE_URE1 did not adhere to the approval process of its Access Control Procedure for Critical Cyber Asset Information (CCAI) when it granted three SCADA/EMS vendor personnel administrative rights and VPN access to make programming changes to SPPRE_URE1’s SharePoint application, which is used to store CCAI. The duration of this instance of noncompliance lasted approximately five (5) months. The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s Access Control Procedure when granting access to CCAI. CIP-003-3 R5 – Instance Number Two SPPRE_URE1 maintains folders on a drive that contain CCAI. Access to these folders is limited to personnel with a business need for such protected information based on their roles and responsibilities. During the duration of this instance of noncompliance, SPPRE_URE1 employed approximately 240 personnel. Approximately 95 SPPRE_URE1 personnel had a business need for the folders containing CCAI and had proper access to such information. For approximately ten (10) months, without the request of SPPRE_URE1, SPPRE_URE1's Parent Organization's Technology Services Department granted all remaining SPPRE_URE1 personnel (approximately 145) electronic access to the folders containing CCAI. This authorization of access to CCAI did not adhere to SPPRE_URE1’s Access Control Procedure for CCAI. The duration of this instance of noncompliance was for approximately ten (10) months. The root cause of this instance of noncompliance was lack of effective workforce management resulting in lack of training for personnel in the Parent Organization's Technology Services Department to ensure they understand that the authorization process of granting access to SPPRE_URE1 CCAI must be completed solely by SPPRE_URE1. CIP-003-3 R5 – Instance Number Three SPPRE_URE1 did not adhere to the approval process of its Access Control Procedure for CCAI when it granted six personnel electronic access to CCAI, which was needed for their roles and responsibilities. The duration of this instance of noncompliance was for approximately eleven (11) months. The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s Access Control Procedure for CCAI. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-003 R5 has the potential risk to affect the reliable operation of the BPS by permitting unauthorized access to CCAI, thus allowing potential compromise of confidential information. Regarding the first and third instances of noncompliance, all individuals had a business need for access to the folders, which contained the CCAI. SPPRE_URE1 hired the three SCADA/EMS vender personnel to make programming changes to SPPRE_URE1’s SharePoint application where the CCAI is stored. The six SPPRE_URE1 personnel were given access because of their roles and responsibilities of their job. All individuals ultimately were properly granted access to the protected information. Regarding the second instance of noncompliance, not only were the approximate 145 personnel unaware of gaining access to CCAI, none of them were capable of accessing such information because they had not been assigned SPPRE_URE1 computers due to their job duties as linemen and plant personnel. Notwithstanding, SPPRE_URE1 detected the instances of noncompliance during its annual CCAI access review, and timely reported them to SPP RE. No actual harm occurred as a result of these instances of noncompliance. | To mitigate these instances of noncompliance, SPPRE_URE1: 1) after a review of business needs, approved/revoked access rights of SPPRE_URE1 and SCADA/EMS vendor personnel in accordance with its Access Control Procedures (Instances Number One and Three); 2) revoked access rights of SPPRE_URE1 personnel who do not have a business need for CCAI that were improperly granted access to such information (Instance Number One); and 3) retrained all affected personnel to ensure they understand their roles and responsibilities for compliance with CIP-003 (Instances One, Two, and Three). SPP RE has verified the completion of all mitigation activity.
2016-01-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015015250 | CIP-004-3a | R4; R4.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4.2. Specifically, TRE_URE1 failed to revoke physical access within 7 calendar days for a single employee who no longer required access to Critical Cyber Assets (CCAs). The employee in question transitioned from Family and Medical Leave Act (FMLA) status to Long Term Disability (LTD). TRE_URE1 considers a FMLA-related absence to be temporary, such that access to CCAs may still be required. In contrast, TRE_URE1 considers employees on LTD to be inactive and accordingly to no longer require access to CCAs. As such, TRE_URE1 should have revoked the single employee’s access to CCAs within 7 days of that employee’s transition to LTD but did not do so. The root cause of the issue was that the TRE_URE1 Human Resources department did not properly differentiate between absences due to FMLA and LTD. Therefore, TRE_URE1 did not provide the appropriate notifications to revoke the employee’s access to CCAs once the individual transitioned to LTD. Texas RE determined the issue duration to be for approximately 45 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, TRE_URE1 uses a layered cyber defense approach to mitigate security risks, including a variety of physical and electronic controls to protect and continuously monitor CCAs within TRE_URE’s Physical Security Perimeter (PSP). Second, although TRE_URE1 considered the employee in question to be inactive, the employee remained employed at TRE_URE1, and the TRE_URE1 access badge was in the employee’s possession throughout the duration of the issue. Finally, the logs show that the TRE_URE1 access badge was not used to access TRE_URE1 facilities throughout the duration of the issue. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) held an internal meeting between Human Resources personnel and Compliance personnel to discuss the importance of timely notification when an employee enters LTD; and 2) created a new internal control in TRE_URE1’s FMLA process that requires TRE_URE1 Human Resources to send an email to appropriate personnel, including compliance personnel, requesting revocation of CCA access for employees on FMLA leave for more than six weeks, which in turn is six weeks prior to the time such employees would transition to LTD. Texas RE has verified the completion of all mitigation activity.
2016-01-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015015044 | CIP-004-3a | R4; R4.1; R4.2 | TRE_URE2 submitted a Self-Report to Texas RE stating that it had two issues with CIP-004-3a R4. In the first instance, TRE_URE2 failed to update its access authorization list and revoke the authorized unescorted physical access to Critical Cyber Assets (CCAs) for one of its contractors within 7 calendar days of the contractor’s resignation as required by CIP-004-3a R4.1 and R4.2. After a contractor resigned, TRE_URE2 did not revoke the contractor’s authorized physical access to CCAs until 8 days after the expiration of the 7-day access revocation period provided under CIP-004-3a R4.2. TRE_URE2 further failed to update the access authorization list to reflect this change. The root cause of the issue was that TRE_URE2’s vendor did not respond timely to TRE_URE2’s email requests for an update regarding any changes in the vendor’s personnel. Accordingly, TRE_URE2 was not aware that the contractor in question had resigned in order to revoke the contractor’s access to TRE_URE2 CCAs and update the corresponding access authorization list to reflect this change. In the second instance, TRE_URE2 failed to revoke physical access of a contractor within 7 calendar days of the contractor’s resignation as required by CIP-004-3a R4.2. TRE_URE2 timely removed the contractor’s from the access authorization list but inadvertently failed to revoke the contractor’s physical access. As a result, the contractor continued to possess physical access to CCAs for 15 days after the expiration of CIP-004-3a R4.2’s 7-day access revocation period. The root cause of this instance was human performance error. In particular, the TRE_URE2 Manager responsible for maintaining TRE_URE2’s access authorization list failed to implement the steps in TRE_URE2’s Authorization Access Procedure for revoking physical access to CCAs. Texas RE determined the issue duration to be for approximately two months and two weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, TRE_URE2 uses a layered cyber defense approach to monitor access points to its PSPs on a 24 hours a day, 7 days a week basis. Second, the two individuals whose physical access was terminated late had been authorized to have physical access prior to departure. Finally, a review of access records confirmed that neither individual actually accessed a TRE_URE2 facility after the end of employment. No harm is known to have occurred. | To mitigate the issue, TRE_URE2: 1) revoked unescorted physical access rights to CCAs for both contractor employees; 2) updated the access authorization list to reflect the revocation of authorized unescorted physical access to CCAs for the contractor referenced in the first instance; 3) added a representative from its security contractor’s Human Resources department to the list of recipients of the twice weekly reminder emails from TRE_URE2 that provide the list of currently authorized contractor personnel and that ask the contractor to confirm whether anyone on the authorized list no longer requires access; 4) implemented a new process that requires a contractor to report to TRE_URE2 by phone and in writing within two hours of an involuntary termination of any employee to whom TRE_URE2 has granted authorized access to CCAs and within 24 hours for all other terminations; 5) began conducting twice yearly meetings with each contractor to emphasize the contractor’s contractual obligations to timely notify TRE_URE2 of personnel changes; and 6) implemented a process for twice daily reviews and comparisons of the access authorization list and the physical access lists, including verification emails from relevant human resources and management personnel at TRE_URE2. Texas RE has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014232 | CIP-006-3c | R2; R2.2 | WECC_URE1 submitted a Self-Report stating that, as a Responsible Entity, it had an issue of CIP-006-3c R2.2. WECC_URE1 reported two issues with CIP-004 R3 applicable to the devices in scope via CIP-006-3c R2.2. Regarding the first issue, WECC_URE1 reported that one employee’s Personnel Risk Assessment (PRA). After the expiration of the PRA, the employee continued to have logical access to one Physical Access Control System (PACS) device. The PACS device was a workstation that could be used to provision temporary access badges for authorized, unescorted physical access. Only employees with elevated account privileges were allowed to provision access. The employee involved in this issue was not granted elevated account privileges and as a result could not provision access for themselves or others. WECC_URE1 ran an annual renewal report and discovered the employee’s expired PRA. WECC_URE1 updated the PRA. Regarding the second issue, WECC_URE1 reported that WECC_URE1’s Human Resources received a request to validate the PRA status for two employees who required physical and logical access to one PACS device. WECC_URE1’s Access Management Program is automated. Because the PRA was not validated within five days, the system sent an escalation to the manager of the HR employee responsible for validating the PRA. The manager approved the escalated request prior to the completion of the PRAs. As a result, two employees were granted physical and logical access to one PACS device prior to the employees’ PRAs being completed. The PACS device in scope in the second issue was a workstation that could be used to provision temporary access badges for authorized, unescorted physical access. Only employees with elevated account privileges were allowed to provision access. Neither of the employees involved in the second issue were granted elevated account privileges and as a result could not have provisioned access for themselves or others. WECC_URE1’s corporate security updated their database and discovered the two employees did not have a PRA recorded in the database. WECC_URE1 revoked both employees’ physical and logical access. Once the PRAs were completed, physical and logical access rights were restored for both employees. The compliance exception start date was when the employee’s PRA expired. The compliance exception end date was when the employee’s PRA was updated. The root cause of the first issue was the failure of WECC_URE1's process resulting in not including a search of individuals with logical-only access when running the PRA renewal report. The root cause of the second issue was training issues with HR management on the process for validating PRAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not obtain an approved PRA for two employees prior to granting logical access to a PACS device and did not update a PRA within seven years. This could potentially cause WECC_URE1 to be unaware of the identity or criminal background of individuals who have access to PACS devices. However, WECC_URE1 implemented controls to mitigate the potential risk. The two locations housing the PACS devices in scope do not contain any other CCAs. The PACS devices can only provision access for the locations where they are located; the PACS devices could not have been used to provision access to PSPs. WECC_URE1 restricts provisioning of access to only employees with elevated account privileges. None of the employees in scope had elevated account privileges and as a result were unable to grant access to any ESP or PSP for themselves or other individuals. The PACS device was housed in a locked cage. The physical key used to unlock the cage is under key control at the facility reducing the likelihood that an unauthorized individual would be able to physically access the PACS device. This PACS device was also monitored by an internal surveillance camera and intrusion detection system. The PACS device was located in a control room that is staffed twenty-four hours a day seven days a week. No harm is known to have occurred. WECC considered WECC_URE1’s CIP-006 R2 compliance history in determining this Compliance Exception. WECC_URE1’s relevant prior noncompliance with CIP-006 R2 includes: NERC Violation ID WECC2012010527. Regarding WECC2012010527, WECC determined WECC_URE1 granted access to a contractor before the contractor completed a PRA. The contractor had access for less than twenty-four hours. WECC_URE1 promptly identified and corrected this noncompliance. WECC considered WECC_URE1’s CIP-006 R1.8 compliance history in determining this Compliance Exception. WECC determined WECC_URE1’s CIP-006 R1.8 compliance history involves distinct facts and Requirements and should not serve as a basis for applying a penalty. WECC_URE1’s relevant prior noncompliance with CIP-006 R1.8 includes WECC2012009096 and WECC2013012368. Regarding WECC2012009096, WECC determined WECC_URE1 failed to assess and document updates and patches to third party software as required by CIP-007 R3. Regarding WECC2013012368, WECC determined WECC_URE1 failed to provide three node controllers the protections of CIP-007 R1, R2, R4, R8, and R9. WECC_URE1 failed to perform an annual exercise of its workstation recovery plan and failed to annually test its workstation backup media as required by CIP-009 R2 and R5. WECC_URE1 failed to document its patch assessments for eight servers as required by CIP-007 R3. WECC_URE1 failed to generate logs of sufficient detail to create historical audit trails of individual user account access activity to one workstation as required by CIP-007 R5. WECC_URE1 also failed to implement automated tools or organizational process controls to monitor system events related to cyber security for one workstation as required by CIP-007 R6. WECC also considered WECC_URE1’s CIP-004 R3 compliance history in determining this Compliance Exception. WECC_URE1’s relevant prior noncompliance with CIP-004 R3 includes WECC2012010525. This prior noncompliance addresses the same facts as WECC_URE1’s prior noncompliance with CIP-006 R2 WECC2012010527, described above. WECC determined WECC_URE1 granted access to a contractor before the contractor completed a PRA, resulting in a noncompliance with CIP-006 R2.2 and CIP-004 R3. WECC determined WECC_URE1’s prior noncompliance with CIP-006 R2 and CIP-004 R3 involve distinct issues and subrequirements of CIP-006 R2.2 and CIP-006 R1.8 than the current noncompliance. As a result, WECC determined that WECC_URE1’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, WECC_URE1: 1) completed a PRA for the employee involved with the first issue; 2) performed a complete check of all individuals with logical access and determined no increase in scope; 3) updated the PRA Renewal Audit Report to include individuals who have logical access; 4) updated the process so that the PRA Renewal Audit Report is reviewed at least twice annually to ensure no PRA renewals are missed; 5) for the second issue, revoked the two employees' access to the PACS device; and 6) development team changed the escalation contact for PRA validation to the appropriate HR manager.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014228 | CIP-006-3c | R5 | WECC_URE1 submitted a Self-Report stating that, as a Responsible Entity, it had an issue with CIP-006-3c R5. As part of the Self-Report, WECC_URE1 reported two issues with CIP-006-3c R5. WECC determined one of the reported issues did not constitute an instance of noncompliance with CIP-006-3c R5. Regarding the remaining issue, WECC_URE1 reported that a security officer inadvertently disabled the alarm monitor on an access point to a Physical Security Perimeter (PSP). As a result, the access point was not being monitor twenty-four hours a day, seven days a week. The access point was a set of double doors used only for egress. The doors do not allow entry because the doors cannot be opened from the outside. The PSP contained one Electronic Security Perimeter (ESP). The ESP contained eight devices. WECC_URE1 discovered the disabled monitor point and re-enabled the alarm monitor point. The compliance exception start date was when the alarm monitor point was inadvertently disabled. The compliance exception end date was when WECC_URE1 re-enabled the alarm monitor point. The root cause of the issue was a lack of training and oversight on the proper procedure to disable a monitor point. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 inadvertently disabled an alarm monitor point at an access point resulting in the failure to monitor physical access at all access points to the PSP twenty-four hours a day, seven days a week. This could potentially result in unauthorized access to the PSP. However, WECC_URE1 implemented controls to prevent unauthorized access. The access point is used only for egress traffic. An individual outside the PSP would be unable to enter the PSP using the double doors. WECC_URE1 uses cameras to monitor the access point and the PSP is staffed with operators twenty-four hours a day, seven days a week reducing the likelihood that an unauthorized individual would be able to use the access point to gain access to the PSP. WECC_URE1 reviewed video footage of the time period when the alarm monitor point was disabled and found that no unauthorized access occurred. No harm is known to have occurred. WECC considered WECC_URE1’s CIP-006 R5 compliance history in determining this Compliance Exception. WECC_URE1’s relevant prior noncompliance with CIP-006 R5 includes: WECC2012009457 and WECC2012011598. Regarding WECC2012009457, WECC determined WECC_URE1 experienced a communication failure of Physical Access Control panels at WECC_URE1’s Backup Control Center as a result WECC_URE1 did not have procedural and technical controls in place to monitor physical access to a PSP for a period of four hours and twenty-two minutes. WECC determined this prior issue involved a distinct cause, a communication failure, than the current issue, an inadvertent disabling. Regarding WECC2012011598, WECC determined one WECC_URE1 substation PSP experienced an outage and monitoring failure at its card readers. WECC determined this prior issued involved a distinct cause, an outage and monitoring failure at its card readers, than the current issue, and inadvertent disabling. Because the underlying causes of the prior noncompliance were distinct, WECC determined that WECC_URE1’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, WECC_URE1: 1) re-enabled the alarm monitor point; 2) reviewed video footage for the period and determined no unauthorized access occurred; 3) met with the employee who disabled the monitor point to review the cause of the issue; 4) established a policy that personnel will contact Security Lead or Corporate Security to verify disabling a monitor point, especially any associated with a PSP-protected area; and 5) renamed the CIP alarm monitor point at issue in order to programmatically separate it from the four non-CIP monitor points utilized in this PSP. WECC has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014767 | CIP-002-1 | R3 | WECC_URE2 submitted a Self-Report citing possible non-compliance with CIP-002-1 R3. WECC_URE2 reported that a protective relaying Cyber Asset associated with its generator was dial-up accessible, but was not identified as a Critical Cyber Asset during the time period when the facility was classified by WECC_URE2’s Risk-Based Assessment Methodology (RBAM) as a Critical Asset facility. A WECC subject-matter expert (SME) reviewed the Self-Report and discussed the issue with WECC_URE2. The SME determined that the Cyber Asset was in service and dial-up accessible prior to the compliance enforcement date. Further, the Cyber Asset should have been classified as a Critical Cyber Asset until the facility was reclassified as low impact, when WECC_URE2 adopted the CIP Version 5 Impact Rating Criteria to identify Critical Asset Facilities in place of its RBAM. WECC reviewed the Self-Report and the SME’s findings and determined that WECC_URE2’s failure to identify a protective relaying Cyber Asset that was dial-up accessible, as a Critical Cyber Asset during the time WECC_URE2’s generator was classified as a Critical Asset facility is a Compliance Exception of CIP-002-1 R3. The start date of this issue was the date the standard became mandatory and enforceable to WECC_URE2. The end date of this issue was the date the facility was reclassified as low impact based on the CIP Version 5 Impact Rating Criteria. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of this issue is a dial-up accessible protective relay at a single, remote generation/black start facility. Although WECC_URE2 did not identify the protective relay as Critical Cyber Asset, WECC_URE2 did have compensating measures in place. Specifically, the modem connected to the Cyber Asset at the facility is accessible only via a telephone line connected through an authentication device in a separate substation that provides 2-factor authentication. Therefore, the relay could only be accessed through the hardened line sharing switches. Further, the enforcement of the relay has been properly maintained since the device was placed into service. No harm is known to have occurred WECC_URE2 has a prior violation of CIP-002-1 R3, making this WECC_URE2’s second violation of CIP-002-1 R3. In the first instance, WECC_URE2 failed to identify or document two fiber switches, which are part of the EMC DMX Storage Area Network solution as Critical Cyber Assets. WECC_URE2 also failed to identify one modem connected service processor used in the support and operation of the storage device as a Critical Cyber Asset. Because the prior violation had a different root cause and different facts and circumstances than the current issue and both instances of non-compliance were minimal risk and no harm is known to have occurred; WECC determined that WECC_URE2's compliance history should not serve as a basis for applying a penalty. The root cause of the prior violation was WECC_URE2’s oversight of the changes being made because the change advisory board that now approves changes was not in effect when the devices in scope were put into production. Whereas the root cause of the current violation is due to multiple factors: 1. The unique nature of the connection between the WECC_URE2 1 Facility and the WECC_URE2 2 Facility. The protective relay at the WECC_URE2 2 facility was not connected to its own security device, but was connected via a phone line to a security device at a separate facility (WECC_URE2 1 Substation). WECC_URE2 2 facility was the only Critical Asset facility with this type of configuration. 2. The personnel who knew WECC_URE2 2 facility was a Critical Asset facility were not aware of the modem connection between WECC_URE2 1 Substation and WECC_URE2 2 Substation. 3. The personnel who knew of the modem connection between WECC_URE2 1 Substation and WECC_URE2 2 facility were not aware that WECC_URE2 2 facility was a Critical Asset facility. 4. The search for modem to security device connections in 2014 did not identify the existence of the additional modem at WECC_URE2 2 facility. A new search methodology developed by IT Security and Risk caught the error by reviewing a device communication report from the security device management server rather than searching for the physical presence of security endpoint devices. | To mitigate this issue, WECC_URE2: 1) updated its annual CVA procedure: included a review of the dial-up management device report(s) to identify dial-up accessible cyber assets; 2) updated annual CVA procedure: updated the on-site visits to focus on the identification of dial-up modems; and 3) increased awareness regarding Critical Assets: ensured that key relay operations personnel are familiar with WECC_URE2's list of Critical Asset (high or medium Impact) facilities.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015015279 | CIP-007-3a | R4 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R4. A WECC Subject Matter Expert (SME) reviewed the Self-Report and communicated further with WECC_URE3 concerning the issue. The WECC SME agreed with WECC_URE3's assessment that it had an issue with CIP-007-3a R4 for failing to ensure that eight Electronic Access Control and Monitoring EACM devices had anti-virus or other malware prevention tools installed, where it was technically feasible. Specifically, WECC_URE3 failed to ensure that EACM devices had anti-virus or other malware prevention tools installed, as required by CIP-007 R4.1. These devices were installed in parallel with an existing appliance to provide the security status monitoring and logging functionality required by CIP-007-3 R6 requirements. WECC determined that WECC_URE3 had an issue with CIP-007-3a R4 for failing to ensure that EACM devices had anti-virus or other malware prevention tools installed, where it was technically feasible. WECC also determined that the start date of the issue was from when the devices were classified as EACM devices and placed on the CCA List; and the end date of the issue was when anti-virus was installed on the servers. The root cause of the issue was a lack of compliance understanding. The WECC_URE3 personnel installing the new devices believed the devices did not require anti-virus because of their operating system; WECC_URE3 personnel believe such devices are hardened and protected against malware without anti-virus. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE3 failed to ensure devices classified as EACMs had anti-virus or other malware prevention tools. The devices were part of its SIEM system and were located at its Primary and Backup Control Centers. Failing to ensure malware prevention tools such as anti-virus are installed on devices could lead to undetected malware on WECC_URE3’s network, which could eventually make its way onto devices within the ESP. To mitigate this risk, WECC_URE3 had firewall rules in place at the ESP to prevent the SIEM devices from sending network traffic into the ESP. Additionally, to compensate for any affects to the SIEM, the devices in scope were part of a new SIEM system which was being tested in parallel with the old SIEM system. If the devices of the new SIEM were somehow compromised by malware, the entity had a backup system it could use. | To mitigate this issue, WECC_URE3: 1 installed anti-virus on all of the devices in scope; and 2 educated its personnel on the need to ensure anti-virus is installed on all devices, where applicable. WECC has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015015361 | CIP-006-3c | R1.7 | WECC_URE4 submitted a self-log stating that it had an issue of CIP-006-3c R1.7. WECC_URE4 failed to have an unpdated physical security plan within 30 calendar days of the completion of any physical security system redesign or reconfiguration.WECC_URE4 physically relocated a Control Center (CC) and Data Center (DC), both of which include cyber assets covered by CIP-006-3, from Facility #1 to Facility #2 and began operations at the new location. Facility #1 is no longer in use by the entity. Both the Facility #1, when it was active, and Facility #2 are secure, non-public, access-controlled facilities (i.e., require card reader access). While located at the Facility #1, the CC and DC, including the connection between them, were configured as two separate Physical Security Perimeters (PSPs) and two separate Electronic Security Perimeters (ESPs). However, following the move to Facility #2, due to a new configuration the connection was arranged as two separate PSPs and one ESP. As such, the CC and DC within Facility #2 are in two separate, completely enclosed (six-wall), access-controlled locations, creating multiple physical access control layers. These PSPs were identified and documented in the Physical Security Plan in accordance with CIP-006-3. The fiber optic/copper cabling between the CC and DC is protected with metal conduit and WECC_URE4 EMS Analysts are notified via email alerts when the fiber changes state such as for device failure, unplugged sfp or fiber, or if the configuration is administratively adjusted to deliberately change the state. However, while the ESP is appropriated protected, it was not identified and documented in the Physical Security Plan. The Security Compliance Analyst identified a second instance at Facility #3 where the Physical Security Plan was not updated to accurately reflect a physical mitigating control at the physical perimeter, around the ESP. While EMS operations initiated at Facility #3 prior to the CIP-006-3 effective date, the Physical Security Plan was not updated at the time of the move, as required. Specific to this event, cabling between the DC and back-up CC is protected within a cable tray located under the floor boards at Facility #3 within a non-public, access controlled facility. However, this mitigating control was not documented in the Physical Security Plan at the time of the move, as required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There was no actual impact to the BPS. The potential impact to the BPS is minimal. All PSPs and ESPs, which include the cables between PSP locations at each facility, were adequately protected and secure, resulting in no physical vulnerabilities to the BES. The Regulatory Compliance department examined photographic evidence, noting wiring between PSP locations was adequately secured with metal conduit (Facility #2) or enclosed within a cable tray located under the floor boards (Facility #3). The respective PSPs and ESPs are within non-public, access-controlled facilities that create multiple control layers at each location. This is consistent with guidance provided in Appendix 1 of CIP-006. Moreover, the entity EMS Analysts are notified via email alerts when the fiber changes state such as for device failure, unplugged sfp or fiber, or if the configuration is administratively adjusted to deliberately change the state. A 90° elbow in the conduit of the ESP at Facility #2 was upgraded with tamper-resistant screws. The conduit met physical security requirements prior to the modification; however, the improvement was a proactive measure to provide additional assurance. | To mitigate this issue, WECC_URE4 updated its Physical Security Plans for the Facility #2 and Facility #3 to include the ESPs as required by CIP-006-3 respectively.
2015-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015378 | CIP-005-3a | R1 | During a Compliance Audit, MRO determined that MRO_URE1 had an issue of CIP-005-3, R1.5 because it failed to afford the protective measure required by CIP-007-3, R3 to cyber assets used in the access control and/or monitoring of its Electronic Security Perimeter (ESP). MRO_URE1 did not implement its security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for the hypervisor, which is used for Electronic Access Control and Monitoring devices. While gathering evidence for the MRO Audit, MRO_URE1 discovered that hypervisor was missing a security patch and that it has no records of patch reviews for this device. This noncompliance was caused by a lack of internal procedures to fully integrate hypervisors into MRO_URE1’s NERC CIP program. The issue began when the device was deployed, and ended when MRO_URE1 stated that it had completed mitigating activities. In determining the appropriate disposition track for this noncompliance, MRO considered that guidance on handling virtualized environments was under discussion during the time of noncompliance and there was some uncertainty regarding virtualized environments across the ERO. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The audit confirmed that a single hypervisor was the only device affected by this noncompliance, and that each device that the hypervisor was attached to had up to date patches. Additionally, the hypervisor resided within an ESP and sat behind a firewall. Additionally, MRO_URE1 had no findings with other CIP requirements that could have detected malicious activity, such as CIP-007-3a R6 (security log reviews) and CIP-007-3a R5.1.3 (account reviews). No harm is known to have occurred. MRO considered MRO_URE1's CIP-005-3a R1 compliance history in determining the disposition track and determined that MRO_URE1 does not have any relevant prior noncompliance. | To mitigate this issue, MRO_URE1: 1) performed a comprehensive review to confirm that there is only one hypervisor that was not patched; 2) assessed all outstanding hypervisor patches and added hypervisor as an asset to the ongoing monthly assessment process; 3) updated the Security Patch Management Policy to include virtual server hosts in the security patch management process; 4) trained all staff with access to the hypervisor assets on the updated security patch review procedures; 5) installed new hardware and applied patches, including security patches installed on a functionally equivalent server and tested against security controls and for asset functionality and cluster servers, with patches successfully tested, the new server is clustered with the existing server and added as a new CIP Supporting Cyber Asset. MRO_URE1 stated that mitigation activities were completed.
2015-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015142 | CIP-007-3a | R2 | During a Compliance Audit, MRO determined that MRO_URE1 had an issue of CIP-007-3a R2 because MRO_URE1 failed to ensure that those ports and services required for normal and emergency operations are documented. For two of six sampled Critical Cyber Assets, there were active ports and services that were not included in the baseline documentation. For one device, the noncompliance was limited to UDP ports inaccurately identified as TCP ports. The second device had numerous ports and services which were found active during a scan but were not properly documented in the baseline. In addition, during the comprehensive review by the Entity, a discrepancy was identified in its baseline documentation for servers. An intermittent management port was both required and enabled but not documented. The first device was used for security monitoring and the mislabeling of the UDP ports as TCP ports was determined by MRO_URE1 to be a typographical error. MRO_URE1's automated process for reviewing ports and services against the approved baseline documentation did not include this type of device. The server concern identified during mitigating activities was the result of the activation of previously installed tools required for debugging. Since these assets were installed as part of an EMS upgrade that had been recently completed, MRO_URE1 had not yet conducted its annual security controls review or undergone any changes that would have triggered a ports and services baseline comparison. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). All of the ports/services that were improperly documented in the baseline were ultimately identified as being required. The ports which were not included in the baseline were either maintenance ports or disabled in software, but still appeared within netstat output. Additionally, these devices were located behind a firewall within a Electronic Security Perimeter (ESP) and all of the devices (except the device whose noncompliance was limited to a typographical error in the documentation) could not be accessed from outside of the ESP. Finally, the noncompliance was limited solely to errors in the baseline documentation, and there were no operation errors that needed to be corrected. No harm is known to have occurred. MRO considered MRO_URE1's CIP-007-3a R2 compliance history in determining the disposition track. MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. Because the noncompliance occurred more than three years prior to the beginning of the current issue, the prior noncompliance cannot be used to apply a penalty. | To mitigate this issue, MRO_URE1: 1) enhanced its Automated Tool that compares ports and services to an approved baseline to work with logging devices; 2) corrected the baseline for the identified assets; 3) completed a comprehensive review of all of its CCAs and Supporting Cyber Assets against its approved baselines to ensure accuracy; 4) reviewed and updated the Approved Ports and Services baseline document to match the actual ports and services that were open/available; 5) reviewed existing processes to ensure that all ports and services are captured and documented when new assets are commissioned. MRO_URE1 stated that mitigation activities were completed.
2015-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015106 | CIP-007-3a | R5.1.2 | During a Compliance Audit, MRO determined that MRO_URE1, had an issue of CIP-007-3a R5 because MRO_URE1 failed to implement technical and procedural controls for four data storage appliances to capture sufficient detail for a minimum of ninety days of historical audit trails of individual user account access activity. While unsuccessful login attempts were properly retained, MRO_URE1 failed to also forward successful login attempts to the long-term log retention server for four devices. As a result, MRO_URE1 was not able to provide historical access activity audit trails for 90 days as required. The successful login attempts were stored locally on the appliance, but due to storage limitations, it was only able to retain approximately 30 days of successful logins. The cause of this noncompliance was based on a misunderstanding that occurred during the onboarding of the device during a recent EMS upgrade. MRO_URE1 believed there was only one configuration necessary to remotely log user activity, but two configurations were necessary as it had to separately configure the storage of failed login attempts and successful logins. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Unsuccessful login attempts, which are an important indicator of an immediate concern, were properly sent to the log retention server for 90-day retention and alerting as required by the standard. The successful logins were being stored on the logging device for approximately 30 days and were available for review. No harm is known to have occurred. MRO considered MRO_URE1's CIP-005-3a R1 compliance history in determining the disposition track and determined that MRO_URE1 does not have any relevant prior noncompliance. | To mitigate this issue, MRO_URE1: 1) corrected the syslog configuration on all Critical Cyber Assets to log all successful logon attempts remotely for ninety days, as well as to continue to log all failed logon attempts, both locally and remotely; 2) updated its NERC CIP Security Log Procedures to include verification of both local and remote logging retention for a minimum of ninety days, as well as logging of successful and failed logon attempts during device commissioning; 3) verified all failed and successful logins for all of MRO_URE1’s Critical and Supporting Cyber Assets are being sent to the syslog servers and retained for ninety days; 4) provided training to appropriate staff on the use of the updated process to ensure that logging capabilities are verified when on-boarding new Critical and supporting Cyber Assets. MRO_URE1 stated that mitigating activities were completed.
2015-12-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015327 | CIP-006-3c | R4 | NPCC_URE1 had an issue of CIP-006-3c, R4. NPCC_URE1 had an incident where the door to the control house at a substation was unlocked for a brief period of time. NPCC_URE1 employee with authorized access to the substation forgot their badge to gain access to the control house. The employee called the Security Operation Center (SOC) to request access to the control house key from the lock box. The SOC verified the employee's identity, and issued the lock box code to the employee. Once the employee unlocked the door, they returned the key to the lock box. A few days later, security changed the lock box combination per NPCC_URE1 Standard Operating Procedure (SOP). Several days later, another NPCC_URE1 employee with authorized access to the substation used their ID badge to enter the control house, and when exiting they realized that the door to the control house was actually unlocked. The employee called the SOC to inform them of the lock status, and the SOC issued the lock box code to the employee to secure the door. The next day, security changed the lock box combination, and verified that the control house door was locked. A root cause analysis was performed by NPCC_URE1 after the issue was discovered, and the results showed that the lock type, in combination with the SOP, contributed to the issue. Without a step in the SOP to check that the control house door was locked, the potential for the door to be left unlocked existed due to the fact that the door was not auto-locking. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the control house door was unlocked, NPCC_URE1 had a number of other controls in place to prevent unauthorized access to the control house. A secured external fence surrounds the substation in question to prevent unauthorized persons from gaining access. Motion detectors and cameras in the control house would have alarmed and alerted the SOC if an intrusion was detected. In addition, a door forced alarm would have been generated if the door was opened without a valid card swipe. NPCC_URE1 reviewed door alarms, motion alarms, and video record after the fact and found no evidence of unauthorized access. No harm is known to have occurred as a result of the violation. | To mitigate this issue, NPCC_URE1: 1) changed the lock on the control room door so that the lock cannot be left in the unlocked position. Door will relock once the key is removed; and 2) modified their SOP for lock box code issuance to include verbal instruction to manually check that the door is locked. NPCC has verified the completion of all mitigation activities.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014940 | CIP-004-3a | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R2. One RFC_URE1 System Protection employee failed to go through the annual CIP refresher training for Critical Cyber Asset (CCA) cyber access. RFC_URE1 installed relays at some of its critical facilities. With these installations, RFC_URE1’s System Protection (SP) group implemented procedures to protect the relays as CCAs. To meet the training requirements to access CCAs, SP personnel received training to get authorized cyber access. One individual from the SP group was granted access to the relays. That individual was the only person from the SP group that received the cyber access password for the relays. During RFC_URE1’s annual compliance review, RFC_URE1 discovered that this individual with access to the relays did not go through the CIP annual refresher training for CCA cyber access. This noncompliance involved the management practice of verification because RFC_URE1 relied on an ineffective manual process to ensure that each individual with cyber access to the relays received his or her refresher training each year. This manual review process did not catch that the individual did not receive refresher training during the prior year. The duration of this noncompliance is from the date the individual with access to the relays did not complete the annual CIP refresher training for CCA cyber access to the date the individual received the overdue refresher training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This noncompliance only involved one individual that did not go through the CIP annual refresher training for CCA cyber access. The individual in question had received the proper training to gain CCA cyber access for these relays. The individual just did not complete the refresher training on time. The individual was retrained and retained access. No unauthorized access occurred as a result of this noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) retrained the individual and reinforced the compliance training requirements and the importance of training with the SP group; 2) hired new CIP personnel to manage CIP processes and support the SP group’s compliance program; 3) performed a yearly review of its basic NERC CIP training module; and 4) expanded the centralized tracking and training program it uses for managing physical access to CCAs to include the management of cyber access.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014416 | CIP-005-3a | R2 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-005-3a R2. An employee of RFC_URE2, who had a current Personnel Risk Assessment (PRA), current CIP training, and authorized access rights, established external, interactive access into RFC_URE2’s Electronic Security Perimeter (ESP) using a method that was not permitted by RFC_URE2’s procedures. Specifically, the employee did not use an established jump host to establish external interactive access into the ESP. Rather, the employee used terminal emulation software installed on a network management server to establish interactive access into the ESP. The main factor contributing to the cause of this noncompliance was a lack of technical controls in place to prevent support personnel from accessing the ESP through this network management server. The duration of this noncompliance is from the date RFC_URE2 was required to comply with CIP-005-3a R2, to the date RFC_URE2 completed the Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, this noncompliance arose out of an isolated circumstance which only involved one specific use of remote interactive access. Second, this particular circumstance involved a violation of a procedural mechanism related to this specific requirement and, therefore, was unlikely to be indicative of further violations. Third, this particular instance involved a known, authorized user with a current PRA and cyber security training. Therefore, the risk posed by this individual failing to follow the proper procedure was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) counseled the employees on the need to understand and comply with the strong procedural controls for CIP external access points to ensure authenticity of the accessing party; 2) modified the application to prevent users from having the technical ability to establish non-procedural remote interactive sessions with a device within this CIP ESP; and 3) further reinforced the procedural controls by modifying the network management application to disable the access path to the ESP and removed the terminal emulation software from the network management server. ReliabilityFirst has verified the completion of all mitigation activity.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014014417 | CIP-005-3a | R2 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-005-3a R2. An employee of RFC_URE3, who had a current Personnel Risk Assessment (PRA), current CIP training, and authorized access rights, established external, interactive access into RFC_URE3’s Electronic Security Perimeter (ESP) using a method that was not permitted by RFC_URE3’s procedures. Specifically, the employee did not use an established jump host to establish external interactive access into the ESP. Rather, the employee used terminal emulation software installed on a network management server to establish interactive access into the ESP. The main factor contributing to the cause of this noncompliance was a lack of technical controls in place to prevent support personnel from accessing the ESP through this network management server. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-005-3a R2, to the date RFC_URE3 completed the Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, this noncompliance arose out of an isolated circumstance which only involved one specific use of remote interactive access. Second, this particular circumstance involved a violation of a procedural mechanism related to this specific requirement and, therefore, was unlikely to be indicative of further violations. Third, this particular instance involved a known, authorized user with a current PRA and cyber security training. Therefore, the risk posed by this individual failing to follow the proper procedure was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) counseled the employees on the need to understand and comply with the strong procedural controls for CIP external access points to ensure authenticity of the accessing party; 2) modified the application to prevent users from having the technical ability to establish non-procedural remote interactive sessions with a device within this CIP ESP; and 3) further reinforced the procedural controls by modifying the network management application to disable the access path to the ESP and removed the terminal emulation software from the network management server. ReliabilityFirst has verified the completion of all mitigation activity.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014957 | CIP-007-3a | R5 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. RFC_URE2 failed to annually update a password for one shared system account, which was used to support inter-process communications for the generation management system and affected two CIP Cyber Assets. However, RFC_URE2’s internal process for updating passwords identified the issue within 37 days and immediately corrected the problem. The main factor contributing to the cause of this noncompliance was human error specifically related to the management practice of information management. The duration of this noncompliance is from the date RFC_URE2 was required to update the password to the date RFC_URE2 identified and resolved the issue by removing the account. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the password at issue only affected one system account with a very limited set of known authorized users having access to it. Second, the two affected CIP Cyber Assets were located within a Physical Security Perimeter, within an Electronic Security Perimeter, and behind firewalls. Third, after RFC_URE2 identified the issue, it determined that the account at issue was of no value and removed it from the system. Because the account was of such little value, it is unlikely that unauthorized access to it would have caused any harm. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) determined that the account in question was no longer necessary, and the account was removed; and 2) also added a verification step to its Annual Account Review and System Password Changes to identify any accounts that were missed during the password change process. ReliabilityFirst has verified the completion of all mitigation activity.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014801 | CIP-002-3 | R3 | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-002-3 R3. RFC_URE4 failed to include a legacy generation dispatch system in its annual assessment of Critical Assets and Critical Cyber Assets (CCAs). This noncompliance concerned the management practice of asset and configuration management. Asset and configuration management was involved because the generation dispatch system was not properly inventoried as a CCA that needed to be assessed during RFC_URE4’s annual assessment of its Critical Assets and CCAs. The duration of this noncompliance is from the date RFC_URE4 was required to complete its annual assessment of its Critical Assets and CCAs, to the date RFC_URE4 included the generation dispatch system in RFC_URE4’s annual assessment of its Critical Assets and CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Throughout the noncompliance, RFC_URE4 provided the generation dispatch system with a number of cyber protections including user account access controlled through an active directory membership, monthly patch management, regular antivirus updates, regular reviews of system logs to monitor for questionable activity, change management procedures that followed corporate policies and industry best practices, system back-up procedures to support cyber asset restoration, cyber asset redundancy across data centers, and many more. Additionally, the generation dispatch system had a limited effect on RFC_URE4’s BES assets because the generation dispatch system did not perform electronic dispatch or remotely start any CIP Critical Assets, did not employ the ability to directly control any equipment that could affect physical operation of a generator facility, did not have the direct capability to bring generating units on or offline, and did not encompass any transmission facilities or substations. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) evaluated the generation dispatch system during its CCA identification and assessment process and included the generation dispatch system on its list of CCAs; 2) completed a project to fully migrate the generation dispatch system into a singular CIP-compliant system; 3) committed to complete a quality assurance review of the entire generation dispatch system to verify that it is CIP-compliant; and 4) committed to complete a review of its internal processes and procedures to identify any improvements needed to ensure fully documented CIP compliance, including the consolidation of any risk based assessment methodologies.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014013843 | CIP-004-3a | R4.1 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-004-3a R4.1. A RFC_URE5 employee with authorized unescorted physical access to a RFC_URE5 Physical Security Perimeter (PSP) resigned. That same morning, the employee’s supervisor confiscated the employee’s electronic access badge. Confiscating the badge removed the employee’s ability to access any RFC_URE5 Critical Cyber Assets (CCAs) because the employee could no longer gain access through a PSP. The employee did not have authorized electronic access to any CCAs. Although the employee’s supervisor properly confiscated the employee’s badge, neither the supervisor nor the employee’s manager notified the RFC_URE5 CIP Compliance group of the employee’s resignation or the fact that his access was no longer needed. Therefore, the RFC_URE5 CIP Compliance Group did not timely initiate its process to manage access revocation and update the CIP Cyber Access List (Access List). The Access List includes all personnel with authorized unescorted physical access to PSPs and authorized electronic access to CCAs. This resulted in a delay in updating the Access List to reflect the change in the employee’s access rights until fifteen days later. There was also a delay in deactivating the employee’s electronic access badge, which was not deactivated until fourteen days later. Resulting from these delays, the Access List was not updated within seven days after the employee resigned, which violates CIP-004-3a R4.1. This noncompliance concerned the management practices of verification and workforce management. Verification was involved because RFC_URE5 did not timely verify that the Access List had been updated after the employee resigned. Workforce management was involved because the employee’s supervisor was not properly trained to timely inform the RFC_URE5 CIP Compliance Group that an employee had resigned, which would allow RFC_URE5 to update its Access List within seven days as CIP-004-3a R4.1 requires. The duration of this noncompliance is from the date the seven day period for updating the Access List after the employee’s resignation ended, to the date RFC_URE5 updated its Access List to reflect the revocation of the resigned employee’s physical access. RFC_URE5 had a second noncompliance with CIP-004-3a R4.1 that began when a RFC_URE5 contractor with authorized unescorted physical access rights voluntarily terminated his employment. The contractor's manager confiscated his electronic access badge, but no one at the contractor's office informed RFC_URE5 that the individual had terminated his employment with the contractor and that his physical access rights had been revoked. RFC_URE5 initiated a periodic review of physical access and identified that the individual had not used his access badge for 60 days. RFC_URE5 contacted the contractor about the individual not using his access badge for 60 days. The contractor informed RFC_URE5 that the individual had been terminated and that his access had been revoked. RFC_URE5 immediately updated its CIP Cyber Access List (Access List) but the list was updated more than seven days after the individual had resigned which violates CIP-004-3a R4.1. This noncompliance concerned the management practices of verification and workforce management. Verification was involved because RFC_URE5 did not timely verify that the Access List had been updated after the individual resigned. Workforce management was involved because the contractor’s manager was not properly trained to timely inform the RFC_URE5 CIP Compliance Group that an individual had resigned, which would allow RFC_URE5 to update the Access List within seven days as CIP-004-3a R4.1 requires. The duration of this noncompliance is from the date the seven day period for updating the Access List after the individual’s resignation ended, to the date RFC_URE5 updated the Access List to reflect the revocation of the terminated individual’s physical access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Throughout the noncompliance, the employee had no remote access to any CCAs and did not have the ability to gain unescorted physical access into a RFC_URE5 PSP because the employee’s electronic access badge was confiscated by his supervisor the same morning that he resigned. The employee could not access any RFC_URE5 PSP without his badge. Additionally, the Access List was updated fifteen days after the employee resigned. The second issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Throughout the noncompliance, the individual had no remote access to any CCAs and did not have the ability to gain unescorted physical access into a RFC_URE5 PSP because the individual’s electronic access badge was confiscated by his contractor manager the same day that he resigned. The individual could not access any RFC_URE5 PSP without his badge. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) updated the Access List by removing the subject employee and individual contractor from the Access List; 2) sent an email to managers of employees reminding them of their responsibilities to inform the CIP Compliance Group immediately after a change in an employee or contractor’s work status. RFC_URE5 intends to send out this reminder email annually; 3) implemented periodic reviews of physical access to identify individuals who have not exercised physical access rights within a roughly 60-day period. This periodic review process serves not only as a control to verify access is needed and that the access list is accurate, but also as an additional reminder to managers and supervisors of the need to advise the CIP Compliance Group of any change in personnel that could implicate CIP access. The very first periodic review identified the second noncompliance discussed above; and 4) implemented a new notification in its personnel workflow which will notify the CIP Compliance Group when an individual is no longer active. If an individual is no longer active in the personnel workflow, it is an indication to the CIP Compliance Group that the individual’s employment has been terminated and triggers an additional review to see if the individual is on the Access List. ReliabilityFirst has verified the completion of all mitigation activity.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014946 | CIP-004-3a | R2 | RFC_URE6 submitted a Self-Report stating that it had an issue of CIP-004-3a R2. An authorized employee of RFC_URE6 permitted an IT engineer from an outside vendor to install a diagnostic utility application on one of RFC_URE6’s servers. The non-RFC_URE6 engineer was not onsite, so the RFC_URE6 employee permitted the non-RFC_URE6 engineer to complete the installation by relinquishing control of the keyboard/mouse/monitor during a remote communications session. The RFC_URE6 employee observed everything that the non-RFC_URE6 engineer did during the session and could have regained control of the session if she had observed anything malicious. However, the FERC-approved interpretation of the currently published version of CIP-004-3a does not permit supervised or “escorted” cyber access to Critical Cyber Assets. The main factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the RFC_URE6 employee at issue was not made appropriately aware of her responsibilities under this particular CIP Standard. The duration of this noncompliance is from the date the RFC_URE6 employee permitted the outside engineer to install the software on the server, to the date RFC_URE6 completed the Mitigation Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the RFC_URE6 employee, who had a current Personnel Risk Assessment (PRA) and who was current on her NERC CIP training, observed everything that the outside engineer did and would have been able to terminate the session if she witnessed anything malicious. Second, the outside engineer would have required specialized knowledge to exploit the server at issue. Because the outside engineer did not have this specialized knowledge, the risk of permitting the engineer to have escorted cyber access to the server was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) Created a latent change record to document the temporary installation and subsequent removal of a configuration utility and performed related security posture verification; 2) Counseled employee on the importance of not permitting escorted vendor cyber access and reinforced the corresponding responsibilities and expectations with the employee’s work group; and 3) Sent a security awareness bulletin to the users of the energy management system with authorized administrative rights for vendor/support reminding them of their specific responsibilities and expectations related to escorting vendors and other persons for the purpose of providing support to Cyber Assets subject to the NERC CIP standards requirements.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015014945 | CIP-004-3a | R2 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-004-3a R2. An authorized employee of RFC_URE7 permitted an IT engineer from an outside vendor to install a diagnostic utility application on one of RFC_URE7’s servers. The non-RFC_URE7 engineer was not onsite, so the RFC_URE7 employee permitted the non-RFC_URE7 engineer to complete the installation by relinquishing control of the keyboard/mouse/monitor during a remote communications session. The RFC_URE7 employee observed everything that the non-RFC_URE7 engineer did during the session and could have regained control of the session if she had observed anything malicious. However, the FERC-approved interpretation of the currently published version of CIP-004-3a does not permit supervised or “escorted” cyber access to Critical Cyber Assets. The main factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the RFC_URE7 employee at issue was not made appropriately aware of her responsibilities under this particular CIP Standard. The duration of this noncompliance is from the date the RFC_URE7 employee permitted the outside engineer to install the software on the server, to the date RFC_URE7 completed the Mitigation Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the RFC_URE7 employee, who had a current Personnel Risk Assessment (PRA) and who was current on her NERC CIP training, observed everything that the outside engineer did and would have been able to terminate the session if she witnessed anything malicious. Second, the outside engineer would have required specialized knowledge to exploit the server at issue. Because the outside engineer did not have this specialized knowledge, the risk of permitting the engineer to have escorted cyber access to the server was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) Created a latent change record to document the temporary installation and subsequent removal of a configuration utility and performed related security posture verification; 2) Counseled employee on the importance of not permitting escorted vendor cyber access and reinforced the corresponding responsibilities and expectations with the employee’s work group; and 3) Sent a security awareness bulletin to the users of the energy management system with authorized administrative rights for vendor/support reminding them of their specific responsibilities and expectations related to escorting vendors and other persons for the purpose of providing support to Cyber Assets subject to the NERC CIP standards requirements.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014846 | CIP-007-1 | R5 | RFC_URE6 submitted a Self-Report stating that it had an issue with CIP-007-1 R5. While investigating and resolving a remedy ticket submitted by a power trader, RFC_URE6 discovered that personnel working in the power trading area would keep their Energy Management System (EMS) computers logged in regardless of who was on shift. In other words, for each shift, one person would log in to a computer and leave it open for anyone else on shift to use. The major factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, this particular group of employees failed to fully understand the relevant Reliability Standard and the company’s corresponding policies. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-007-1 R5, to the date RFC_URE6 completed the Mitigation Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the room in which these computers resided was manned 24 hours per day, 7 days per week by operations personnel who are authorized to use the computers. Second, all of the computers involved were protected within an Electronic Security Perimeter and Physical Security Perimeter with proper access and security controls, logging, monitoring, and alerts. Third, these computers were designed to perform a very limited type of work. Thus, any potential harm posed by possible unauthorized use was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) sent communication explaining required behavior changes; 2) relocated an EMS PC within the Power Operations work area to eliminate the need for two day-ahead planners to share a single EMS PC; and 3) sent a security awareness bulletin to all company personnel who have been granted authorized cyber access to Critical Cyber Assets reminding them of specific responsibilities related to such rights.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015014845 | CIP-007-3a | R5 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-007-3a R5. While investigating and resolving a remedy ticket submitted by a power trader, RFC_URE7 discovered that personnel working in the power trading area would keep their Energy Management System (EMS) computers logged in regardless of who was on shift. In other words, for each shift, one person would log in to a computer and leave it open for anyone else on shift to use. The major factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, this particular group of employees failed to fully understand the relevant Reliability Standard and the company’s corresponding policies. The duration of this noncompliance is from the date RFC_URE7 was required to comply with CIP-007-3a R5, to the date RFC_URE7 completed the Mitigation Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the room in which these computers resided was manned 24 hours per day, 7 days per week by operations personnel who are authorized to use the computers. Second, all of the computers involved were protected within an Electronic Security Perimeter and Physical Security Perimeter with proper access and security controls, logging, monitoring, and alerts. Third, these computers were designed to perform a very limited type of work. Thus, any potential harm posed by possible unauthorized use was minimal. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) sent communication explaining required behavior changes; 2) relocated an EMS PC within the Power Operations work area to eliminate the need for two day-ahead planners to share a single EMS PC; and 3) sent a security awareness bulletin to all company personnel who have been granted authorized cyber access to Critical Cyber Assets reminding them of specific responsibilities related to such rights.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015015148 | CIP-007-3a | R5 | RFC_URE6 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. During an internal audit, RFC_URE6 found that a shared account for servers used in the security management system (e.g., alarm monitoring, etc.) was not adequately managed or tracked. This particular account would automatically login to the servers to perform the administrative function of updating the Domain Name System (DNS) address entry for the servers. Because the account was not assigned to a particular individual, it is considered a shared account. However, the account was not listed on the corresponding shared account list. Therefore, RFC_URE6 failed to identify the individuals who had access to the account. The major factor contributing to the cause of this noncompliance was the fact that the company procedure for identifying shared accounts did not expressly identify service accounts, like the one at issue, as shared accounts. The duration of this noncompliance is from the date by which RFC_URE6 was required to update the shared account list to include this particular account, to the date RFC_URE6 updated the shared account list to include this particular account. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the servers to which this account had access were not Critical Cyber Assets (CCAs) because they did not perform any Bulk Electric System reliability operating service functions and cannot access any CCAs. Second, although the account could access these servers, the only function it could perform was an administrative function. Therefore, even if an unauthorized user had access to the account, that person could not have exploited the account to perform any physical security functions. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) Changed the shared account password; 2) Documented the shared account password change; 3) Documented the shared account password distribution; 4) Updated the shared account spreadsheet; and 5) Updated the Shared Account Management procedure to expressly identify service accounts as shared accounts.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015015147 | CIP-007-3a | R5 | RFC_URE7 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. During an internal audit, RFC_URE7 found that a shared account for servers used in the security management system (e.g., alarm monitoring, etc.) was not adequately managed or tracked. This particular account would automatically login to the servers to perform the administrative function of updating the Domain Name System (DNS) address entry for the servers. Because the account was not assigned to a particular individual, it is considered a shared account. However, the account was not listed on the corresponding shared account list. Therefore, RFC_URE7 failed to identify the individuals who had access to the account. The major factor contributing to the cause of this noncompliance was the fact that the company procedure for identifying shared accounts did not expressly identify service accounts, like the one at issue, as shared accounts. The duration of this noncompliance is from the date by which RFC_URE7 was required to update the shared account list to include this particular account, to the date RFC_URE7 updated the shared account list to include this particular account. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the servers to which this account had access were not Critical Cyber Assets (CCAs) because they did not perform any Bulk Electric System reliability operating service functions and cannot access any CCAs. Second, although the account could access these servers, the only function it could perform was an administrative function. Therefore, even if an unauthorized user had access to the account, that person could not have exploited the account to perform any physical security functions. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) Changed the shared account password; 2) Documented the shared account password change; 3) Documented the shared account password distribution; 4) Updated the shared account spreadsheet; and 5) Updated the Shared Account Management procedure to expressly identify service accounts as shared accounts.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015015269 | CIP-004-3a | R4 | RFC_URE6 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. In the first instance of noncompliance, a RFC_URE6 employee retired. Although this employee’s supervisor timely revoked the employee’s access rights pursuant to the requirements of CIP-004-3a R4, the supervisor failed to update the cyber access authorization list to reflect this change within seven days of the employee’s retirement. Rather, the list was updated 11 days later, or four days late. In the second instance of noncompliance, another RFC_URE6 employee retired. On that day, an executive assistant took possession of the employee’s ID card and sent it to his supervisor. However, the supervisor was on vacation and did not complete the revocation of the retired employee’s access rights until thirteen days later, or 6 days late. The main factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the supervisor at issue failed to follow the company procedure for proactive revocation of access rights. The duration of this noncompliance is from the date RFC_URE6 was required to update the cyber access authorization list for the first instance of noncompliance, to the date RFC_URE6 revoked the access privileges for the employee in the second instance of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. As to the first instance of noncompliance, the employee’s access privileges were revoked in a timely manner and the only violation was a documentation issue. Furthermore, the error was identified and corrected within only four days. As to the second instance of noncompliance, even though the employee’s ID badge was not deactivated within 7 days, the ID badge was collected from the employee and no longer in his possession, which reduced the risk of any inadvertent or unauthorized use of the badge. No harm is known to have occurred. | To mitigate this issue, RFC_URE6: 1) Referred the supervisor’s failure to follow direction provided in annual training and quarterly awareness reminders to his manager for appropriate disciplinary action; 2) Sent targeted awareness message illustrating this situation and expected behaviors to current supervisors; and 3) Enhanced current manual process related to revocation requests sent proactively to set the expiration date in the Physical and/or Cyber Access Control Monitoring Systems as soon as a tentative revocation date is stated.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015015270 | CIP-004-3a | R4 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. In the first instance of noncompliance, a RFC_URE7 employee retired. Although this employee’s supervisor timely revoked the employee’s access rights pursuant to the requirements of CIP-004-3a R4, the supervisor failed to update the cyber access authorization list to reflect this change within seven days of the employee’s retirement. Rather, the list was updated 11 days later, or four days late. In the second instance of noncompliance, another RFC_URE7 employee retired. On that day, an executive assistant took possession of the employee’s ID card and sent it to his supervisor. However, the supervisor was on vacation and did not complete the revocation of the retired employee’s access rights until thirteen days later, or 6 days late. The main factor contributing to the cause of this noncompliance was human error related to the management practice of workforce management. Specifically, the supervisor at issue failed to follow the company procedure for proactive revocation of access rights. The duration of this noncompliance is from the date RFC_URE7 was required to update the cyber access authorization list for the first instance of noncompliance, to the date RFC_URE7 revoked the access privileges for the employee in the second instance of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. As to the first instance of noncompliance, the employee’s access privileges were revoked in a timely manner and the only violation was a documentation issue. Furthermore, the error was identified and corrected within only four days. As to the second instance of noncompliance, even though the employee’s ID badge was not deactivated within 7 days, the ID badge was collected from the employee and no longer in his possession, which reduced the risk of any inadvertent or unauthorized use of the badge. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) Referred the supervisor’s failure to follow direction provided in annual training and quarterly awareness reminders to his manager for appropriate disciplinary action; 2) Sent targeted awareness message illustrating this situation and expected behaviors to current supervisors; and 3) Enhanced current manual process related to revocation requests sent proactively to set the expiration date in the Physical and/or Cyber Access Control Monitoring Systems as soon as a tentative revocation date is stated.
2015-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014132 | CIP-006-3c | R2; R2.2 | SPPRE_URE1 submitted a Self-Report stating that it had minimal risk instances of noncompliance with CIP-006-3c R2.2 by not affording the protective measures specified in CIP-003-3 R6, CIP-005-3 R3.2, CIP-007-3 R1.5.3, CIP-007-3 R5.2.3, and CIP-009-3 R1. CIP-003-3 R6: SPPRE_URE1 implemented an upgrade to its physical access control system (PACS) by installing a new sever and designating the original server as a backup without adherence to its change control process. As a result, the new server had not been subjected to security controls testing before it was introduced into the PACS. The duration of this instance of noncompliance was one day. The root cause of this instance of noncompliance was human error due to personnel not following SPPRE_URE1’s change control process. CIP-005-3 R3.2: Windows Event logs associated with an SPPRE_URE1 PACS workstation were maintained on the workstation itself; however, it was technically infeasible for the PACS to send the logs to the log collection server for alerting of attempts at or actual unauthorized access. As a result, SPPRE_URE1 was required to manually review the access logs for unauthorized attempts and actual unauthorized access to the PACS workstation, but such reviews had not been conducted. The duration of this instance of noncompliance was six (6) months. The root cause of this instance of noncompliance was a procedural gap of not requiring manual reviews of the access logs, when an automated alerting solution was not technically feasible. CIP-007-3 R5.1.3: The user accounts associated with the PACS were not reviewed annually for two years. Additionally, SPPRE_URE1 was unable to provide approval records for four SPPRE_URE1 personnel who were granted electronic access to the PACS via individual administrator application accounts residing on one of the PACS servers. The duration of this instance of noncompliance was for forty (40) months. The root causes of these instances of noncompliance were a lack of effective management controls to ensure that the annual reviews had been conducted and human error due to personnel not adhering to SPPRE_URE1’s approval process for access to its PACS. CIP-007-3 R5.2.3: Although SPPRE_URE1’s policy addressed management of shared user accounts, it did not include management of shared PACS accounts. As a result, SPPRE_URE1 was unable to provide an audit trail of the account usage for its PACS to demonstrate that it had been properly managing the use of the shared account by verifying that only authorized personnel accessed the account. The duration of this instance of noncompliance was twenty-nine (29) months. The root cause of this instance of noncompliance was a lack of effective user access management controls, which led to a procedural gap of not properly managing the track usage of the shared PACS account. CIP-009-3 R1: During a Compliance Audit, SPP RE discovered an additional minimal risk instance of noncompliance with CIP-006-3c R2.2 by not affording all the protective measures specified in CIP-009-3 R1. CIP-009-3 R1 requires SPPRE_URE1 to “create and annually review recovery plan(s) for Critical Cyber Assets.” Although SPPRE_URE1’s recovery plan included procedures to recover its PACS, the plan did not explicitly reference PACS to make it clear to personnel who would be responsible for activating the recovery procedures. The duration of this instance of noncompliance was twenty-nine (29) months. The root cause of this instance of noncompliance was a lack of effective physical security monitoring controls, which led to a procedural gap of not explicitly referring to PACS in the recovery plan. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CIP-003-3 R6: SPPRE_URE1 had a documented change control process. This was an isolated incident of not adhering to the process. CIP-005-3 R3.2: Although SPPRE_URE1’s PACS was not sending logs to the log collection servers, which was technically infeasible at the time, the logs were available on the PACS itself. Thus, had an event occurred, forensics would have been available for investigative purposes. The PACS was isolated from SPPRE_URE1’s other Cyber Assets inside the ESP, which further reduced any potential risk. CIP-007-3 R5.1.3: Although the accounts associated with the PACS were not reviewed annually for two years, all of the personnel with access were verified as appropriate during the the following review. SPPRE_URE1 was aware of all personnel with physical access to the PACS throughout the audit period. Regarding the four individuals in which no access authorization documentation could be produced, SPPRE_URE1 was aware that they had access because they were tasked with managing the access to the Physical Security Perimeter (PSP). For all four individuals, personal risk assessments and Cyber Security Training had been conducted, and they had been granted proper electronic access to other Critical Cyber Assets prior to this instance of improper access to the PACS. Thus, there was no risk introduced to the environment, as it was mearly a procedural oversight. CIP-007-3 R5.2.3: Logs showing when a shared account was being used were being captured by the PACS; however, the specific individuals using the account were not being formally tracked. If malicious activity had occurred on the PACS, SPPRE_URE1 would have been able to use the PSP access logs, personnel schedules, system event logs, and ask the 24/7 on-site personnel to determine who used the PACS. CIP-009-3 R1: Although the PACS system was not formally mentioned in SPPRE_URE1’s recovery plan, the PACS is fully backed up, with a redundant system at the backup site. Notwithstanding this deficiency, SPPRE_URE1 personnel responsible for the recovery of Critical Cyber Assets were familiar with the recovery plan procedures and would have implemented them to recover the PACS. Additionally, for all instances of noncompliance, SPPRE_URE1’s Cyber Assets were protected by a firewall specifically configured to allow only traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1 also used system logging to analyze network traffic at access points to the ESP for known and suspected malicious activity. Access to Critical Cyber Assets was limited to only those individuals with authorized physical and/or electronic access rights (absent the four individuals who were granted electronic access associated with the PACS). No actual harm is known to have occurred as a result of the noncompliance. | To mitigate these minimal risk instances of noncompliance for CIP-006-3c R2.2, SPPRE_URE1: 1) updated its change control procedure, instituted a change management application for documenting changes, and trained all affected personnel on the new procedure (CIP-003-3 R6); 2) configured the PACS system and log collection software to gather and monitor event logs, which will alert for attempts at, or actual, unauthorized access into the ESP (CIP-005-3 R3.2); 3) reviewed the PACS user accounts, updated them as necessary, and added the account review requirement to the CIP Compliance Calendar for future compliance (CIP-007-3 R1.5.3); 4) instituted a manual logging process to track PACS shared user account usage (CIP-007-3 R5.2.3); and 5) revised its recovery plan to explicitly reference PACS (CIP-009-3 R1). SPP RE has verified the completion of all mitigation activity.
2015-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014283 | CIP-006-3c | R1; R1.6.1 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had multiple minimal risk instances of noncompliance with CIP-006-3c R1.6.1. Although SPPRE_URE1 had a documented and implemented physical security plan, for a period of nine (9) months, the exit time for eight visitors was not documented in the logbooks associated with SPPRE_URE1’s primary and backup operating centers. The duration of this instance of noncompliance was 18 months. The root causes of these instances of noncompliance were the combination of human error due to personnel not adhering to SPPRE_URE1’s logging procedures and lack of effective internal controls to ensure such procedures were being strictly followed. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE1 was aware of all eight visitors who entered its operating centers, and all visitors were accompanied by escorts the entire time they were inside such areas. SPPRE_URE1 completed all sections of the logs except for the exit time for each visitor. No actual harm occurred as a result of the noncompliance. | To mitigate these minimal risk instances of noncompliance for CIP-006-3c R1.6.1, SPPRE_URE1: 1) retrained all affected personnel on the visitor logging procedures; and 2) reviewed and confirmed complete visitor logs since the date of the audit exit presentation. SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015246 | CIP-002-3 | R4 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-3 R4. URE Self-Reported that it did not have a signed and dated record of the CIP Senior Manager's annual approval of its risk-based assessment methodology (RBAM), the list of Critical Assets, or the list of Critical Cyber Assets (CCAs) for one year. The root cause of the noncompliance is that FRCC_URE1's CIP senior manager had delegated approval of the RBAM to the FRCC_URE1 compliance officer, however, the compliance officer departed the company prior to approving the document. The CIP senior manager then realized the document still needed approval, and performed that action approximately 50 days late. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The technical documentation for the RBAM, Critical Assets list, and CCAs list had been reviewed and updated, verifying that FRCC_URE1's list of Critical Assets (null) and list of CCAs (null) were unchanged. The URE CIP senior manager signed the documentation only approximately 50 days beyond which the approval should have occurred. With FRCC_URE1 not having any Critical Assets or CCAs, this a documentation issue as the entity has no CIP effect to the BPS based upon the application of its RBAM to its assets. No harm is known to have occurred. FRCC_URE1 has no relevant prior noncompliance with CIP-002-3 R4. | To mitigate this issue, FRCC_URE1's: 1) CIP senior manager signed and dated the RBAM, Critical Asset list, and CCA list; and 2) CIP senior manager created a scheduled task list, with key compliance deliverables and due dates, and made it available to the FRCC_URE1 compliance team.
2015-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013157 | CIP-006-3c | R1 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R1.6.2 because it failed to provide a continuous escort to a contractor in the Physical Security Perimeter (PSP). Specifically, an MRO_URE1 employee was providing an escort to a contractor who was located within the Backup Control Center (BUCC) PSP. This contractor had provided service to MRO_URE1 for multiple years, and was well known by MRO_URE1 staff. The MRO_URE1 employee received a telephone call from his supervisor and he left the room to answer the call in private, and because of poor cell reception in the BUCC. Per MRO_URE1, a few minutes into the phone call, the MRO_URE1 employee realized his error, terminated the phone call, and returned to the contractor. The cause of this issue was human error, as the employee apparently became too comfortable around the well known contractor, and did not apply the MRO_URE1's policies or the training that had been provided. The instance of noncompliance ended within a few minutes. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The duration of the noncompliance was limited to only a few minutes and the noncompliance was limited to one unescorted contractor who was well known to MRO_URE1. Further, even if the contractor did suddenly exhibit a malicious intent, his actions would have been limited to damaging back up equipment and he would not have been able to disable real time operations. No harm is known to have occurred. MRO considered MRO_URE1's CIP-006-3c R1 compliance history in determining the disposition track. MRO_URE1's relevant prior noncompliance with CIP-006-3c R1 include NERC Violation ID MRO2012010539 (CIP-006-1 R1). MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The prior violation related to MRO_URE1's failure to identify physical access points to the PSP and did not relate to the current instance of non-compliance which is limited solely to escorting a contractor within the PSP. Further, MRO_URE1 effectively mitigated the prior issue and the prior issue did not contribute to the current instance of noncompliance. Finally, MRO considered the short duration of the issue, MRO_URE1's prompt self-reporting and mitigation in determining the disposition of this instance of noncompliance. | To mitigate this issue, MRO_URE1: 1) Provided an escort to the contractor; 2) reprimanded the employee who left the contractor unattended and revoked the employee's PSP access; and 3) augmented the PSP training and completed the training for all applicable employees.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013613 | CIP-005-3a | R1.4 R1.5 | RFC_URE1 submitted two Self-Reports stating that it had an issue of CIP-005-3a R1.4, R1.5. In the Self-Report for CIP-005-3a R1.4, RFC_URE1 discovered an issue with CIP-005-3a R1.4 during a quarterly compliance touch point meeting. These meetings, which take the form of periodic compliance calls, force the station engineer and manager to talk with site-level and compliance supervisors and are tracked via a spreadsheet. As part of a mitigation plan, an printer was removed from an Electronic Security Perimeter (ESP). When the printer was removed from the ESP, an operational need for the printer still remained and RFC_URE1 lacked a program to support CIP compliance for the printer. While RFC_URE1 developed a program to support CIP compliance for the printer, the printer was stored inside a Physical Security Perimeter (PSP) until it could be reconnected. A controls vendor was onsite to perform an annual control system upgrade and a Cyber Vulnerability Assessment (CVA). During the visit from the vendor, the printer was connected to the control system via CAT 5 cabling without notice or authorization. Reconnecting the printer inside a PSP with CAT 5 cabling and without notice or authorization, instead of reconnecting the printer with a serial connection, caused the subject noncompliance. The compliance team was notified that the printer had been reinstalled. The next day, the printer was disconnected. One week later, the compliance team reconnected the printer using a serial connection reestablishing compliance with CIP-005-3 R2. The root cause of this noncompliance concerned the management practices of asset and configuration management and external interdependencies. Asset and configuration management was implicated because the printer at issue was not properly inventoried or monitored. External interdependencies was implicated because improved organizational processes that manage and train vendors could have helped prevent the vendor from reconnecting the printer without using a serial connection. The duration of this noncompliance is from the date RFC_URE1 reconnected the printer to the control system via CAT 5 cabling, to the date RFC_URE1 reconnected the printer using a serial connection. In the Self-Report for CIP-005-3a R1.5, RFC_URE1 identified an issue pertaining to the change control and configuration management of an electronic access point to an ESP. The RFC_URE1 Telecom team was informed that a substation was having problems with certain network traffic through the router. The next day, an engineer was onsite troubleshooting the ongoing errors with the router and determined that the router configuration was at fault. The engineer loaded a backup configuration to the router. The backup configuration did not contain controls that limited network access to the substation’s micro control panel. These missing controls allowed network access to the micro control panel from anywhere on the RFC_URE1 network. Approximately one month later, while opening a port on the router to allow IT to scan the micro control panel at the substation, an engineer noticed that the controls limiting network access were missing. A change ticket to reapply the controls to the router was entered that day and completed two weeks later. The root cause of this noncompliance concerned the management practice of access and configuration management. Asset and configuration management was implicated because the attributes of the router were not properly inventoried, configured, or maintained. The duration of this noncompliance is from the date RFC_URE1 uploaded a known good configuration that did not contain statements that applied the access control lists to the network interface to the router, to the date all access control lists were reapplied to the routers. | R1.4: This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At the time of and throughout the noncompliance, the printer was protected within the ESP and afforded all of the protections of a device residing within an ESP. After the printer was installed, a vulnerability assessment was performed that revealed no issues. No harm is known to have occurred. R1.5: This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The access control lists exist only to provide an extra layer of access control to devices at the site. At the time of the noncompliance, logical access controls on the routers in question would have prevented unauthorized persons from directly accessing the routers despite the fact that the router was opened to all of RFC_URE1’s internal network. The router also controls access to no NERC CIP CCAs. No misoperations, emergencies, or other adverse consequences occurred as a result of this noncompliance. No harm is known to have occurred. | To mitigate these issues, RFC_URE1: 1) developed a compliant solution for the station to use the printer by utilizing a serial connection to reconnect the printer; 2) implemented the compliant solution as it disconnected the printer from the controls network and reconnected the printer as a serially connected device; 3) updated its Critical Cyber Asset (CCA) inventory list; 4) reviewed its NERC CIP asset disposal and redeployment process with its team responsible for completing disposals and redeployments; 5) incorporated connection specifics, such that even if an item is on a CCA list, the item should not be re-connected or connected differently without CIP team involvement, into annual site training; 6) evaluated and determined the tools necessary to perform monitoring of configuration changes for the routers and will deploy those tools on the routers; 7) created and documented processes to manage configuration changes to the routers; 8) identified personnel in-scope for required training on the change control process and associated configuration management tool processes; 9) developed training for IT personnel that will train them on the change control process and educate them on the process for using the change management tool; and 10) provided training to certain in-scope personnel on the change control process and the associated configuration management process. ReliabilityFirst has verified the completion of all mitigatin activity.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014266 | CIP-006-3c | R1.6.1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1.6.1. RFC_URE1’s Physical Security Plan requires RFC_URE1 to have a visitor control program that addresses the logs CIP-006-3c R1.6.1 requires. Manual logs are to be used for persons without authorized access to the Physical Security Perimeter (PSP). RFC_URE1 further requires visitor logs to be used to document the entry and exit of visitors, including the date and time, to and from the PSPs and that designated escorts sign in their visitors using the visitor log book provided at each PSP at the beginning of their work day and at the conclusion of their work scope or work day, whichever comes first. Two new employees were at RFC_URE1’s Center (the Center) for training. The two employees’ training required a tour of the Center as their jobs require them to access that location. A trainer, who had authorized access to the Center’s PSP, met the two employees outside of the PSP, and the trainer entered the PSP by scanning his employee badge. The two new employees entered the PSP area directly behind the trainer by also scanning their badges. The new employees’ badges scanned active meaning a green light appeared when they scanned their badges. The two new employees were escorted by the trainer throughout their time in the PSP area. The two new employees tried to re-enter the PSP area the next day by scanning their badges, but their badges did not work. After this, the two new employees went back to their supervisor who confirmed that the employees’ access had not yet been cleared. RFC_URE1’s Physical Access Control Systems (PACS) recorded and logged the two employees’ badge scans both days as invalid attempts. Although logged as invalid on the first day, the two new employees’ badges scanned active that day. After completing their required training and personnel risk assessments, access to the Center’s PSP was granted to the two new employees. The root cause of this noncompliance concerned the management practices of verification, validation, and workforce management. Verification was implicated because RFC_URE1 did not immediately verify the cause of the invalid badge access attempts and did not take immediate corrective action. Validation was implicated because the badge scanner scanned the two new employees’ badges as active incorrectly. Workforce management was implicated because the trainer and two new employees were not properly trained on how to enter the PSP. The duration of this noncompliance is from the date two new employees without authorized access first entered the PSP without their visitor access being logged on the visitor book, to the date both new employees had their access to the PSP in question granted. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The trainer provided continuous escorted access to the two new employees during their entire time at the Center’s PSP. Although RFC_URE1’s PACS did not properly alert that the first access attempts by the two new employees were invalid, RFC_URE1’s PACS recorded and logged the two employees’ badge scans as invalid attempts and tracked their entrance to and from the Center’s PSP. The two new employees were continuously monitored by the trainer for their entire time inside the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) reviewed the cause of the invalid entry scans for the two unauthorized badges, addressed that cause, and ensured that the PACS will prevent such invalid entry attempts in the future; 2) documented the two employees’ access to the Center PSP; 3) provided the required cyber security training to the two employees, and both completed this training; 4) requested personnel risk assessments for the two employees, one was completed five days later and the other was completed twelve days later; 5) authorized and granted unescorted physical access to the PSP for the two employees; 6) reviewed to verify and ensure that security awareness information on visitor control and management is current, correct, and available for management reinforcement. RFC_URE1 will update the security awareness information if necessary and will send this information to individuals, including those without CIP access, in the distribution coordination group; 7) conducted a counseling/coaching session with the involved RFC_URE1 employees to discuss the issue and reinforce visitor control procedures, specifically the no tailgating rule, and visitor management expectations; and 8) reviewed to verify and ensure that the cyber security training includes a section on completing visitor logs, how to properly scan access cards and enter a PSP, and information on how tailgating into PSPs is prohibited. ReliabilityFirst has verified the compleiton of all mitigation activity.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013614 | CIP-006-3c | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R4. During RFC_URE1’s re-badging project at its Operations Center (the Center), RFC_URE1’s Security Command Center received and responded to 13 unauthorized access attempt alarms. As part of the response, the Security Command Center started an investigation to identify and resolve the issue. The investigation revealed that during the re-badging project two employees had their access swapped meaning each employee’s access was incorrectly assigned to the other employee’s badge. When Employee A, who was supposed to have authorized access, attempted to return to his work area within a NERC Protected Space, his badge would not allow him access. Employee A continued to attempt to gain access and these attempts triggered the unauthorized access alarm. As a result of the alarm, Employee A sent in a copy of his badge to validate his access and the Security Command Center discovered the badge identification number printed on Employee A’s badge was correct, but did not match the badge identification number recorded in the software. Employee A’s badge identification number was recorded as belonging to Employee B and further investigation revealed that the badge identification number for Employee B was recorded in the software as belonging to Employee A. The Security Command Center corrected the issue in the software system by assigning the correct badge identification numbers to the correct employees. The root cause of this noncompliance concerned the management practices of verification and validation. Verification was implicated because the badge identification numbers were assigned to the wrong employee in the software system. Validation was implicated because RFC_URE1 did not ensure that each employees’ badge worked correctly. The duration of this noncompliance is from the date the employees’ badge identification numbers were switched, to the date RFC_URE1 reassigned the correct badge identification numbers to the correct employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The employee with improper access had it for a short amount of time, less than 24 hours, and both employees were not aware of the improper access. The rebadging project was a one time, corporate wide project related to RFC_URE1’s merger to consolidate badging systems across the new company and the project required all company badges to be remade. The size and scope of the rebadging project increased the likelihood that an error in assigning new badges would occur. Lastly, a review of badging access records indicated that Employee B did not attempt to access any NERC protected areas. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) corrected the badge access rights for both employees; 2) reviewed the current physical access badge creation processes and determined where improvements can be made for badge validation steps; 3) implemented enhanced validation checks to ensure that all information being entered for new badges is correct for the individual receiving the badge; and 4) undertook awareness efforts for those with rights to create badge access within the Physical Access Control Systems to ensure that enhanced validation steps are properly understood and implemented. ReliabilityFirst has verified the completion of all mitigation activity.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014542 | CIP-006-3c | R8 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R8. RFC_URE1 discovered that when it intended to remove the Generation Physical Security Perimeter (PSP) for one of its substations from its maintenance and testing program, it inadvertently removed the Transmission PSP for that substation from its maintenance and testing schedule. This error resulted in RFC_URE1 missing the maintenance and testing for the substation’s Transmission PSP. During preparation of the mitigation plan for this missed maintenance and testing, RFC_URE1 discovered a second incident where it missed maintenance and testing. In this instance a second substation was scheduled to have maintenance and testing for a PSP completed, but maintenance and testing was performed for the wrong PSP at that substation. This error resulted in RFC_URE1 missing the maintenance and testing at one of the substation’s PSPs. The root cause of this noncompliance concerned the management practices of validation and verification. Validation was implicated because the process used to assign maintenance and testing for substations lacked effective oversight and checks to ensure errors in assigning maintenance and testing to the proper substation did not occur. Verification was implicated because maintenance and testing schedules for substations were not properly inventoried or monitored. The duration of this noncompliance is from the date RFC_URE1 was scheduled to complete the maintenance and testing at the first substation, to the date RFC_URE1 completed the overdue maintenance and testing for both substations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At the time of the instant noncompliance, the first substation’s Transmission PSP had two Critical Cyber Assets (CCAs) and both CCAs were remote terminal units. Throughout the noncompliance, the substation was secured and monitored on a constant basis. Additionally, RFC_URE1’s access control system was operating as designed and this was validated by operational testing that was performed. There were no misoperations, emergencies, or other adverse consequences to the Bulk Power System as a result of this noncompliance. RFC_URE1 discovered and remediated this missed maintenance and testing quickly, in a little more than a month, with an informal walk down of the substation occurring within 12 days of discovery. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) performed the maintenance and testing for the first substation; 2) performed the maintenance and testing for the second substation; 3) performed an audit of the existing maintenance and testing schedule to ensure all NERC CIP sites are listed and dates are accurate; 4) updated the existing 2 EPS procedural documents that support CIP-006-3c R8 to remove outdated information and incorporate current processes; 5) redesigned the maintenance and testing tracking spreadsheet to include additional information needed for tracking and coordination with the Business Units such as PSP names, region information, field device information, and site points of contact; 6) retired and replaced legacy/local procedures with new enterprise-wide procedures to ensure consistency in performing CIP-006-3c R8 maintenance and testing; and 7) retired the existing maintenance and testing checklist and revised the existing version to meet the requirements of the new enterprise-wide procedures and compliance with CIP-006-3c R8.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015280 | CIP-006-3c | R5 | RFC_URE2 submitted a self-log stating that it had an issues of CIP-006-3c R5. A Security Operations Center (SOC) operator inadvertently unlocked the main door of a substation, a CIP substation. The SOC operator received a routine request to have the main door unlocked at a second station, a non-CIP substation. The SOC operator followed the RFC_URE2 procedure for this situation, but inadvertently selected the first substation in the access control system. The first substation is alphabetically one item below the second station, and the SOC operator mistakenly clicked it. The SOC operator received a second call from the individual requesting the unlocking of the second station, informing him that the station was not unlocked. The SOC operator stated "oh, it must not have saved" and unlocked the second station. RFC_URE2 discovered that the first station door was unlocked when an authorized RFC_URE2 employee called the SOC and informed the operator that the reader on the main door at the first station was green and the door was unlocked. The SOC checked the access control system, discovered that the door was unlocked, and immediately locked the door. While the door was unlocked, a card would not be required. The doors electric strike was engaged, leaving the door open. However, unless an individual first pulled on the door before swiping they would not have known it was unlocked. Normal operation is swipe first, then pull. Regardless, the door was unlocked to the control house. Additionally, during the time that this door was unlocked, the door alarm for both the primary and secondary system were not functioning such that the SOC would not receive an alarm indicating a door was opened by an unauthorized person. After the incident, RFC_URE2 ran a badge history report for the first station for thirty-two hours from the time the main door was unlocked and the only results was for the individual who reported the unlocked door. In addition, a review of the station entry logs does not show anyone logging into the first station other than that individual on the day of the discovery. The SOC received no Gate or Fence alarms for the first Station during the time the door to the control house was mistakenly unlocked. The duration of this issue is from the date RFC_URE2 inadvertently unlocked the main door to a CIP substation to the date RFC_URE2 remediated this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the relaibility of the bulk power system based on the following factors. First, the employee has approved CIP access. Second, the corporate laptop has protections in place, such as anti-virus and anti-malware software, which protect against infection. Third, this incident would not qualify as a compliance incident under Version 5 of the CIP Standards, reducing the likelihood that it is an incident that would impact grid reliability. While CIP v5 is not valid in determining whether this is a violation or not, it can help provide a framework for evaluating risk since it's aiming to improve grid reliability by reducing risk. In that sense, RFC_URE2 believes a comparison of current practices in relation to CIP v5 (good or bad) can be helpful to determine whether we are heading the right direction in reducing risk. As a result, the likelihood of compromise based on this error is low. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) required three-way communication refresher training for all operators; and 2) reminded operators to not end the call until receiving confirmation that the door is unlocked.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015281 | CIP-006-3c | R2.2 | RFC_URE2 submitted a self-log stating that it had a minimal risk instance of noncompliance with CIP-006-3c R2.2. Regional Entity requested a list of local user accounts with their enabled/disabled status and password age on a subset of Cyber Assets. RFC_URE2 invoked its internal compliance incident process to understand the extent to which CIP‐007 R5.3.3 was potentially violated. At the time, RFC_URE2 found enabled local accounts with passwords more than 15 months old on four servers but decided to defer the investigation until completion of the CIP audit. IT’s Compliance and Risk Services team opened the investigation and discovered two of the servers specified in Regional Entity’s original request had since been retired while two remained deployed. Both are classified as physical access control system (PACS) servers and support software used for physical security. Both were assessed for compliance with the CIP-007 R5.3.3 requirement to change account passwords “at least annually”. Thirteen accounts were found where the date of the last password change was more than 15 months. Twelve accounts are process-IDs used by systems or processes necessary for PACS operations. One account is a user-ID. The user-ID's password was changed several days after discovery. The violation was caused by human performance errors. The duration of this issue is from the date the passwords should have been changed, to the date CIP version 5 becomes effective (and this noncompliance will not be an issue under CIP version 5). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because of a number of factors, including: - All but 2 of the accounts could not be accessed remotely. As such, a user would have to be inside the Physical Security Perimeter (PSP) to use them -- which means they would either have authorized unescorted access or be escorted. - Had any of these accounts been logged into (something that is not done by individuals as they were process ID accounts), there are detective controls in place that would have generated alerts to security personnel to investigate. No harm is known to have occurred. | To mitigate this issue, RFC_URE2 will complete the following mitigation activities by April 1, 2016: 1) Process-ID passwords are not forced to expire to avoid PACS disruptions. User-ID passwords are forced to expire every 12 weeks. Password changes are required before a subsequent login attempt would be successful; 2) Controls prevent process-ID misuse. Eleven of twelve process-IDs are incapable of individual, remote login. While one process-ID (ppadmin) has this capability, it exists to support PACS operations, not individual use. Twelve process-IDs can be used by individuals for local login. These individuals are responsible for PACS application and operating system administration; 3) Controls also detect process-ID misuse. All server login attempts are logged and monitored and the IT Security team would be alerted following a login attempt with a process-ID. A review of server and monitoring logs found no evidence of attempted or actual misuse with any of the twelve process-IDs noted above; and 4) The user-ID is owned by an individual responsible for administering the PACS servers’ operating system software. As described above, since the user-ID password expired, subsequent login attempts would only be successful following a password change. Nonetheless, the user-ID password was changed several days after discovery.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015179 | CIP-007-3a | R2.3 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R2.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE3 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-007-3a R2.3, the date RFC_URE3 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE3 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE3 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015180 | CIP-007-3a | R2.3 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-3a R2.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE4 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-007-3a R2.3, to the date RFC_URE4 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE4 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE4 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE4 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015181 | CIP-007-3a | R2.3 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R2.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE5 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-3a R2.3, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE5 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE5 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015182 | CIP-007-3a | R4 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R4. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE3 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-007-3a R4, to the date RFC_URE3 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE3 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE3 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015183 | CIP-007-3a | R4 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-3a R4. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE4 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-007-3a R4, to the date RFC_URE4 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE4 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE4 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE4 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015184 | CIP-007-3a | R4 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R4. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE5 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-3a R4, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE5 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE5 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015185 | CIP-007-3a | R5.3 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R5.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE3 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-007-3a R5.3, to the date RFC_URE3 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE3 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE3 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015186 | CIP-007-3a | R5.3 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-3a R5.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE4 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-007-3a R5.3, to the date RFC_URE4 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE4 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE4 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE4 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015187 | CIP-007-3a | R5.3 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R5.3. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE5 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-3a R5.3, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE5 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE5 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015188 | CIP-007-3a | R6 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-3a R6. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE3 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-007-3a R6, to the date RFC_URE3 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE3 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE3 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015189 | CIP-007-3a | R6 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-3a R6. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE4 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-007-3a R6, to the date RFC_URE4 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE4 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE4 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE4 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015190 | CIP-007-3a | R6 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R6. As a result of initial discrepancies identified during a year-end review of Technical Feasibility Exception (TFE) documentation and 2014 Cyber Vulnerability Assessment results, RFC_URE5 initiated a comprehensive review of its CIP devices and related TFEs. This review identified: (i) devices in production that were not included in existing TFE counts; and (ii) devices that were included in existing TFE counts, but that had since been removed/decommissioned and therefore no longer required TFE protections. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-3a R6, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was determined to be a lack of streamlined processes for amending TFE device counts once a new device is commissioned or existing device is decommissioned, resulting in human error when communicating such changes and manually updating internal TFE documentation to account for such changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While certain devices were not documented under a TFE, compensating and mitigating measures (CMM) were in place. The issue identified is one of maintaining accurate documentation of TFE device counts, and did not impact CMM or justifications. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 performed a comprehensive review of its devices and related TFEs. TFE device counts have now been corrected, and material change reports were updated to align with the devices that require TFE protections. All affected TFEs will be amended to reflect accurate device counts on internal documentation; and for those TFEs transitioning through to CIP version 5, the updated TFEs (including updated device counts) will be submitted to ReliabilityFirst. Moreover, as RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to reviewing and improving upon its TFE tracking processes to ensure that device changes are accurately communicated and captured in corresponding TFE documentation. Additionally, RFC_URE5 commits to performing all appropriate personnel training on the updated processes. This training will ensure that RFC_URE5 employees responsible for tracking TFEs under version 5 will have full knowledge and awareness of the relevant requirements and of the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015194 | CIP-006-3c | R1.6 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-006-3c R1.6. The NERC Compliance Office was notified of a possible escorting issue in one of its Physical Security Perimeters (PSP). An investigation revealed that a new contractor was not properly escorted and logged, in accordance with RFC_URE3’s PSP visitor control program. During the contractor’s first week, before the contractor had completed the required NERC training and was granted authorized unescorted physical access, the contractor was required to be logged on the PSP specific log sheet and continuously escorted while going to and from the office area located within the PSP. A review of the PSP log sheets for that week indicated: (i) 3 days where the exit time of the contractor was not entered, and (ii) 2 days where there was no entry for the entire work day. Further investigation determined that in the first instance the contractor was allowed to exit the PSP on his own at the end of the work day, and therefore was not properly logged out or monitored by the escort upon exit. In the second instance, there was confusion with the escort on those particular days as to which log was required for PSP entry. The building which holds the PSP also requires visitors to show ID and log into the general access log in order to gain access to the general work area. On these particular 2 days, the general access log was used as opposed to the PSP specific access log. The contractor completed the required NERC training and was subsequently granted unescorted physical access two days later . The contractor had a valid personnel risk assessment (PRA) on file at the time he began work. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-006-3c R1.6, to the date the contractor was granted unescorted physical access. The root cause of the issue was ineffective training as the new contractor's escort did not fully understand how to properly log the new contractor's entrance into and exit from the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contractor had a valid personnel risk assessment on record and the work for which he was hired required access to the office area within the PSP. Moreover, while the office area where the contractor worked was located within the PSP, the PSP areas that hold CIP assets are protected by additional doors that require key card access, which this individual did not have. Accordingly, the contractor never gained access to any protected CIP assets within the PSP. Finally, after the contractor completed his required NERC training, he was ultimately granted authorized unescorted physical assess to the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) interviewed all individuals involved in the incident and made them clearly aware of their failure to follow process; 2) retrained on the logging and escorting requirements in the visitor control program; and 3) issued a notification to all personnel with authorized unescorted physical access reinforcing their PSP visitor access and escorting responsibilities. As RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to performing all appropriate personnel training on the updated procedures, including the visitor control program. This training will ensure that the RFC_URE3 employees responsible for implementation of the version 5 visitor control program will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. Moreover, in accordance with the version 5 program, the company will continue providing appropriate communications designed to periodically reinforce RFC_URE3’s visitor control procedures with responsible personnel.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015195 | CIP-006-3c | R1.6 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-006-3c R1.6. The NERC Compliance Office was notified of a possible escorting issue in one of its Physical Security Perimeters (PSP). An investigation revealed that a new contractor was not properly escorted and logged, in accordance with RFC_URE4’s PSP visitor control program. During the contractor’s first week, before the contractor had completed the required NERC training and was granted authorized unescorted physical access, the contractor was required to be logged on the PSP specific log sheet and continuously escorted while going to and from the office area located within the PSP. A review of the PSP log sheets for that week indicated: (i) 3 days where the exit time of the contractor was not entered, and (ii) 2 days where there was no entry for the entire work day. Further investigation determined that in the first instance the contractor was allowed to exit the PSP on his own at the end of the work day, and therefore was not properly logged out or monitored by the escort upon exit. In the second instance, there was confusion with the escort on those particular days as to which log was required for PSP entry. The building which holds the PSP also requires visitors to show ID and log into the general access log in order to gain access to the general work area. On these particular 2 days, the general access log was used as opposed to the PSP specific access log. The contractor completed the required NERC training and was subsequently granted unescorted physical access two days later . The contractor had a valid personnel risk assessment (PRA) on file at the time he began work. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-006-3c R1.6, to the date the contractor was granted unescorted physical access. The root cause of the issue was ineffective training as the new contractor's escort did not fully understand how to properly log the new contractor's entrance into and exit from the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contractor had a valid personnel risk assessment on record and the work for which he was hired required access to the office area within the PSP. Moreover, while the office area where the contractor worked was located within the PSP, the PSP areas that hold CIP assets are protected by additional doors that require key card access, which this individual did not have. Accordingly, the contractor never gained access to any protected CIP assets within the PSP. Finally, after the contractor completed his required NERC training, he was ultimately granted authorized unescorted physical assess to the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE4: 1) interviewed all individuals involved in the incident and made them clearly aware of their failure to follow process; 2) retrained on the logging and escorting requirements in the visitor control program; and 3) issued a notification to all personnel with authorized unescorted physical access reinforcing their PSP visitor access and escorting responsibilities. As RFC_URE4 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures, including the visitor control program. This training will ensure that the RFC_URE4 employees responsible for implementation of the version 5 visitor control program will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. Moreover, in accordance with the version 5 program, the company will continue providing appropriate communications designed to periodically reinforce RFC_URE4’s visitor control procedures with responsible personnel.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015196 | CIP-006-3c | R1.6 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-006-3c R1.6. The NERC Compliance Office was notified of a possible escorting issue in one of its Physical Security Perimeters (PSP). An investigation revealed that a new contractor was not properly escorted and logged, in accordance with RFC_URE5’s PSP visitor control program. During the contractor’s first week, before the contractor had completed the required NERC training and was granted authorized unescorted physical access, the contractor was required to be logged on the PSP specific log sheet and continuously escorted while going to and from the office area located within the PSP. A review of the PSP log sheets for that week indicated: (i) 3 days where the exit time of the contractor was not entered, and (ii) 2 days where there was no entry for the entire work day. Further investigation determined that in the first instance the contractor was allowed to exit the PSP on his own at the end of the work day, and therefore was not properly logged out or monitored by the escort upon exit. In the second instance, there was confusion with the escort on those particular days as to which log was required for PSP entry. The building which holds the PSP also requires visitors to show ID and log into the general access log in order to gain access to the general work area. On these particular 2 days, the general access log was used as opposed to the PSP specific access log. The contractor completed the required NERC training and was subsequently granted unescorted physical access two days later . The contractor had a valid personnel risk assessment (PRA) on file at the time he began work. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-006-3c R1.6, to the date the contractor was granted unescorted physical access. The root cause of the issue was ineffective training as the new contractor's escort did not fully understand how to properly log the new contractor's entrance into and exit from the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contractor had a valid personnel risk assessment on record and the work for which he was hired required access to the office area within the PSP. Moreover, while the office area where the contractor worked was located within the PSP, the PSP areas that hold CIP assets are protected by additional doors that require key card access, which this individual did not have. Accordingly, the contractor never gained access to any protected CIP assets within the PSP. Finally, after the contractor completed his required NERC training, he was ultimately granted authorized unescorted physical assess to the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE5: 1) interviewed all individuals involved in the incident and made them clearly aware of their failure to follow process; 2) retrained on the logging and escorting requirements in the visitor control program; and 3) issued a notification to all personnel with authorized unescorted physical access reinforcing their PSP visitor access and escorting responsibilities. As RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures, including the visitor control program. This training will ensure that the RFC_URE5 employees responsible for implementation of the version 5 visitor control program will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. Moreover, in accordance with the version 5 program, the company will continue providing appropriate communications designed to periodically reinforce RFC_URE5’s visitor control procedures with responsible personnel.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015197 | CIP-007-3a | R6 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-3a R6. While testing a server solution that concentrates and stores syslog data, RFC_URE5 identified a switch that was not sending local login messages. Further system review found that there were a total of 7 switches within the Electronic Security Perimeter that were not logging local login success/failures. It was also determined that 1 additional switch that was removed from service three months earlier was also not properly configured to log local login success/failures while that device was in service. For all of these switches, remote login attempts are properly captured, monitored and alerted via software. Accordingly, the issue here is specific to logs for local account access. Remote login is the more common of the two methods (local versus remote) by which the switches at issue are accessed. A review of the device documentation determined that at the time of commissioning, remote login success/failures were tested and verified, but human error played a part in not thoroughly identifying the necessity to setup and test logging for local access attempts. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-3a R6, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was an oversight in the initial procedure development as the 7 switches within the ESP were not checked to ensure that they were logging local login successes/failures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Attempts to login to these devices locally require physical access to the secure Physical Security Perimeters (PSPs) in which these devices reside. To gain unauthorized physical access, a person would have to bypass the security desk, and then breach several additional layers of secured, alarmed doors without being detected. Moreover, since these protected areas are active working areas with authorized RFC_URE5 personnel constantly on alert and working therein, the likelihood of an unauthorized individual going undetected in the PSP is highly unlikely. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 immediately configured the 7 switches to log local login success/failure attempts. The 1 additional device had been already removed from service before the issue was identified. Moreover, since the time these devices were first commissioned, substantial program improvements have been made with the implementation of tests for purposes of ensuring that CIP devices in production are appropriately logging both locally and remotely (as applicable) upon commissioning. Additionally, as RFC_URE5 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the logging requirements of CIP-007-5 R4.1. This training will ensure that the RFC_URE5 employees responsible for commissioning new devices into production have full knowledge and awareness of the relevant version 5 logging requirements and the processes in place to achieve compliance with those requirements. Moreover, in accordance with the version 5 program, the company will continue providing appropriate communications designed to periodically reinforce RFC_URE5’s compliance program with responsible personnel.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015198 | CIP-006-3c | R6 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-006-3c R6. Five RFC_URE3 technicians were dispatched to a substation Physical Security Perimeter (PSP) to perform certain field maintenance tasks. All 5 individuals had authorized unescorted physical access rights to the PSP. However, 2 of the individuals (who were let into the PSP by the 3 individuals that preceded them and that had correctly swiped their respective access badges upon entry) failed to swipe their access badges upon entry into PSP. Specifically, one of individuals swiped his badge upon exit, and the other did not swipe upon entry or exit. Accordingly, as a result of personnel failure to follow process, these 2 individuals were not appropriately logged into the physical access logging system at the time of access into the PSP. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-006-3c R6, to the date RFC_URE3 logged the two individuals entrance and exit from the PSP into the physical access logging system later on in the day. The root cause of the issue was ineffective training as the 2 individuals did not follow RFC_URE3's documented process to badge into and out of a PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP doorway is fitted with badge controlled locks and is alarmed to prevent access by unauthorized individuals. In this instance, the individuals all had authorized unescorted physical access rights to the PSP (including valid personnel risk assessments and requisite NERC training), and they all had a valid work reason to be at the PSP. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) interviewed all individuals involved in the incident and made them clearly aware of the failure to follow process; 2) retrained on the PSP physical access requirements and logging procedures; and 3) notification was also issued to all personnel with authorized unescorted physical access reinforcing their PSP access and logging responsibilities. As RFC_URE3 continues to transition to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE3 commits to performing all appropriate personnel training on the updated procedures, including PSP entry and logging requirements. This training will ensure that the RFC_URE3 employees responsible for activities in accordance with version 5 will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. Moreover, in accordance with the version 5 program, the company will continue providing appropriate communications designed to periodically reinforce RFC_URE3’s PSP entry and logging policies.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015199 | CIP-007-1 | R5.2.2 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-007-1 R5.2.2. A RFC_URE3 internal audit found that certain local shared accounts and personnel with access to those accounts may not have been appropriately tracked as required under CIP-007-3a, R5.2.2. Further investigation into the issue identified 34 device types for which local shared accounts are enabled and necessary. Of the 34 device types, 4 device types and their associated shared accounts were not captured on the master account tracking list. Specifically, these included 3 relay and 1 data device types. Additionally, for 16 device types, while the devices themselves were captured on the master account tracking list, the enabled local shared accounts associated with these devices were not. These devices included a combination of relays, remote terminal units, and switches. Given that these devices and/or shared accounts associated with these devices had not been identified on the master account tracking list, personnel with access to these accounts and their access levels similarly were not identified. This oversight was determined to be the result of human error in the manual maintenance of the list used to track these accounts. The duration of this issue is from the date RFC_URE3 was required to comply with CIP-007-1 R5.2.2, to the date RFC_URE3 completed its Mitigating Activities. The root cause of the issue was human error in the manual maintenance of the list used to track these accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of all individuals with access to the local shared accounts in question were determined to have satisfied pre-requisites for authorized electronic access and were granted unescorted physical access to the associated devices, including valid personnel risk assessments and requisite NERC training. Moreover, attempts to login to these devices via the local shared accounts require approved physical access to the secure Physical Security Perimeters in which these devices reside. No harm is known to have occurred. | To mitigate this issue, RFC_URE3 updated the master account tracking list to include the local shared accounts identified and the specific personnel with authorized access. As part of the on-going transition efforts, RFC_URE3 commits to reviewing and improving upon its shared account tracking procedures in order to comply with version 5 of CIP Reliability Standards. Additionally, RFC_URE3 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that RFC_URE3 employees responsible for implementing shared accounts tracking under version 5 will have full knowledge and awareness of the relevant requirements, and the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015200 | CIP-007-1 | R5.2.2 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-1 R5.2.2. A RFC_URE4 internal audit found that certain local shared accounts and personnel with access to those accounts may not have been appropriately tracked as required under CIP-007-3a, R5.2.2. Further investigation into the issue identified 34 device types for which local shared accounts are enabled and necessary. Of the 34 device types, 4 device types and their associated shared accounts were not captured on the master account tracking list. Specifically, these included 3 relay and 1 data device types. Additionally, for 16 device types, while the devices themselves were captured on the master account tracking list, the enabled local shared accounts associated with these devices were not. These devices included a combination of relays, RTUs, and switches. Given that these devices and/or shared accounts associated with these devices had not been identified on the master account tracking list, personnel with access to these accounts and their access levels similarly were not identified. This oversight was determined to be the result of human error in the manual maintenance of the list used to track these accounts. The duration of this issue is from the date RFC_URE4 was required to comply with CIP-007-1 R5.2.2, to the date RFC_URE4 completed its Mitigating Activities. The root cause of the issue was human error in the manual maintenance of the list used to track these accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of all individuals with access to the local shared accounts in question were determined to have satisfied pre-requisites for authorized electronic access and were granted unescorted physical access to the associated devices, including valid personnel risk assessments and requisite NERC training. Moreover, attempts to login to these devices via the local shared accounts require approved physical access to the secure Physical Security Perimeters in which these devices reside. No harm is known to have occurred. | To mitigate this issue, RFC_URE4 updated the master account tracking list to include the local shared accounts identified and the specific personnel with authorized access. As part of the on-going transition efforts, RFC_URE4 commits to reviewing and improving upon its shared account tracking procedures in order to comply with version 5 of CIP Reliability Standards. Additionally, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that RFC_URE4 employees responsible for implementing shared accounts tracking under version 5 will have full knowledge and awareness of the relevant requirements, and the processes in place to achieve compliance with those requirements.
2015-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015201 | CIP-007-1 | R5.2.2 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-1 R5.2.2. A RFC_URE5 internal audit found that certain local shared accounts and personnel with access to those accounts may not have been appropriately tracked as required under CIP-007-3a, R5.2.2. Further investigation into the issue identified 34 device types for which local shared accounts are enabled and necessary. Of the 34 device types, 4 device types and their associated shared accounts were not captured on the master account tracking list. Specifically, these included 3 relay and 1 data device types. Additionally, for 16 device types, while the devices themselves were captured on the master account tracking list, the enabled local shared accounts associated with these devices were not. These devices included a combination of relays, RTUs, and switches. Given that these devices and/or shared accounts associated with these devices had not been identified on the master account tracking list, personnel with access to these accounts and their access levels similarly were not identified. This oversight was determined to be the result of human error in the manual maintenance of the list used to track these accounts. The duration of this issue is from the date RFC_URE5 was required to comply with CIP-007-1 R5.2.2, to the date RFC_URE5 completed its Mitigating Activities. The root cause of the issue was human error in the manual maintenance of the list used to track these accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A review of all individuals with access to the local shared accounts in question were determined to have satisfied pre-requisites for authorized electronic access and were granted unescorted physical access to the associated devices, including valid personnel risk assessments and requisite NERC training. Moreover, attempts to login to these devices via the local shared accounts require approved physical access to the secure Physical Security Perimeters in which these devices reside. No harm is known to have occurred. | To mitigate this issue, RFC_URE5 updated the master account tracking list to include the local shared accounts identified and the specific personnel with authorized access. As part of the on-going transition efforts, RFC_URE5 commits to reviewing and improving upon its shared account tracking procedures in order to comply with version 5 of CIP Reliability Standards. Additionally, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that RFC_URE5 employees responsible for implementing shared accounts tracking under version 5 will have full knowledge and awareness of the relevant requirements, and the processes in place to achieve compliance with those requirements.
2015-11-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015043 | CIP-002-3 | R3 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R3. SERC_URE1 failed to properly identify all Critical Cyber Assets (CCAs) essential to the operation of the Critical Assets. During a mock audit conducted by an external third party, the mock auditors identified workstations that were identified as non-CCAs that should have been considered CCAs due to their ability to facilitate control through the energy management system (EMS). These workstations were used as ancillary workstations for training or by support staff and non-operators for read-only data analysis. However, the workstations did have the ability to initiate EMS control if personnel with proper operator user IDs, credentials, and permissions logged onto the workstations. Over a period of approximately three years, SERC_URE1 transmission department incorrectly classified approximately 15% of its Cyber Assets as non-CCAs within the Electronic Security Perimeter (ESP), and over a period of approximately two years and one month, the generation department incorrectly classified approximately 5% of its Cyber Assets as non-CCAs within the ESP. All Cyber Assets at issue should have been considered CCAs due to their ability to initiate EMS control. The root-cause of this issue was that during the process of re-interpreting the definition of “essential to the operation of the Critical Asset,” SERC_URE1’s subject matter experts relied on an outside consultant’s guidance based on a NERC approved interpretation that FERC had not approved. This issue lasted approximately three years and two months from when SERC_URE1 first removed workstations from the CCA list through when SERC_URE1 updated the CCA list to include the workstations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to include all Cyber Assets that had the ability to control and operate Critical Assets as CCAs could have permitted these Cyber Assets to be overlooked or misused. However, SERC_URE1 originally treated all the workstations as CCAs and protected them as such and continued to protect the workstations during the duration of the violation. The workstations at issue were not primary operator workstations, and although having the ability to initiate control if an authorized user had logged in, SERC_URE1 did not consider or use the workstations as operator workstations. All the workstations at issue were secured with an established ESP and Physical Security Perimeter with logging and monitoring enabled. The workstations at issue were within control centers which were staffed twenty-fours per day/seven days a week. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-002 R3 compliance history in determining the disposition track. SERC determined that SERC_URE1's compliance history should not serve as a basis for aggravating the penalty. Although the issues involved the same Standard and Requirement, the underlying conduct of the prior instance was different than the instant issue. The original Mitigation Plan and actions taken for the original CIP-002-1 R3 violation would not have prevented this occurrence. | To mitigate this issue, SERC_URE1: 1) updated the EMS CCA and Non-CCA list to properly identify the workstations as CCAs; 2) updated multiple checklists utilized in identifying and determining cyber assets related to Critical Assets to include or reference the criteria supplied in the NERC Guidance for Identifying Critical Cyber Assets; and 3) utilized the criteria supplied in the NERC Guidance for Identifying Critical Cyber Assets to re-evaluate all cyber assets identified on the CCA and Non-CCA list and confirmed the identification of CCAs and Non-CCAs.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014281 | CIP-005-3a | R1; R1.5, R1.6 | During a Compliance Audit , SPP RE determined that SPPRE_URE1 had minimal risk instances of noncompliance with CIP-005-3a, two instances of noncompliance with R1.5 and one instance of noncompliance with R1.6. CIP-005-3a R1.5 – Instance Number One SPPRE_URE1 was utilizing one demilitarized zone (DMZ) firewall and one server for electronic access control and monitoring (EACM) of its Electronic Security Perimeter (ESP). SPPRE_URE1’s server was a virtual machine (VM) running on a VM cluster with three additional VM servers. These four VM servers shared one physical server. SPPRE_URE1 managed the DMZ firewall and one VM server. The physical server and three of the VM servers were utilized and managed by a thrid party department. The DMZ firewall and the four VM servers had not been identified as Cyber Assets used in the access control and monitoring of SPPRE_URE1's Electronic Security Perimeter (ESP). As a result, these five devices were not afforded the protective measures specified in CIP-005-3 R1.5. All four VM servers were required to be identified and protected as EACM devices because they shared the same physical server. The duration of this instance of noncompliance was approximately 42 months. The root cause of this instance of noncompliance was a lack of understanding that the devices utilized and managed by the third party department, which were not utilized as EACM devices for SPPRE_URE1, needed to be afforded the protective measures of CIP-005-3 R1.5 simply because they shared the same physical server. CIP-005-3a R1.5 – Instance Number Two Although SPPRE_URE1’s Recovery Plan for Critical Cyber Assets included procedures to recover its EACM devices, the plan did not explicitly reference EACM devices as required by CIP-009-3 R1. The duration of this instance of noncompliance was approximately 29 months. The root cause of this instance of noncompliance was a lack of understanding of the Reliability Standards, which led to a procedural gap of not explicitly referring to EACM devices in the recovery plan. CIP-005-3a R1.6 – Instance Number Three SPPRE_URE1 did not properly maintain documentation of all non-critical Cyber Assets within the ESP. An SPPRE_URE1 EMS laptop was moved inside the ESP on May 13, 2014 ; however, SPPRE_URE1’s ESP diagram indicated that the EMS laptop was moved inside the ESP on February 3, 2014. The duration of this instance of noncompliance was approximately 3 months. The root cause of this instance of noncompliance was human error due to personnel updating the network diagram prior to the EMS laptop being introduced into the ESP. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Regarding Instance Number One, the use of the EACM devices were limited to remote access and performed as expected. These devices were also protected by a network firewall. The one VM server that controlled remote access was managed by SPPRE_URE1 and had been protected as an EACM device. Therefore, alerting capabilities had been activated and access logs had been reviewed for this EACM device as required. No unauthorized access to SPPRE_URE1’s ESP occurred during the duration of this instance. Regarding Instance Number Two, although SPPRE_URE1’s Recovery Plan for Critical Cyber Assets did not explicitly reference EACM devices in its recovery procedures, they nonetheless were intended to recover all Cyber Assets. SPPRE_URE1 personnel responsible for the recovery of the EACM devices were familiar with the recovery plan procedures and would have implemented them to recover the EACM devices had they been adversely affected by an incident. Regarding Instance Number Three, this was merely a documentation error of not updating the ESP diagram at the same time the EMS laptop was introduced to the ESP. | To mitigate the minimal risk instances of noncompliance for CIP-005-3a R1.5 and R1.6, SPPRE_URE1: 1) moved the VM server from the third party department’s physical server to its own network (R1.5); 2) identified and protected the newly moved VM server and DMZ firewall as an EACM (R1.5); 3) revised its Recovery Plan for Critical Cyber Assets to explicitly reference EACM devices in the procedures to recover its EACM devices (R1.5); 4) updated its EMS Diagram to reflect the correct date that the EMS laptop was moved inside the ESP (R1.6); and 5) added the EMS Diagram to its document management system to control the version history (R1.6). SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014282 | CIP-005-3a | R2; R2.1 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had two minimal risk instances of noncompliance with CIP-005-3 R2.1. Although SPPRE_URE1 applied an electronic access control model that denies access by default, explicit access permissions for some of its networks were overly broad. More specifically, SPPRE_URE1’s Backup Control Center firewall contained overly broad access permissions for Internet Protocol (IP) communication between two networks. Additionally, SPPRE_URE1 utilizes Internet Control Message Protocol (ICMP), which is an error reporting and diagnostic utility used by network administrators to troubleshoot IP connectivity when it is experiencing problems sending or receiving data (e.g., email). IP connectivity is tested by various methods, including “ping” and “traceroute.” Ping is used to determine whether or not a specific IP address is accessible. Traceroute is used to trace the route of the data to determine the location the data is being held up (e.g., down server). Due to SPPRE_URE1’s network configuration, the ICMP access control list (ACL) broad access permissions allowed any IP address residing on any external network interface to ping or traceroute any IP address sourced from SPPRE_URE1’s network interface for which the ACL is applied. The duration of these instances of noncompliance was aprroximately 30 months. The root cause of these instances of noncompliance was a lack of internal controls to ensure that the explicitly specified electronic access permissions were not overly broad. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Regarding the ICMP diagnostic utility, it is merely an Internet connectivity troubleshooting protocol, which does not open any ports and services used for operations and monitoring of Cyber Assets within SPPRE_URE1’s Electronic Security Perimeter. Therefore, the ICMP utility does not allow external access to any SPPRE_URE1’s systems. Regarding both instances of noncompliance, all network communications were restricted to protected CIP networks that were isolated from external networks using firewall technology that only allowed necessary in-bound communications. SPPRE_URE1 also uses network traffic logging to analyze network traffic at access points to the Electronic Security Perimeter for known and suspect malicious activity. No actual harm occurred as a result of the noncompliance. | To mitigate the minimal risk instance of noncompliance for CIP-005-3a R2.1, SPPRE_URE1: 1) created new firewall baselines; and 2) removed overly broad access permissions for the firewall and the ICMP ACL. SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014284 | CIP-009-3 | R2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had two minimal risk instances of noncompliance with CIP-009-3 R2. Although SPPRE_URE1 conducted table top paper drill exercises of its recovery plan, it could not provide documentation of the explicit steps that were followed in the exercises to recover the particular Critical Cyber Assets. The duration of these instances of noncompliance was approximately 18 months. The root cause of these instances of noncompliance was a misunderstanding of the documentation needed to show full compliance with CIP-009-3 R2. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The instances were documentation deficiencies. SPPRE_URE1 had a compliant recovery plan in place. SPPRE_URE1 provided evidence that table top paper drill exercises of its recovery plan had been conducted in 2012 and 2013; however, the evidence did not include the specific steps to recover the Critical Cyber Assets. Had an incident occurred requiring a Critical Cyber Asset to be recovered, SPPRE_URE1’s recovery plan would have been activated and coordinated by an experienced operations supervisor, who is the individual to which cyber incidents were required to be reported. No actual harm occurred as a result of the noncompliance. | To mitigate the minimal risk instances of noncompliance for CIP-009-3 R2, SPPRE_URE1 revised its recovery plan to include a checklist to be completed during recovery plan exercises to document the specific steps used to recover the particular Critical Cyber Assets that were tested. SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013222 | CIP-005-3a | R1; R1.1, R1.4, R1.6 | SPPRE_URE2 submitted a Self-Report stating that it had minimal risk instances of noncompliance with CIP-005-3a R1.1, R1.4, and R1.6. CIP-005-3a R1.4 (Instance Number One) SPPRE_URE2 did not include satellite clocks on its ESP Cyber Asset list as required by CIP-005-3a R1.4. SPPRE_URE2 personnel did not understand that all Cyber Assets residing within an ESP must be identified on its Cyber Asset list as either Critical Cyber Assets, electronic access control and monitoring (EACM), physical access control system (PACS), or Protection Cyber Asset even if the Cyber Asset is not directly connected to the ESP internal network. The root cause of this instance of noncompliance was a lack of understanding of CIP requirements for Cyber Asset identification. CIP-005-3a R1.1 (Instance Number 2) SPPRE_URE2 maintained a physical management port that was located outside SPPRE_URE2’s ESP. The port had access to SPPRE_URE2’s ESP and externally communicated with a server inside the ESP used for electronic access control and monitoring (EACM). As a result, the port was required to have been identified as an electronic access point (EAP) to the ESP per CIP-005-3a R1.1 but was not. The root causes of this instance of noncompliance were human error due to personnel not adhering to SPPRE_URE2’s process to identify EAP and EACM devices and lack of training of such process. CIP-005-3a R1.6 (Instance Number 3) SPPRE_URE2 maintained a firewall that was used in the access control and monitoring of SPPRE_URE2’s ESP because it authenticated access of two switches inside the ESP. As a result, SPPRE_URE2 was required to document the firewall as a Cyber Assets deployed for the access control and monitoring of the switch access points per CIP-005-3a R1.6. The root causes of this instance of noncompliance were human error due to personnel not adhering to SPPRE_URE2’s process to identify EAP and EACM devices and lack of training of such process. CIP-005-3a R1.6 (Instance Number 4) SPPRE_URE2 had a server used in the access control and monitoring of SPPRE_URE2’s ESP because it authenticated electronic remote user access to the ESP. Therefore, SPPRE_URE2 was required to document the server as a Cyber Assets deployed for the access control and monitoring of the ESP per CIP-005-3a R1.6. The root causes of this instance of noncompliance were human error due to personnel not adhering to SPPRE_URE2’s process to identify EAP and EACM devices and lack of training of such process. The duration of these four instances was approximately 52 months. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Regarding the satellite clocks (Instance Number One), they were not considered essential to the operation of the Control Center. They resided within an ESP and Physical Security Perimeter (PSP), and they are not directly accessible from the internet, but rather only locally accessible, and thus were protected from unauthorized access. Regarding the physical management port (Instance Number Two), to access EACM server via the port, the specific name or IP address of the port, as well as an authorized username and password, would have been required. The EACMS server was being logged and monitored for attempts and unauthorized access to the server. Regarding the firewall (Instance Number Three), although it was not identified as an EACM, it was afforded the protections listed in CIP-005-3a R1.5. Regarding the server (Instance Number Four), it was afforded the protections listed in CIP-005-3a R1.5. Because the server resided within an ESP and PSP, both physical and remote access was limited to personnel with a business need and authorized physical and electronic access. Remote access to these devices was restricted via a firewall which requires multi-factor authentication. The server was being logged and monitored for attempts at and unauthorized access to the server. No actual harm is known to have occurred as a result of these instances of noncompliance. | To mitigate these instances of noncompliance, SPPRE_URE2: 1) conducted a full review of its environment; 2) developed and implemented a commissioning process for ESP devices, which includes a quality review step for compliance validation prior to putting an asset in service; 3) provided training and communications materials on inventory and commissioning processes to affected personnel; 4) commissioned newly identified assets according to the commissioning processes; and appropriately classified its devices and modified its Master CIP Device List. SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013228 | CIP-007-3a | R5; R5.2.1 | SPPRE_URE2 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-007-3a R5.2.1. Although SPPRE_URE2 implemented an account management policy to minimize and manage the scope and acceptable use of administrator account privileges per CIP-007-3a R5.2, the policy did not include removal, disabling, or renaming of administrator accounts on workstations. The duration of this minimal risk instance of noncompliance was approximately 52 months. The root cause of the instance of noncompliance was inattention to detail in SPPRE_URE2’s account management policy. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE2’s account management policy did not include a section addressing the removal, disabling, or renaming of workstation administrator accounts, its workstations were afforded the protective measures covered under SPPRE_URE2’s account management policy per CIP-007-3a R5. For instance, the workstation administrator user accounts were subjected to logging and monitoring, and passwords controls, and any changes to the workstation accounts would have been recorded with SPPRE_URE2’s account change management tickets. Finally, no actual harm occurred as the result of this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) revised its account management policy to include workstation administrator user accounts; and 2) trained all affected personnel on the new policy. SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014013562 | CIP-005-3 | R5; R5.3 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-005 R5, R5.3 because it had not retained electronic access logs for at least ninety calendar days. Shortly before the self-certification, a SPPRE_URE2 server had to reboot after scheduled maintenance, which took a total of ten (10) minutes. During this time, SPPRE_URE2 was not able to log electronic access to the server. The duration of this minimal risk instance of noncompliance was approximately 90 days The root cause of this instance of noncompliance was ineffective oversight of systems security logging to ensure that a complete set of logs was retained for at least 90 calendar days. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The period of time that logs were not captured was limited to ten minutes. To further diminish the risk to the BPS, SPPRE_URE2 maintains firewalls that are configured to only allow electronic traffic using specific protocols to enter the network, preventing unsolicited traffic from passing into the Electronic Security Perimeter. SPPRE_URE2 also uses a network intrusion detection system (IDS) to analyze network traffic at access points to the ESP for known and suspect malicious activity. Access to Cyber Assets inside the ESP was limited to those individuals with authorized physical and/or electronic access rights. Finally, no actual harm occurred as a result of this noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1. Enhanced and implemented its commissioning process including TFE identification on CIP related Cyber Assets; 2. Implemented tool(s) for monitoring, alerting, and log retention (LMA) for applicable CIP related Cyber Assets; 3. Developed a process to identify and remediate gaps in monitoring or alerting; and 4. Delivered training and awareness communications (LMA) to applicable staff SPP RE has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014043 | CIP-007-3a | R6 | WECC_URE1 submitted a Self-Report stating that it was in possible noncompliance with CIP-007-3a R6. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE1’s compliance staff, and determined that WECC_URE1 had a compliance exception with CIP-007-3a R6.4, for its failure to retain all logs specified in Requirement R6, for 90 calendar days. WECC_URE1 reported that the system that monitors its CIP ESP was disrupted and failed to retain logs for a five-day period. WECC_URE1’s security monitoring system consists of a redundant pair of Security Information Event Management (SIEM) proprietary devices designed for automatic failover in the case of an operational disruption to the primary device performing active monitoring, logging and alerting. The devices remain synchronized in real time. WECC_URE1's redundant pair of devices failed over from primary to secondary (backup) but continued to receive logs, monitor logs, and alert if necessary during the failover.The secondary failed back over to the primary and overwrote the 5 days of logs the secondary had collected. During each failover, the SIEM device continued to receive logs and send alerts if necessary. Also, WECC_URE1 security personnel were able to review the logs in real time on monitoring stations as normal. WECC_URE1 recovered some logs that had been retained on the cyber assets themselves for some of the 5-day period. WECC_URE1 also contacted the SIEM vendor to ask if the logs could be recovered and to gain further understanding of the system response. The vendor determined that when the primary SIEM unfroze, the system failed to correctly save the log set on the secondary SIEM and instead saved the empty log set on the primary SIEM, effectively deleting the log set on the secondary SIEM when the data synchronized. Had the system correctly retained the log set of the secondary SIEM, no logs would have been lost. The root cause of the compliance exception was WECC_URE1's less than adequate compliance process to ensure that WECC_URE1 retained system event logs for 90 calendar days. No harm was known to have occurred. | This compliance exception posed a minimal risk, but did not pose a serious or substantial risk to the reliability of the bulk electric system. In this instance, WECC_URE1 failed to retain all logs of system events related to cyber security for cyber assets in WECC_URE1's ESPs for up to 5 days. Specifically, the SIEM logging server failed and overwrote 5 days of logs for cyber assets. This compliance exception poses potential risk to WECC_URE1, because these devices are located in the primary and backup control center ESPs, and could control and affect WECC_URE1's transmission and generation functions. Failure to retain all logs related to cyber security could result in WECC_URE1 being unaware of cyber security incidents, malicious traffic, or unauthorized access into the ESP. If WECC_URE1 does not retain the logs, it may be unable to look back at events leading up to an incident, to discover the full impact of unauthorized access within the ESP. WECC_URE1 implemented preventive and detective controls to prevent a loss of load and generation. Specifically, WECC_URE1 was able to review system event logs relating to cyber security during the 5 days and was still able to get alerts of cyber security events 24 x 7 and respond as necessary. Also, WECC_URE1 was using an intrusion detection system to monitor the ESPs for anomalous network activity, beyond that of system events on the devices within the ESP; and would likely detect and prevent events leading up to the compromise of CCAs, any change in SCADA functions, and any loss of load or generation. Additionally, WECC_URE1 implemented compensating measures to restrict access into the ESP through access points, and continued to log and monitor network activity within the ESP. All devices within the ESP had restricted ports and services. Credentials for logical access could likely prevent any unauthorized access to CCAs, and prevent any change in SCADA functions. If any cyber security events were detected, WECC_URE1 would still be able to get alerts and respond, and to correct any abnormal condition as a result of compromise or of attempted compromise of CCAs. | WECC_URE1 mitigated this compliance exception when the primary SIEM device was again operational. WECC_URE1 reported the log synchronization issue to the vendor as a bug in the device logic. WECC_URE1 has taken steps to implement back-up monitoring and logging to ensure logs are retained, should a similar future outage with the primary system occur.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014691 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Certification stating that it was in possible noncompliance with CIP-004-3a R4. A WECC SME reviewed the Self-Certification documentation, conducted interviews with WECC_URE1 compliance staff, and determined that WECC_URE1 had a compliance exception of CIP-004-3a R4, for its failure to ensure that it has updated lists of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, for all applicable WECC_URE1 personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors. As background, WECC_URE1 reported that a third-party review of WECC_URE1’s compliance with CIP-004-3a showed that certain employees in WECC_URE1’s electric distribution department may have external interactive cyber access (EIA) to WECC_URE1’s Control Center Electronic Security Perimeter (ESP). For that reason, the security controls required by CIP-004-3a R1-R4 were applicable to these employees. WECC_URE1 then conducted its own full investigation and review of all job positions that had the described EIA to WECC_URE1’s SCADA System. Based on its review, WECC determined WECC_URE1 failed to include those employees in a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs); failed to train these personnel on the proper use of CCAs and perform annual checks for training; perform PRAs; and maintain lists of authorized personnel for both PRAs and training attendees.In addition to Read-Only access to the SCADA system, the dispatchers also had the capability to re-close breakers in line in case of tripping. The root cause of this compliance exception was WECC_URE1's less than adequate compliance process to ensure its cyber security awareness program was implemented for all applicable WECC_URE1 personnel. No harm was known to have occurred. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets, train the personnel on the proper use of Critical Cyber Assets CCAs, provide quarterly awareness for personnel with access to CCAs, perform annual checks for training, perform PRAs, and maintain lists of authorized personnel for both PRAs and training attendees. The employees had physical access to two PSPs and Read-Only permission to workstations for the use of reviewing SCADA information. These compliance exceptions pose potential harm to WECC_URE1, because all employees had access to the PSPs and if improperly trained, or absent a valid PRA, an employee’s unauthorized access could introduce malicious activities in the PSP. WECC_URE1 implemented preventative and detective controls by training the staff in the Control Centers to monitor the activities of employees entering the Control Center, including the individuals who had access to the PSPs. WECC_URE1 had appropriate protections in place for employees entering and exiting the PSPs, and the majority of these individuals’ functions were limited. WECC_URE1 also implemented compensating controls by limiting the access of these employees to Read-Only with the Distribution Dispatchers also having permission to close line-breaks. Training staff on monitoring the systems should also detect and correct any malicious activity. | WECC_URE1 mitigated this compliance exceptions by identifying all individuals with possible EIA to the SCADA system, adding the individuals to the list of personnel with authorized access to CCAs, and including their specific electronic and physical access rights to CCAs.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014701 | CIP-004-3a | R2 | WECC_URE1 submitted a Self-Report stating that it was in possible noncompliance with CIP-004-3a R2. A WECC SME reviewed the Self-Report documentation and conducted interviews with WECC_URE1 compliance staff, and determined that WECC_URE1 had a compliance exception of CIP-004-3a R2, for its failure to ensure that all applicable WECC_URE1 personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have an annual cyber security training program. As background, WECC_URE1 reported that a third-party review of WECC_URE1’s compliance with CIP-004-3a showed that certain employees in WECC_URE1’s electric distribution department may have external interactive cyber access (EIA) to WECC_URE1’s Control Center Electronic Security Perimeter (ESP). For that reason, the security controls required by CIP-004-3a R1-R4 were applicable to these employees. WECC_URE1 then conducted its own full investigation and review of all job positions that had the described EIA to WECC_URE1’s SCADA System. Based on its review, WECC determined WECC_URE1 failed to include those employees in a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs); failed to train these personnel on the proper use of CCAs and perform annual checks for training; perform PRAs; and maintain lists of authorized personnel for both PRAs and training attendees.In addition to Read-Only access to the SCADA system, the dispatchers also had the capability to re-close breakers in line in case of tripping. The root cause of this compliance exception was WECC_URE1's less than adequate compliance process to ensure its cyber security awareness program was implemented for all applicable WECC_URE1 personnel. No harm was known to have occurred. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets, train the personnel on the proper use of Critical Cyber Assets CCAs, provide quarterly awareness for personnel with access to CCAs, perform annual checks for training, perform PRAs, and maintain lists of authorized personnel for both PRAs and training attendees. The employees had physical access to two PSPs and Read-Only permission to workstations for the use of reviewing SCADA information. These compliance exceptions pose potential harm to WECC_URE1, because all employees had access to the PSPs and if improperly trained, or absent a valid PRA, an employee’s unauthorized access could introduce malicious activities in the PSP. WECC_URE1 implemented preventative and detective controls by training the staff in the Control Centers to monitor the activities of employees entering the Control Center, including the individuals who had access to the PSPs. WECC_URE1 had appropriate protections in place for employees entering and exiting the PSPs, and the majority of these individuals’ functions were limited. WECC_URE1 also implemented compensating controls by limiting the access of these employees to Read-Only with the Distribution Dispatchers also having permission to close line-breaks. Training staff on monitoring the systems should also detect and correct any malicious activity. | WECC_URE1 mitigated this compliance exceptions by identifying all individuals with possible EIA to the SCADA system, adding the individuals to the list of personnel with authorized access to CCAs, and including their specific electronic and physical access rights to CCAs.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014702 | CIP-004-3a | R3 | WECC_URE1 submitted a Self-Report stating that it was in possible noncompliance with CIP-004-3a R3. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE1 compliance staff, and determined that WECC_URE1 had a compliance exception of CIP-004-3a R3, for its failure to ensure that all applicable WECC_URE1 personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have a personnel risk assessment (PRA) program. As background, WECC_URE1 reported that a third-party review of WECC_URE1’s compliance with CIP-004-3a showed that certain employees in WECC_URE1’s electric distribution department may have external interactive cyber access (EIA) to WECC_URE1’s Control Center Electronic Security Perimeter (ESP). For that reason, the security controls required by CIP-004-3a R1-R4 were applicable to these employees. WECC_URE1 then conducted its own full investigation and review of all job positions that had the described EIA to WECC_URE1’s SCADA System. Based on its review, WECC determined WECC_URE1 failed to include those employees in a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs); failed to train these personnel on the proper use of CCAs and perform annual checks for training; perform PRAs; and maintain lists of authorized personnel for both PRAs and training attendees.In addition to Read-Only access to the SCADA system, the dispatchers also had the capability to re-close breakers in line in case of tripping. The root cause of this compliance exception was WECC_URE1's less than adequate compliance process to ensure its cyber security awareness program was implemented for all applicable WECC_URE1 personnel. No harm was known to have occurred. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets, train the personnel on the proper use of Critical Cyber Assets CCAs, provide quarterly awareness for personnel with access to CCAs, perform annual checks for training, perform PRAs, and maintain lists of authorized personnel for both PRAs and training attendees. The employees had physical access to two PSPs and Read-Only permission to workstations for the use of reviewing SCADA information. These compliance exceptions pose potential harm to WECC_URE1, because all employees had access to the PSPs and if improperly trained, or absent a valid PRA, an employee’s unauthorized access could introduce malicious activities in the PSP. WECC_URE1 implemented preventative and detective controls by training the staff in the Control Centers to monitor the activities of employees entering the Control Center, including the individuals who had access to the PSPs. WECC_URE1 had appropriate protections in place for employees entering and exiting the PSPs, and the majority of these individuals’ functions were limited. WECC_URE1 also implemented compensating controls by limiting the access of these employees to Read-Only with the Distribution Dispatchers also having permission to close line-breaks. Training staff on monitoring the systems should also detect and correct any malicious activity. | WECC_URE1 mitigated this compliance exceptions by identifying all individuals with possible EIA to the SCADA system, adding the individuals to the list of personnel with authorized access to CCAs, and including their specific electronic and physical access rights to CCAs.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014889 | CIP-004-3a | R1 | WECC_URE1 submitted a Self-Report stating that it was in possible noncompliance with CIP-004-3a R1. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE1 compliance staff. The SMEs determined that WECC_URE1 had a compliance exception of CIP-004-3a R1 for its failure to ensure that all applicable WECC_URE1 personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including contractors and service vendors, have access to WECC_URE1’s security awareness program. As background, WECC_URE1 reported that a third-party review of WECC_URE1’s compliance with CIP-004-3a showed that certain employees in WECC_URE1’s electric distribution department may have external interactive cyber access (EIA) to WECC_URE1’s Control Center Electronic Security Perimeter (ESP). For that reason, the security controls required by CIP-004-3a R1-R4 were applicable to these employees. WECC_URE1 then conducted its own full investigation and review of all job positions that had the described EIA to WECC_URE1’s SCADA System. Based on its review, WECC determined WECC_URE1 failed to include those employees in a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs); failed to train these personnel on the proper use of CCAs and perform annual checks for training; perform PRAs; and maintain lists of authorized personnel for both PRAs and training attendees.In addition to Read-Only access to the SCADA system, the dispatchers also had the capability to re-close breakers in line in case of tripping. The root cause of this compliance exception was WECC_URE1's less than adequate compliance process to ensure its cyber security awareness program was implemented for all applicable WECC_URE1 personnel. No harm was known to have occurred. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets, train the personnel on the proper use of Critical Cyber Assets CCAs, provide quarterly awareness for personnel with access to CCAs, perform annual checks for training, perform PRAs, and maintain lists of authorized personnel for both PRAs and training attendees. The employees had physical access to two PSPs and Read-Only permission to workstations for the use of reviewing SCADA information. These compliance exceptions pose potential harm to WECC_URE1, because all employees had access to the PSPs and if improperly trained, or absent a valid PRA, an employee’s unauthorized access could introduce malicious activities in the PSP. WECC_URE1 implemented preventative and detective controls by training the staff in the Control Centers to monitor the activities of employees entering the Control Center, including the individuals who had access to the PSPs. WECC_URE1 had appropriate protections in place for employees entering and exiting the PSPs, and the majority of these individuals’ functions were limited. WECC_URE1 also implemented compensating controls by limiting the access of these employees to Read-Only with the Distribution Dispatchers also having permission to close line-breaks. Training staff on monitoring the systems should also detect and correct any malicious activity. | WECC_URE1 mitigated this compliance exceptions by identifying all individuals with possible EIA to the SCADA system, adding the individuals to the list of personnel with authorized access to CCAs, and including their specific electronic and physical access rights to CCAs.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013579 | CIP-003-3 | R2 | WECC_URE2 submitted a Self-Certification stating it was in possible non-compliance with CIP-003-3 R2. A WECC Subject Matter Expert (SME) reviewed the Self-Certification and conducted interviews with WECC_URE2 compliance staff and determined that WECC_URE2 had a compliance exception with CIP-003-3 R2 for its failure to document changes to the senior manager role within thirty calendar days of the effective date. According to WECC_URE2, the engineering manager who was serving as WECC_URE2’s CIP senior manager left WECC_URE2. After his departure, WECC_URE2 performed a compliance review and discovered that WECC_URE2 should have assigned another senior manager to be in charge of managing the implementation of Standards CIP-002-3 through CIP-009-3, within thirty calendar days. Subsequent to that review, WECC_URE2 reassigned the senior manager role. The root cause of this compliance exception is WECC_URE2’s lack of a compliance process to ensure that WECC_URE2 timely reassigns and documents changes in the CIP senior manager role. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 did not timely assign a senior manager for leading and managing WECC_URE2’s compliance with Standard CIP-002-3 through CIP-009-3. If WECC_URE2 does not document changes to the CIP senior manager, WECC_URE2 may not have a manager overseeing compliance, and the associated staff may not be aware of who has overall responsibility and authority for leading and managing WECC_URE2’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. No harm was known to have occurred. WECC_URE2 implemented preventive controls, because it had earlier developed its Risk Based Assessment Methodology and determined that it does not have any Critical Cyber Assets requiring the CIP protections. | WECC_URE2 remediated this compliance exception when WECC_URE2 self-certified that it had subsequently reassigned the senior manager role.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014901 | CIP-004-3a | R4; R4.1 | WECC_URE3 submitted a Self Report stating that it was in noncompliance with CIP-004-3a R4.1. The root cause of this issue was less than adequate content in the written communication in the alerting mechanism for quarterly CCA reviews. This issue began on April 1, 2015 and ended April 30, 2015 when WECC_URE3 identified the issue and reviewed the EMS access list. This is WECC_URE3's first instance of noncompliance of this requirement in more than three years, was identified and reported timely, and posed minimal risk to the BPS. WECC_URE3 self-reported that the issue was identified by an SME revising personnel authorizations. WECC_URE3 did not review its EMS access list during the first quarter of 2015. Upon discovery, WECC_URE3 immediately reviewed the access list and revised the content of its alerting mechanisms to specifically include the EMS access list. WECC_URE3 confirmed there were no attempted intrusions detected and no changes made that would impact the security of protected assets during the period in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 implemented detective and compensating controls to identify and correct the issue. WECC_URE3 identified this issue within one month of the lapse, and reported and mitigated the issue timely. WECC_URE3 reviewed quarterly evidence to confirm that the issue was limited to one quarter, and verified that during that quarter there were no attempted intrusions detected, no changes to Cyber Access security definitions, and no other changes that would impact the security of protected assets. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) reviewed the EMS access list; 2) revised the content of its alerting mechanisms to specifically include the EMS access list; 3) provided training to the individual responsible for conducting future WECC_URE3 reviews; and 4) reviewed this issue with a broader audience within the organization during an internal “lessons learned” discussion. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013436 | CIP-005-3a | R1 | During a Compliance Audit, WECC determined that WECC_URE4 had an issue of CIP-005-3a R1. The WECC Auditors found that WECC_URE4 failed to adequately protect/identify one Cyber Asset (CA) used in the access control and/or monitoring of the Electronic Security Perimeter (ESP) and afford it all protections specified in CIP-005-3a R1.5. WECC Auditors discovered that WECC_URE4 conducted a cyber vulnerability assessment at least annually. During WECC_URE4’s vulnerability assessment, one CA was discovered as performing the functions of an Electronic Access Control and Monitoring (EACM) device, but had not been identified or classified as such. WECC Auditors issued a data request to WECC_URE4 requesting that WECC_URE4 demonstrate that all protections specified in R1.5 had been afforded to this previously unidentified EACM during the entire audit period. WECC_URE4 responded with various files that addressed most of the protections required in R1.5, but failed to demonstrate that the device was included in previous years’ vulnerability assessments and that the proper backup and recovery plans were implemented pursuant to CIP-009-3 and CIP 007 R8. Therefore, the Audit Team determined WECC_URE4 had an issue of CIP-005-3a R1.5 and forwarded the audit findings to Enforcement. Enforcement reviewed the audit findings and determined that WECC_URE4 failed to afford the protective measure to one CA used in the access control or monitoring of the ESP as required in CIP-005-3a R1.5. Specifically, WECC_URE4 failed to afford the protections of CIP 007 R8 and CIP-009-3. WECC_URE4. The root cause is a lack of compliance understanding. WECC_URE4 did not understand the device needed to be classified as an EACM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to adequately protect/identify one CA used in the access control and/or monitoring the ESP and afford it all protections specified in CIP-005 R1.5. However, WECC_URE4 implemented strong preventive controls to prevent the unauthorized access of CCAs. For example, WECC_URE4 ensured that every CCA resided within an ESP, and identified and documented the ESP and all access points to the perimeter. Further, the CA is protected within a designated Physical Security Perimeter (PSP) and logically resides on a protected demilitarized zone (DMZ). Additionally, WECC_URE4 implemented a defense in depth security approach to its ESP and Critical Cyber Assets (CCAs) through multiple layers of network security, which includes restrictive logical and physical access controls, as a compensating measure. For these reasons, Enforcement determined that this issue poses a Minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE4: 1) Completed a change order ticket to review all CIP-005-3a R1.5 EACM protection requirements and document changes made for deficient requirements, which included: i. CIP-007-3a R8 ii. CIP-009-3a 2) Updated device on WECC_URE4 inventory list to identify the Cyber Asset as an EACM device. 3) Had the CIP Senior Manager sign the updated inventory list. 4) Replaced one device with updated device, affording all protections specified by CIP-005-3a R1.5. WECC_URE4 needed to replace original device with an updated model that could support its two-factor authentication solution, pursuant to its CIP-005-3a R2 issue. Therefore, no CVA was performed on the original device. 5) Updated new device on WECC_URE4 inventory list to identify the Cyber Asset as an EACM device. 6) Had the CIP Senior Manager sign the updated inventory list. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013434 | CIP-005-3a | R2 | During a Compliance Audit, WECC determined that WECC_URE4 had an issue of CIP-005-3a R2. Specifically, the WECC Auditors found one access point to be deficient in its capability to properly segment secure networks from lower security networks, due to the fact that Layer 2 devices do not have an access control model that allows for explicit access permissions. The Layer 2 device is also known to be vulnerable to VLAN Hopping. Although WECC_URE4 displayed that it applied explicit access permissions on ports, WECC Auditors found that WECC_URE4 failed to implement technical controls for control of electronic access at one access point to the ESP, as required by CIP 005-3a R2.1. Additionally, during the review of WECC_URE4’s baseline documentation, the WECC Auditors found that WECC_URE4’s baseline documentation contained remarks within its running configuration. The WECC Auditors issued data requests to WECC_URE4 and found that although WECC_URE4 listed brief descriptions and remarks within the running configuration, not all descriptions and remarks described the business justification for all open ports and services, as required by CIP 005-3a R2.2. Further, WECC Auditors discovered that WECC_URE4’s process for external interactive access into the ESP and Physical Access Control (PACs) Network had deployed single-factor authentication (username/password) for external interactive access into the ESP and PACs Networks. Single-factor authentication does not provide strong procedural or technical controls at the access points to ensure authenticity of the accessing party, per CIP 005-3a R2.4. The WECC Auditors found that WECC_URE4 failed to implement technical mechanisms for control of electronic access at one electronic access point to the Electronic Security Perimeter (ESP), completely document business justifications for enabled ports and services at all electronic access points, and implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party. Therefore WECC Auditors forwarded this information to Enforcement. Enforcement reviewed the Auditors findings and determined that WECC_URE4 failed to implement technical mechanisms for control of electronic access at one electronic access point to the Electronic Security Perimeter (ESP), completely document business justifications for enabled ports and services at all electronic access points, and implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party. As a result, Enforcement determined that WECC_URE4 was in issue of CIP-005-3a R2. Enforcement determined that the start. The root cause was a lack of compliance understanding. WECC_URE4 believed its controls were necessary to meet compliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to implement technical mechanisms for control of electronic access at one electronic access point to the Electronic Security Perimeter (ESP), completely document business justifications for enabled ports and services at all electronic access points, and implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party. However, WECC_URE4 did implement strong preventive measures to restrict unauthorized individuals from gaining access to the devices within WECC_URE4’s ESP. Specifically, the Layer 2 switch in scope was configured to explicitly forbid all physical interface ports external to the ESP with the “forbid” command. The physical maintenance serial port is located on the Access Point inside the PSP, and the logical maintenance VLAN interface is located inside the ESP. Additionally, all external ESP VLANs are protected by another ESP Access Point. WECC_URE4 stated that the Layer 2 switch also uses port security to control access. WECC_URE4 also implemented strong, complex passwords via policy, which are technically enforced by Active Directory. Additionally, the ESP firewall only allows SSH sessions from selected corporate desktops with all other interactive access denied. Based on the above reasons, Enforcement determined that this issue poses a Minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE4: 1) Implemented a new EACM device to replace the old device so that two-factor authentication would be supported; 2) Completed the update of the "Information Technology Hardware Inventory" list to include new device; 3) Completed review by Sr. Managers (Reliability Compliance Committee) and obtained signature from the CIP Sr. Manager on the revised CCA List; 4) Created a new spreadsheet to document the business justification for those “network device” services, protocols/ports, and related/affected servers required for normal and emergency operations. WECC_URE4 reviewed all configurations line-by-line and created a justification for each service, grouped configuration syntax by manufacturer and model; 5) Researched available Layer 3 switches; including two for primary control center, two for backup control center, and two for testing. 6) Coordinated outages, install, perform tests, and update associated documentation for the Layer 3 switches.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013424 | CIP-006-3a | R5 | During a Compliance Audit, WECC determined that WECC_URE4 had an issue of CIP-006-3a R5. The Audit Team conducted site tour visits to confirm the compliance evidence that WECC_URE4 submitted had Physical access control, monitoring, and logging at all access points. During the site tour, the Audit Team identified four access points located within the PSP that houses the Primary Control Center and Data Center to have the “wrong door” or “Unauthorized Access Attempt Indicator” alarm disabled. The doors were tested and no alarm went off. A visual confirmation occurred at the Human Machine Interface (HMI) to the PACS server identifying the parameter setting was disabled. Therefore, the Audit Team determined that WECC_URE4 failed to configure the PACS alarm at four PSP access doors which is a issue of CIP-006-3a R5. The Audit Team forwarded the audit findings to Enforcement for review. Enforcement reviewed the audit findings. Enforcement determined that WECC_URE4 failed to enable the parameter settings within the PACS for unauthorized access attempt alerting at four access points of the PSP, as required by CIP 006-3a R5. The root cause is a lack of process. WECC_URE4 personnel did not have a complete checklist of all tasks that needed to be done for the triennial PACS testing (CIP-006 R8). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to enable the parameter settings within the PACS for unauthorized access attempt alerting at four access points of the PSP per CIP 006-3a R5. However, WECC_URE4 implemented strong preventive controls to prevent the unauthorized access of CCAs. A portion of the PSP in scope of the issue is manned 24 hours a day, 7 days a week. The CA is protected within a designated Physical Security Perimeter (PSP) and logically resides on a protected demilitarized zone. Additionally, WECC_URE4 did deploy a defense in depth security approach to all access points within a controlled access building and employee parking lot that has Closed Circuit Television as a compensating measure. For these reasons, Enforcement determined that this issue poses a Minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE4: 1) Enabled alarming for “unauthorized access” for each of the access point card readers to the Primary Control Center Red Zone doors. 2) Removed the card reader from the interior mantrap door and moved the motion detector sensor within the mantrap, thus reducing the number of access points to three doors. 3) Created a Physical Site Perimeter Report Check List to ensure that in future testing of the physical security system perimeter, card readers, all points are tested appropriately. 4) Performed and documented test of the physical security system card readers and verified that all the alarms could be seen on the operators’ consoles. 5) Updated the Physical Security Layers and Boundaries Visio diagram to reflect the changes. Changes to the Physical Security Perimeter were reviewed and signed-off by Sr. Management at the Reliability Compliance Committee Meeting. 6) Changes to the Physical Security Perimeter were reviewed and signed-off by Sr. Management at the Reliability Compliance Committee Meeting that included the CIP Sr. Manager. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013426 | CIP-007-3a | R2 | During a Compliance Audit WECC determined that WECC_URE4 had an issue of CIP-007-3a R2. 34. The WECC Auditors reviewed WECC_URE4’s baseline for a network switch device and were unable to find documented business justification for four services enabled on the switch. The WECC auditors issued a data request to WECC_URE4. In response to the data request, WECC_URE4 referenced descriptions of the Access Control List (ACL) from firewall configurations on other devices, but were unable to provide documentation for a switch. Therefore, the Audit Team determined WECC_URE4 had a issue of CIP-007 R2. The WECC Auditor forwarded this information to Enforcement. Enforcement reviewed the information submitted by the WECC Auditors and WECC_URE4. After reviewing the information provided, Enforcement found that WECC_URE4 failed to provide documented justification for four services enabled on the switch device. As a result, Enforcement determined that WECC_URE4 was in issue of CIP-007-3a R2.The root cause was a lack of compliance understanding. The entity believed referencing ACLs on firewalls was sufficient to meet the requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to provide proper justification for four services enabled on a network switch device. However, WECC_URE4 had preventive controls in place to prevent the unauthorized access to WECC_URE4’s devices. WECC_URE4 knew the switch was being used and had user accounts which were specifically configured to connect to that device and its services. WECC_URE4 user accounts had strong, complex passwords and WECC_URE4 monitored the network switch device and its services, even though it was not listed in their baseline. WECC_URE4 knew the switch was there and the services were enabled on the device, but they failed to have proper documentation for the network switch device. Additionally, WECC_URE4 had strong compensating controls in place to compensate if the affected open ports and services were compromised. For example, WECC_URE4 implemented a defense-in-depth architecture of physical and logical Cyber Security controls, including physical security mechanisms, special locks, closed circuit television (CCTV), and logical perimeter and internal Cyber Security controls. The internal Cyber Security controls included firewalls, vulnerability scanning tools, and a Security Events Management System (SEM logging). Based on the above reasons, Enforcement determined that this matter poses a Minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE4 created a spreadsheet to document the business justification for those network device services, protocols-ports, and related/affected servers required for normal and emergency operations. WECC_URE4 reviewed each configuration line-by-line and created a justification for each service, grouping configuration syntax by manufacturer and model. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015014878 | CIP-003-3 | R6 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. However, because WECC_URE5 submitted the Self-Report during the Self-Certification period, WECC dismissed the Self-Report and a new Self-Certification record was created. A WECC SME reviewed the Self-Certification and discussed the possible noncompliance with WECC_URE5. The SME determined that for two changes, WECC_URE5 failed to follow its change control process. All devices are in the SCADA Electronic Security Perimeter (“ESP”). The SME determined that because WECC_URE5 failed to follow its change control process for CCAs, WECC_URE5 had a possible issue of CIP-003-3 R6, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Certification and the SME’s findings. Enforcement determined that WECC_URE5’s failure to follow its change control process for CCAs is a compliance exception of CIP-003-3 R6. Enforcement further determined the compliance exception began when WECC_URE5 implemented the change without following its change control procedure, and continued through when WECC_URE5 completed remediating activities. The root cause was personnel not understanding the change control process, and the lack of oversight to ensure the processed were being followed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to follow its change control and configuration management processes for changes involving CCAs. All devices are in the SCADA ESP and are located at facilities. WECC_URE5’s change control process includes security testing, which WECC_URE5 failed to perform. However, WECC_URE5 implements multiple detective controls in the form of tools that continuously monitor the health and security posture of the SCADA network and the devices therein. If a failure was detected on any device, these tools could alert WECC_URE5 to the problem. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE5: 1) Performed all change control steps necessary on the new CCAs; and 2) WECC_URE5 improved its change control processing and training of personnel on those changes. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015014881 | CIP-005-3a | R1 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP-005-3a R1. However, because WECC_URE5 submitted the Self-Report during the Self-Certification period, WECC dismissed the Self-Report and a new Self-Certification record was created. A WECC SME reviewed the Self-Certification and discussed the issue with WECC_URE5. The SME determined that for two changes, WECC_URE5 failed to follow its change control process. The two changes impacted Electronic Access Control and Monitoring (“EACM”) devices. Because WECC_URE5 failed to provide the EACMs with the protective measures of CIP-003-3, as mandated by CIP-005-3a R1.5, the SME determined that WECC_URE5 had a possible issue of CIP-005-3a R1.5, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Certification and the SME’s findings. Enforcement determined that WECC_URE5’s failure to provide EACMs the protective measures required under the Standard is a compliance exception of CIP-005-3a R1.5. Enforcement further determined the compliance exception began owhen WECC_URE5 implemented the change without following its change control procedure, and continued through when WECC_URE5 completed remediating activities. The root cause was personnel not understanding the change control process, and the lack of oversight to ensure the processed were being followed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to follow its change control and configuration management processes for two changes involving EACMS. The EACMS are located at different substations and are connected with the SCADA network. WECC_URE5’s change control process includes security testing, which WECC_URE5 failed to perform. However, WECC_URE5 implements multiple detective controls in the form of tools that continuously monitor the health and security posture of the SCADA network and the EACM devices that monitor the SCADA network. If a failure was detected on any device, these tools could alert WECC_URE5 to the problem. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE5: 1) Performed all change control steps necessary on the new EACMs; and 2) WECC_URE5 improved its change control processing and training of personnel on those changes. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015014877 | CIP-007-3a | R1 | WECC_URE5 submitted a Self-Report stating that, as a Transmission Owner, Transmission Operator, Transmission Service Provider, it had an issue of CIP-007-3a R1. However, because WECC_URE5 submitted the Self-Report during the Self-Certification period, WECC dismissed the Self-Report and a new Self-Certification record was created. A WECC SME reviewed the Self-Certification and discussed the issue with WECC_URE5. The SME determined that for two significant changes, WECC_URE5 failed to ensure that the changes did not adversely affect existing cyber security controls. The two changes affected Cyber Assets within different facilities. The devices consist of workstations and servers, with some devices located at the control center, and all devices are on the SCADA network. The SME determined that WECC_URE5 had a possible issue of CIP-007-3a R1, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Certification and the SME’s findings. Enforcement determined that WECC_URE5’s failure to ensure that significant changes to existing Cyber Assets within the ESP do not adversely affect existing cyber security controls is a compliance exception of CIP-007-3a R1. Enforcement further determined the compliance exception began when WECC_URE5 implemented the change without following its change control procedure, and continued through when WECC_URE5 completed remediating activities. The root cause was personnel not understanding the change control process, and the lack of oversight to ensure the processed were being followed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to follow its change control and configuration management processes for two changes involving Cyber Assets. These devices consist of workstations and servers, with some devices located at the control center and all devices are on the SCADA network. WECC_URE5’s change control process includes security testing, which WECC_URE5 failed to perform. However, WECC_URE5 implements multiple detective controls in the form of tools that continuously monitor the health and security posture of the SCADA network and the devices therein. If a failure was detected on any device, these tools could alert WECC_URE5 to the problem. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE5: 1) Performed all change control steps necessary on the new non-CCA devices; and 2) WECC_URE5 improved its change control processing and training of personnel on those changes. WECC has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2015014590 | CIP-007-3a | R7; R7.1 | WECC_URE6 submitted a Self-Report stating that, as a Responsible Entity, it had an issue with CIP-007-3a R7.1. WECC_URE6 removed certain assets from the PSP. The assets included servers and switches. WECC_URE6 transported the servers to an WECC_URE6 salvage yard. The salvage yard is enclosed by a fence and requires electronic badge access to enter the site. The salvage yard is also monitored by video surveillance and twenty-four hours a day, seven days a week security guards. WECC_URE6 transported the switches to a restricted area within an WECC_URE6 building. The restricted area protections include a perimeter fence that requires electronic badge access to enter the site, internal building electronic badge access, video surveillance, and twenty-four hours a day, seven days a week security guards. Additionally, access to the restricted area is limited to a small number of WECC_URE6 employees most of whom have CIP PRA access credentials. The devices still required a local Administrator password. The password is controlled and availability restricted to CIP trained personnel. When the assets were removed from the PSP, WECC_URE6 thought that all CIP confidential information was sanitized and removed from the systems. However, an WECC_URE6 employee followed up on the status of the decommission effort and discovered the devices were not properly sanitized prior to their removal from the PSP. WECC_URE6 completed the decommissioning process and purged the devices of all confidential information per WECC_URE6’s CIP program. The compliance exception start date was when WECC_URE6 disposed of ten assets by transferring the assets outside the PSP. The compliance exception end date was when WECC_URE6 erased the data storage media by purging the devices of all confidential information. The root cause was that WECC_URE6's process allowed for human performance errors to be made during the removal process which led to incomplete decommissioning of the devices. | This issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE6 did not verify that sensitive cyber security data was completely erased from the assets before the assets were disposed of outside the PSP. However, WECC_URE6 implemented controls to prevent any issues from occurring. Allassets were transported to sites requiring electronic badge authentication for site access. The sites were also monitored by video surveillance and twenty four hours a day, seven days a week security guards. The six switches were stored inside a restricted area building that required authorized individuals to use their badge to access the restricted area. Access to the restricted area was limited to a small number of WECC_URE6 employees; most of whom had CIP PRA access credentials. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) identified all devices that were affected by this condition; 2) collected and cleared all information from identified devices and finalized decommissioning; 3) met with internal teams, determined extent of condition, and identified next steps; 4) utilized internal Corrective Action Program to identify root cause; 5) developed plan to prevent future incidents based on root cause analysis; 6) developed lockout-tagout (LOTO) procedure to track removal and decommissioning tasks; 7) finalized the implementation of the LOTO process; and 8) conducted training with relevant groups on new LOTO procedure.
2015-10-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015235 | CIP-002-3 | R2 | MRO_URE1 submitted a Self-Report stating that, as a GO and GOP, it had an issue of CIP-002-3 R2. Specifically, MRO_URE1 did not develop a list of its identified Critical Assets. The cause of this issue was MRO_URE1's misunderstanding of the standard, and its belief that if it had no Critical Assets, it was not required to create a null list. The issue began when the standard became applicable to MRO_URE1, and ended on September 10, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE1 did not have any Critical Assets, and the scope of the issue is limited to MRO_URE1's failure to create a null list. The risk is further reduced because MRO_URE1 is a lower voltage generator with non-dispatchable energy that is not interconnected at high voltages. Moreover, in determining this issue was appropriate for compliance exception treatment, MRO considered that MRO_URE1 Self-Reported and promptly mitigated this issue. Finally, MRO_URE1 will not have any medium or high impact facilities under CIP version 5. No harm is known to have occurred. This is MRO_URE1's first instance of noncompliance with CIP-002-3 R2. | To mitigate this issue, MRO_URE1: 1) Created a null list of Critical Assets; 2) distributed a memorandum regarding the applicability and requirements of CIP-002-3 and the criteria that will be used in CIP-002-5; and 3) reviewed and applied the bright line criteria used in CIP-002-5. MRO_URE1 stated that mitigating activities were complete as of September 10, 2015.
2015-10-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015236 | CIP-002-3 | R3 | MRO_URE1 submitted a Self-Report stating that, as GO and GOP, it had an issue of CIP-002-3 R3. Specifically, MRO_URE1 did not develop a list of its associated Critical Cyber Assets. The cause of this issue was MRO_URE1's misunderstanding of the standard, and its belief that if it had no Critical Assets, then it was not required to create a list of associated Critical Cyber Assets. The issue began when the standard became applicable to MRO_URE1, and ended on September 10, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE1 did not have any associated Critical Cyber Assets, and the scope of the issue is limited to MRO_URE1's failure to create a null list of associated Critical Cyber Assets. The risk is further reduced because MRO_URE1 is a lower voltage generator with non-dispatchable energy that is not interconnected at high voltages. Moreover, in determining this issue was appropriate for compliance exception treatment, MRO considered that MRO_URE1 Self-Reported and promptly mitigated this issue. Finally, MRO_URE1 will not have any medium or high impact facilities under CIP version 5. No harm is known to have occurred. This is MRO_URE1's first instance of noncompliance with CIP-002-3 R3. | To mitigate this issue, MRO_URE1: 1) Created a null list of Critical Assets; 2) created a null list of Critical Cyber Assets; 3) distributed a memorandum regarding the applicability and requirements of CIP-002-3 and the criteria that will be used in CIP-002-5; and 4) reviewed and applied the bright line criteria used in CIP-002-5. MRO_URE1 stated that mitigating activities were complete as of September 10, 2015.
2015-10-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015015237 | CIP-002-3 | R4 | MRO_URE1 submitted a Self-Report stating that, as a GO and GOP, it had an issue of CIP-002-3 R4. Specifically, MRO_URE1 did not have a senior manager or delegate sign a null list of Cyber Assets, or a list of associated Critical Cyber Assets. The cause of this issue was MRO_URE1's misunderstanding of the standard, and its belief that if it had no Critical Assets, it was not required to create a null list of Critical Assets or associated Critical Cyber Assets. The issue began when the standard became applicable to MRO_URE1, and ended on September 10, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue is only a documentation issue as MRO_URE1 did not have any Critical Assets, and the scope of the issue is limited to MRO_URE1's failure to create a null list of Critical Cyber Assets, and a null list of Cyber Assets, that are both signed by a senior manager or delegate. The risk is further reduced because MRO_URE1 is a lower voltage generator with non-dispatchable energy that is not interconnected at high voltages. Moreover, in determining this issue was appropriate for compliance exception treatment, MRO considered that MRO_URE1 Self-Reported and promptly mitigated this issue. Finally, MRO_URE1 will not have any medium or high impact facilities under CIP version 5. No harm is known to have occurred. This is MRO_URE1's first instance of noncompliance with CIP-002-3 R4. | To mitigate this issue, MRO_URE1: 1) Created a null list of Critical Cyber Assets and a null list of Critical Assets that was signed by a senior manager or delegate MRO_URE1 stated that mitigating activities were complete as of September 10, 2015.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015027 | CIP-006-3c | R4 | NPCC_URE1 had an issue of CIP-006-3c R4. An employee of an affiliate company was performing security checks at a facility. The affiliate employee performing security checks presented his card-key (badge) and access was denied, however, the employee proceeded to pull on the door and was able to gain access. A “forced door alarm” was received at the NPCC_URE1control center. Upon entering, the employee called the control center and informed them of the situation. The control center confirmed that a “forced door alarm” had been received and that it was monitoring activity by camera. A technician was dispatched and observed the door was in a locked state, however, the technician was able to force the door open to gain access. Upon inspection, the technician determined that a spring in the door locking mechanism had come partially loose and proceeded to repair the door locking mechanism. The maintenance and testing record states that no defects were noted. The employee that was involved with this incident was previously granted unescorted physical access rights to critical cyber assets at the location. The employee’s unescorted physical access rights were revoked while the employee was on medical leave. At the time of the incident, the employee thought that his unescorted physical access rights to critical cyber assets within the location had been reinstated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A manned checkpoint controls access to the facility. Access to the facility requires check-in at a security guard station. A security guard contacts the senior operator at the control room to obtain permission to grant key access to the perimeter fence. Inside the fence, access is controlled by a badge reader. The employee that was involved with this incident had an up-to-date Personnel Risk Assessment and a continued business need for authorized unescorted physical access to Critical Cyber Assets at the location. Additionally, he was in communication with the control center and informed them of the situation. Subsequent to this incident, the employee's unescorted physical access rights were reinstated. | To mitigate this issue, NPCC_URE1: 1. Repaired the door locking mechanism. 2. Reviewed the incident regarding Physical Access Controls and what should be done when a card key reader denies access. NPCC has verified the completion of all mitigation activity.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015139 | CIP-007-3a | R5 5.3.2 | NPCC_URE1 had an issue of CIP-007-3a R5. During preparation for their cyber vulnerability assessment, a discrepancy involving substation revenue meters (protected cyber assets) was discovered. Read-only user accounts for the revenue meters consisted of six numbers instead of a combination of alpha, numeric, and "special" characters. The group responsible for the read-only user account passwords mistakenly believed that the CIP-007-3a R5.3.2 password complexity requirements did not apply to read-only user account passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The revenue meters had passwords for read-only access that consisted of six numbers. Revenue meters take measurements on the various circuits and report back to the Energy Management System (EMS) through remote terminal units. The administrative account passwords for the revenue meters did consist of a combination of alpha, numeric, and "special" characters. | To mitigate this issue NPCC_URE1: 1. changed read only user account passwords on the revenue meters to consist of a combination of alpha, numeric, and "special" characters. 2. updated procedures to explicitly state that both “write” and “read-only” passwords must be changed annually and comply with complexity requirements per CIP-007 R5. NPCC has verified the completion of all mitigation activity.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015015113 | CIP-004-3a | R4 | NPCC_URE2 had an issue of CIP-004-3a R4. An employee of a vendor working for NPCC_URE2, resigned from their position with the vendor. The vendor was assisting with building renovations. The vendor failed to timely notify NPCC_URE2 of their employee's resignation. The vendor notified NPCC_URE2 of their employee's resignation / voluntary termination three months later and access was removed. Additionally, the error was not detected during the quarterly physical access list review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The vendor's employee's unescorted physical access rights to critical cyber assets were at a distribution control center and distribution back-up control center. A review of access records confirmed that the vendor's employee did not access the control centers during the period in question. The vendor's employee had up-to-date CIP training and a Personnel Risk Assessment. The vendor's employee did not have cyber access rights. | To mitigate this issue, NPCC_URE2: 1. Reviewed the list of personnel who have authorized unescorted physical access rights to critical cyber assets at NPCC_URE2's distribution control center and back-up control center for continued business need. 2. Conducted CIP awareness training with the vendor. 3. Obtained confirmation of the vendor's procedures regarding employee terminations and notification requirements. NPCC has verified the completion of all mitigation activity.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015015026 | CIP-006-3c | R2 2.2 | NPCC_URE3 had an issue with CIP-006-3c R2. NPCC_URE3 discovered a logging issue related to a few back up servers associated with the Physical Access Control System (PACS). These servers were not communicating with the system that reviews and retains security logs and provides alerting when required. These security logs were not recorded for 51 days. An investigation of the system found that changes were made to the corporate network which resulted in the communication path between the backup servers and the logging server being affected. The local servers did not have adequate storage to retain 90 days of logs. The security system continued to function properly during this time and retained logs locally for a period of 5 days. The remaining servers at issue retained logs locally for 10 days. No other servers were affected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three servers are backup servers in case one of the primary servers fails. The primary servers were communicating with the central security servers and did not fail to operate during the time the backup servers were not sending logs to the primary server. Additionally, the PACS system and the EMS utilize separate independent networks. Both systems are protected by their own set of network hardware and software. | To mitigate this issue, NPCC_URE3: 1. re-enabled the communication path and the logs were recovered from the local servers and reviewed. 2. met with all parties involved to discuss the incident and explain the occurance and reviewed the procedures in place that could have prevented it. The meeting also included awareness and training of NPCC_URE3's internal compliance procedures and the CIP standards. 3. reviewed the dashboard to ensure logs are received until the central logging server is reconfigured to provide timely alerting. NPCC has verified the completion of all mitigation activity.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015015108 | CIP-006-3c | R2; 2.2 | NPCC_URE3 had an issue with CIP-006-3c R2. While using the electronic Patch Management Application to assess security patches and security upgrades for applicability for the physical access control system (PACS) Windows devices (Workstations/Servers), several patch updates for two months were unexpectedly deployed. The patches for one month were assessed, evaluated, and approved prior to the unexpected deployment. However, the second month's patches had not been approved prior to the unexpected deployment, as required by the change management process under CIP-003-3, R6. A roll back of the unexpectedly deployed patches was not performed since no adverse impact to the system was identified and the security posture was improved. The security system continued to function properly during this time. A root cause analysis pointed to an inadvertent operator action with the patching application. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected servers contain panel configurations, physical access logs, alerting and monitoring functions, and the database for the PACS system. The affected workstations are used by the security command center operators to access the security system user interface. In the event of a total loss of all servers and workstations, the panels would still control access based on their existing local data. However, updates, monitoring and alerting functions would not be available real-time. Access attempts and alerts would be logged and buffered on the local panels. | To mitigate this issue, NPCC_URE3: 1. suspended the use of the patching application for evalutating PACS patches. Future patches will be manually evaluated. 2. held meetings with all parties involved to discuss the incident and to understand how the unexpected action occurred. 3. submitted a change ticket that was approved by the change board for the already deployed patches. NPCC has verified the completion of all mitigation activity.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015015025 | CIP-006-3c | R2 2.2 | NPCC_URE3 had an issue with CIP-006-3c R2. NPCC_URE3 completed a quarterly cyber access review and discovered a generic account existed on one of the switches associated with the physical access control system (PACS). The account was established during the newly established system build, and it was not deleted prior to the system being placed in service. A review of the logs showed the generic account was not used during the violation duration. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE3 discovered a possible violation during their quarterly cyber access review which shows a functional internal compliance program. This generic account was created with no privilege access which is the minimum level of access granted (read only). The generic account was not a default account and did not have a default username or password. | To mitigate this issue, NPCC_URE3: 1. revoked the account during the cyber access review 2. reviewed all accounts and compared against the approved cyber access list. No other unapproved accounts were identified. 3. held meetings with all parties involved to discuss this incident, explain why it occurred and reviewed the procedures in place that could have prevented it. These meetings also included awareness and refresher training of internal compliance procedures and the CIP Standards. 4. focused the content of the next Quarterly Cyber Security Awareness message on the procedure for requesting and granting cyber access. 5. incorporated lessons learned into annual NERC CIP Training Program. NPCC has verified the completion of all mitigation activity.
2015-10-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014822 | CIP-003-3 | R6 | RFC_URE1 submitted a Self-Certification stating it had an issue of CIP-003-3 R6. RFC_URE1 determined that changes to ports and services on its Cyber Assets were made following the annual vulnerability assessment yet those changes were not documented in accordance with its change management procedures. The root cause of this noncompliance concerned the management practice of workforce management and asset and configuration management. Workforce management was implicated because improved training and oversight could have helped prevent the failure to document changes to ports and services in accordance with RFC_URE1's change management procedures. Similarly, asset and configuration management was implicated because improved checks and balances can better ensure that documentation accurately reflects and helps manage the status of and changes to RFC_URE1's ports and services. The duration of this noncompliance is from the date RFC_URE1 failed to document changes to its ports and services in accordance with its change management procedure, to the date RFC_URE1 will complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The changes to ports and services on RFC_URE1's Cyber Assets were tracked and documented on RFC_URE1's vulnerability assessment action report following RFC_URE1's vulnerability assessment. The noncompliance stems from the fact that RFC_URE1 did not document the ports and services changes pursuant to its change management procedure. The changes, however, were documented and the open ports and services were disabled appropriately. In short, this noncompliance was a documentation issue. No harm is known to have occurred. There are no compensating measures in place to reduce the risk to reliablity while mitigation is ongoing because this was solely a documenation issue. All changes to ports and services on RFC_URE1's Cyber Assets were tracked and documented, RFC_URE1 just did not document the ports and services changes pursuant to its change management procedure. | To mitigate this issue, RFC_URE1 will complete the following mitigation activities by December 30, 2015: 1) Discuss with the employee responsible for the noncompliance the circumstances surrounding the issue and reinforce the importance of properly following the CIP procedures including all documentation related requirements; 2) Edit its change management procedure to ensure it properly addresses instances where change or configuration processes are needed. RFC_URE1 also committed to create process flowcharts to identify the required steps for each type of change or configuration management activity; and 3) Review its change management workflow to determine if additional checks and balances are necessary to verify all change management or configuration management process steps are appropriately implemented. RFC_URE1 needs until December 30, 2015 to complete its mitigation because reviewing its entire change management workflow is a lengthy process.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015104 | CIP-006-3c | R1; R1.5 | SPPRE_URE1 submitted a Self-Report stating that it had two minimal risk instances of noncompliance with CIP-006-3c R1.5 because three employees were granted physical access to Critical Cyber Assets prior to receiving final authorization from management. Specifically, SPPRE_URE1’s supervisor of janitorial services was granted physical access to one of SPPRE_URE1’s protected CIP areas in its general office prior to final approval by management. Later, two employees, who had recently transferred from other departments into SPPRE_URE1’s Transmission Operations department, were granted temporary physical access to the Transmission Operations department prior to final approval by management. The first instance of noncompliance's duration was approximately one month, and the second instance of noncompliance's duration was nine days. The root cause of these instances of noncompliance was human error due to personnel not adhering to SPPRE_URE1’s documented physical access plan. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The noncompliance with CIP-006 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity to physically access Cyber Assets that are not protected by the implementation of a physical security plan. Nonetheless, the three employees had a business need for physical access to the area containing Critical Cyber Assets; all had completed CIP training and have current personnel risk assessments. Furthermore, the two employees from the July 2015 incident were granted physical access to the Transmission Operations department for a period of only two hours and were accompanied by escorts while inside the protected area. No actual harm occurred as a result of these instances of noncompliance. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE1: 1) revised its physical security plan to include an access approval checklist that the Supervisor of NERC Compliance or the Manager of NERC Compliance and Training must complete before authorizing and granting physical access; 2) revised its step-by-step instruction sheet for issuing CIP temporary physical access to protected areas; and 3) trained all affected staff on the revised physical security plan and physical access instruction sheet. SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013219 | CIP-004-3 | R1 | SPPRE_URE2 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-004-3 R1. Specifically, SPPRE_URE2 had not ensured that all personnel who had authorized cyber access to its Critical Cyber Assets had been provided security awareness reinforcement on, at least, a quarterly basis. SPPRE_URE2 provides security reinforcement training to its employees through email distributions or intranet postings. However, SPPRE_URE2’s remote contractors with authorized electronic access to SPPRE_URE2’s Critical Cyber Assets were not provided the security awareness reinforcement training because these contractors did not have SPPRE_URE2 e-mail accounts or access to the SPPRE_URE2 intranet. The duration of this minimal risk instance of noncompliance was approximately 35 months. The root cause of these instances of noncompliance was SPPRE_URE2’s failure to realize that its remote contractors/ third-party vendors were not receiving the security reinforcement training. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to reinforce continuing security awareness for all personnel having authorized cyber access to Critical Cyber Assets could cause personnel to become complacent, inattentive, and/or unresponsive to potential security threats. Although SPPRE_URE2 did not send its remote contractors security awareness reinforcement training, at least quarterly, the remote contractors had received training on cyber security awareness, had Personal Risk Assessments completed on them, and given the nature of the work they were performing for SPPRE_URE2 and their professional experience, the contractors were intimately aware of potential cyber security threats. Finally, no actual harm occurred as a result of this noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) Sent security reinforcement information materials to remote contractors that had not been receiving such materials; 2) Improved vendor and contractor on-boarding information to ensure personnel list would include vendors and contractors; 3) Integrated security reinforcement information materials with SPPRE_URE2 access management process; and 4) Integrated validation steps into SPPRE_URE2’s communication and awareness procedure to verify contractors and vendors receive materials SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013221 | CIP-004-3 | R4 | SPPRE_URE2 submitted a Self-Certification stating that it had instances of noncompliance with CIP-004-3 R4, R4.1, and R4.2. SPPRE_URE2 discovered the following issues of noncompliance: 1) A SPPRE_URE2 contract employee was granted unescorted physical access to certain Critical Cyber Assets; however, the employee’s name and access rights were inadvertently included on SPPRE_URE2’s electronic access list. Further, although SPPRE_URE2 revoked the employee’s physical access to Critical Cyber Assets when such access was no longer required, SPPRE_URE2 did not update the access list within seven calendar days to reflect the change. 2) A request to revoke access of a SPPRE_URE2 employee was submitted but access was not revoked within seven calendar days of the request. 3) For a limited number of employees, whose roles changed but whose access rights remained the same, SPPRE_URE2 did not follow its process of removing and reinstating access. Instead, it allowed the employees to keep their original access rights during the approval process for the new roles. 4) SPPRE_URE2 revoked an employee’s electronic access to Critical Cyber Assets within seven calendar days of the employee no longer requiring such access, but did not revoke the firewall access rights of the same employee for 29 days. The duration of this minimal risk instance of noncompliance was approximately 35 months. The root cause of these instances of noncompliance was a lack of effective internal controls to ensure compliance with CIP-004-3 R4, R4.1 and R4.2. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-004-3 R4, R4.1, and R4.2 has the potential to affect the BPS by allowing unauthorized access to Critical Cyber Assets. The risk to the BPS was reduced by the following factors. 1) Regarding the contract employee, he was given physical access rights for only 10 days, which automatically expired at the end of the tenth day. This mitigated the contractor’s ability to gain physical access to any of SPPRE_URE2’s Critical Cyber Assets after the request was made to remove his physical access. 2) Regarding the employee whose access was not revoked within seven calendar days of the revocation request, it was subsequently determined that the employee required continued access and that the revocation request was made in error. 3) Although SPPRE_URE2 allowed access to continue for certain SPPRE_URE2 employees during the vetting of the required access following a change in the employees’ responsibilities, these employees’ need for access to Critical Cyber Assets continued and did not change. This instance was a documentation error only. 4) Regarding the employee who retained access rights to the firewall, the employee did not have any electronic access to the SPPRE_URE2’s network or the firewall. Further, the employee had his physical access to SPPRE_URE2’s Critical Cyber Assets revoked in a timely manner. Finally, this employee’s access rights to the SPPRE_URE2 firewall were revoked 29 days after the request for revocation had been submitted. Additionally, regarding all instances of noncompliance, all employees had a business need for access when access was granted; all had completed CIP training and possessed current Personal Risk Assessments; and none of the employee’s access changes were due to termination of employment. Finally, no actual harm occurred as a result of these instances of noncompliance. | To mitigate these minimal risk instances of noncompliance, SPPRE_URE2: 1) Implemented additional controls and workflow elements to programmatically ensure that revocation of access to Critical Cyber Assets occurs within the timeframes required in CIP-004-3 R4.2; 2) Delivered training and awareness communications to company personnel; and 3) Created a centralized database for access management information for employees and contract personnel. SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013223 | CIP-005-3a | R2; R2.3, R2.4 | SPPRE_URE2 submitted a Self-Report stating that it had an instance of non-compliance with CIP-005-3a, R2; R2.3 because it did not implement or maintain a procedure for securing dial-up access to its Electronic Security Perimeter (ESP). Because SPPRE_URE2 did not have any dial-up access points to its ESP, it had not documented a process for securing dial-up access as required by R2.3. This noncompliance was assigned a NERC Violation Identification Number. Subsequently, during a Compliance Audit, SPP RE determined that SPPRE_URE2 had a minimal risk instance of noncompliance with CIP-005-3a R2.4. Specifically, a rule within a SPPRE_URE2 firewall ruleset enabling a particular service access also enabled external interactive access into the SPPRE_URE2 ESP, via an admin group. However, SPPRE_URE2 did not established strong procedural or technical controls to ensure the authenticity of anyone accessing the ESP via the admin group because the group was a shared account. This noncompliance was assigned a separate NERC Violation Identification Number. On September 15, 2015 SPP RE administratively dismissed the audit finding, consolidating its facts and circumstances with self report. The duration of this minimal risk instance of noncompliance was approximately 22 months. The root cause of these instances of noncompliance was a lack of effective internal controls to ensure authenticity of access to its ESP. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because SPPRE_URE2 did not have any dial-up access points to its ESP, a procedure for securing dial-up access to the ESP was not necessary. Moreover, under CIP Version 5, since SPPRE_URE2 did not have dial-up access to its ESP, it would not be required to implement or maintain such a procedure. Failure to strongly authenticate external interactive access to the ESP could expose the ESP to unauthorized access. Although SPPRE_URE2 did not have strong technical controls in place to ensure the authenticity for external access via the admin group, the risk of unauthorized access to its ESP is mitigated because: 1) Only certain staff had access to the administrative account that enabled external interactive access; 2) That staff was a small group consisting of 9 people; 3) SPPRE_URE2 had a procedural control for not allowing the admin account to actually be used for external interactive access; 4) SPPRE_URE2 performed regular reviews of logs of any interactive use from the administrative account; and 5) the admin account was for system to system communication. No actual harm occurred as a result of this noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2 1) Disabled the certain service/ rule 2) Developed and implemented procedure(s) for use of administrator accounts; and 3) Executed a commissioning process for all CIP-related cyber assets to validate elements for compliance. SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013013229 | CIP-009-3 | R2 | SPPRE_URE2 submitted a Self-Report stating that it had a minimal risk instance of noncompliance with CIP-009-3 R2. Specifically, SPPRE_URE2 did not have documented evidence to demonstrate it had performed a recovery plan exercise for its Electronic Access Monitoring and Notification System (EACMS) in two years. The duration of this minimal risk instance of noncompliance was approximately 21months. The root cause of these instances of noncompliance was SPPRE_URE2’s lack of internal controls regarding annual recovery plan exercises. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to perform an annual exercise of a recovery plan may result in a lack of preparedness or failure of staff to appropriately respond to an event requiring the recovery of a Critical Cyber Asset. Although SPPRE_URE2 could not demonstrate it exercised its EACMS recovery plan, SPPRE_URE2 was able to demonstrate it exercised the recovery plans for other SPPRE_URE2 Critical Cyber Assets. These exercises ensured SPPRE_URE2 staff was aware of its recovery plans and established business continuity and disaster recovery techniques and practices for its Critical Cyber Assets. SPPRE_URE2’s EACMS recovery plan, although not exercised, contained specific actions and defined the roles and responsibilities necessary for SPPRE_URE2 employee to recover the EACMS. No actual harm occurred as a result of this instance of non-compliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1) Exercised the recovery plan for its EACMS; 2) Revised its backup and recovery plan, which had included individual recovery plans based on device type, to include one overall recovery plan for all CIP related cyber assets, including RSA EnVision (EACMS), SPPRE_URE2’s EACMS; 3) Established mechanism for tracking and monitoring exercises of recovery plans to provide additional controls for execution; 4) Delivered training and provided awareness communications (backup and recovery plans) to applicable staff. SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015169 | CIP-005-3a | R1.5 | WECC_URE1 submitted a Self-Report stating that, as a Responsible Entity, it had an issue of CIP-005-3a R1.5. During WECC_URE1’s annual review of CIP access, WECC_URE13 discovered that one employee’s CIP access was not fully revoked after a change in the employee’s access rights. The employee in scope originally had a network administrator role that granted the employee logical access to WECC_URE1’s Cyber Assets used in the access control and/or monitoring of the ESP. The employee transitioned to a new role that required CIP access for compliance and assessment of the CIP program, but did not require logical access to Cyber Assets used in the access control and/or monitoring of the ESP. WECC_URE1 requested revocation of the employee’s original access rights within seven calendar days. WECC_URE1 discovered that the individual responsible for revoking CIP access did not follow all of the steps of WECC_URE1’s revocation process. As a result, WECC_URE1 did not revoke the access rights for all user roles that were no longer required in the employee’s new role. The employee had logical access to four devices within the ESP. WECC_URE1 conducted a full review of all CIP access types to determine the extent and scope of the issue. An independent third party reviewed the results of the review. The review confirmed there were no additional instances of CIP-005 R1 issues. WECC_URE1 revoked the access rights that were no longer required in the employee’s new role. The root cause of the compliance exception was that the procedures used allowed for human performance errors which led to incomplete deprovisioning of CIP-related user access. The procedures provided complete steps for access provisioning, but left it to the user to mentally reverse the steps to process a revocation. The compliance exception start date was eight calendar days after the employee’s access rights changed. The compliance exception end date was when WECC_URE1 removed the employee’s access for all user roles no longer required in the employee’s new role. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not revoke access within seven calendar days for one employee who no longer required access to Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter. The employee had access to four devices within the Electronic Security Perimeter. The employee has been an WECC_URE1 employee in good standing for 15 years. The employee in scope remains employed by WECC_URE1 and continues to maintain authorized cyber access to a number of CIP Cyber Assets and Cyber Asset information. The employee has been trained to properly handle CCAs and CCA information. Additionally, the employee had a current PRA and CIP training. WECC_URE1 performs annual reviews of CIP access rights. Additionally, WECC_URE1 performed a full review of all CIP access rights and found no additional issues. The results of the full review were verified by an independent third party. No harm is known to have occurred from this noncompliance. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) deprovisioned access no longer required for the employee's job duties; 2) internally investigated to determine extent of condition; 3) third-party review verified internal findings; 4) utilized internal Corrective Action Program to identify root cause of this situation; 5) developed plan to prevent future incidents based on Root Cause Analysis findings; 6) updated access creation and revocation procedure to include detailed steps to perform all account request scenarios for adding and deleting accounts; and 7) conducted department training on updated procedure, including account management processes defined in the access control server and defender procedures.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014103 | CIP-007-1 | R5 | WECC_URE2 self-reported that it was in possible non-compliance with CIP-007-3a R5. According to the Self-Report, certain WECC_URE2 employees were not using user accounts as approved by WECC_URE2, resulting in an inaccurate audit trail of individual user account access history. A WECC Subject Matter Expert (SME) reviewed the Self-Report and conducted interviews with WECC_URE2’s compliance staff. According to the SME, a workstation provides read-only access to WECC_URE2’s EMS. Certain WECC_URE2 employees did not lock the workstation during their shifts, and did not log off of their accounts after their shifts. Sometimes, the next employee would use the account of the previous employee, instead of his/her own, violating WECC_URE2’s user account policy. WECC Enforcement reviewed the Self-Report and the SME’s findings and determined that WECC_URE2 had a compliance exception with CIP-007-1 R5, for its failure to ensure that user accounts were implemented as approved, and therefore, could not show an audit trail for individual user account access. The root cause of this non-compliance is a lack of compliance understanding of the importance of following WECC_URE2's user account policy. | This compliance exception posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk electric system. In this instance, WECC_URE2 failed to ensure that user accounts were implemented as approved and failed to have an audit trail for individual user account access for 90 days. If WECC_URE2 does not know if the accounts were being used by appropriate personnel, it would not know if an unauthorized person was using the account, or if unauthorized personnel had access to the EMS software installed on the workstations. No harm was known to have occurred. However, WECC_URE2 implemented preventative controls by disabling USB ports and CD drives, to prevent someone from using code on a USB or CD to attack the workstation; or to install malicious code or run port scanning from a USB or CD. Also, WECC_URE2 granted read-only access rights, preventing these users from using any application that would install malicious software. WECC_URE2 implemented detective controls by setting up an alerting system that generated alerts when the system detected port or system scanning, which would detect any port scanning attempts. The alerting system also sends an alarm if any changes in generation or transmission are detected, thus alerting the appropriate personnel of any issues. Additionally, the area where the workstation is located is manned 24x7 by at least one individual, who would likely detect any physical damage being done to the device, or if anyone attempted to use a USB, or other device. Also, WECC_URE2 deploys anti-virus software to detect any malicious software. | To mitigate this compliance exception,WECC_URE2 removed the EMS workstation from the ESP and PSP, and provided to WECC an updated network diagram showing that the asset had been removed. WECC verified completion of the mitigation plan.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015015163 | CIP-004-3a | R3; R3.2 | WECC_URE3 submitted a Self-Report stating that it was in non-compliance with CIP-004-3a R3. The root cause of this issue was that the entity did not have a formal process to review PRA dates. WECC_URE3 self-reported that the issue was identified in a report relating to CIP-004-3a R3.2. The report indicated that the personnel risk assessment (PRA) for one employee exceeded its seven year renewal and should have expired. Though the employee had physical access to control centers after the PRA expired, they did not have logical access to any of the CCAs in the PSPs. Upon verification of this discovery, WECC_URE3 immediately revoked access to the employee pending completion of an updated PRA. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. WECC_URE3 implemented good internal controls to identify and correct the lapse. Specifically, WECC_URE3 generated and reviewed a report identifying the oversight within one month of the PRA expiration date, and revoked access within hours of discovering the issue. Further, the employee in question did not have electronic access to the ESP or to any CCAs, and only had physical access to facilities that are continuously staffed and monitored. The employee did not access PSPs during the period in question. The employee has worked for WECC_URE3 for more than 10 years, with an exemplary employment history, and passed the updated PRA. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) revoked access to the employee pending completion of an updated PRA; 2) validated the PRA dates for all other individuals and confirmed the lapse was limited to one employee; 3) performed a review to confirm that the employee did not access PSPs during the period in question; and 4) provided training and revised its quarterly access review process to identify pending PRA renewals. WECC has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015015050 | CIP-003-3 | R2 | WECC_URE4 self-reported that it had a compliance exception with CIP-003-3 R2, for failing to document a CIP senior manager change within 30 days of the change occurring. A WECC Subject Matter Expert (SME) reviewed the Self-Report and conducted interviews with WECC_URE4 compliance staff. The WECC_URE4 CIP senior manager delegate left WECC_URE4, and WECC_URE4 did not document the change within 30 calendar days, per CIP-003-3 R2. WECC_URE4 discovered this oversight when WECC_URE4 changed its CIP senior manager in its documentation. Enforcement reviewed the Self-Report and the SME’s findings and determined that WECC_URE4 had a compliance exception of CIP-003-3 R2, for its failure to document a change to its CIP senior manager delegate within 30 calendar days of the change. The root cause of this compliance exception was a lack of compliance understanding and a lack of compliance process, to ensure WECC_URE4 timely updated its documentation. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to document a CIP senior manager delegate change within 30 days of the change. Failing to document changes to delegates could lead to other compliance tasks not being completed in a timely matter. For instance, if the delegate were responsible for approving WECC_URE4's risk-based assessment methodology, Critical Asset list, and/or Critical Cyber Asset list each year, the task may not be completed timely each year, which could lead to WECC_URE4’s failure to identify and approve changes to its RBAM, CA or CCA lists. No harm was known to have occurred. WECC_URE4 had preventive controls in place. WECC_URE4's CIP senior manager could have performed any task delegated to the delegate, preventing any task from not being completed in a timely manner. | WECC_URE4 mitigated this compliance exception. The mitigation concluded on the date WECC_URE4 updated its CIP senior manager and delegate in its documentation.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015014848 | CIP-006-3c | R1 | WECC_URE5 self-reported its possible noncompliance with CIP-006-3c R1. WECC_URE5 reported that it failed to escort one visitor within a CIP protected facility. WECC_URE5 reported it left the visitor alone for 1 minute and 14 seconds. WECC_URE5 submitted a second Self-Report citing another possible noncompliance with this Standard. In the second Self-Report, WECC_URE5 reported that it left a visitor alone for 12 seconds who was attending a training program. A WECC Subject Matter Expert (“SME”) reviewed the two Self-Reports, consolidated in this one compliance exception. Regarding the first Self-Report, the SME determined thatprior to entering the Physical Security Perimeter (“PSP”), a visitor signed in to the appropriate visitors’ log and acquired a visitor’s badge. However, the visitor was not continuously escorted while within the PSP, and was left alone for a total of 1 minute and 14 seconds. Regarding the second Self-Report, the SME determined that WECC_URE5 hosted a training program attended by a number of visitors. The employee serving as the escort was also leading the training. During the training, one visitor was alone in the PSP for a total of 12 seconds. However, the visitor was recorded on video during this time. The SME determined that WECC_URE5 had a possible noncompliance with CIP-006-3c R1, and forwarded the information to Enforcement for review. Enforcement reviewed the Self-Reports and the SME’s findings and determined that WECC_URE5’s failure to continuously escort a visitor within the PSP on two occasions is a compliance exception of CIP-006-3c R1.6.2. The root cause of the compliance exception is a lack of compliance understanding and a lack of compliance process to ensure that WECC_URE5's employees understand and follow WECC_URE5's physical security procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to provide continuous escort to PSP visitors on two occasions. On the first occasion, the visitor was left unattended for 1 minute and 14 seconds. On the second occasion, the visitor was left unattended for a period of 12 seconds. Failure to provide a consistent escort to a PSP visitor could potentially result in the visitor gaining access and possibly physically and/or logically compromising a Critical Cyber Asset (“CCA”) within the PSP. No harm is known to have occurred. However, neither visitor attempted to nor had actual access to any CCAs during the unescorted periods. In the first instance, all CCAs were located behind cabinet doors that are monitored with alarms. Should the visitor have opened a CCA cabinet door, an alarm would have registered in the Physical Access Control System, and an email alert would have been sent to SCADA staff. Also, WECC_URE5 uses continuous video monitoring within the PSP. In both instances, the visitors were recorded for the entire duration of their unescorted access. WECC_URE5 reviewed the videos and confirmed that neither visitor attempted to access or approach any CCAs. | To mitigate this compliance exception, WECC_URE5: 1) developed a handout to supplement the WECC_URE5 visitor control program that outlines escorting responsibilities within PSPs; 2) distributed the handout from the CIP senior manager to all WECC_URE5 employees; 3) developed and attached to the lanyard of each visitor access badge a bright pink card that acts as a reminder to the escort and contains a list of escort responsibilities; 4) updated its program to require escorts submit a statement, along with each submitted visitor badge request, stating that they have reviewed this program and understands their responsibilities as a PSP Escort; and 5) will not issue a visitor badge without the required statement of understanding.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2014014231 | CIP-004-3a | R4 | WECC_URE6 submitted a Self-Report stating that, as a Responsible Entity, it had two issues with CIP-004-3a Requirement 4. Regarding the first issue, WECC_URE6 reported a contract employee terminated her employment with WECC_URE6. Because the termination was voluntary and not for cause, WECC_URE6 had seven calendar days to update its list of personnel who have access to Critical Cyber Assets (CCAs). WECC_URE6 also had seven calendar days to revoke the employee’s access to CCAs. However, WECC_URE6 did not update its list or revoke access until 14 calendar days after the contract employee terminated her employment. WECC_URE6’s security ran a report and identified the contract employee was still on WECC_URE6’s list and had physical access to WECC_URE6’s CCAs. Security disabled the contract employee’s access to the CCAs. From termination to revocation, the employee’s access badge was in the possession of the contract employee’s manager. The access badge was not used while in possession of the manager. The compliance exception start date for the first issue was the eighth calendar day after the contract employee terminated her employment. The compliance exception end date for the first issue was when WECC_URE6 updated its list and revoked access. Regarding the second issue, WECC_URE6 reported an employee retired. WECC_URE6 revoked the employee’s physical and logical access to CCAs within seven calendar days. However, WECC_URE6 discovered that it had not removed the retired employee’s name from the list of personnel who have access to CCAs. WECC_URE6 updated the list to show that the retired employee no longer had access to CCAs. The two employees had access to substations containing CCAs. The compliance exception start date for the second issue was the eighth calendar day after the employee retired. The compliance exception end date for the second issue was when WECC_URE6 updated its list. The root cause of the compliance exception was lack of training on the correct method to process employee terminations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE6 did not revoke physical access rights or update the access list within seven calendar days for one employee who no longer required access. WECC_URE6 also did not update the access list within seven calendar days for another employee who no longer required access. Failing to revoke access rights could have led to unauthorized access of the substations. The potential harm is limited by the controls implemented by WECC_URE6. Specifically, WECC_URE6 physically monitors the PSPs twenty-four hours a day, seven days a week using cameras, motion detectors, access control, alarm monitoring, and a backup monitoring system via an Intrusion Protection System. This reduces the likelihood that an unauthorized individual would be able to remain undetected while attempting to access the substations or while attempting to cause damage to the devices. WECC_URE6 staff at the control center would also likely detect any significant changes made at a substation. WECC_URE6’s substations are designed so that devices from one substation cannot directly cause an outage at another substation. This control of isolating substations reduces the potential load loss to a single substation. WECC_URE6’s substations are also set up with parallel redundancy, which could allow WECC_URE6 to switch to another substation if a substation experiences issues. This control reduces the likelihood of a local outage. No harm is known to have occurred from this compliance exception. | To mitigate this issue, WECC_URE6: 1) disabled the contract employee’s physical access to Critical Asset substations; 2) revised its procedure to use a report listing contract expiration dates to revoke physical access; 3) ensured logical access was removed and updated the access list to reflect the actual access rights of the retired employee; and 4) developed a check list of steps that need to be completed upon revocation of logical access to CIP Cyber Assets.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2014014309 | CIP-006-3c | R1.4 | On August 15, 2014, WECC_URE6 submitted a Self-Report stating that, as a Responsible Entity, it had an issue of CIP-006-3c R1.4. Specifically, WECC_URE6 reported two instances of noncompliance with CIP-006-3c R1.4. Regarding the first instance, WECC_URE6 reported an employee requested a temporary badge from a WECC_URE6 security officer. Instead of applying the employee access privileges to the temporary badge, the security officer applied the access privileges of a different WECC_URE6 employee who had a similar name. As a result, the employee was provisioned unauthorized access to ESPs, PSPs, and devices consisting of workstations, firewalls, servers, and power-line communication devices located at a remote facility. WECC_URE6 discovered the error and revoked the employee's temporary access rights. The employee did not attempt to access any of the unauthorized PSPs. The root cause of the first instance was the security officer confusing similar names and not requesting identification from the employee for validation. Regarding the second instance, WECC_URE6 reported that an employee was provisioning physical access for a group of WECC_URE6 employees to specific CIP-protected assets at a generating facility. The employee was granting access to a number of areas within the facility, and in the process of granting access, inadvertently added access for one employee to a PSP that the employee was not authorized to access. The employee had access to ESP, PSP, and devices consisting of a power-line communication device and a firewall. WECC_URE6 security discovered the error and revoked access. The employee was not aware that he had access to the PSP, nor did the employee attempt to access the PSP while he had access. The root cause of the second instance was a training issue on how to provision specific access rights in WECC_URE6's system. The compliance exception start date for the first instance of noncompliance was when WECC_URE6 provisioned physical access rights to an employee who did not require the access rights. The compliance exception start date for the second instance of noncompliance was when WECC_URE6 provisioned physical access rights to an employee who did not require access rights to the PSP. The compliance exception end date for the first instance of noncompliance was when WECC_URE6 revoked the physical access rights. The compliance exception end date for the second instance of noncompliance was when WECC_URE6 revoked access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE6 provisioned physical access rights to one employee who did not require access to ESPs, PSPs, and devices. WECC_URE6 also provisioned physical access rights to one employee who did not require access to ESP, PSP, and devices. Failing to properly provision physical access to employees could result in devices becoming compromised. Any potential issues are limited by the controls implemented by WECC_URE6. Regarding the first instance of noncompliance, due to the distance between the two facilities, it was unlikely that the employee could have traveled to the remote facility before WECC_URE6 revoked unauthorized access. WECC_URE6 placed most of the devices in locked cabinets that generate alarms if accessed, reducing the likelihood that an unauthorized individual would be able to physically access or damage the devices. WECC_URE6 implements video surveillance in all PSPs, which could also detect any unauthorized use of the devices. The devices are further protected by USB port blockers preventing individuals from using malware on a USB to gain logical access to the devices. WECC_URE6 also uses antivirus that would likely prevent a malware attack. WECC_URE6 implements an active syslog server that could detect any unauthorized use of devices and alert personnel via an alarm. No harm is known to have occurred from this compliance exception. | To mitigate this issue, WECC_URE6: 1) updated the existing procedure for how a temporary badge is created to now state that a photo ID or WECC_URE6 employee number is required so that security personnel can verify the requester's identity before provisioning a temporary badge; 2) updated the operations procedure to include a new section about reader groups and readers and updated the lists of monitoring points (i.e. readers, cameras) found in the Appendix of the procedure; and 3) trained staff that have workstation logical access on the new procedures.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2014014529 | CIP-007-3a | R1 | WECC_URE6 submitted a Self-Report stating that it had an issue of CIP-007-3a R1. WECC_URE6 reported that a technician working at s substation connected a laptop to four gas monitors. The gas monitors monitor the transformers’ gas composition and are used to diagnose transformer issues. The software on the laptop was more current than the software on the gas monitors. The new software on the laptop could not communicate with the old firmware on the gas monitors. As a result, the software on the laptop automatically pushed out a firmware update to upgrade the software on the monitors. Because the upgrade occurred automatically, WECC_URE6 did not ensure that significant changes to existing Cyber Assets did not adversely affect existing cyber security controls. The root cause of the compliance exception was WECC_URE6 did not consider system interactions before connecting two devices leading to an unplanned upgrade. The compliance exception start date was when the laptop was connected and the gas monitors’ firmware upgraded creating a significant change to an existing Cyber Asset. The compliance exception end date was when WECC_URE6 performed security testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE6 did not test a significant change to an existing Cyber Asset to ensure the change did not adversely affect existing cyber security controls. Specifically, a technician connected a laptop, with more current software. This prevented the laptop from communicating with four gas monitors and caused the gas monitors to automatically upgrade to the new software. However, WECC_URE6 implemented controls to address any potential issues. The technician was on-site during the firmware upgrade and could have detected an unsuccessful upgrade. If the technician discovered that the firmware upgrade was unsuccessful, as evidenced by the laptop’s continued failure to communicate with the gas monitors, the technician could have worked with the vendor to restore the gas monitors to a previous firmware version. This would restore the gas monitors’ diagnostic capabilities. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) performed security testing on each device to ensure the firmware upgrade did not adversely affect existing cyber security controls; 2) worked with the vendor to make sure future firmware upgrades are communicated and there are no automatic upgrades if firmware does not match between the laptop and monitors; and 3) trained personnel to raise awareness about these issues and steps to take to avoid future violations. WECC has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014013934 | CIP-007-3a | R2.1 | WECC_URE7 submitted a Self-Report stating that it had an issue with CIP-007-3a R2. Specifically, WECC_URE7 reported that it had several devices that did not have baseline documentation to demonstrate that the ports had not previously been authorized when those ports were put into operation. WECC determined that for three devices, WECC_URE7 failed to establish a baseline of ports and services. WECC_URE7’s failure to enable only those ports and services required for normal and emergency operations is a compliance exception of CIP-007-3a R2.1. The compliance exception began when WECC_URE7 failed to establish a baseline of authorized ports and services prior to adding new ports to the Electronic Security Perimeter (“ESP”), and continued until WECC_URE7 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 failed to establish a ports and services baseline for three devices and therefore could not ensure it enabled only those ports and services required for normal and emergency operations. However, WECC_URE7 implemented preventive, detective and compensating controls. As a preventive control, WECC_URE7’s operating system is configured to limit which ports are allowed to open and start. As a detective control, WECC_URE7 monitored logs and sent alerts for potential security issues. An alert would have informed security personnel of unauthorized access, allowing them to close the ports. As a compensating control, WECC_URE7’s operating system was configured to prevent unknown ddresses from connecting to the network. WECC_URE7 also implemented physical locks on the cabinets that contain the devices. Finally, WECC_URE7 uses firewalls to restrict network access within the ESP and to provide access point protections. | To mitigate this issue, WECC_URE7: 1) performed a vulnerability assessment; and 2) provided evidence of a current baseline of authorized ports and services for the devices in scope. WECC has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014013936 | CIP-007-3a | R8; R8.2 | WECC_URE7 submitted a Self-Report stating that it had an issue with CIP-007-3a R8. Specifically, WECC_URE7 reported that several network devices did not have a baseline vulnerability assessment performed in the 2012 program year. WECC determined that WECC_URE7 failed to perform a Cyber Vulnerability Assessment (“CVA”) on nine devices located within the ESP. WECC_URE7’s failure to perform a CVA on all cyber assets within the ESP at least annually is a compliance exception of CIP-007-3a R8. WECC_URE7’s failure to verify that only ports and services required for operation of the cyber assets within the ESP are enabled is a compliance exception of CIP-007-3a R8.2. Enforcement further determined that the compliance exception began on the beginning of the year in which WECC_URE7 failed to complete a CVA, and continued until WECC_URE7 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 failed to run a vulnerability scan and establish a CVA baseline for nine devices. However, WECC_URE7 implemented preventative, detective and compensating controls. As a preventive control, WECC_URE7’s operating system is configured to limit which ports are allowed to open and start. As a detective control, WECC_URE7 monitored logs and sent alerts for potential security issues. An alert would have informed security personnel of unauthorized access, allowing them to close the ports. As a compensating control, WECC_URE7’s operating system was configured to prevent unknown addresses from connecting to the network. WECC_URE7 also implemented physical locks on the cabinets that contain the devices. Finally, WECC_URE7 uses firewalls to restrict network access within the ESP and to provide access point protections. | To mitigate this issue, WECC_URE7: 1) performed a vulnerability assessment; and 2) updated the vulnerability assessment task schedule to improve accountability for tasks. WECC has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014014085 | CIP-007-3a | R9 | During a Compliance Audit WECC determined that WECC_URE7 had an issue of CIP-007-3a R9. Evidence provided by WECC_URE7 demonstrated a detailed annual review of CIP-007 related evidence, but WECC_URE7 was unable to provide evidence that it reviewed overarching process/procedure documents developed for each Requirement in CIP-007. WECC determined that WECC_URE7’s failure to review and update the documentation for policies and/or procedures specified in CIP-007 at least annually is a compliance exception of CIP-007-3a R9. WECC further determined that the compliance exception began when the Standard became enforceable, and continued until WECC_URE7 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 failed to annually review process and/or procedure documentation associated with CIP-007. Such failure could result in out of date processes and procedures, which then can lead to erroneous practices that do not meet compliance obligations. All Critical Cyber Assets (“CCAs”), non-CCAs inside the ESP, Electronic Access Control and Monitoring devices, and Physical Access Control System cyber assets were affected. While WECC_URE7’s failure to perform an annual review on its CIP-007 documentation presented an opportunity where changes to the documents would not have been properly reflected and protections offered to Critical Cyber Assets may not have been properly applied or removed, the potential risks associated with this violation are limited. Specifically, as a compensating measure, WECC_URE7 conducts a robust annual review of all evidence associated with CIP-007. Such review would alert WECC_URE7 of any issues with potentially out of date processes and procedures. | To mitigate this issue, WECC_URE7: 1) created a task notification that details the recovery plan sections under review and confirms the performance of the review will be dispatched as a recurring reminder on an annual basis; and 2) incorporated a review block with CIP-007-3a R1 to R8 showing the date of annual review. WECC has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014013932 | CIP-005-3a | R1 | WECC_URE7 self-reported that it was in possible non-compliance with CIP-005-3a R1. A WECC Subject Matter Expert (SME) reviewed the Self-Report and conducted interviews with WECC_URE7 compliance staff, and determined that WECC_URE7 had a compliance exception under CIP-005-3a R1, for its failure to afford the protective measures specified in standards CIP-007 R4, CIP-007 R5 and CIP-007 R6, (as incorporated in CIP-005 R1,) for devices used for access control and monitoring of the electronic security perimeter (ESP). For CIP-007 R4 and R5, WECC_URE7 failed to timely update existing TFEs. For CIP-007 R6, WECC_URE7 failed to maintain 90 days of logs, because the firewall could not forward its logs to the security information and event management (SIEM). Specifically, after an upgrade of the SIEM, the SIEM rejected the logs from the firewall, resulting in lost logs. The root cause of this compliance exception was WECC_URE7’s lack of compliance understanding of all requirements of the Standard, leading to its failure to timely update the appropriate TFEs, and its failure to ensure that its systems could maintain the required 90-day log information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE7 failed to implement the protections for CIP-007 R4, R5 and R6, as incorporated in CIP-005-3a R1. No harm was known to have occurred. For CIP-007 R4 and R5, failing to update its existing TFEs could result in WECC_URE7 misidentifying the critical role or function of these devices, resulting in incorrect compensating measures that could weaken the overall security of the. For CIP-007 R6, WECC_URE7 failed to log and generate security events on firewalls used in the access control and monitoring of ESPs. WECC_URE7 implemented preventative controls. Specifically, the devices will not allow any code injection or virus installation. They also control, by design, traffic based on ports/services with deep packet inspection and the ability to capture malicious traffic with an internal or external host destination, reducing the likelihood of weakening the overall security of the ESP. Also, WECC_URE7 had account management policies in place to restrict unauthorized logical user access and physical controls in place to protect and restrict physical access to the ESP. The devices essential to the EMS had access to WECC_URE7’s intranet, but not the internet, reducing the likelihood that someone external to WECC_URE7 could access these devices or maliciously damage the software applications that are used in the EMS. The firewalls were also configured to be restrictive, such that, network access was configured to limit access to the ESP and prevent unnecessary TCP/IP and UDP/IP ports and services from being enabled in order to block unauthorized access. WECC_URE7 implemented detective controls, using logging with automated alerting/notifications on all CCAs and non-CCAs within the ESP. For that reason, WECC_URE7 would receive notifications if there were any unauthorized access attempts to its ESP. WECC_URE7 implemented corrective controls, employing a backup and recovery policy to restore data in case of a cyber-security incident; thus, the integrity of the data could be restored, if needed. WECC_URE7 has additional strong corrective controls. WECC_URE7 had the capability to log into each firewall and review the logs manually. And, WECC_URE7 implemented patch management controls to strengthen its overall ESP environment by fixing software issues via patches. | To mitigate this compliance exception, WECC_URE7: 1. Submitted revised TFEs; 2. Updated the SIEM configuration; and 3. Provided evidence to WECC that the devices are visible by WECC_URE7’s log aggregation device. WECC verified that WECC_URE7 completed all actions outlined in the plan.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014013933 | CIP-009-3 | R5 | WECC_URE7 self-reported it was in possible non-compliance with CIP-009-3 R5. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE7 compliance staff, and determined that WECC_URE7 had a compliance exception under CIP-009-3 R5, for its failure to document its annual test of its backup media for a single program year . WECC determined that although WECC_URE7 performed backup for some devices that were not Critical Cyber Assets, it did not perform the annual test for the program year. WECC_URE7 did perform the test in the next program year. The root cause of this compliance exception was a human performance issue, resulting in the individual tasked with the Annual Backup testing not performing that job function. In addition, WECC_URE7’s lack of a compliance process for one calendar year to ensure that annual tests on WECC_URE7’s backup media were documented ultimately resulted in a missing test. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE7 failed to test information essential to recovery for certain switches. No harm was known to have occurred. Failing to test the running configuration of its operating system could result in making the false assumption that the back-ups are intact. Falsely assuming that these devices have good back-ups could lead WECC_URE7 to assume that these back-ups could be restored and work correctly during a software and/or hardware incident, or when new switches are added to the ESP. WECC_URE7 implemented preventative controls by using switch back connections on every switch; adding an extra layer of hardware redundancy to prevent the network connections within the ESP from going down if one switch within the configuration goes down. WECC_URE7 also has extra back-up switches in the event of hardware failure in stand-by mode. WECC_URE7 can enable the back-up switches to take over for switches that have hardware issues, allowing the operators to connect to the EMS application with little downtime. And, WECC_URE7 installed locks on cabinets that contain these switches, preventing unauthorized personnel from physically damaging the switches. WECC_URE7 implemented detective controls that can monitor the switch logs and send alerts when it finds hardware failures. WECC_URE7’s SIEM is configured to scan logs for hardware failure alert messages 24 x 7, to alert on-call personnel. | To mitigate this compliance exception, WECC_URE7: 1) submitted backup testing evidence; and 2) submitted a description of its reminder system set up for testing of backup media. WECC verified that WECC_URE7 completed all actions outlined in the plan as of the date WECC_URE7 completed the annual testing of the backups for the switches.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2015014753 | CIP-006-3c | R5 | WECC_URE8 submitted a Self-Report stating that it was in possible non-compliance with CIP-006-3c R5. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE8 compliance staff, and determined that WECC_URE8 had a compliance exception with CIP-006-3c R5, for its failure to implement the necessary technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) 24 hours a day, seven days a week. Specifically, the WECC_URE8 security guards failed to investigate and document approximately 20% of PSP Door Alarms (primarily forced entry alarms) and contractor security guards also failed to investigate certain other alarms. WECC_URE8 discovered the discrepancies by comparing a complete list of door alarms compiled by a WECC_URE8 Compliance Engineer and the contractor security guard logs. The root cause for this compliance exception is miscommunication of WECC_URE8’ compliance practices; because some guards cleared the alarms without investigation (doors were held open too long). In addition, WECC_URE8 had a lack of compliance understanding related to its new logging system that requires security guards to make a log entry in the PAC system after he or she investigates an alarm. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE8 failed to review its records for Physical Security Perimeter door alarms for three months and failed to investigate general alarm alerts for six months. WECC_URE8 implemented preventative controls by stationing guards within view of some doors, card readers, and separate physical control room door with a Common Access Card (CAC) reader. In addition, WECC_URE8 does not have remote access to CCAs outside of the ESP/PSP, and the facility is restricted for personnel who have been granted access. WECC_URE8 implemented detective controls with PSP door alarms, general (fire) alarms, guards, monthly security log reviews and trained authorized personnel looking for suspicious activities pertaining to malicious individuals. WECC_URE8 also verifies security log reviews every 30 days for the physical door within the control room that requires a CAC. | WECC_URE8 remediated this compliance exception by updating its PACS policy documentation to reflect the new logging system.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2015014873 | CIP-004-3a | R4 | WECC_URE8 submitted a self-certification stating that it was in possible non-compliance with CIP-004-3a R4. A WECC Subject Matter Expert (SME) reviewed the self-certification and conducted interviews with WECC_URE8’s compliance staff, and determined that WECC_URE8 had a compliance exception with CIP-004-3a R4, for its failure to timely revoke access, and to update the associated access list within seven days. Specifically, one employee had unescorted physical access to the control center. The employee was on a group with access to the control center. WECC_URE8 timely revoked access, the employee was given the cyber security training, and WECC_URE8 restored access; and updated the associated access list. WECC_URE8 does not have records of WECC_URE8 revoking the access in question, because it replaced its PACS system and did not retain the logs. Another employee had authorized unescorted physical access and was granted logical access to the PACS, to oversee the PACS for that day. The employee retained access, but WECC_URE8 did not complete the approval process. WECC_URE8 discovered the issue during the CVA process, because the list showed the employee’s physical access but not the logical access. WECC_URE8 added the employee to the list and then obtained the appropriate approvals. The root cause of this compliance exception is human error, as the employees granting the access did not follow WECC_URE8’s procedures; and a lack of compliance process to generate the access lists required for review for the Physical Access Control System (PACS). | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE8 failed to revoke access rights and update the access list within seven days of the access changing, for three employees. Specifically, there are three people in scope: WECC_URE8 granted access to two employees without following WECC_URE8’s approval process or updating the list; and the third employee no longer needed access, but WECC_URE8 did not timely revoke access and update the list. WECC_URE8 implemented preventive and detective controls, by stationing WECC_URE8 personnel in the control center 24 hours, seven days a week, to detect any unscheduled changes to the generator, and to prevent an unauthorized person from affecting generation. WECC_URE8 implemented other compensating controls ensuring each of the employees in question has a clean record at WECC_URE8, with the proper CIP training and PRAs; reducing the risk that they would attempt to affect generation. | To mitigate this compliance exception, WECC_URE8 obtained the necessary access approvals and added the three employees to the appropriate list.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014525 | CIP-007-3a | R5.1.1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R5.1.1. A RFC_URE1 employee requested access to a specific RFC_URE1 device, and selected “Normal” non-administrator access in RFC_URE1’s access request system. The employee’s manager then approved the “Normal” access request. However, the access provisioner gave the employee “Privileged” access, which is administrator access on the system. The employee should have requested “Privileged” access based on his job responsibilities. Also, the access request system should not have had an option for “Normal” access, which is non-administrative access. The only users who are allowed to login onto this particular system are administrators, and the provisioner knew that this was the case. The provisioner should have rejected the access request and contacted the user to inform him to request the correct, “Privileged”, access. However, because the provisioner knew that only administrators are allowed access to the system, the provisioner believed “Normal” access was administrative access for the system. In addition, the provisioner knew the person requesting access and his role in maintaining these systems. RFC_URE1 detected the error through its daily reconciliation report the following day, and revoked the “Privileged” access. The daily reconciliation report is a detective control that compares requested access to provisioned access to identify errors. Upon discovering the noncompliance, RFC_URE1 immediately revoked the “Privileged” access, and then reinstated it after the proper request was made, and requested a system change to update the available access request type for the particular system. The duration of this noncompliance is from the date the employee received a different level of access than requested, to the date RFC_URE1 revoked the “Privileged” access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee did in fact need administrator access, which the provisioner gave him, but the employee mistakenly requested the wrong access. Thus, this is an administrative error and there was no increased harm to the Bulk Electric System as a result of the provisioner giving the employee the access he actually needed. Second, RFC_URE1’s daily reconciliation process detected the issue within one day of its occurrence and RFC_URE1 immediately corrected the issue prior to the user utilizing the access, thus reducing the likelihood of any potential impact being realized. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) immediately revoked the incorrect account access and re-provisioned access as appropriate; 2) changed the instructions on the access request form to inform users and approvers to not request or approve “Normal” access for specific devices; 3) reviewed current accounts for the system at issue and confirmed proper level of access; and 4) refreshed the Provisioner Training with the provisioner employee.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015154 | CIP-004-3a | R4.2 | RFC_URE2 submitted a self-log stating that it had an issue of CIP-004-3 R4.2. RFC_URE2 determined that it had an issue of CIP-004-3 R4.2 because access was not revoked timely. RFC_URE2 personnel entered a Security Request System (SRS) ticket to remove physical access for a RFC_URE2 employee effective that day. The SRS ticket was not approved by the supervisor until nine days later and access was removed ten days later. Therefore, it was greater than seven days from the time it was determined that access was no longer needed until it was removed. The root cause of this violation was the supervisor’s decision to wait for information prior to approving the SRS ticket within the required timeframe. Despite the human performance issue in this instance, this was the only SRS ticket not processed in a timely manner at a time when a substantial number of employees were changing job functions due to the upcoming spin-off of the RFC_URE2 assets. This indicates that the existing training and procedures are largely effective in controlling against untimely removal of access. However, because this one individual’s access was not removed in a timely manner, there is a small risk that he could have continued to access these locations without a business need and taken actions that could have resulted in additional violations. The duration of this noncompliance is from the date the employee's access should have been removed to the date access was removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm to the reliability of the Bulk Electric System that could have occurred during the situation was close to none. Although the individual retained access to Physical Access Control Systems (PACS), Electronic Access Control and Monitoring Systems (EACMS) and Critical Cyber Assets (CCAs) and could have impacted a PACS device, electronic access control and monitoring equipment or a subset of Transmission Control Center (TCC) consoles, these actions would have triggered alarms initiating the necessary responses with regards to physical and cyber security through various monitoring methods. In addition, operator consoles at the Backup Operations Center would not have been impacted. RFC_URE2 considered the harm level was unlikely to be realized for the following reasons: • The individual understood the importance of the devices. • The individual had a valid personnel risk assessment (PRA) and training as well as a prior business need for access to these assets. • The individual continued working for RFC_URE2 in a different capacity during the period as a responsible and reliable employee. • Although access was available, the individual did not utilize the access during the timeframe from the ticket initiation to the access removal. • The individual was not disgruntled and displayed no intention of causing harm. • The SRS ticket was entered and access was removed ten days later which was a very short time past the required seven days. • Any changes to the PACS, EACMS, and CCA devices supporting EACMS activities would have been detected through various monitoring methods. These changes would have been investigated and corrected in a timely manner. RFC_URE2 has several internal controls in place to detect or prevent this violation from occurring, including: • SRS sends an email notification for SRS ticket processing to primary and secondary ticket approvers. • SRS sends an email reminder notification after two and four days to the primary and secondary ticket approvers. • The supervisor received annual NERC CIP training which includes information on access revocation requirements. • The supervisor was NERC CIP Cleared (PRA and security awareness training). • Quarterly reviews of all authorized access are performed. • Procedures to document access requirements, including business need and access revocation requirements. No harm is known to have occurred. | To mitigate this issue, RFC_URE2 took the following actions: 1) Compliance staff met with the Supervisor to explain the situation and provided clarification on the process while stressing timely removal of access once access is no longer required; 2) the Supervisor approved the SRS ticket and access was removed; 3) RFC_URE2;s CIP Sr Manager issued a communication to Supervisors of all NERC CIP cleared personnel, emphasizing the importance of their responsibility to timely update their direct report's NERC CIP unescorted physical and electronic access privileges, as conditions change; ande 4) RFC_URE2 assigned the RFC_URE2 NERC CIP Supervisor Training course to all RFC_URE2 employees who are supervisors of NERC CIP Cleared individuals to further reinforce responsibilities relating to NERC CIP access. This will be an annual requirement.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015160 | CIP-004-3a | R4.2 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-004-3a R4.2. RFC_URE3 determined that it had an issue with CIP-004-3 R4.2 because access was not revoked timely. RFC_URE3 IT personnel entered a Security Request System (SRS) ticket to remove physical access for a RFC_URE3 employee effective that day. The SRS ticket was not approved by the supervisor until nine days later and access was removed ten days later. Therefore, it was greater than seven days from the time it was determined that access was no longer needed until it was removed. The root cause of this violation was the supervisor’s decision to wait for information prior to approving the SRS ticket within the required timeframe. Despite the human performance issue in this instance, this was the only SRS ticket not processed in a timely manner at a time when a substantial number of employees were changing job functions due to the upcoming spin-off of the RFC_URE3 assets. This indicates that the existing training and procedures are largely effective in controlling against untimely removal of access. However, because this one individual’s access was not removed in a timely manner, there is a small risk that he could have continued to access these locations without a business need and taken actions that could have resulted in additional violations. The duration of this noncompliance is from the date the employee's access should have been removed to the date access was removed. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The root cause of this violation was the supervisor’s decision to wait for information prior to approving the SRS ticket within the required timeframe between the date the access was to be removed and the date the access was actually removed which was limited to four days. The supervisor waited because the employee was in transition beetween job roles (performing duties for both old and new role simultaneously) due to a corporate reorganization. The supervisor was uncertain as to whether it was appropriate to remove the employee's access at that time. In addition, the supervisor's delay was a result of their attempt to re-confirm access was no longer needed prior to approving the ticket. The individual remained a trusted employee during the timeframe that access was retained but no longer needed. If there would have been any unauthorized changes during the timeframe mentioned, the changes would have been detected through monitoring and would have been corrected immediately. Since the SRS ticket was not approved in a timely manner, the individual retained physical access to Electronic Access Control and Monitoring Systems (EACMS) and Critical Cyber Assets after the supervisor determined there was no longer a business need for access due to a change of duties. The individual fully understood the importance of the devices and had a valid personnel risk assessment (PRA) and up-to-date training in place. There was also a prior business need for access to these assets. The supervisor consciously did not approve the SRS ticket to revoke access while awaiting additional information. Even with this delay, existing controls would have detected the unapproved SRS ticket and the access would have been revoked. The individual was not disgruntled and had no intention of causing harm. The SRS ticket was entered, approved nine days later, and access was removed ten days later, exceeding the seven days required by CIP-004 R4.2. There are several internal controls in place to detect or prevent this violation from occurring. The SRS system sends an email notification for SRS ticket processing to the primary ticket approver. If the ticket is not approved timely, the SRS sends an escalation email reminder notification after 2 and 4 days to the primary and secondary ticket approvers. The supervisor received annual NERC CIP training which includes information on access revocation requirements and was NERC CIP Cleared (PRA and security awareness training). Quarterly reviews of all authorized access are performed along with procedures that document access requirements, including business need and access revocation requirements. Corporate Security checked the logs to verify the employee did not access the physical restricted location during the time period in question. No harm is known to have occurred. | To mitigate the issue, RFC_URE3: 1) Compliance staff met with the Supervisor to explain the situation and provided clarification on the process while stressing timely removal of access once access is no longer required; 2) approved the SRS ticket and access was removed; and 3) issued a communication to Supervisors of all NERC CIP cleared personnel, emphasizing the importance of their responsibility to timely update their direct report's NERC CIP unescorted physical and electronic access privileges, as conditions change.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015161 | CIP-003-3 | R5 | RFC_URE3 submitted a self-log stating that it had an issue of CIP-003-3 R5. RFC_URE3 discovered that a RFC_URE3 IT Supervisor was able to approve access using the Security Request System (SRS) to a repository, used by both RFC_URE2 and RFC_URE3, but was not designated on the RFC_URE3 access list of personnel designated for authorizing electronic and/or physical access to NERC CIP protected assets/information, to authorize access to this repository. The root cause of this noncompliance was ineffective training resulting in a human error. At the time of the noncompliance, it was appropriate for the RFC_URE3 IT Supersivor to have the ability to approve access using the SRS to a repository used by both RFC_URE2 and RFC_URE3. The human error resulted in the RFC_URE3 IT Supervisor inadvertently not being designated as authorized on the RFC_URE3 access list. The duration of this noncompliance is from the date by which RFC_URE3 was subject to compliance with CIP-003-3 R5, to the date RFC_URE3 completed its Mitigating Activities. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. An administrative error occurred during the access list update process as it did not update both the RFC_URE2 and RFC_URE3 access lists at the same time for the shared assets. The Security Request System (SRS) is used as the vehicle to approve access to individuals for the shared repository. The human error occurred when the individual responsible for identifying changes to the appropriate access lists missed that both RFC_URE2 and RFC_URE3 needed updating for this change. The individual did not communicate to RFC_URE3 to update their access list to include this approver. The individual, at this time, was processing multiple changes to both access lists and this was a factor in the oversight. A quarterly review of list accesses and authorizers is performed in preparation for the CIP-004 R4 review cycle. The individuals that received access authorization were appropriate and should have access to the approved repository. It was appropriate for the RFC_URE3 IT Supervisor, with his responsibilities, to authorize access to this repository. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) had an authorized approver on both access lists approve future access requests; 2) updated it's access list to include the RFC_URE3 IT Supervisor as authorizer for the repository; 3) submitted an SRS ticket to reauthorize access to the repository for the 8 individuals, to ensure each had access as authorized by the appropriate indivdual designated on the access list; 4) implemented additional peer checks for each access list change, which includes cross referencing accesses used by both RFC_URE2 and RFC_URE3; and 5) updated its access list with a field to indicate accesses used by both RFC_URE2 and RFC_URE3.
2015-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014962 | CIP-002-3 | R4 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. SERC_URE1 did not have a signed and dated record of the senior manager’s annual approval of the risk-based assessment methodology (RBAM), the list of Critical Assets and the list of Critical Cyber Assets (CCAs) for two consecutive years. During an annual review, SERC_URE1 could not locate the annual approval documents required by CIP-002-3 R4 for two separate years. SERC reviewed SERC_URE1’s annual approvals of the RBAM, null Critical Asset list, and null CCA list from the year before and the year after the missed two years. SERC verified that the designated SERC_URE1 CIP senior manager conducted the two documented reviews and approvals. The primary causes of this issue were that SERC_URE1 appointed a single point of responsibility and SERC_URE1 personnel lacked awareness. Further, SERC_URE1’s management system only notified the single individual responsible for compliance. SERC determined that SERC_URE1 had an issue with CIP-002-3 R4 because SERC_URE1 did not have a signed and dated record of the senior manager’s annual approval of the RBAM, the null list of Critical Assets, and the null list of CCAs for two consecutive years. This issue lasted from the day after SERC_URE1 failed to record the annual approval of its RBAM, Critical Asset list, and CCA list, through approximately 28 months later, when SERC_URE1 recorded the annual approval of its RBAM, Critical Asset list, and CCA list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to annually approve a list of Critical Assets and CCAs could introduce additional vulnerabilities to the system as SERC_URE1 would likely not provide the Critical Assets and CCAs the protection required by the CIP Standards. However, SERC_URE1 is a minimal size entity with its output contracted to and dispatched by a large utility, and does not own any Critical Assets and therefore has no CCAs. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) immediately reviewed the risk assessment and determined that there was no change to risk status (non-critical or Low Impact); 2) reviewed and enhanced its plant compliance management procedures, annual review procedures, as well as file backup procedures, to ensure that periodic compliance tasks get completed in a timely manner and any risk of file system loss is properly managed; 3) retrained the primary compliance contact on the requirements of CIP-002; 4) implemented a task management program that will notify the primary compliance contact of upcoming task due dates and escalate the notification to other levels of management if the task is not completed within a defined time frame; 5) revised its annual internal NERC program review instructions to enhance awareness of and attention to routine NERC submissions required in the previous 18 months; and 6) implemented a process to back up the complete compliance folder to a read-only file every six months.
2015-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014289 | CIP-007-3a | R5; R5.1.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1, had a minimal risk instance of noncompliance with CIP-007-3 R5 R5.1.3. SPPRE_URE1 did not conduct annual reviews from 2011-2013 of its user accounts to Critical Cyber Assets and associated non-Critical Cyber Assets within its Electronic Security Perimeter (ESP) so that access privileges to such assets could be verified. The duration of this instance of noncompliance was from the date the annual review was required to be conducted, through the date SPPRE_URE1 conducted an annual review of its user accounts for cyber assets within SPPRE_URE1’s ESP and verified access privileges to such accounts. The root cause of this instance of noncompliance was a lack of internal controls to ensure that the user accounts were reviewed at least annually. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007 R5 has the potential to affect the reliable operation of the BPS by providing the opportunity for unauthorized system access. Nonetheless, SPPRE_URE1 did maintain a list of approved users for cyber asset accounts, all of whom had CIP training and cleared background checks. SPPRE_URE1’s Cyber Assets were protected by a firewall specifically configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1 also used system logging to analyze network traffic at access points to the ESP for known and suspect malicious activity. No actual harm is known to have occurred as a result of the noncompliance. | To mitigate the minimal risk instance of noncompliance, SPPRE_URE1: 1) conducted a review of its user accounts for cyber assets within SPPRE_URE1’s ESP, and verified and revised as necessary, access privileges to such accounts; and 2) added the review requirement to its CIP Compliance Calendar. SPP RE has verified the completion of all mitigation activity.
2015-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014014479 | CIP-007-3a | R6; R6.1, R6.2, R6.3, R6.4, R6.5 | SPPRE_URE2 submitted a Self-Report stating that it had two instances of minimal risk noncompliance with CIP-007-3a R6. System event logs from 36 assets were not captured and retained. SPPRE_URE2 determined that the failure to retain the logs was due to a syslog application issue but was unable to determine the specific issue or its cause. Network device logs captured by a different syslog application on the same server were not affected. The second instance cited by SPPRE_URE2 occurred when the service that logs network events on two syslog servers crashed unexpectedly due to a memory error. This occurred when SPPRE_URE2 ran scans against its entire network as part of its annual Cyber Vulnerability Assessment (CVA) which caused an increase in log volume in excess of the log server’s capabilities. Log volume returned to normal once scanning was stopped and the service restarted. The issue of non-compliance began when the logging service was restarted. SPPRE_URE2 submitted a Self-Report stating that it had two instances of minimal risk noncompliance with CIP-007-3a R6. In the first instance, SPPRE_URE2 discovered that two non-access point switches were configured to send event logs to only one of two syslog servers. As a result, any event logs for the two switches would not have been maintained, retained, or reviewed for 15 minutes when one of the syslog servers was out of service for maintenance. The second instance occurred when SPPRE_URE2’s Network Administrator logged into a non-access point switch logically located within the PACS ESP-like environment and noticed that an email notification alert for that activity was not received. The root cause of the issue is due to employee inadvertent oversight: when the switch was introduced into the environment, the access point firewall for the PACS was not configured to allow for the switch’s event logs. As a result, any event logs for the switch would not have been maintained, retained, or reviewed when configuration changes were completed so that event logs from the switch would be captured by the syslog servers. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The risk of not implementing, maintaining, or reviewing logs or failing to retain logs could lead to undetected security incidents. However, SPPRE_URE2 implemented strong preventative controls so that any undetected security incidents were unlikely to occur. SPPRE_URE2 implements Windows security event log filtering, including collection and review of the logs. Antivirus logs and access point firewall event logs were unaffected. SPPRE_URE2’s SCADA network was actively scanned for cyber vulnerabilities and SCADA applications were not affected, nor were the network assets themselves. The issues were further mitigated by SPPRE_URE2’s implementation of a Network Intrusion Detection System (NIDS) that continuously monitors and alarms for unauthorized access within its network. SPPRE_URE2’s NIDS provides a redundant detection mechanism in the event that SPPRE_URE2 fails to identify an unintended change in its security controls. SPPRE_URE2’s access control and monitoring devices are configured to deny all access attempts originating from outside its ESPs, thereby limiting the risk that unauthorized access could occur. SPPRE_URE2 has implemented applicable patches and installed anti-virus for all technically feasible Cyber Assets. Access to SPPRE_URE2’s network and server assets is strictly limited to authorized personnel. No harm is known to have occurred to any SPPRE_URE2 Cyber Asset as a result of these issues. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE2: 1. set a logging feature that checks to be sure the log is functioning properly and generates an alert to the System Administrators if there is a problem with the log. 2. configured the syslog service to automatically restart upon unexpected service stoppage, and set an alert to send an email notification for any unexpected stoppage of the syslog service. 3. configured the non-access point switches to send logs to both syslog servers. 4. configured the PACS environment firewall to allow event logs from the PACS switch to be sent to both syslog servers. 5. added a process in its Change Management program for the Information Security Officer to review all pre- and post- change documentation related to network assets to confirm results and configurations. SPP RE has verified the completion of all mitigation activity.
2015-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015014930 | CIP-007-3a | R6; R6.4 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R6.4. Specifically, TRE_URE1 determined that a number of its Cyber Assets were not sending logs to its management system. Therefore, TRE_URE1 failed to retain all logs specified in CIP-007-3a R6 for a minimum of 90 calendar days. This issue was discovered when TRE_URE1 manually performed a reconciliation of its Cyber Assets within the Electronic Security Perimeter (ESP) and associated logs. The root cause of this failure was an annual password change. After the password change occurred, the systems continued to operate until they were restarted approximately one month later. At that time, the affected assets were unable to log into the third party log collector and, therefore, were unable to send the logs. Texas RE determined the issue duration to be for approximately three weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE1 uses a layered cyber defense approach to mitigate security risks, including the use of dual-factor authentication to access network devices. TRE_URE1 also did not experience any known Cyber Security Incidents that required a review of logs during the issue duration. Finally, only 7.33% of TRE_URE1’s total in-scope systems were missing logs. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) changed service account passwords so that log collection resumed; 2) incorporated all applicable account name/password combinations into the password vault; 3) created a group policy object to force local storage of logs; and 4) created a process for a daily maintenance checklist of its management system. Texas RE has verified the completion of all mitigation activity.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015034 | CIP-006-3c | R1.6 | WECC_URE1 submitted a self-log stating that it had an issue of CIP-006-3c R1.6. In preparation for an upgrade of the Energy Management System (“EMS”), a contractor working for the EMS vendor (“Contractor”) was granted escorted access to the EMC. The entity’s EMS staff served as the continuous escort for the Contractor throughout the day, but eventually left the contractor alone to use the restroom. After completing his work, the Contractor tried to exit the EMC without an escort. Physical Security personnel stopped the Contractor until his identity could be verified. The Contractor was then logged out and exited the EMC in accordance with the entity’s visitor control program. An employee of the entity (“Employee 1”) attempted to gain access to the EMC to conduct work in one of its offices. A short time later, two additional employees of the entity entered the building to conduct work in the same office, one of which was authorized for unescorted access (“Authorized Employee”) and was going to serve as the escort for the other employee (“Employee 2”). Employee 1 and Employee 2 were granted escorted access to the EMC with the Authorized Employee serving as the escort for both visitors, however, the Authorized Employee did not know he was the escort for Employee 1. After completing his work, Employee 1 tried to exit the EMC without an escort. Physical Security personnel stopped the employee until his identity could be verified. The employee was then logged out and exited the EMC in accordance with the entity’s visitor control program. The entity’s power system staff operator arrived for work at the EMC, but forgot his employee badge. The EMC is a designated Physical Security Perimeter (“PSP”). Security issued him a temporary badge that authorized him for unescorted physical access to the EMC. Although the temporary badge allows the employee to be in the building unescorted, it does not provide access to any of its internal doors that are equipped with card readers. Two employees of the entity were granted access to a control room as escorted visitors. Security staff reviewed the visitor log later that evening and noticed that there was no time logged for when the two employees left. | This issue posed a minimal risk to the bulk power system (BPS) for the following reasons: the Contractor did not have physical access to any CCA; the Contractor did not have cyber access to any CCA; the Contractor has completed a CIP-004 cyber security training program; a CIP-004 personnel risk assessment was performed on the Contractor; during the time the Contractor did not have an escort, he only had access to the EMS work area and the restroom. These rooms do not contain any CCAs. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. This issue posed a minimal risk for the following reasons: the Employee 1 did not have physical access to any CCA; the Employee 1 did not have cyber access to any CCA; the Employee 1 is a regular entity employee and has completed a criminal history check. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. This issue posed a minimal risk for the following reasons: both employees are regular entity employees, authorized for unescorted physical access and cyber access to CCAs; both employees have completed the CIP-004-3 cyber security training; both employees have completed CIP-004-3 personnel risk assessments; both employee expressed a thorough understanding of the entity's access control policies, and clearly stated that they were aware that they used poor judgement in borrowing another employee's badge. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. This issue posed a minimal risk for the following reasons: the employees were both authorized for unescorted physical access to the EC-OC DSO Control Room; the employees had completed their CIP-004 cyber security training program and had a current personnel risk assessment on file; the employees were accompanied by a designated escort while in the secured area (even though they had been authorized for unescorted physical access). This issue was an isolated event that was quickly identified and resolved through the access monitoring controls in effect at the time of the incident. | To mitigate this issue, WECC_URE1: 1) reviewed the visitor control program. Additional guidance will be provided in appropriate documentation during the conversion from CIP-006-3c to CIP-006-5 in Security Program and Security Plan to address this issue along with the new visitor control requirements. 2) a reiteration of the requirements and process for visitor access to controlled areas was communicated separately to all Security Operations personnel. Until determined otherwise Security Operations personnel, in addition to ensuring that visitors are logged into and out of controlled areas and that authorized escorts are with them, will be providing visitors and their initial escorts with a document that describes the visitor control process, the handing off of escort duties to another authorized escort, and the requirement that visitors in controlled areas must be escorted at all times; 3) a communication was sent to all employees to remind and reinforce the visitor and escort responsibilities for CIP controlled areas, and the process for granting visitor access to controlled areas; 4) held a meeting and worked with EMS and physical security to ensure that this potential violation was fully identified, assessed and corrected in a manner that meets the principals outlined in the CIP V5 Study; 5) unescorted physical access to Critical Cyber Assets (CCA) was immediately disabled for both employees until the matter was resolved with senior management, legal and compliance; 6) the employees involved in this issue were immediately counseled at the time of the event by senior management; 7) discussed the lessons learned from this event with the operators on shift and of the following shift; 8) a reminder “not to let anyone use your [employee] badge for any reason” was included in the quarterly awareness communication to CIP personnel with authorized electronic or unescorted physical access to CCA. 9) the supervisor of the entity's Security Operations addressed this circumstance as a "lessons-learned" in an email addressed to security staff to reiterate the need for security personnel to review visitor logs for accuracy and completeness; and 10) the employees involved in the event were counseled by the on-duty Supervisor of Security Operations on the appropriate means of gaining entry to and exiting from physical security perimeters as authorized unescorted access badge holders.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015036 | CIP-006-3c | R1.6 | WECC_URE2 submitted a self-log stating that it had an issue of CIP-006-3c R1.6. In preparation for the upgrade of the Energy Management System (“EMS”), a contractor working for the EMS vendor (“Contractor”) was granted escorted access to the EMC. The contracted entity’s EMS staff served as the continuous escort for the Contractor throughout the day, but eventually left the Contractor alone to use the restroom. After completing his work, the Contractor tried to exit the EMC without an escort. Physical Security personnel stopped the Contractor until his identity could be verified. The Contractor was then logged out and exited the EMC in accordance with the contracted entity’s visitor control program. An employee of the contracted entity (“Employee 1”) attempted to gain access to the EMC to conduct work in one of its offices. A short time later, two additional employees of the contracted entity entered the building to conduct work in the same office, one of which was authorized for unescorted access (“Authorized Employee”) and was going to serve as the escort for the other employee (“Employee 2”). Employee 1 and Employee 2 were granted escorted access to the EMC with the Authorized Employee serving as the escort for both visitors, however, the Authorized Employee did not know he was the escort for Employee 1. After completing his work, Employee 1 tried to exit the EMC without an escort. Physical Security personnel stopped the employee until his identity could be verified. The employee was then logged out and exited the EMC in accordance with the contracted entity’s visitor control program. The contracted entity Power System Operator (“PSO Staff #1”) arrived for work at the EMC, but forgot his employee badge. The EMC is a designated Physical Security Perimeter (“PSP”). Security Operations issued him a temporary badge that authorized him for unescorted physical access to the EMC. Although the temporary badge allows the employee to be in the building unescorted, it does not provide access to any of its internal doors that are equipped with card readers. PSO Staff #1 made arrangements for his spouse to bring his badge to work. When it arrived, PSO Staff #1 borrowed a badge from another PSO employee who was on shift (“PSO Staff #2”); and used this badge to exit the building for the purpose of retrieving his own badge. PSO Staff #1 re-entered the EMC using the employee badge of PSO Staff #2. Later, PSO Staff #1 turned in his temporary badge to Security Operations. Security Operations personnel noticed PSO Staff #1 leave and re-enter the EMC using an employee badge, and not the temporary badge they issued to him. Security Operations identified the badge being used as belonging to PSO Staff #2, and disabled PSO Staff #1 and PSO Staff #2 employee badges in the Physical Access Control System (“PACS”), thereby removing their unescorted physical access to the EMC. Both employees were advised of the situation and informed that they had been placed in “escorted visitor” status until the matter could be fully investigated. A co-worker (“PSO Staff #3”) became their assigned escort for the remainder of the work shift. | Incident 1: This issue posed a minimal risk to the bulk power system (BPS) for the following reasons: the Contractor did not have physical access to any CCA; the Contractor did not have cyber access to any CCA; the Contractor has completed a CIP-004 cyber security training program; a CIP-004 personnel risk assessment was performed on the Contractor; during the time the Contractor did not have an escort, he only had access to the EMS work area and the restroom. These rooms do not contain any CCAs. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. Incident 2: This issue posed a minimal risk for the following reasons: the Employee 1 did not have physical access to any CCA; the Employee 1 did not have cyber access to any CCA; the Employee 1 is a regular entity employee and has completed a criminal history check. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. Incident 3: This issue posed a minimal risk for the following reasons: both employees are regular entity employees, authorized for unescorted physical access and cyber access to CCAs; both employees have completed the CIP-004-3 cyber security training; both employees have completed CIP-004-3 personnel risk assessments; both employee expressed a thorough understanding of the entity's access control policies, and clearly stated that they were aware that they used poor judgement in borrowing another employee's badge. This issue was a one-time occurrence, was quickly identified by the processes in place, and is not ongoing. | To mitigate this issue, WECC_URE1: 1) reviewed the visitor control program. Additional guidance will be provided in appropriate documentation during the conversion from CIP-006-3c to CIP-006-5 in Security Program and Security Plan to address this issue along with the new visitor control requirements. 2) a reiteration of the requirements and process for visitor access to controlled areas was communicated separately to all Security Operations personnel. Until determined otherwise Security Operations personnel, in addition to ensuring that visitors are logged into and out of controlled areas and that authorized escorts are with them, will be providing visitors and their initial escorts with a document that describes the visitor control process, the handing off of escort duties to another authorized escort, and the requirement that visitors in controlled areas must be escorted at all times; 3) a communication was sent to all employees to remind and reinforce the visitor and escort responsibilities for CIP controlled areas, and the process for granting visitor access to controlled areas; 4) held a meeting and worked with EMS and physical security to ensure that this potential violation was fully identified, assessed and corrected in a manner that meets the principals outlined in the CIP V5 Study; 5) unescorted physical access to Critical Cyber Assets (CCA) was immediately disabled for both employees until the matter was resolved with senior management, legal and compliance; 6) the employees involved in this issue were immediately counseled at the time of the event by senior management; 7) discussed the lessons learned from this event with the operators on shift and of the following shift; 8) a reminder “not to let anyone use your [employee] badge for any reason” was included in the quarterly awareness communication to CIP personnel with authorized electronic or unescorted physical access to CCA. 9) the supervisor of the entity's Security Operations addressed this circumstance as a "lessons-learned" in an email addressed to security staff to reiterate the need for security personnel to review visitor logs for accuracy and completeness; and 10) the employees involved in the event were counseled by the on-duty Supervisor of Security Operations on the appropriate means of gaining entry to and exiting from physical security perimeters as authorized unescorted access badge holders.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014138 | CIP-004-3a | R4; R4.1; R4.2 | WECC_URE3 submitted a Self-Report stating that, as a Responsible Entity, it had an issue of CIP-004-3a Requirement 4. WECC_URE3 transitioned to a new contract security service company. As part of the transition, WECC_URE3 compiled a roster of existing contract security officers with access rights to WECC_URE3’s Critical Cyber Assets (CCAs). WECC_URE3 provided the roster to the new contract security company to validate that all security officers on the roster had been hired by the new security company and thus would require continued access to WECC_URE3’s CCAs. If security officers appeared on the roster, but were not hired by the new security provider, WECC_URE3 would remove their physical access rights to WECC_URE3’s CCAs. While compiling the roster of existing contract security officers, WECC_URE3 omitted the name of one security officer. The security officer had physical access rights to three PSPs. The one security officer in scope was not hired by the new security company and no longer required physical access to WECC_URE3’s CCAs. However, because the name of the security officer in scope was omitted from the roster, the new security company was unable to inform WECC_URE3 that the security officer had not been hired and that their physical access rights should be removed. The new contract security company began providing security for WECC_URE3 and as a result, the security officer in scope no longer required physical access to WECC_URE3’s CCAs. WECC_URE3 conducted a quality control review of its security officer roster and discovered the name of the security officer in scope was omitted from the roster WECC_URE3 sent to the new contract security company. WECC_URE3 revoked the security officer’s physical access rights and updated the CCA physical access list. The root cause of this noncompliance was an individual oversight during the original roster compilation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 did not revoke access and update its list of personnel who have access to Critical Cyber Assets within seven calendar days of a change in personnel. This noncompliance involved one security officer who was not retained by WECC_URE3’s new contract security company. The noncompliance and associated potential consequences were limited due to the controls implemented by WECC_URE3. WECC_URE3 did not grant electronic access to the personnel in scope. The devices in the PSPs in scope use Active Directory where each device had its own username and password. The personnel in scope did not have access to any of the device’s usernames or passwords. The PSPs are monitored twenty-four hours a day seven days a week by the other WECC_URE3 personnel working at the PSPs. This reduces the likelihood that an unauthorized individual would be able to successfully gain logical access using a USB, CD, or other device and cause damage to the devices within the PSPs. No harm is known to have occurred from this compliance exception. | To mitigate this issue, WECC_URE3 revoked the security officer's physical access rights and updated the list of personnel who have access to the Critical Cyber Assets.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014646 | CIP-007-3a | R5.3 | WECC_URE3 submitted a Self-Report stating that, as a Responsible Entity, it had an issue with CIP-007-3a R5.3. WECC_URE3 reported an issue with the annual password change on satellite clock devices in one calendar year. The devices are non-Critical Cyber Assets that provide accurate timing for non-NERC CIP functions such as digital fault recorders. The devices do not interact with any CCAs. The devices are located within an Electronic Security Perimeter. While attempting to change the password as scheduled, WECC_URE3’s SMEs experienced technical issues and tried to contact the manufacturer to find a solution to the technical issues. However, WECC_URE3’s SMEs were unable to get in contact with the manufacturer because the manufacturer was unavailable during the holidays. Later, WECC_URE3 was able to coordinate with the manufacturer and come up with a solution to change the passwords. WECC_URE3 also reported an issue with complex passwords on switches. WECC_URE3 removed centralized authentication from the switches in scope to mitigate a prior issue. WECC_URE3 enabled local user accounts on each switch to allow for management of the devices. The users entered passwords that did not consist of “special” characters. Once testing was complete, WECC_URE3 did not change the passwords to include special characters. The passwords were displayed as hash marks, making it difficult for WECC_URE3 to notice the lack of special characters. WECC_URE3 identified the passwords as lacking CIP-007 R5.3 complexity during an annual Cyber Vulnerability Assessment. WECC_URE3 changed the passwords to include special characters. The root cause of this noncompliance was less than adequate post-maintenance testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to change the passwords or use complex passwords could have made the passwords easier to crack leading to a potential compromise of the devices. However, the noncompliance and associated potential consequences were limited by WECC_URE3’s controls. WECC_URE3 implemented a defense-in-depth structure on its network by putting the switches behind firewalls and other access points. A potential attacker would need to traverse multiple layers of protections before being able to attempt to scan the networks where the switches reside. WECC_URE3 also changes the default account names, making it more difficult for a potential attacker to discover and use the account name in conjunction with a brute force attack of the password. The clock devices are within a six-wall boundary protected by WECC_URE3 Corporate Security’s Physical Access Control System (PACS). The PACS uses a badge reader that limits physical access to personnel with NERC CIP qualifications. Electronic access to the clocks is limited and controlled via access control lists to ensure communications with authorized devices. WECC_URE3 uses antivirus, which could prevent an attempted malware attack. WECC_URE3 also uses an Intrusion Detection System, which could also detect malware on the network. WECC_URE3 has logging enabled on the devices. WECC_URE3 reviewed the logs and did not find any compromise of the devices in scope. No harm is known to have occurred from this compliance exception. | To mitigate this issue, WECC_URE3: 1) changed the passwords on the clock devices; 2) updated the calendar for annual compliance activities to ensure timely completeness; 3) changed the passwords on the switches; and 4) updated the Request for Change template to ensure password length and strong password requirements are validated during the change management process.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013917 | CIP-005-1 | R2.4. | WECC_URE4 self-reported a possible issue of CIP-005-1 R2. A WECC Subject Matter Expert (SME) had a call with WECC_URE4 to determine the full scope of the Self-Report. WECC_URE4 stated that it was not enforcing the two-factor authentication at the access point for remote access to a switch inside the Electronic Security Perimeter (ESP). The switch allows remote control access of WECC_URE4’s switch management server, which is used to manage WECC_URE4’s Energy Management System (EMS) switches. WECC_URE4 was not performing two-factor authentication for external interactive access into the switch, which controlled one switch management server. The switch management server could then control EMS switches all inside separate ESP’s. The WECC SME forwarded this information to Enforcement for review. Enforcement reviewed the Self-Report and the SME findings and determined that WECC_URE4 did not implement strong technical controls at the access points to ensure authenticity of the accessing party. Further, WECC_URE4 failed to establish two-factor authentication between the switch management server and the switch within the ESP, which resulted in an issue with CIP-005-1 R2.4. The root cause of this Compliance Exception is WECC_URE4's less than adequate understanding of the standard. It wasn't until the exchange of emails and conversations between WECC_URE4 staff and a WECC SME that it became apparent to WECC_URE4 that they were not in compliance with the standard. In addition to WECC_URE4’s less than adequate understand of the standard, WECC_URE4's technical staff has LTA training and knowledge on the standard and requirements of CIP-005-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 implemented preventative and detective controls. Specifically, WECC_URE4 implemented an Intrusion Detection System (IDS) inside the ESP that works in conjunction with a Security Information and Event Management (SIEM) that monitors log files and sends suspicious activity alert messages via email to technicians. The IDS would likely detect the USB key logger and communication coming from the logger. The SIEM is designed to send an alert message about the key logger to technicians and/or the IT department to immediately cut off further communication and access into the ESP or EMS. Additionally, WECC_URE4 restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. Thus, a malicious user would have to use known ports and services to remotely log into the switch management server and/or the ESP switch(es). Further, if a malicious user attempted to open up an unauthorized port and/or service then an alert message could be sent via the IDS. WECC_URE4 implemented detective controls. Specifically, WECC_URE4 has operators in the PSPs 24 hours a day and 7 days a week. These operators could detect if a malicious user was on-site attempting to install a key logger into the switch management server. WECC_URE4 also implemented corrective controls. Specifically, WECC_URE4's operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. WECC_URE4 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. No harm is known to have occurred. | To mitigate this issue, WECC_URE4: 1) Added the switch management server which now uses strong (two-factor) authentication; and 2) Updated its firewall rule set to only allow certain messages from the switch management server to the switches when there is an authorized, authenticated user logged onto the domain via the switch management server. WECC verified completion of all mitigation activities.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014013743 | CIP-006-3c | R1; R1.6 | WECC_URE3 submitted a Self-Report stating that, as a Responsible Entity, it had an issue of CIP-006-3c R1. A security guard (Officer A) with unescorted physical access rights to WECC_URE3’s trade floor, used his badge to allow another security guard (Officer B) to physically access the PSP. Officer B attempted to enter the PSP to ask if Officer C needed to go on break, but WECC_URE3’s PACS denied entry because Officer B had not been granted unescorted physical access rights to the PSP in scope. Officer B had recently completed his annual NERC CIP Cybersecurity training, but not yet been cleared to enter the PSP unescorted. After Officer A used his badge to allow Officer B to access the PSP, Officer B was left unescorted inside the PSP for approximately 15 minutes before exiting. The root cause of this instance of noncompliance was less than adequate procedures and training on accessing PSPs. WECC_URE3 later reported an additional instance of noncompliance. Three interns were visiting WECC_URE3’s same PSP in scope during the above instance of noncompliance. While inside the PSP, the three interns were not continuously escorted. The WECC_URE3 personnel responsible for escorting the interns did not keep the interns within their line-of-sight throughout the entire day. Later, WECC_URE3 Compliance personnel were made aware that the interns were not continuously escorted. WECC_URE3 Compliance personnel informed the escorts of the correct procedure. The root cause of this instance of noncompliance was less than adequate procedures and training on the requirements of escorting PSP visitors. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 experienced two instances of noncompliance when visitors were not continuously escorted within a PSP. In the first instance, a security guard was left unescorted inside a PSP for approximately 15 minutes. In the second instance, three interns were not continuously escorted while they were inside the same PSP. WECC_URE3 implemented controls to prevent negative consequences from occurring. The PSP in scope is staffed with personnel twenty-four hours a day, seven days a week. This reduces the likelihood that any of the individuals could successfully damage the devices or install malware using a USB device or CD. All of the devices inside the PSP in scope have unique usernames and passwords reducing the likelihood that any of the individuals could successfully access the devices. The software on the workstations requires several steps in order to affect generation. The individuals in scope were not trained on the software, further reducing the likelihood that they could successfully access and operate the workstations to affect generation. WECC_URE3 also monitors each generation unit’s operation twenty-four hours a day, seven days a week increasing the likelihood that WECC_URE3 would detect any unauthorized change in generation. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) adopted a new version of the Trade Floor visitor procedure; and 2) completed training for employees (including security guards) with authorized unescorted access to the Trade Floor.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2015014917 | CIP-006-3c | R2.2 | WECC conducted an on-site Audit of WECC_URE5’s facilities. The WECC Audit Team determined WECC_URE5 had a possible issue of CIP-006-3c R2.2 for failing to protect Cyber Assets that authorize and/or log access to the Physical Security Perimeter. The Audit Team found that for Physical Access Control Systems (PACS), WECC_URE5 did not afford the protections specified in CIP-006-3c Requirement R2.2. Specifically, WECC_URE5 failed to afford the PACS the protective measures specified in Standard CIP-003-3; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. Regarding CIP-003-3, the Audit Team found WECC_URE5’s PACS Panels were not included in its protection program for NERC CIP, change control was not documented, and configuration was not managed for the PACS Panels. For the protections outlined in CIP-007-3 R1-R9, the Audit Team found WECC_URE5 did not track significant changes to the PACS Panels, did not monitor enabled ports and services on the PACS Panels, did not track security firmware updates for the PACS Panels, and did not install malware prevention on the PACS Panels. The Audit Team also found the PACS Panels did not maintain logs of system events related to cyber security and were not included in WECC_URE5’s Cyber Vulnerability Assessments. The Audit Team found WECC_URE5’s NERC CIP-008 Cyber Security Incident Response Plan and WECC_URE5’s NERC CIP-009 Recovery Plans include procedures for PACS; however, the PACS Panels were not classified as PACS during the audit period. The root cause of this Compliance Exception is that WECC_URE5’s didn’t know the two panels should have been included in PACS. WECC_URE5 thought the PACS were physical hardware not included in PACS. The issue was corrected when an external consultant came in before the audit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Two PACS panels were not identified as cyber assets and afforded the protections required in CIP-006 R2.2. These instances occurred at WECC_URE5’s System Control Center and Back Up Control Center. Failure to implement physical access controls at all access points to the Physical Security Perimeter (PSP) could allow unauthorized and malicious access to cyber assets in the PSP. Such access may then be used to cause harm to Critical Cyber Assets essential to the operation of the Bulk Electric System (BES), thereby potentially negatively impacting the BES. As compensating measures, the facilities in scope were identified as Physical Security Perimeters; therefore, they have the protections required under CIP 006. Both PACS panels can only be accessed using special lock keys, which are maintained and logged at the Security Control Center located at the facility. Physical access to both PACS panels is monitored by the PACS system. Additionally, the devices were protected in a defense-in-depth strategy and protected within WECC_URE5’s controlled network. Further, all persons with access have PRA and training. | To mitigate this issue, WECC_URE5: Updated the classification of the PACS devices to cyber assets and provided the protections outlined in CIP-006-3c R2.2. The WECC Audit Team reviewed the evidence during the audit and verified the issue has been mitigated.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2015014894 | CIP-004-3a | R2.1 | WECC_URE6 submitted this violation in a Self-log. The entity’s Physical Security initiated a request to add unescorted physical access to a Physical Security Perimeter (PSP) for 15 security guards who are contract workers (CWs). Once the tickets were created, the entity’s security sent the request for Critical Cyber Asset (CCA) unescorted physical access to the entity’s CCA group. The entity’s administrator then went to the Independent Contractor (IC) CW SharePoint library, where the entity’s CW list resides and is maintained, to verify current Personnel Risk Assessment (PRA) and Critical Infrastructure Protection (CIP) Access training dates. After PRA and CIP Access training dates were verified, the entity’s administrator replied to the CCA Notification group indicating that “all the CWs listed have completed and met the PRA and CIP contractor requirements and can be granted access based on CCA custodian approval.” The entity then approved the request and authorized unescorted physical access to a PSP was added to the physical access badges associated with each of the applicable CWs. The administrator received and reviewed the entity’s CIP Access Report Exceptions Only report and noticed that one CW’s name was flagged for both no personnel business need listed and for the CIP training date. The entity’s administrator then reviewed its CW list and realized that the CIP access training date she had noted earlier for the flagged CW was associated with a different CW’s record rather than flagged CW’s record. Upon further review, the entity’s administrator realized that the flagged CW had never successfully completed CIP Access training. The entity’s administrator immediately contacted Physical Security to inform them that the flagged CW had not completed the required CIP Access training. Physical Security then removed the PSP access from the flagged CW’s physical access badge. The flagged CW only had authorized unescorted physical access to a PSP for one day. Additionally, at no time during the flagged CW’s assignment to the entity did he have electronic access to the entity’s corporate network or authorized electronic access to any of the entity’s CCAs/ACMs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, the entity failed to ensure that all personnel having access to CCAs are trained prior to their being granted access. If the flagged CW entered the PSP prior to completing the entity’s required CIP Access training, he may not have fully understood his responsibilities related to having unescorted physical access to this CIP restricted area. However, when the CW was granted authorized unescorted physical access to the PSP, the notification related to his access being granted to the PSP was only sent to the CCA Notification group. The CW had no knowledge of PSP access. In addition, Physical Security verified that the CW did not access the PSP after he had been granted unescorted physical access. Additionally, the CW was not on the entity’s property during the time that he had unescorted physical access to the PSP. The CW also had a valid PRA, was in good standing with the entity, and did not have electronic access to the entity’s corporate network or authorized electronic access to any of the entity’s CCAs/ACMs. Although the CW did not complete the entity’s required CIP Access training prior to being granted unescorted physical access to a PSP, he did complete training required by his employer. Employees and CWs are required to comply with the entity’s internal policies and standards. If the CW had accessed the PSP for purposes other than his defined job duties, he would be in violation of the entity’s internal policies and standards. Any employee or CW who fails to comply with the entity’s internal policies and standards may be subject to disciplinary and other actions, possibly including termination of employment/contract. When the contractor was granted authorized unescorted physical access to PSP-5 the notification related to his access being granted was only sent to the CCA group of which the contractor is not a member. Per further inquiry with Physical Security, the contractor did not receive notification that he had been granted unescorted physical access and thus was unaware that he had unescorted physical access . Upon learning that the contractor had not completed CIP training, Physical security immediately removed his unescorted physical access. In addition, security verified that the contractor did not access PSP after he had been granted unescorted physical access. Further, the security company validated that during the time frame that the contractor had unescorted physical access he was not on the property as he was performing patrol duties for another customer. The contractor role was a patrol officer. Patrol officers patrol, by vehicle and foot, the perimeter of the facilities. Their duties include but are not limited to checking external doors to ensure they are closed, further investigation of unsecured doors, etc. Additionally, any unused network ports related to the network devices and servers that reside within the PSP have been disabled. The system has been configured to alert on any failed log on attempts to the network devices and servers within the PSP. If an individual physically damaged the network devices and/or servers that reside within the PSP and the system stopped receiving logs for the network devices and/or servers that reside within the PSP, alarming would occur. In addition, the EMS system would indicate that communication to the backup site had been lost and EMS alerts would be generated in the EMS system and be visible to the EMS Analysts. | To mitigate this issue, WECC_URE6: 1) Upon learning that the contractor had not completed CIP training, Physical security immediately removed his unescorted physical access. In addition, security verified that the contractor did not access PSP after he had been granted unescorted physical access. Further, the security company validated that during the time frame that the contractor had unescorted physical access he was not on the property as he was performing patrol duties for another customer. 2) The administrator opened and viewed each CWs record rather than scrolling across the screen to gather the required information. Prior to responding to any electronic and/or physical CIP access requests, a member completes a Quality Review Checklist verifying the correct PRA and CIP Access training completion dates have been captured. Once the team member completes their verification, the administrator will respond to the electronic and/or physical CIP access request including the CWs actual PRA and CIP Access training completion dates in the response. 3) Additionally, on a monthly basis for a period of six months, the manager will validate that the administrator captured the correct PRA and CIP Access training completion dates for all CWs with authorized electronic and/or authorized unescorted physical CIP access. If the manager validates that no errors occurred during that six month period, the Supply Chain Quality Manager’s validation will continue on an as needed basis.
2015-08-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012781 | CIP-007-3a | R5 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R5. Specifically, MRO_URE1 self-reported, three of the 28 shared accounts on the Energy Management System (EMS) did not meet the complexity requirements for passwords. A subsequent comprehensive review uncovered an additionally 38 substation shared accounts that did not meet the password complexity requirements. Finally, MRO_URE1 updated its self-report to reflect that it identified a password on a protective relay at a substation that did not meet the complexity requirements. The root cause of these instances of non-compliance was a combination of human error and an inadequate password generation tool. No harm is known to have occurred. The instance of noncompliance began on April 3, 2013 and ended on August 21, 2013. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The identified passwords were all updated and kept secure. The potential risk for all passwords was limited to either insufficient password complexity (R5.3.2) or length (R5.3.1). Additionally, for those passwords with insufficient complexity, each password was only missing one of the three requirements for complexity, either an alpha, a numeric, or a special character. MRO considered MRO_URE1's CIP-007-3a R5 compliance history in determining the disposition track. MRO_URE1's relevant prior noncompliance with CIP-007-3a R5 include NERC Violation ID MRO2012010806 (CIP-007-1 R5). MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The prior violation related to MRO_URE1's failure to annually change passwords and did not relate to the current instance of non-compliance which is limited solely to password complexity. Further, the passwords in question had all been changed within the last year, meaning that MRO_URE1 had effectively mitigated the prior issue and that the prior issue did not contribute to the current instance of noncompliance. Finally, MRO considered MRO_URE1's prompt self-reporting and mitigation in determining the disposition of this instance of noncompliance. | To mitigate this issue, MRO_URE1: 1) Passwords were corrected to meet the complexity requirements as soon as the noncompliance was discovered; 2) For the EMS passwords, technical controls were added to assure future password changes would meet complexity requirements. For the substation related password complexity noncompliance, an additional level of password selection review was incorporated to verify complexity requirements were achieved; and 3) To mitigate the risk of future password length non-compliance caused by human error in entering passwords from the master list, the password change process was updated to include logging off the device and re-logging in with the new password to assure the password was entered as expected.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014112 | CIP-004-3a | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R2. RFC_URE1 identified the noncompliance as part of its review of Personnel Risk Assessment (PRA) and training qualifications required for access privileges. Due to a clerical error when access privileges were being assigned in the Physical Access Control System (PACS), RFC_URE1 inadvertently assigned access privileges to the wrong individual. RFC_URE1 uses a PACS to monitor and control access for entry points to NERC CIP Physical Security Perimeters (PSPs). Individuals are granted unescorted physical access to PSPs through a process approved by RFC_URE1's senior management. Access to multiple PSPs for an employee was requested. A clerical error occurred during the assignment of access privileges which resulted in the inadvertent assignment to an individual who did not have the training required for such access. The individual receiving the inadvertent access privileges had almost the exact same name as the correct individual: the same first name and middle initial as well as a surname that was spelled the same but for one letter. The individual that was inadvertently granted access privileges did not have the requisite training. Upon discovery of the issue, RFC_URE1 immediately revoked the individual’s access. Following revocation, RFC_URE1 conducted an access review and confirmed that the individual inadvertently assigned access privileges never used those privileges to access any PSP. The root cause of this noncompliance was a combination of ineffective training and human error caused by the highly unlikely similarity of two employees’ names. An employee with a similar name to the employee that was supposed to get access was inadvertently granted access. Although this noncompliance in isolation could have been attributed to human error alone, RFC_URE1’s other recent self-reported issues with granting access privileges to individuals not authorized to have such access reveals that ineffective training also played a causal role in this noncompliance. The duration of this noncompliance is from the date the RFC_URE1 employee inadvertently granted access to the wrong individual to the date RFC_URE1 removed the access privileges. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All RFC_URE1 employees and contractors have received background checks, including the employee that is the subject of the instant noncompliance. Moreover, RFC_URE1 conducts an on-site monthly review to ensure that the individuals receiving access privileges are the intended recipients. Furthermore, all RFC_URE1 employees and contractors are required to attend position-specific trainings before being assigned to perform work at site locations. The job responsibilities of the employee inadvertently granted access privileges does not require access to any PSPs, Cyber Assets, or Critical Cyber Assets. Finally, once an employee receives access privileges, the system does not notify the employee of such privileges. The employee’s manager, after being notified by the system, informs the employee of his or her access privileges. In this instance, the employee inadvertently granted access privileges was not yet aware of the access privileges as he had not been informed by his manager. No harm is known to have occured. | To mitigate this issue, RFC_URE1: 1) immediately revoked the access privileges inadvertently assigned to the wrong individual; 2) conducted reinforcement training for the Administrator and Security Manager. This training focused on (a) ensuring that the correct doors and areas are selected prior to assigning access privileges, (b) the importance of reviewing logs detailing access changes, and (c) verifying the names receiving access with the names on the document initially requesting access to ensure the correct individuals are granted access privileges; and 3) through its centralized compliance group will perform a monthly spot check to assure compliance with the procedures and to reinforce oversight of the access granting process. This new layer of review will help prevent recurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014113 | CIP-004-3a | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R2. Due to a clerical error, an employee whose access privileges approval was pending completion of his Personnel Risk Assessment (PRA) was given access privileges to multiple Physical Security Perimeters (PSPs). RFC_URE1 uses a Physical Access Control System (PACS) to monitor and control access for entry points to PSPs. Individuals are granted unescorted physical access to PSPs through a process approved by RFC_URE1 senior management. Access to multiple PSPs was requested for multiple employees. An employee whose approval was pending completion of his PRA was inadvertently given access privileges. The employee that made the error immediately detected the error and attempted to remove all of the incorrectly granted access privileges. All of the incorrectly assigned access privileges, except for two PSPs, were successfully and promptly removed. As part of the very next quarterly periodic access review of PRA and training qualifications to occur after the access privileges were incorrectly granted, RFC_URE1 identified this issue and immediately corrected it by revoking the employee’s access privileges to the two remaining PSPs. RFC_URE1 conducted a review of access records from the PACs and confirmed that the employee with the incorrectly assigned access privileges never used those privileges to access any NERC PSP. The root cause of this noncompliance was ineffective training, as evidenced by RFC_URE1’s multiple issues with granting access privileges to individuals not authorized to have such access. RFC_URE1 addresses this root cause in its mitigation plan through retraining of the employees responsible for granting access privileges. The duration of this noncompliance is from the date access to multiple PSPs was granted to a RFC_URE1 employee before his PRA had been completed, to the date RFC_URE1 removed all of the incorrectly granted access privileges. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All RFC_URE1 employees and contractors have received background checks, including the employee that is the subject of the instant noncompliance. Moreover, RFC_URE1 conducts an on-site monthly review to ensure that everyone granted access privileges is supposed to have them, which is what led to RFC_URE1 detecting this issue. Furthermore, all RFC_URE1 employees and contractors are required to attend position-specific trainings before being assigned to perform work at site locations. The job responsibilities of the employee inadvertently granted access privileges does not require access to any PSPs, Cyber Assets, or Critical Cyber Assets. Finally, once an employee receives access privileges, the system does not notify the employee of the privileges. The employee’s manager, after being notified by the system, informs the employee of his or her access privileges. In this instance, the employee inadvertently granted access privileges was not yet aware of the access privileges as he had not been informed by his manager. No harm is known to have occured. | To mitigate this issue, RFC_URE1: 1) revoked the access privileges inadvertently assigned to the wrong individual; 2) conducted reinforcement training for the Administrator and Security Manager. This training focused on (a) ensuring that the correct doors and areas are selected prior to assigning access privileges, (b) the importance of reviewing logs detailing access changes, and (c) verifying the names receiving access with the names on the document initially requesting access to ensure the correct individuals are granted access privileges; and 3) through its centralized compliance group will perform a monthly spot check to assure compliance with the procedures and to reinforce oversight of the access granting process. This new layer of review will help prevent recurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014191 | CIP-003-3 | R6 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3a R6. RFC_URE1 assigned a system administrator to install three applications in the Electronic Access Control and Monitoring (EACM) jump servers located in the main general office and in the Disaster Recovery (DR) site. The Administrator followed the established change control process, created a change ticket, and was approved to install the applications at the change control review meeting. The applications were successfully installed at the main general office and subsequently in the DR site. However, the change ticket was written to install the applications in the main general office; it did not explicitly detail the installation at the DR site. The additional installation at the DR site bypassed RFC_URE1’s change management procedure per CIP-003-3a R6. RFC_URE1 followed all other steps in the change control process, including testing and implementing procedures for the installation of the applications. The root cause of this noncompliance was inadequate training. For this noncompliance, the administrator was not properly trained in RFC_URE1’s change management procedure. The administrator did not understand that the change ticket needed to explicitly include installation at the DR site. The duration of this noncompliance is from the date the applications were successfully installed at the DR site to the date RFC_URE1 completed its Mitigation Plan. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RFC_URE1 performed all appropriate testing on the applications prior to installation of the applications at the DR site. The applications’ installation had been tested and approved for the DR site at the time of the noncompliance. This was a pure documentation issue; the installation was actually tested and approved for the two sites, but was only documented for the main general office. Additionally, the DR site systems are not associated with providing control functions for the Bulk Electric System as the DR site systems are not on the Electronic Security Perimeter or part of the Energy Management System. The DR site only provides remote access to the system. Lastly, no systems were impacted by the noncompliance, as all systems continued to operate as expected. No harm is known to have occured. | To mitigate this issue, RFC_URE1: 1) reinforced, through formal and informal training, both the requirements of the CIP Standards and the documented RFC_URE1 procedures as they relate to change management; and 2) reinforced the importance of following established procedures, RFC_URE1 removed the access of the administrator (who committed the error resulting in the noncompliance) to the subject systems for three months. To perform necessary activity, the administrator was granted temporary access to the specific system after the relevant change record was approved. Additionally, the administrator’s work was closely supervised and access was disabled after the work was completed. RFC_URE1 committed to restore the administrator’s access, assuming it was still required by his job, after the three month period and management’s satisfaction that the administrator has demonstrated his ability to comply with all required change management processes. ReliabilityFirst has verified the completion of all mitigation activity.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014824 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Certification and a self-log stating it had an issue of CIP-004-3a R4. It was discovered that three plant operators (employees) had access to a Critical Cyber Asset (CCA) without documentation of authorization. The three employees were new operators that were NERC CIP cleared, (i.e., they had a current Personnel Risk Assessment (PRA) and current cyber security training) and also had authorized unescorted physical access to the control room, within the Physical Security Perimeter (PSP) that protects the referenced CCA. These individuals were previously in positions for which their job assignments did not require access to the asset. They were subsequently promoted into positions that did require access. Their supervision permitted them to access the Electronic Security Perimeter (ESP) without proper authorization, including failure to submit the Security Request System (SRS) ticket that would trigger an update to the Authorized Access List. The requirement for authorization of the electronic access for the employees prior to their accessing the CCA was not understood by plant management. This CCA is part of RFC_URE2's periodic review process. The review process is managed by utilizing an application that provides an electronic window for each supervisor to review their authorized users. As a final step, the application then requires the Designated Compliance Managers to complete a final review. The duration of this noncompliance is from the date RFC_URE2 was subject to compliance with CIP-004-3a R4 to the date RFC_URE2 completed its Mitigating Activities. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three plant operators that had access to a CCA without documentation of authorization were NERC CIP cleared, meaning they had a current PRA and current cyber security training, at the time of the noncompliance. The cyber security training covered authorized electronic access to CCAs. Additionally, the three plant operators were under direct supervision at all times, which reduces the chance any of the operators could cause damage during their unauthorized access. No harm is known to have occured. | To mitigate this issue, RFC_URE2: 1) submitted (on date of discovery) a SRS ticket to authorize electronic access and update the Authorized Access List; 2) updated the Authorized Access List; 3) posted the Authorized Access List; 4) reviewed the process with the supervisor; 5) assigned additional training to emphasize requirement; 6) trained employees; and 7) conducted and documented a tailboard to emphasize the requirements. Mitigation activities that fix the issue and also prevent recurrence: 1. Assignment of NER200 training to emphasize requirement.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013301 | CIP-005-1 | R4 R4.2 R4.4 | ReliabilityFirst determined that RFC_URE3 had an issue with CIP-005-1 R4 as a result of a Compliance Audit. At the Compliance Audit, RFC_URE3 did not provide sufficient evidence to demonstrate that its Cyber Vulnerability Assessment (CVA) included a review of ports and services and a review of controls for default accounts, passwords, and network community strings for all access points into RFC_URE3’s Electronic Security Perimeter (ESP). Specifically, RFC_URE3 did not provide adequate evidence to demonstrate that its review of all ports and services for all access points into RFC_URE3’s ESP was compared against a baseline to determine that only those required for operations were enabled. RFC_URE3’s vulnerability assessment methodology stated that the verification of default passwords was changed in accordance with RFC_URE3’s CIP-007 R5 account management documented procedures. RFC_URE3 provided evidence that a default account review was completed, but RFC_URE3 did not provide sufficient evidence to show that password verifications were completed for the access points as part of this review. Overall, RFC_URE3’s CVA process document and the CVA performed did not properly align. The root cause of this violation is RFC_URE3’s failure to fully understand what was required to demonstrate compliance with the Reliability Standard at issue. RFC_URE3 believed it had provided sufficient evidence demonstrating that the CVA included a review to verify that only ports and services required for operations are enabled at the access points and a review of controls for default accounts, passwords, and network management community strings for all access points into RFC_URE3’s ESP. Although RFC_URE3 did provide some evidence of compliance with CIP-005 R4, RFC_URE3 lacked evidence that a review of all ports and services was compared against a baseline and that password verification was completed for the access points. ReliabilityFirst observed that the process for reviewing default accounts and passwords needed more detail for RFC_URE3 employees to implement it effectively. The duration of this noncompliance is from the date RFC_URE3 was subject to compliance with CIP-005-1 R4 to the date RFC_URE3 committed to complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 had a formalized CVA process document that incorporated all of the explicit requirements of CIP-005 R4 in place at the time of the Compliance Audit. RFC_URE3 also evaluates this process document on an annual basis. RFC_URE3’s CVA process document, if followed and documented with all supporting evidence, would have sufficiently demonstrated compliance with CIP-005 R4. Although RFC_URE3 believed that it followed its process document and that it was compliant, it could not provide an entirely complete package of evidence to demonstrate that it followed its process when performing its CVA in 2013. However, RFC_URE3 did provide evidence demonstrating its review of default accounts and passwords in its CVA, which reduces the risk posed by the noncompliance. No harm is known to have occured. | To mitigate this issue, RFC_URE3 will complete the following mitigation activities: 1) will address the issues identified by ReliabilityFirst by improving and clarifying its entire CVA process document, and specifically addressing its documentation of performance of the CVA; 2) will complete an evaluation of its current CVA process document and initiate drafting of applicable updates for internal review; 3) will complete all revisions to the CVA process document; 4) will complete an evaluation of appropriate forms of evidence to document completion of a CVA; and 5) will complete and document its CVA pursuant to RFC_URE3’s revised CVA process document.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013307 | CIP-007-1 | R8 R8.2 R8.3 | ReliabilityFirst determined that RFC_URE3 had an issue with CIP-007-1 R8 as a result of a Compliance Audit. At the Compliance Audit, RFC_URE3 did not provide sufficient evidence to demonstrate that the Cyber Vulnerability Assessment (CVA) followed the documented process and included a review of ports and services and a review of controls for default accounts, passwords, and network community strings for all Cyber Assets within the Electronic Security Perimeter (ESP). ReliabilityFirst identified two key issues. First, RFC_URE3 did not provide sufficient evidence to demonstrate that a review of all ports and services was compared against a baseline to determine that only those required for operations are enabled. Second, RFC_URE3’s passwords were not reviewed under CIP-007-3 R8 as a default account control. RFC_URE3’s vulnerability assessment methodology states that the verification of default passwords must be changed in accordance with procedures documented in RFC_URE3’s CIP-007 R5 account management procedure. RFC_URE3 provided evidence that indicated that it performed a default account review, but RFC_URE3 did not provide sufficient evidence that it performed the password verification for all Cyber Assets within the ESP. The root cause of this violation is RFC_URE3’s failure to fully understand the requirements of the Reliability Standard at issue. RFC_URE3’s CVA process document lacks detail regarding the performance of the CVA, such as how a review of controls for default accounts, passwords, and network community strings will be conducted, and how evidence will be kept. Because the process document lacked sufficient detail, RFC_URE3’s performance of the CVA did not match the CVA process document. RFC_URE3 believed that the evidence it provided to ReliabilityFirst demonstrated full compliance with CIP-007-1 R8 because it showed that RFC_URE3 performed a CVA and generally followed its CVA process document in performing that CVA. Although RFC_URE3 did provide some evidence of compliance with CIP-007-1 R8, RFC_URE3 was missing evidence that it performed password verification for all Cyber Assets within the ESP. The duration of this noncompliance is from the date RFC_URE3 was subject to compliance with CIP-007-1 R8 to the date RFC_URE3 committed to complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 had a formalized CVA process document that incorporated all of the explicit requirements of CIP-007 R8 in place at the time of the Compliance Audit. RFC_URE3 also evaluates the process document on an annual basis. RFC_URE3’s process document, if followed and documented with all supporting evidence, would have sufficiently demonstrated compliance with CIP-007 R8. Although RFC_URE3 believed that it followed its process document and that it was compliant, it could not provide an entirely complete package of evidence to demonstrate that it followed its process when performing its CVA in 2013. However, RFC_URE3 provided some evidence explaining how ports and services are assessed, before and during the CVA, to determine only those required for operation are enabled. This reduces the risk to the Bulk Electric System because it demonstrates that RFC_URE3 was assessing ports and services and ensuring that only ports and services required for operation were enabled at the time of the violation. No harm is known to have occured. | To mitigate this issue, RFC_URE3 will complete the following mitigation activities: 1) will address the issues identified by ReliabilityFirst by improving and clarifying its entire CVA process document, and specifically addressing its documentation of performance of the CVA; 2) will complete an evaluation of its current CVA process document and initiate drafting of applicable updates for internal review; 3) will complete all revisions to the CVA process document; 4) will complete an evaluation of appropriate forms of evidence to document completion of a CVA; and 5) will complete and document its CVA pursuant to RFC_URE3’s revised CVA process document.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013302 | CIP-006-1 | R2 R2.2 | ReliabilityFirst determined that RFC_URE3 had an issue with CIP-006-1 R2 as a result of a Compliance Audit. Specifically, ReliabilityFirst determined that while RFC_URE3 is providing some protective measures to: (a) two terminal servers (which function as workstation access for Physical Access Control Systems (PACS) and authorize access to the Physical Security Perimeters (PSPs)) and (b) three control panels (which authenticate and log access to the PSPs), RFC_URE3 did not declare these five devices as Physical Security System Cyber Assets (Cyber Assets) throughout the entire compliance monitoring period. These five devices should have been declared as Cyber Assets and should have had all of the protections required by CIP-006-3c R2.2 (specified in CIP-003-3; CIP-004-3a R3; CIP-005-3a R2 and R3; CIP-006-3c R4 and R5; CIP-007-3a; CIP-008-3; and CIP-009-3). Although RFC_URE3 resolved the issues associated with the control panels before the Compliance Audit by integrating these devices into its CIP Program as PACS and obtaining Technical Feasibility Exceptions (TFE) as necessary, the control panels should have been identified as PACS as of the compliance date for CIP-006-1 R2. The root cause of this noncompliance is RFC_URE3’s failure to fully understand the requirements of the Reliability Standard at issue. RFC_URE3 believed that it was compliant with CIP-006-1 R2 because its terminal servers do not provide a client-server connection and only provide screen shots from the C-Cure PACS server, which, to RFC_URE3, meant the terminal servers are not PACS. However, the terminal servers and the connections they provide to the PACS C-Cure System Database provide the “functionality” of a PACS system workstation for authorizing PSP access. The terminal servers are also on a protected network and provide some of the required CIP security controls. Therefore, the terminal servers are PACS because they are part of the PACS infrastructure by authorizing access to devices that authorize and/or log access to the PSPs. The duration of this noncompliance is from the date RFC_URE3 was subject to compliance with CIP-006-1 R2 to the date RFC_URE3 committed to complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the subject devices were not declared as Cyber Assets, the devices were afforded many of the protections detailed in CIP-005-3 R2 and R3. At the time of the violation, RFC_URE3 had strong monitoring controls for physical and logical access to CCAs in place. Specifically, RFC_URE3’s PACS logically reside within an internal protected network with specific access control and physically reside within an identified PSP. The PACS are in their own Windows Active Directory, requiring users to have a unique account defined in the Windows Active Directory in order to gain access to these servers, and no trust relationships exist between the physical security Active Directory and any other RFC_URE3 or RFC_URE3’s parent company's Active Directory. To gain access to the application that makes physical access additions, changes, and removals, a RFC_URE3 compliance engineer must first be authenticated to the server that houses the application. RFC_URE3 provided evidence of these protective measures applied to jump hosts, a type of server, and panels, despite lacking certain protections required by the Reliability Standard at issue. No harm is known to have occured. | To mitigate this issue, RFC_URE3 will complete the following mitigation activities: 1) will determine whether the Remote Desktop Web server will be a Microsoft or Citrix product; 2) will complete testing of the servers and applications needed for the re-architecture of remote interactive access to the Remote Desktop Servers (RDS) environment; 3) will apply the following protective measures to the Intermediate Systems: malicious code prevention, alarming, logging, account management, physical and electronic access controls, and configuration management; 4) will complete a re-architecture of remote interactive access to the RDS environment; 5) will revise compliance documentation to reflect the RDS environment and protective measures applied to these Intermediate Systems; 6) will integrate the Intermediate Systems in the RDS environment into the security patch assessment program; and 7) will integrate the Intermediate Systems into the information protection procedures and recovery plans.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015065 | CIP-007-1 | R5.2 R5.3 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-007-1 R5.2 and R5.3. Having completed compliance investigations of several issues, RFC_URE4 determined that certain possible violations had occurred involving CIP-007-3a R5 as applied to RFC_URE4’s Account Management processes. While performing annual password changes on shared accounts, RFC_URE4 discovered a generic account that had not been previously identified. Because the account had not been identified, the original default password had not been changed. The investigation determined that this account and password were auto-generated when the energy management system (EMS) was created. The EMS vendor had supplied the EMS staff scripts to change passwords in the system, but this account was not included in the scripts and went unnoticed until it was identified approximately two years later. Additionally, RFC_URE4 discovered a root password on a proxy server that had not been changed after a person left the EMS department. This issue was identified while troubleshooting a non-related maintenance issue, during which it was discovered that the root password did not match the format of other shared passwords for like accounts. The following investigation determined that all shared account passwords had been changed upon personnel departure, with the exception of the one root password on the proxy server. The duration of this noncompliance is from the date RFC_URE4 was required to comply with CIP-007-1 R5.2 and R5.3, through the date RFC_URE4 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The generic account was a management view account that allowed read only access without any capabilities for modification into the system. Authorized personnel with the ability to access the view account would need to be within the secure EMS Physical Security Perimeter (PSP) area with knowledge of the accounts existence. Moreover, because the account was auto-generated when the system was built and had not been subsequently changed, no personnel had knowledge of the password associated with the account within the EMS. The delay in changing the root password to the device also posed minimal risk to the Bulk Electric System, because the person left the company voluntarily, physical access was revoked at the time of departures, and all electronic access was promptly revoked as well. Given the secure nature of the EMS (enclosed within a PSP and under strict security watch), it would be extremely unlikely that the person would come back into the EMS to access that specific device without being detected. No harm is known to have occured. | To mitigate this issue, RFC_URE4 changed the root password on the proxy server soon after it was identified. To mitigate this issue, RFC_URE4 will also complete the following mitigation activities: 1) test the impact of changing the password on the system prior to an EMS production change; 2) system and service accounts will be modified per vendor recommendations; and 3) the EMS technical procedure will be created to include specific instructions for changing relevant passwords. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE4 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE4 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014796 | CIP-005-3a | R1.4 R1.6 | RFC_URE4 submitted a Self-Certification and a self-log stating that it had an issue of CIP-005-3a R1.4 and R1.6. RFC_URE4 completed two investigations and determined that a possible violation had occurred involving CIP-005-3a R1. Specifically, it was determined that (1) two unauthorized RFC_URE4 corporate laptops were connected to devices within an Electronic Security Perimeter (ESP) to perform work related activities; and (2) a device was removed from service but not updated on the ESP drawing and list. The first laptop in question was connected to the ESP within a substation on three separate occasions in order to conduct work related to Bitronics metering. The brief connections were identified during a security log review. In this case, the RFC_URE4 authorized laptop was not used because the software and required dongle would not work due to USB port restrictions. The second laptop was connected to a RTU in the ESP within a substation while performing testing on a stuck breaker relay, as well as installing a new cyber asset. The connection of the second laptop was identified by the Protection & Control supervisor, who immediately stopped the connection and reported the issue. In both cases, RFC_URE4's corporate laptops were used as opposed to RFC_URE4's authorized laptops. Finally, during the Cyber Vulnerability Assessment (CVA), a dial up modem listed and depicted on certain RFC_URE4 ESP documentation could not be physically located. Further review determined that the device had been removed from service, but the documentation was not updated to reflect the change. This dial-up connection was the only access point into the defined ESP. The cause stemmed from not having at the time a detailed change control process to concurrently capture and document all changes when the device was removed. The duration of this noncompliance is from the date RFC_URE4 was required to comply with CIP-005-3a R1.4 and R1.6, through the date RFC_URE4 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The laptops were used by personnel authorized and qualified (i.e., personnel risk assessments and training) to be in and work on devices within the secure areas. The laptops are RFC_URE4 issued laptops that are routinely patched and run active, updated, anti-virus protection software. Log review controls and personnel awareness detected the issues which were promptly reported to Compliance. Removal of the modem eliminated all connectivity into the ESP, therefore no additional risk was posed to the devices or the Bulk Electric System. No harm is known to have occured. | To mitigate this issue, RFC_URE4 circulated a security message to enforce awareness that no unauthorized devices are to be connected to an ESP. To mitigate this issue, RFC_URE4 will also complete the following mitigation activities: 1) review and verify dial-up access points captured on its ESP diagrams; 2) elevate the assessments of all access points when a CVA is performed. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE4 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE4 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014808 | CIP-007-3a | R6.3 | RFC_URE4 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-3a R6.3. While conducting a manual log review of device security logs, RFC_URE4 identified that security logs for several Non-Critical Cyber Asset (CCA) devices were not captured via the server for one month. Although several Non-CCA devices were affected, a majority of the security logs were ultimately retrieved through internal logs captured on the devices themselves. The devices for which logs could not be retrieved included 25 switches and 5 PCs. An investigation determined the cause was a misconfiguration that took place while preparing to migrate to a new server. Before the migration occurred, there was a failure of the existing system. The system issue was thought to have been corrected and the system was restarted, but a misconfiguration upon restart caused the device logs to be redirected to a non-functioning server. Lack of detail in the change control process to check the impact of planned or unplanned changes (including system restarts) contributed to the issue. The duration of this noncompliance is from the date RFC_URE4 was required to comply with CIP-007-3a R6.3, through the date RFC_URE4 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Internal controls for log review detected the issue and allowed the issue to be corrected the same day it was discovered. Security logs were ultimately retrieved for a majority of the devices impacted. Of the limited devices for which logs could not receive, the issue was isolated to a 3 week period and immediately corrected upon discovery. All affected devices were physically protected within secure Physical Security Perimeters, and electronically protected by firewalls and defense-in-depth protections associated with the Electronic Security Perimeter. No harm is known to have occured. | To mitigate this issue RFC_URE4 corrected the misconfiguration and Syslogs reinitiated for all Non-CCA devices, including the switches and PCs at issue. To mitigate this issue, RFC_URE4 will also complete the following mitigation activities: 1) to prevent future reoccurrence, devices will be configured to generate, at a minimum, a daily log in order to verify the device is sending logs to the log server; 2) an alert will be configured on the system to provide notification if a device fails to generate a log; and 3) supporting procedures will be reviewed and enhanced to account for these additional controls. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE4 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE4 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015015069 | CIP-004-3a | R4 | RFC_URE4 submitted a self-log stating that it had an issue of CIP-004-3a R4. Specifically, RFC_URE4 identified three instances where user tracking lists were not updated within 7 days of an account status change. The energy management system (EMS) area uses two separate lists to track accounts; (i) the EMS Master User List (MUL), and (ii) the EMS Master User Account Tracking List (MUATL). The EMS MUL contains all of the users who have cyber access granted to an EMS system. The EMS MUATL contains the specific systems and accounts a user has been granted access to. User #1 was not updated on the MUL, but was updated on the MUATL when access was revoked, User #2 was not updated on the MUL, nor the MUATL when access was revoked, and User #3 was added to the MUL, but not the MUATL when access was granted The lists were updated and back in compliance in 14 days, 29 days, and 99 days respectively. The duration of this noncompliance is from the date RFC_URE4 was required to comply with CIP-004-3a R4, through the date RFC_URE4 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In all instances the personnel were granted access or access was removed within the required timeframe. What was not timely was the updating of the documentation associated with tracking the people who have access to an EMS system. Current controls performed as designed and detected the issues, although stronger controls need to be in place to ensure timely updates of the documentation. No harm is known to have occured. | To mitigate this issue RFC_URE4: 1) EMS updated the user tracking lists to reflect current user status and system access; 2) EMS transitioned to a new NERC Information Tracking System (“NERC ITS”) as a central repository for EMS users as a control to assist with capturing user status changes in a timely manner; and 3) undertook personnel training to assure full awareness of the procedures under the new NERC ITS. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE4 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE4 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014827 | CIP-007-1 | R2 | RFC_URE4 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-1 R2. Having completed an investigation of several issues identified in RFC_URE4’s 2014 Cyber Vulnerability Assessment (CVA), RFC_URE4 determined that certain possible violations had occurred involving CIP-007-3a R2. Specifically, RFC_URE4’s 2014 CVA identified devices where open ports and services found in the scans did not match the baseline documentation. The IT and Security devices included Physical Access Control Systems (PACS), Intrusion Detection System (IDS) appliances, and an Electronic Access Control and Monitoring (EACM) server, for a total of 27 devices. A Non-Critical Cyber Asset (CCA) device was also identified in Substations. Excluding the IDS sensors, review of the ports and services confirmed that all of the devices in question had only ports and services open that were required for normal or emergency operation. However, for these device types, baseline documentation needed to be updated. Therefore, the IDS sensors were being evaluated and information requests were presented to the vendor, however, before the operational purpose of the identified ports and services could be determined, the devices were removed from NERC program scope because they were no longer monitoring NERC cyber assets. In addition, the 2014 CVA identified a device (Non-CCA) that did not have a documented ports and services baseline. This device was the only device of its kind in the environment, and when commissioned a spare was not available to port testing. RFC_URE4 is in the process of procuring an additional device to include in its test environment, and upon which to establish the production device baseline. The duration of this noncompliance is from the date RFC_URE4 was required to comply with CIP-007-1 R2, through the date RFC_URE4 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the port and services baselines were in question for these devices, all other requisite CIP protections, including up-to-date security patching, antivirus software, and access log monitoring and alerting were fully in place and being performed. Additionally, windows devices have local firewalls enabled to further secure the device. The device is located within a physically and electronically secure substation control house with defense-in-depth protections. No harm is known to have occured. | To mitigate this issue RFC_URE4: 1) updated its ports and services baselines for the effected devices or removed the devices from the NERC CIP program where they are no longer required; 2) reviewed test procedures for Windows servers and workstations to ensure instructions are clear regarding the review and update of ports and services documentation to ensure only those ports and services needed for normal or emergency operations are enabled at all times. These instructions will be reviewed with testing personnel; 3) procured an additional device; 4) tested and documented a ports and services baseline; and 5) reviewed and updated as necessary operational and technical procedures to ensure requirements are adhered to prior to commissioning. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE4 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE4 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE4 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015066 | CIP-007-1 | R5.2 R5.3 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-007-1 R5.2 and R5.3. Having completed compliance investigations of several issues, RFC_URE5 determined that certain possible violations had occurred involving CIP-007-3a R5 as applied to RFC_URE5’s Account Management processes. While performing annual password changes on shared accounts, RFC_URE5 discovered a generic account that had not been previously identified. Because the account had not been identified, the original default password had not been changed. The investigation determined that this account and password were auto-generated when the energy management system (EMS) system was created. The EMS vendor had supplied the EMS staff scripts to change passwords in the system, but this account was not included in the scripts and went unnoticed until it was identified approximatley two years later. Additionally, RFC_URE5 discovered a root password on a proxy server that had not been changed after a person left the EMS department. This issue was identified while troubleshooting a non-related maintenance issue, during which it was discovered that the root password did not match the format of other shared passwords for like accounts. The following investigation determined that all shared account passwords had been changed upon personnel departure, with the exception of the one root password on the proxy server. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-007-1 R5.2 and R5.3, through the date RFC_URE5 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The generic account was a management view account that allowed read only access without any capabilities for modification into the system. Authorized personnel with the ability to access the view account would need to be within the secure EMS Physical Security Perimeter (PSP) area with knowledge of the accounts existence. Moreover, because the account was auto-generated when the system was built and had not been subsequently changed, no personnel had knowledge of the password associated with the account within the EMS. The delay in changing the root password to the device also posed minimal risk to the Bulk Electric System, because the person left the company voluntarily, physical access was revoked at the time of departures, and all electronic access was promptly revoked as well. Given the secure nature of the EMS (enclosed within a PSP and under strict security watch), it would be extremely unlikely that the person would come back into the EMS to access that specific device without being detected. No harm is known to have occured. | To mitigate this issue, RFC_URE5 changed the root password on the proxy server soon after it was identified. To mitigate this issue, RFC_URE5 will also complete the following mitigation activities: 1) test the impact of changing the password on the system prior to an EMS production change; 2) system and service accounts will be modified per vendor recommendations; and 3) the EMS technical procedure will be created to include specific instructions for changing relevant passwords. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE5 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE5 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015014813 | CIP-007-3a | R6.3 | RFC_URE5 submitted a Self-Certification a self-log stating that it had an issue of CIP-007-3a R6.3. While conducting a manual log review of device security logs, RFC_URE5, identified that security logs for several Non-Critical Cyber Asset (CCA) devices were not captured via the server for one month. Although several Non-CCA devices were affected, a majority of the security logs were ultimately retrieved through internal logs captured on the devices themselves. The devices for which logs could not be retrieved included 25 switches and 5 PCs. An investigation determined the cause was a misconfiguration that took place while preparing to migrate to a new server. Before the migration occurred, there was a failure of the existing system. The system issue was thought to have been corrected and the system was restarted, but a misconfiguration upon restart caused the device logs to be redirected to a non-functioning server. Lack of detail in the change control process to check the impact of planned or unplanned changes (including system restarts) contributed to the issue. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-007-3a R6.3, through the date RFC_URE5 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Internal controls for log review detected the issue and allowed the issue to be corrected the same day it was discovered. Security logs were ultimately retrieved for a majority of the devices impacted. Of the limited devices for which logs could not receive, the issue was isolated to a 3 week period and immediately corrected upon discovery. All affected devices were physically protected within secure Physical Security Perimeters, and electronically protected by firewalls and defense-in-depth protections associated with the Electronic Security Perimeter. No harm is known to have occured. | To mitigate this issue RFC_URE5 corrected the misconfiguration and logs reinitiated for all Non-CCA devices, including the switches and PCs at issue. To mitigate this issue, RFC_URE5 will also complete the following mitigation activities by: 1) to prevent future reoccurrence, devices will be configured to generate, at a minimum, a daily log in order to verify the device is sending logs to the log server; 2) an alert will be configured on the system to provide notification if a device fails to generate a log; and 3) supporting procedures will be reviewed and enhanced to account for these additional controls. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE5 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE5 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015015070 | CIP-004-3a | R4 | RFC_URE5 submitted a self-log stating that it had an issue of CIP-004-3a R4. Specifically, RFC_URE5 identified three instances where user tracking lists were not updated within 7 days of an account status change. The energy management system (EMS) area uses two separate lists to track accounts; (i) the EMS Master User List (MUL), and (ii) the EMS Master User Account Tracking List (MUATL). The EMS MUL contains all of the users who have cyber access granted to an EMS system. The EMS MUATL contains the specific systems and accounts a user has been granted access to. User #1 was not updated on the MUL, but was updated on the MUATL when access was revoked, User #2 was not updated on the MUL, nor the MUATL when access was revoked, and User #3 was added to the MUL, but not the MUATL when access was granted The lists were updated and back in compliance in 14 days, 29 days, and 99 days respectively. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-004-3a R4, through the date RFC_URE5 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In all instances the personnel were granted access or access was removed within the required timeframe. What was not timely was the updating of the documentation associated with tracking the people who have access to an EMS system. Current controls performed as designed and detected the issues, although stronger controls need to be in place to ensure timely updates of the documentation. No harm is known to have occured. | To mitigate this issue RFC_URE5: 1) EMS updated the user tracking lists to reflect current user status and system access; 2) EMS transitioned to a new NERC Information Tracking System (NERC ITS) as a central repository for EMS users as a control to assist with capturing user status changes in a timely manner; and 3) undertook personnel training to assure full awareness of the procedures under the new NERC ITS. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE5 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE5 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2015014828 | CIP-007-1 | R2 | RFC_URE5 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-1 R2. Having completed an investigation of several issues identified in RFC_URE5’s Cyber Vulnerability Assessment (CVA), RFC_URE5 determined that certain possible violations had occurred involving CIP-007-3a R2. Specifically, RFC_URE5’s CVA identified devices where open ports and services found in the scans did not match the baseline documentation. The IT and Security devices included PACS, Intrusion Detection System (IDS) appliances, and an Electronic Access Control and Monitoring (EACM) server, for a total of 27 devices. A Non-Critical Cyber Asset (CCA) devices was also identified in Substations. Excluding the IDS sensors, review of the ports and services confirmed that all of the devices in question had only ports and services open that were required for normal or emergency operation. However, for these device types, baseline documentation needed to be updated. Therefore, the IDS sensors were being evaluated and information requests were presented to the vendor, however, before the operational purpose of the identified ports and services could be determined, the devices were removed from NERC program scope because they were no longer monitoring NERC cyber assets. In addition, the 2014 CVA identified a device (Non-CCA) that did not have a documented ports and services baseline. This device was the only device of its kind in the environment, and when commissioned a spare was not available to port testing. RFC_URE5 is in the process of procuring an additional device to include in its test environment, and upon which to establish the production device baseline. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-007-1 R2, through the date RFC_URE5 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the port and services baselines were in question for these devices, all other requisite CIP protections, including up-to-date security patching, antivirus software, and access log monitoring and alerting were fully in place and being performed. Additionally, windows devices have local firewalls enabled to further secure the device. The device is located within a physically and electronically secure substation control house with defense-in-depth protections. No harm is known to have occured. | To mitigate this issue RFC_URE5: 1) updated its ports and services baselines for the effected devices or removed the devices from the NERC CIP program where they are no longer required; 2) reviewed test procedures for Windows servers and workstations to ensure instructions are clear regarding the review and update of ports and services documentation to ensure only those ports and services needed for normal or emergency operations are enabled at all times. These instructions will be reviewed with testing personnel; 3) procured an additional device; 4) tested and documented a ports and services baseline; and 5) reviewed and updated as necessary operational and technical procedures to ensure requirements are adhered to prior to commissioning. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE5 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE5 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE5 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015015067 | CIP-007-1 | R5.2 R5.3 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-007-1 R5.2 and R5.3. Having completed compliance investigations of several issues, RFC_URE6 determined that certain possible violations had occurred involving CIP-007-3a R5 as applied to RFC_URE6’s Account Management processes. As a result of an internal assessment of substation maintenance devices, RFC_URE6 identified two (2) device types that did not fully adhere to CIP-007 R5.2. Specifically, PCs and maintenance laptops had not been configured to require user authentication to log on to these devices. The devices would automatically log on upon boot-up without entering any access credentials, i.e. a user name and password. The first device type, PCs, host the HMI software that provides a graphical representation of RTU data, allowing a user to view substation equipment data. These PCs also have RTU software and a number of relay management software packages installed. This software is used to view relay configurations and modify relay settings, but in order to do so users must have specific relay access credentials in order to make any significant changes. These PCs are located within secure control houses, where access is limited to personnel with authorized unescorted physical access. The second device type, maintenance laptops, also has RTU software and a number of relay management software packages installed. This software is used to view relay configurations and modify relay settings, but again, users must have specific relay access credentials in order to make any significant changes. The maintenance laptops are stored securely within locked cabinets within a Physical Security Perimeter. Only maintenance personnel with authorized access have a key to retrieve the maintenance laptops from the locked cabinets to perform necessary maintenance tasks, and are required to manually log their use of the maintenance laptops upon retrieval and returned. Additionally, RFC_URE6’s Cyber Vulnerability Assessment (CVA) identified (i) a network switch that did not contain a complex password that meets the requirements of R5.3.2, (ii) a network switch that contained a public read-only Simple Network Management Protocal (SNMP) community string, and (iii) user accounts on PCs that had not had their passwords changed within the annual period. (i) The console password on a switch within an EMS ESP was found not to contain at least one (1) uppercase character. Generally, RADIUS is the default method used to authenticate users. As a result, when a physical connection is made to the console, the user is not prompted for a console password, but rather RADIUS overrides the console login with a domain username and password prompt that does meet the password complexity requirements. Nonetheless, if a user logged in via the local console by physically connecting a console cable (serial) from an authorized laptop to a switch, they would be prompted to enter the console password, which did not meet the complexity requirements. Again, however, RADIUS is the default method by which authentication to the switches occurs. Use of a physically connected console cable is not the accepted protocol for normal operations. (ii) An SNMP community string of “snmp-server community public RO” was discovered on EMS network switch. “Public RO” indicates a “read only” option of SNMP protocol. Read only allows a preview of switch interfaces and does not allow modification of the switch. (iii) Previously, the PC configuration included a script in which the RADIUS servers were queried by the PCs to retrieve accounts which were in scope for that device type. This effort resulted in the provisioning of RADIUS accounts onto those PCs in the RFC_URE6 region. The script was no longer required so it was disabled and removed. Our investigation determined that this did not mitigate the presence of the Radius accounts on the PC, and resulted in their identification within the CVA as accounts whose passwords had not been changed within the annual time period. Lastly, while performing annual password changes on shared accounts, RFC_URE6 discovered a generic account that had not been previously identified. Because the account had not been identified, the original default password had not been changed. The investigation determined that this account and password were auto-generated when the energy management system (EMS) system was created. The EMS vendor had supplied the EMS staff scripts to change passwords in the system, but this account was not included in the scripts and went unnoticed until it was identified approximately two years later. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-007-1 R5.2 and R5.3, through the date RFC_URE6 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was identified by performing an internal assessment of the maintenance devices used in substations. This internal control identified a deficiency in the program allowing for improvements to the account management controls associated with the PCs and maintenance laptops. Only personnel with authorized unescorted physical access or individuals escorted by personnel with authorized unescorted physical access could have gained access to these devices within the control houses. Moreover, although initial login was not required upon system boot-up, the PCs and maintenance laptops themselves permitted view only access to displayed RTU and relay data. The system strictly limited the ability to perform changes to such devices by requiring the user to have elevated credentials to the relays. Therefore, any risk to the Bulk Electric System (BES) was reduced. With regard to the non-complex console password, RADIUS is the default method of authentication, and requires the use a domain user name and complex password in order to access the Cisco switch at issue. Although a non-complex console password was identified on the switch configuration itself, this password would only have been used/prompted if a physical serial connection had been made from an authorized laptop to the switch. Because physically connecting via a console cable is not the accepted protocol for normal operations, the local console password has since been removed from the switch configuration, so as to prevent such connections from taking place. With regard to the identified community string, the switch is within a monitored Electronic Security Perimeter (ESP) behind several layers of defense-in-depth protections, reducing the probability of the device being compromised or the attempt to compromise going undetected. Therefore, any risk that someone could access the community string and make changes to the switch is very low. Finally, the passwords associated with the INFO-PC RADIUS accounts had not been changed within the annual time frame because the accounts had not been accessed/used in over a year. Expired account enforcement controls would have required a user to provide the expired complex password before receiving a prompt for a new complex password and permitting access to the account. Moreover, the INFO-PCs are housed within a secure PSP, where access is limited to those with authorized unescorted or escorted physical access. Furthermore, credentials to logon to the INFO-PCs is tightly controlled, and only issued to personnel with a business need who have been granted authorized electronic access. The generic account was a management view account that allowed read only access without any capabilities for modification into the system. Authorized personnel with the ability to access the view account would need to be within the secure EMS PSP area with knowledge of the accounts existence. Moreover, because the account was auto-generated when the system was built and had not been subsequently changed, no personnel had knowledge of the password associated with the account within the EMS. The delay in changing the root password to the device also posed minimal risk to the BES, because the person left the company voluntarily, physical access was revoked at the time of departures, and all electronic access was promptly revoked as well. Given the secure nature of the EMS (enclosed within a PSP and under strict security watch), it would be extremely unlikely that the person would come back into the EMS to access that specific device without being detected. No harm is known to have occured. | To mitigate this issue, RFC_URE6 changed the root password on the proxy server soon after it was identified. To mitigate this issue, RFC_URE6 will also complete the following mitigation activities: 1) identify a technical solution to facilitate the management of unique user accounts for the PC and maintenance laptop workstations; 2) update and implement operational and technical procedures; 3) train end-users to ensure the process is understood and followed; 4) perform a quality assurance review to ensure the solution is working as expected; 5) remove the local console non-complex password; 6) create an EMS technical procedure to include password complexity requirements as defined in the Account Management procedure; 7) ensure personnel are trained on the EMS technical procedure; 8) remove the public read-only community string from the switch at issue; 9) implement a technical control to alert if SNMP changes are made to network switches: 10) provide training on the implementation; 11) identify and remove all expired or unnecessary accounts from the windows devices at issue; 12) update User Account tracking documentation as appropriate; 13) develop and implement a tool that will disable accounts as they expire; 14) train the appropriate personnel on new processes or procedures; 15) test the impact of changing the password on the system prior to an EMS production change; 16) modify system and service accounts per vendor recommendations; and 17) create the EMS technical procedure to include specific instructions for changing relevant passwords. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014817 | CIP-005-3a | R2.2 | RFC_URE6 submitted a Self-Certification and a self-log stating that it had an issue of CIP-005-3a R2.2. Having completed a compliance review of an identified issue, RFC_URE6 determined that a possible violation had occurred involving CIP-005-3a R2.2. Specifically, while preparing to replace the Energy Management System (EMS) and Emergency Backup System (EBS) firewalls, RFC_URE6 identified rules in the firewall rulesets that were not removed from the rulesets when they were no longer required for normal or emergency operation. Specifically, RFC_URE6 identified that 31% rules on the EMS firewall and 24% rules on the EBS firewall were potentially not necessary, requiring review, modification and/or removal. The investigation identified rules in place, dating back over two years, for devices that had been removed from service or moved to another LAN segment. The devices included printers, Industrial Defender (SEM), and Network Intrusion Detection System (NIDS). The source and destination of the rules were as follows: (a) EMS to EBS and EBS to EMS allowing bidirectional EMS System traffic. (b) EMS/EBS to DMZ and DMZ to EMS/EBS for printer and WSUS traffic (c) One LAN segment to another LAN segment within the EMS/EBS Electronic Security Perimeters (ESPs) used for routing purposes within the ESP and did not transverse the boundary of the ESP. The cause of the deficiency was found in RFC_URE6’s change control process that did not sufficiently include reviewing and updating rulesets when a device or system was removed from service. The duration of this noncompliance was approximately three years and eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The rules found to be in question were also reviewed by a Subject Matter Expert who provided an evaluation to the Risk-Harm assessment team. Accordingly, a thorough review of the rules found that a minimal number of changes were required for rules from a low secure to high secure network, and that most rules were from a high secure to low secure network or originating and terminating within the same secure Electronic Security Perimeter network. Because IP addresses for the devices were not reused, there were no new devices present that would allow traffic into or out of the secure networks. No harm is known to have occured. | To mitigate this issue, RFC_URE6: 1) replaced the firewalls within 3 weeks of the possible issue being identified; 2) evaluated the rules and each change was tested in the Quality Assurance System (QAS) prior to making the rules changes in production; 3) EMS enhanced the impact analysis section of their change control form to specifically identify the need to review and update the ruleset baseline as necessary; 4) EMS updated its change control and configuration management procedure; 5) created a technical document to serve as guidance when developing and updating firewall rules; and 6) provided training to ensure awareness as to firewall configurations and the importance of maintaining the baseline. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015015068 | CIP-005-3a | R1.4 R1.6 | RFC_URE6 submitted a self-log stating that it had an issue of CIP-005-3a R1.4 and R1.6. RFC_URE6 completed two investigations and determined that a possible violation had occurred involving CIP-005-3a R1. Specifically, it was determined that (1) two unauthorized RFC_URE6 corporate laptops were connected to devices within an Electronic Security Perimeter (ESP) to perform work related activities; and (2) a device was removed from service but not updated on the ESP drawing and list. The first laptop in question was connected to the ESP within a substation on three separate occasions in order to conduct work related to Bitronics metering. The brief connections were identified during a security log review on. In this case, the RFC_URE6 authorized laptop was not used because the software and required dongle would not work due to USB port restrictions. The second laptop was connected to a RTU in the ESP within a substation while performing testing on a stuck breaker relay, as well as installing a new cyber asset. The connection of the second laptop was identified by the Protection & Control supervisor, who immediately stopped the connection and reported the issue. In both cases, RFC_URE6 corporate laptops were used as opposed to RFC_URE6 authorized laptops. Finally, during the Cyber Vulnerability Assessment (CVA), a dial up modem listed and depicted on certain RFC_URE6 ESP documentation could not be physically located. Further review determined that the device had been removed from service, but the documentation was not updated to reflect the change. This dial-up connection was the only access point into the defined ESP. The cause stemmed from not having at the time a detailed change control process to concurrently capture and document all changes when the device was removed. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-005-3a R1.4 and R1.6, through the date RFC_URE6 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The laptops were used by personnel authorized and qualified (i.e., personnel risk assessments and training) to be in and work on devices within the secure areas. The laptops are RFC_URE6 issued laptops that are routinely patched and run active, updated, anti-virus protection software. Log review controls and personnel awareness detected the issues which were promptly reported to Compliance. Removal of the modem eliminated all connectivity into the ESP, therefore no additional risk was posed to the devices or the Bulk Electric System. No harm is known to have occured. | To mitigate this issue RFC_URE6 circulated a security message to enforce awareness that no unauthorized devices are to be connected to an ESP. To mitigate this issue, RFC_URE6 will also complete the following mitigation activities: 1) restrict open ports on the switches; and 2) install tags on the switches to further clarify that these are CIP devices. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014820 | CIP-007-3a | R6.3 | RFC_URE6 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-3a R6.3. While conducting a manual log review of device security logs, RFC_URE6 identified that security logs for several Non-Critical Cyber Asset (CCA) devices were not captured via the server for one month. Although several Non-CCA devices were affected, a majority of the security logs were ultimately retrieved through internal logs captured on the devices themselves. The devices for which logs could not be retrieved included 25 switches and 5 PCs. An investigation determined the cause was a misconfiguration that took place while preparing to migrate to a new server. Before the migration occurred, there was a failure of the existing system. The system issue was thought to have been corrected and the system was restarted, but a misconfiguration upon restart caused the device logs to be redirected to a non-functioning server. Lack of detail in the change control process to check the impact of planned or unplanned changes (including system restarts) contributed to the issue. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-007-3a R6.3, through the date RFC_URE6 committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Internal controls for log review detected the issue and allowed the issue to be corrected the same day it was discovered. Security logs were ultimately retrieved for a majority of the devices impacted. Of the limited devices for which logs could not receive, the issue was isolated to a 3 week period and immediately corrected upon discovery. All affected devices were physically protected within secure Physical Security Perimeters, and electronically protected by firewalls and defense-in-depth protections associated with the Electronic Security Perimeter. No harm is known to have occured. | To mitigate this issue RFC_URE6 corrected the misconfiguration and logs reinitiated for all Non-CCA devices, including the switches and PCs at issue. To mitigate this issue, RFC_URE6 will also complete the following mitigation activities: 1) to prevent future reoccurrence, devices will be configured to generate, at a minimum, a daily log in order to verify the device is sending logs to the log server; 2) an alert will be configured on the system to provide notification if a device fails to generate a log; and 3) supporting procedures will be reviewed and enhanced to account for these additional controls. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014815 | CIP-004-3a | R4 | RFC_URE6 submitted a Self-Certification and a self-log stating that it had an issue of CIP-004-3a R4. Specifically, RFC_URE6 identified three instances where user tracking lists were not updated within 7 days of an account status change. The energy management system (EMS) area uses two separate lists to track accounts; (i) the EMS Master User List (MUL), and (ii) the EMS Master User Account Tracking List (MUATL). The EMS MUL contains all of the users who have cyber access granted to an EMS system. The EMS MUATL contains the specific systems and accounts a user has been granted access to. User #1 was not updated on the MUL, but was updated on the MUATL when access was revoked, User #2 was not updated on the MUL, nor the MUATL when access was revoked, and User #3 was added to the MUL, but not the MUATL when access was granted The lists were updated and back in compliance in 14 days, 29 days, and 99 days respectively. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-004-3a R4, through the date RFC_URE6 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In all instances the personnel were granted access or access was removed within the required timeframe. What was not timely was the updating of the documentation associated with tracking the people who have access to an EMS system. Current controls performed as designed and detected the issues, although stronger controls need to be in place to ensure timely updates of the documentation. No harm is known to have occured. | To mitigate this issue RFC_URE6: 1) EMS updated the user tracking lists to reflect current user status and system access. 2) EMS will transition to a new NERC Information Tracking System (NERC ITS) as a central repository for EMS users as a control to assist with capturing user status changes in a timely manner: and 3) personnel training will be undertaken to assure full awareness of the procedures under the new NERC ITS. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2015014826 | CIP-007-1 | R2 | RFC_URE6 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-1 R2. Having completed an investigation of several issues identified in RFC_URE6’s Cyber Vulnerability Assessment (CVA), RFC_URE6 determined that certain possible violations had occurred involving CIP-007-3a R2. Specifically, RFC_URE6’s CVA identified devices where open ports and services found in the scans did not match the baseline documentation. The IT and Security devices included PACS, Intrusion Detection System (IDS) appliances, and an Electronic Access Control and Monitoring (EACM) server, for a total of 27 devices. A Non-Critical Cyber Asset (CCA) devices was also identified in Substations. Excluding the IDS sensors, review of the ports and services confirmed that all of the devices in question had only ports and services open that were required for normal or emergency operation. However, for these device types, baseline documentation needed to be updated. Therefore, the IDS sensors were being evaluated and information requests were presented to the vendor, however, before the operational purpose of the identified ports and services could be determined, the devices were removed from NERC program scope because they were no longer monitoring NERC cyber assets. In addition, the CVA identified a device (Non-CCA) that did not have a documented ports and services baseline. This device was the only device of its kind in the environment, and when commissioned a spare was not available to port testing. RFC_URE6 is in the process of procuring an additional device to include in its test environment, and upon which to establish the production device baseline. The duration of this noncompliance is from the date RFC_URE6 was required to comply with CIP-007-1 R2, through the date RFC_URE6 completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the port and services baselines were in question for these devices, all other requisite CIP protections, including up-to-date security patching, antivirus software, and access log monitoring and alerting were fully in place and being performed. Additionally, windows devices have local firewalls enabled to further secure the device. The device is located within a physically and electronically secure substation control house with defense-in-depth protections. No harm is known to have occured. | To mitigate this issue RFC_URE6: 1) updated its ports and services baselines for the effected devices or removed the devices from the NERC CIP program where they are no longer required; 2) reviewed test procedures for Windows servers and workstations to ensure instructions are clear regarding the review and update of ports and services documentation to ensure only those ports and services needed for normal or emergency operations are enabled at all times. These instructions will be reviewed with testing personnel; 3) procured an additional device; 4) tested and documented a ports and services baseline; and 5) reviewed and updated as necessary operational and technical procedures to ensure requirements are adhered to prior to commissioning. In addition to the mitigation measures required to resolve the issue described above, as RFC_URE6 transitions to procedures that comply with version 5 of the CIP Reliability Standards, RFC_URE6 commits to performing all appropriate personnel training on the updated procedures. This training will ensure that the RFC_URE6 employees responsible for implementation of the procedures will have full knowledge and awareness of the relevant requirements and the processes in place to achieve compliance with those requirements. The company will continue providing appropriate communications designed to ensure effective awareness of its commitment to achieving compliance with the NERC Reliability Standards.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015014655 | CIP-004-3a | R4 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. RFC_URE7 discovered that it failed to remove Physical Security Perimeter (PSP) access for an employee who transferred to another position with the company and no longer required physical access to the PSPs. RFC_URE7 identified this noncompliance during its PSP review. RFC_URE7 immediately removed access for this employee upon discovery. The root cause of this noncompliance was human error related to the management practice area of reliability quality management. Specifically, the procedure that RFC_URE7 had in place for revoking access to PSPs failed to account for human error. It was a largely manual process with no secondary reviewer to ensure accuracy. In these two instances of noncompliance, the responsible employee failed to recognize that these employees’ new positions no longer required access to the PSPs. The duration of this noncompliance is from the date RFC_URE7 was required to remove access for the first employee, the date RFC_URE7 removed access for the first employee. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the violation was identified and corrected in a relatively short period of time. Second, RFC_URE7's access privileges are granted on a limited basis, meaning that they are limited to specific PSPs. In other words, each employee could only have entered the specific PSP to which he was originally assigned. Third, the employees were trusted individuals who simply no longer needed access to the particular PSPs due to work transfers. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) removed the physical access for the employee who transferred to another company position; 2) modified the process for one employee to process all regulated job change notifications; 3) modified the process to incorporate a secondary verification; 4 checked with vendor to determine if software change is viable; and, 5) counseled employee and documented year end performance review. ReliabilityFirst hs verified the completion of all mitigation activity.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2015014656 | CIP-004-3a | R4 | RFC_URE7 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. The RFC_URE7 employee responsible for setting the revocation date on a second employee’s badge mistakenly populated the year, allowing access to remain on that second employee’s badge for fourteen days after he no longer needed access. The responsible employee did not actually type in the mistaken year as the revocation date. Rather, RFC_URE7 uses a software program that automatically sets the revocation date. The user inputs the month and date, but the software program automatically fills in the year field. This program has a default setting of 30 days, which cannot be modified by RFC_URE7. Rather, the responsible employee at RFC_URE7 must manually change the year field when required. In this case, because of the 30 day default setting, the software program inserted into the year field, a revocation date of one year later. The responsible employee at RFC_URE7 failed to identify this error and correct it. The root cause of this noncompliance was human error related to the management practice area of reliability quality management. Specifically, the procedure that RFC_URE7 had in place for revoking access to Physical Security Perimeters (PSPs) failed to account for human error. It was a largely manual process with no secondary reviewer to ensure accuracy. In these two instances of noncompliance, the responsible employee failed to recognize that these employees’ new positions no longer required access to the PSPs. Moreover, the responsible employee failed to identify the problem with the year field in the revocation software program. The duration of this noncompliance is from the date RFC_URE7 was required to remove access for the second employee, through the date RFC_URE7 removed access for the second employee. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the violation was identified and corrected in a relatively short period of time. Second, RFC_URE7's access privileges are granted on a limited basis, meaning that they are limited to specific PSPs. In other words, each employee could only have entered the specific PSP to which he was originally assigned. Third, the employees were trusted individuals who simply no longer needed access to the particular PSPs due to work transfers. No harm is known to have occurred. | To mitigate this issue, RFC_URE7: 1) removed the physical access for the employee who transferred to another company position; 2) modified the process for one employee to process all regulated job change notifications; 3) modified the process to incorporate a secondary verification; 4 checked with vendor to determine if software change is viable; and, 5) counseled employee and documented year end performance review. ReliabilityFirst hs verified the completion of all mitigation activity.
2015-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015014875 | CIP-006-3c | R5 | TRE_URE1 submitted a Self-Log stating that it had three minimal risk instances of noncompliance with CIP-006-3c R5. TRE_URE1 failed to implement technical and procedural controls for monitoring physical access at all access points to multiple Physical Security Perimeters (PSPs) 24 hours a day, seven days a week. Specifically, TRE_URE1 was unable to monitor physical access at multiple control houses. According to TRE_URE1, it experienced outages on its substation alarm systems at multiple substation PSPs. Each substation has a backup cellemetry system functioning as an alarm. During each incident, cellemetry failed to start, causing human observation to be dispatched to the affected sites. Sites were unable to be monitored and without human observation for approximately for two hours and 30 minutes until human observation arrived at the sites. The root cause of these issues was that the old cellemetry network was running on an older technology, which was weak at times due to the remote location of the sites. In the first instance, TRE_URE1 experienced a network outage at one of its substations for approximately four hours and 42 minutes. TRE_URE1's backup alarm system also had no signal. TRE_URE1 worked with its vendor to restore normal communications. The noncompliance occurred for two hours and 43 minutes. In the second instance, TRE_URE1 experienced a network outage at one of its substations for approximately six hours and 42 minutes. TRE_URE1's backup alarm system also had no signal. TRE_URE1 worked with its vendors to restore the micro and repair the backup unit. The issue duration was for approximately two hours and 24 minutes. In the third instance, a network outage impacted the micro (primary alarm system) at one of TRE_URE1’s control house PSPs for approximately two hours and 32 minutes. TRE_URE1’s cellemetry unit (the alarm system backup) was also not functional. Therefore, TRE_URE1 was unable to maintain 24 hour continuous monitoring. After TRE_URE1 received notification that the system was down, human observation was dispatched. The noncompliance occurred for two hours and five minutes. The duration of these issues was for approximately three months. | These instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE1’s failure to monitor physical access to the PSPs at all access points 24 hours a day, seven days a week, provided an opportunity for unauthorized access into the substation. This failure could have compromised the system and affected the BPS. The risk to the reliability of the BPS was reduced because of the following factors. Although no monitoring system and associated alarms were functioning during that time of the network failure, physical access control systems (PACS) at these substations continued to work in local mode, ensuring the PSP doors remained locked and access-controlled. Additionally, TRE_URE1 has other safeguards at its substations locally, including audible alarms and strobes to deter intruders. Furthermore, each issue was resolved within a few hours of failure. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate these instances of noncompliance, TRE_URE1: 1) began human observation at the substation during the first instance; 2) restored communication and the alarm system at the substation for the second instance; 3) began human observation at the control house during the third instance; and 4) upgraded its cellemetry to a higher cellular network service. Texas RE has verified the completion of all mitigation activity.
2015-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014876 | CIP-006-3c | R5 | TRE_URE2 submitted a Self-Log stating that it had an issue with CIP-006-3c R5. TRE_URE2 failed to implement technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeters (PSP) 24 hours a day, seven days a week. Specifically, TRE_URE2 was unable to monitor physical access at a station control house for two hours and five minutes. During a network outage, TRE_URE2’s primary alarm system at a station control house PSP and the cellemetry unit (the alarm system backup) were not functional. Therefore, TRE_URE2 was unable to maintain 24 hour continuous monitoring of its station control house PSP. After TRE_URE2 received notification that the system was down, human observation was dispatched. Human observation of the station control house PSP was in place two hours and five minutes after the initial loss of monitoring capability. The root cause of this issue was that the cellemetry network was running on an older technology, which was weak at times due to the remote location of the site. The duration of this issue was for approximately two hours and five minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2’s failure to monitor physical access to the PSPs at all access points 24 hours a day, seven days a week, provided an opportunity for unauthorized access into the substation. This failure could have compromised the system and affected the BPS. The risk to the reliability of the BPS was reduced because of the following factors. Although no monitoring system and associated alarms were functioning during that time of the network failure, physical access control systems (PACS) at this substation continued to work in local mode, ensuring the PSP doors remained locked and access-controlled. Additionally, TRE_URE2 has other safeguards at its substations locally, including audible alarms and strobes to deter intruders. Furthermore, the issue was resolved within a short duration. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) began human observation at the applicable station control house; and 2) upgraded its cellemetry to a higher cellular network service. Texas RE has verified the completion of all mitigation activity.
2015-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2015014571 | CIP-007-3a | R5; R5.3.3 | TRE_URE3 submitted a Self-Report stating that it had an issue with CIP-007-3a R.5.3.3. A contractor hired to assist in remediating issues with TRE_URE3’s management system discovered that passwords for Cyber Assets located inside its Electronic Security Perimeter (ESP) had not been changed at least annually. Specifically, TRE_URE3 failed to change passwords at least annually or more frequently based on risk for 20% of its in-scope Cyber Assets. The root cause of the issue was a lack of an implemented formal process that comprehensively addressed all in-scope accounts. TRE_URE3 policy documentation requires the use of passwords subject to CIP requirements. Passwords for in-scope Cyber Assets are changed at least annually (when technically feasible) or more often as needed for personnel terminations or transfers. TRE_URE3 submitted Technical Feasibility Exceptions (TFEs) for the inability to change passwords. Texas RE determined the issue duration to be for nearly three years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Authorized personnel must VPN through the corporate network using an RSA key and PIN number, log into an assigned desktop computer, and then use Remote Desktop Protocol (RDP) to access a server in the ESP and to gain access to the production environment. TRE_URE3 only allows logical and physical access for personnel with a "need to know" and who are authorized for administering the system. Personnel with the need to know are issued domain credentials that allow for access to an endpoint in the ESP. Additional credentials are required to get to other landscapes within the ESP. Local accounts are only used when necessary to resolve an issue. The local accounts are restricted to those with access to the password vault where the reason for accessing the account is logged as well as tracked. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) reset the passwords for applicable devices. The last device possessed an account in which the password could not be changed and was addressed in a TFE; 2) added all relevant account credentials into a centralized password storage vault; 3) renamed the local administrator accounts; 4) deleted, renamed, or disabled all local administrator accounts that were no longer needed; and 5) updated its list of all accounts that require annual password changes. Texas RE has verified the completion of all mitigation activity.
2015-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012270 | CIP-006-3c | R5 | WECC_URE1 submitted a Self-Report stating that, as Responsible Entity, it had a noncompliance of CIP-006-3c R5. Two WECC_URE1 system operators were conducting routine switching at a substation. The two WECC_URE1 system operators contacted WECC_URE1’s alarm station to report that they would need to prop open a control room door in order to perform the switching. The system operators contacted WECC_URE1’s alarm station in accordance with WECC_URE1’s procedures. The system operators also notified WECC_URE3’s dispatcher that they would be performing the routine switching and that they would take a radio with them for emergency or routine communication during the switching activities. During the time the control room door was propped open, WECC_URE3’s dispatcher electronically monitored the system for alarms or abnormal activity. WECC_URE1’s operator was also viewing the control room via monitors. While viewing the monitors, the operator noticed that no one was physically observing the open control room door. The operator called the control room, but received no answer. The system operators re-entered the control room a few minutes later. The operator ordered the control room door closed and notified a supervisor about the event. The control room door was propped open and left unmonitored for approximately 15 minutes. At the time the door was left unmonitored, the two system operators in scope were the only personnel at the control room. The control room was a Physical Security Perimeter (PSP) housing Critical Cyber Assets (CCAs) such as networking equipment and workstations. The root cause of this compliance exception was that the two WECC_URE1 personnel in scope had a lapse in judgment and failed to follow their NERC CIP training and Company policy. The noncompliance start date was when the door was propped open and WECC_URE1 was not monitoring physical access at all access points to the PSP. The noncompliance end date was when the door was secured. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, for approximately 15 minutes WECC_URE1 did not monitor physical access to a PSP housing CCAs. This had the potential to allow unauthorized access to the PSP to go unnoticed or unchecked. Although WECC_URE1 did not monitor physical access to the PSP for 15 minutes, several compensating measures mitigated the risk. The PSP in scope is in a remote location and is surrounded by a fence with proximity monitoring. The PSP in scope is also under video surveillance and is monitored in real-time by WECC_URE1’s security team. WECC_URE1’s EMS activity is monitored at the control center and control can be removed from the control room in scope if any malicious activity is detected. For these reasons, and because no harm is known to have occurred from this compliance exception, WECC determined this noncompliance poses a minimal risk to the reliability of the BPS. WECC considered URE's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment | To mitigate this compliance exception, WECC_URE1 reprimanded the two system operators in scope per WECC_URE1’s policies. WECC has verified the completion of all mitigation activity.
2015-07-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012727 | CIP-003-2 | R5 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-003-2 R5. Specifically, MRO_URE1 failed to review the access privileges of two employees. A clerical error resulted in two employees being inadvertently deleted from the Master List of employees with access to Critical Cyber Asset (CCA) protected information. The error occurred when MRO_URE1 was properly removing the two employees from physical access (for lack of need), and then accidently deleted the record of them having required access to the CCA information. MRO_URE1 only reviews the access privileges for employees that are on the Master List. As a result, the employees (which still had access as intended) were not annually reviewed for access to the protected information as required. The root cause of the issue was human error and a lack of any secondary controls to detect discrepancies between the Master List and access privileges. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this case, the two employees in question did not improperly access CCAs as they both had been granted CCA access and their access privileges were not changed during the duration of the instance of non-compliance. The issue did not result in an employee acquiring unintentional or unpermitted CCA access. The extent of the noncompliance was limited to the failure to review access to protected information for two employees. No harm is known to have occurred. This is MRO_URE1's first instance of noncompliance with CIP-003-2. | To mitigate this issue, MRO_URE1: 1) Revoked the two employees' access to CCAs pending investigation as to whether these employees needed CCA access. The investigation determined that while these employees could appropriately have CCA access in their roles, it would be revoked because they were not actively utilizing their CCA access; and 2) the CCA list was reduced to a single access approval list which allows for automated comparisons to Active Directory content to avoid future discrepancies such as this instance.
2015-07-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012728 | CIP-004-3 | R2 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R2. Specifically, MRO_URE1 failed to maintain training documentation for a contractor's employee who had unescorted physical access to Critical Cyber Assets (CCA). A handwritten note indicated that the employee in question had completed training, but no records could corroborate that notation. The root cause of the issue was human error. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Ensuring that contractors and service vendors with unescorted CCA access rights have appropriate level of personnel risk assessment, training, and security awareness helps protect CCAs. In this case, this instant contractor employee was the only individual with unescorted access whose training documentation could not be located. A review of the specific individual's unescorted access during the instance of non-compliance was limited to a single 14 minute carpet inspection. No harm is known to have occurred This is MRO_URE1's first instance of noncompliance with CIP-004-3 R2. | To mitigate this issue, MRO_URE1: 1) Immediately revoked the contractor employee's unescorted access upon discovery of the issue and only restored it after training had been completed.
2015-07-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012729 | CIP-004-3a | R4 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. Specifically, MRO_URE1 failed to revoke unescorted physical access privileges to Critical Cyber Assets (CCA) within seven days for individuals who no longer required access. The issue covers two separate instances of non-compliance. In the first instance, a copier service provider failed to timely notify MRO_URE1 that an employee had retired. The individual retired and his access was not revokedseveral months later. In the second instance, the contractor emailed MRO_URE1 about an individual's retirement, but the MRO_URE1 employee who read the email failed to revoke the individual's access. The root cause of the first instance of noncompliance was a contractor's failure to follow MRO_URE1's established security policies. The root cause of the second instance of noncompliance was human error. | The issues posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The risk was reduced by MRO_URE1's strong secondary controls that detect instances of noncompliance. The risk was further reduced because the individuals in question retired, and were not terminated for cause and the individuals did not have electronic access to CCAs. Finally, MRO_URE1 conducted a review that confirmed that no actual unauthorized physical access occurred as a result of the delays in revocation. No harm is known to have occurred. MRO considered MRO_URE1's CIP-004-3a R4 compliance history in determining the disposition track. MRO_URE1's relevant prior noncompliance with CIP-004-3a R4 include NERC Violation ID MRO2012010574 (CIP-004-1 R4). MRO determined that MRO_URE1's compliance history should not serve as a basis for applying a penalty. The prior violation related to MRO_URE1's failure to revoke access of multiple contractor's employees after those employees were either terminated or resigned. As part of its mitigation plan for MRO2012010574 (CIP-004-1 R4), MRO_URE1 implemented detective controls. Those detective controls successfully resulted in the duration for the instant issues being so short. Additionally, the root cause of the first instance of noncompliance was the contractor's noncompliance with MRO_URE1's security policies. Finally, MRO considered MRO_URE1's prompt self-reporting and mitigation in determining the disposition of this instance of noncompliance. | To mitigate this issue, MRO_URE1: 1) Immediately revoked the access rights for the two individuals who retired; 2) For the first instance of noncompliance, Corporate Security Staff met with the contractor to communicate the security risks that can result from failing to adhere to MRO_URE1's requirements and validated the employment status of the contractor's employees with CCA access; and 3) For the second instance of noncompliance, Corporate Security made changes to the electronic inbox to provide additional levels of review to prevent a reoccurrence.
2015-07-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012730 | CIP-007-3a | R6 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R6. Specifically, MRO_URE1 deployed 6 Keyboard-Video-Mouse (KVM) devices on EMS servers without properly configuring the security status monitoring tool to process and alert the logs being transmitted by the KVM devices. This resulted in a Cyber Asset in the Electric Security Perimeter (ESP) not having the feasible automatized tools to monitor system events related to cyber security. The root cause of the instance of noncompliance is process weakness. The KVM device was a new technology to MRO_URE1 and it was unable to recognize that the device had not been properly configured and it did not conduct a peer review of the configuration. The product's instructions were also vague and this contributed to the instance of noncompliance. | The issues posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The risk was reduced by MRO_URE1's strong secondary controls that detect instances of noncompliance as evidenced by the short duration of the noncompliance in this matter. Further, during this period, the devices were located with an effective ESP and Physical Security Perimeter which limited access to the devices. No harm is known to have occurred. This is MRO_URE1's first issue of noncompliance with CIP-007-3a R6. | To mitigate this issue, MRO_URE1: 1) Reviewed and corrected the configurations on each of the KVMs to confirm that status monitoring was working properly; and 2) Updated the procedures and checklists to include additional testing of this type of device.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014907 | CIP-006-3c | R2; R2.1 | NPCC_URE1 had an issue of CIP-006-3c R2. NPCC_URE1's contractor that staffs the guard house at the NPCC_URE1 control center was granted unescorted physical access to the facility before his required CIP training and before a background check was received from the contracting company. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The guard house is stationed outside the physical security perimeter (PSP) that maintains access to the facility. It contains a cyber asset that provides door access control. The guard did not have electronic access to any critical cyber assets and the facility is manned 24/7. Once processed, the guard background check was clean and the CIP training was successfully completed for this guard. NPCC_URE1 did not activate the control center during the period in question. No harm is known to have occurred. | To mitigate this issue: 1) The application for physical access was submitted for the guard in question, and granted by delivering the required physical token for access before that guard was allowed to work on shift again. NPCC_URE1 contacted the vendor supplying the guard, informed them of the issue, and instructed them not to do this again. 2) A weekly report for the guard physical access will be obtained on a weekly basis by the Facilities & Security staff and reviewed to prevent similar missed approvals from happening in the future. NPCC has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014904 | CIP-007-3a | R6 | NPCC_URE1 had an issue of CIP-007-3a R6. During a quarterly review, NPCC_URE1 discovered physical security monitoring and control systems and workstations in a control center were left outside the normal procedures to collect and analyze system logs. Logs are locally stored on the cyber assets and sent to a central server for analysis and storage. Logs were not sent to the central sever for analysis and storage. The root cause of the issue is failure of NPCC_URE1's cyber security team to configure security monitoring systems appropriately and follow up with the network support team on access control list (ACL) modifications required for newly deployed systems at their facility. The oversight took place during a migration from their old control center site to the new site in 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There was the remote chance that systems could have been operated without logs being collected and analyzed as part of routine event and incident response. NPCC_URE1 did not activate the control center during the period in question. The ability to collect logs did not affect the reliable operation of the control center if the facility were called upon to activate. Logs were stored locally and can be analyzed in the event of an occurance. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Undertook network ACL changes and security monitoring system configuration changes to remediate the initial issues for all affected systems. 2) Developed a process to audit networks currently being tested for compliant systems that will include checking for consistent records with the Network Support team as well as the configurations of the network equipment supporting network segregation. This process provides a detailed list of networks and systems available for testing that will be used to check monitoring systems to ensure consistent and comprehensive test coverage. 3) Verified networks on a weekly basis using the output from the written procedure developed in the second mitigation activity. To mitigate this issue, NPCC_URE1 will complete the following mitigation activities, 1) Develop a procedure to ensure monitoring systems are configured correctly to include networks required for critical areas.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014905 | CIP-007-3a | R2 | NPCC_URE1 had an issue of CIP-007-3a R2. During a quarterly review, NPCC_URE1 discovered physical security monitoring and control systems and workstations in a control center were not included in determining port restrictions or services. The root cause of the issue is failure of NPCC_URE1's cyber security team to configure security monitoring systems appropriately and follow up with the network support team on access control list (ACL) modifications required for newly deployed systems at their facility. The oversight took place during a migration from their old control center site to the new site in 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 did not activate the control center during the period in question. The newly added assets were installed with the correct baseline configurations. However, NPCC_URE1 did not update their testing procedures to include these cyber assets for further maintenance. After the mitigation activity was performed, no changes to the ports and services were needed. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Undertook network ACL changes and security monitoring system configuration changes to remediate the initial issues for all affected systems. 2) Developed a process to audit networks currently being tested for compliant systems that will include checking for consistent records with the Network Support team as well as the configurations of the network equipment supporting network segregation. This process provides a detailed list of networks and systems available for testing that will be used to check monitoring systems to ensure consistent and comprehensive test coverage. 3) Verified networks on a weekly basis using the output from the written procedure developed in the second mitigation activity. To mitigate this issue, NPCC_URE1 will complete the following mitigation activities, 1) Develop a procedure to ensure monitoring systems are configured correctly to include networks required for critical areas.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014906 | CIP-007-3a | R1; R1.2 | NPCC_URE1 had an issue of CIP-007-3a R1. During a quarterly review, NPCC_URE1 discovered physical security monitoring and control systems and workstations in a control center were left outside the normal procedures to test. The root cause of the issue is failure of NPCC_URE1's cyber security team to configure security monitoring systems appropriately and follow up with the network support team on access control list (ACL) modifications required for newly deployed systems at their facility. The oversight took place during a migration from their old control center site to the new site in 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 did not activate the control center during the period in question. The newly added assets were installed with the correct baseline configurations. However, NPCC_URE1 did not update their testing procedures to include these cyber assets for further maintenance. After the mitigation activity was performed, no changes to the assets were found to be needed. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) Undertook network ACL changes and security monitoring system configuration changes to remediate the initial issues for all affected systems. 2) Developed a process to audit networks currently being tested for compliant systems that will include checking for consistent records with the Network Support team as well as the configurations of the network equipment supporting network segregation. This process provides a detailed list of networks and systems available for testing that will be used to check monitoring systems to ensure consistent and comprehensive test coverage. 3) Verified networks on a weekly basis using the output from the written procedure developed in the second mitigation activity. To mitigate this issue, NPCC_URE1 will complete the following mitigation activities, 1) Develop a procedure to ensure monitoring systems are configured correctly to include networks required for critical areas.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015014984 | CIP-003-3 | R6. | NPCC_URE2 had an issue of CIP-003-3 R6. NPCC_URE2 conducted a planned data move for a quarterly NPCC_URE2 Energy Management System (EMS) maintenance. During the maintenance, a database change requiring additonal CIP change controls was not performed. Specifically, a CIP change control ticket was not initiated, approved, or issued. The root cause was a miscommunication between NPCC_URE2's IT group and their EMS group during the planning phase of the maintenance. Additionally, the database resize test document procedure did not have additional steps to help control change. It lacked steps to ensure a CIP change ticket was approved prior to performing a diatabase resize on the production servers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The maintenance was a planned evolution (merge and resizing) that occurs on a routine basis. NPCC_URE2 Operators were using their procedure which provides guidelines for performing routine maintenance on equipment necessary for effective operation at the control center. The procedure also coordinates this maintenance with support technicians and the reliability coordinator. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) Created a CIP ticket 2) Updated the "Database Resize Test Document" procedure to add a verification step that an approved CIP ticket was created for the database resize task. 3) Lessons Learned Issued and reviewed by appropriate IT and EMS personnel. 4) Coaching and counseling of appropriate IT and EMS personnel. NPCC has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015014992 | CIP-007-3a | R6. | NPCC_URE3 had an issue of CIP-007-3a R6. During the daily morning operational health checks, the SCADA/EMS Systems support group noticed slightly higher than normal CPU usage on one specific server prompting an investigation. During the investigation, it was discovered that this single Critical Cyber Asset (CCA) server stopped logging activity logs locally. Consequently, from December through January, activity logs were not collected by the central logging server via syslog, and security monitoring was not done for this single CCA asset. The syslog service was restarted by the SCADA/EMS Systems support group and it was confirmed that the central logging server was receiving the logs. The SCADA/EMS Systems support group validatef that no other CCA servers had this issue. There were no indicators of any cyber security incidents occurring during the duration of the issue. The exact cause of the incident could not be determined by the investigation team. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). There was no actual impact to the BES during the period where the logging for the single asset did not occur. Security controls protect the NPCC_URE3 CCA including electronic access controls for authentication and encryption at the Electronic Security Perimeter (ESP) Network traffic monitoring is in place and sends alerts to energy management system/supervisory control and data acquisition (EMS/SCADA) personnel when unusual activity is detected. NPCC_URE3 has monitoring processes in place that provides protection to the ESP by detecting and alerting for unauthorized access. There were no security alerts or incidents that were directly related to the specific server at issue reported throughout the loss of logging and monitoring period. All assets run anti-malware software and all assets are monitored for security events, where technically feasible. None of these security controls triggered an alert or suggested any indicator of compromise during the period where the single asset was not logging. In addition, NPCC_URE3 has physical security controls in place at the Physical Security Perimeter (PSP) which includes key card readers, locked doors, and cameras. The server is located within a PSP and an ESP. No harm is known to have occurred. | To mitigate the issue, NPCC_URE3: 1) Created IT incident ticket to investigate the issue 2) Created new Loglogic Alert to send an alert to the Support Team if any CIP Systems cease to log for 24 hours. 3) Implemented alternate monitoring to detect syslog logging failure on a server which sends alerts to the SCADA/EMS support team if syslog is not logging for 24 hours. 4) Reviewed and verified all CIP servers to confirm that the issue was isolated to the one CCA. NPCC has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2015015023 | CIP-006-3c | R4 | NPCC_URE4 had an issue with CIP-006-3c R4. Substation employees with approved access were working at a substation. The substation employees needed to temporarily hold open the PSP door to bring in equipment. The security guard at the security operations center remotely unlocked the door to aid with the substation employees' work. The door remained unlocked after the employees had finished for the day. The unlocked door was discovered and relocked by another security guard the day after. During this timeframe, the substation PSP did not have active access control beyond the main substation fence and gate. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The control house is protected by a barbed fence that surrounds the perimeter of the facility and is monitored by video cameras. The PSP door alarm was enabled and the PSP is monitored by video cameras. Motion detectors were also in place within the PSP. There were no invalid attempts or motion alarms detected during the time the door was unlocked. No harm is known to have occurred. | To mitigate this issue, NPCC_URE4: 1) removed the ability for guards at the security operations center to remotely unlock CIP doors. NPCC has verified the completion of all mitigation activity.
2015-07-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014467 | CIP-006-3c | R1 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R1.1. SERC_URE1 failed to maintain a single Critical Cyber Asset (CCA) within an identified Physical Security Perimeter (PSP) as required. A SERC_URE1 intern who worked within the secured control center PSP left SERC_URE1 to return to school. Three days later, a SERC_URE1 technician removed a CCA workstation assigned to the former intern from within the established control center PSP. The purpose of the technician accessing the workstation was to back-up the data prior to reassignment, in order to ensure that a legal data hold associated with previously Self-Reported issues was fulfilled. The technician took the workstation at issue to the technician’s desk, which was outside of the PSP, to perform the data back-up. Approximately two weeks after the workstation was removed, while conducting normal work activities including the upcoming reassignment of the workstation, an energy management system (EMS) administrator discovered the CCA workstation was not within the PSP. SERC_URE1 staff contacted the technician assigned to the work and the technician immediately returned the workstation to inside the PSP and isolated it in a cabinet pending investigation. The root cause of this issue was the lack of proper training around the removal of Cyber Assets from within a secured PSP. Additionally, procedures lacked details on how to handle CCAs while executing the legal hold process of data and information that may be required to demonstrate compliance. This issue lasted from when the technician removed the CCA workstation from the PSP, through approximately two weeks later, when SERC_URE1 discovered the issue and returned the CCA workstation to the PSP for appropriate wiping and disposal pursuant to its CIP-007 R7 procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s removal of a CCA from within a secured PSP could have permitted the CCA to be accessed by unauthorized personnel, and permitted sensitive information, network identifiers, or critical network data to be obtained and used to impact EMS operations through other assets. However, SERC_URE1 removed the workstation, which was unidentifiable as a CCA, from the PSP by an approved and authorized individual. SERC_URE1 kept the workstation within a secured facility that had security staff 24 hours a day, 7 days a week, controlled access via corporate card readers, and cameras with recorded feeds from each access door. SERC_URE1 disabled all wireless capabilities on the workstation. The workstation was never connected to any network (enterprise or secured) once the technician removed it from within the PSP. SERC_URE1 never intended to reintroduce the workstation to the EMS network and instead planned to wipe and dispose of the workstation pursuant to its CIP-007 R7 procedures. No one logged onto the workstation’s operating system after the technician removed it from the PSP. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-006 R1 compliance history in determining the disposition track. The prior instances were violations of different sub-requirements and are unrelated to the removal of a CCA from a PSP. | To mitigate this issue, SERC_URE1: 1) returned the asset to the PSP to implement the appropriate physical security controls; 2) provided awareness to the teams supporting the primary and backup systems operations centers; 3) provided awareness to all teams regarding the proper handling of CCAs within the PSP; 4) created a procedure for executing enterprise processes on CCAs; and 5) trained the team on the new procedures.
2015-07-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014468 | CIP-004-3a | R4 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4.1. SERC_URE1 failed to update the list of personnel with authorized Cyber or authorized, unescorted physical access rights to Critical Cyber Assets (CCAs) within seven days of a change in access rights. SERC_URE1 had four instances where the physical access list under CIP-004-3a R4.1 was not updated within seven days as required. One issue involved a college intern, and a second issue involved three post-graduate college students, referred to as contractors, who were working for SERC_URE1 on their doctorate under a federally-funded university grant. In the first issue, SERC_URE1 granted an intern physical access to CCAs. Approximately two and half months later, the intern left SERC_URE1 to return to college, so access to CCAs was no longer required. The intern’s manager collected the access badge at that time and sent the required email to Human Resources (HR) the same day. HR staff misplaced the email it received from the intern’s manager and failed to update the access list until approximately three weeks after the intern left. Once discovered, HR disabled the access badge in the Physical Access Control System which triggered the automatic update to the list of individuals with authorized, unescorted access rights to CCAs. SERC_URE1 discovered this issue during an internal HR review of active interns with access to CCAs. The root cause is that HR staff misplaced the email indicating that the intern no longer required access and that HR should update the list. In the second issue, SERC_URE1 granted the three contactors physical access to CCAs . SERC_URE1 noted the official termination date for all three contractors as approximately a month and a half later, which was the date the federal money funding the university grant for the three positions ended. However, the contractors’ last days all occurred within the 30 days prior to the official termination date. SERC_URE1 collected the assigned access badge for each contractor on their last day. SERC_URE1 had assigned responsibility for all three contractors to a non-management consulting engineer. However, because the engineer was not in management and had not been trained in the access revocation process, the engineer failed to send the proper email follow-up to HR to terminate access and update the required lists of personnel with authorized, unescorted access SERC_URE1 discovered this issue, and all three associated instances, while conducting the third quarter 2014 review of physical access lists. This review concluded approximately two months after the first contractor left SERC_URE1, and SERC_URE1 updated the access lists on the same day. The root cause of this issue was the assignment of the three contractors to a non-management individual who was not trained in the SERC_URE1 off-boarding procedures and the access revocation process. SERC_URE1 performed an extent of condition investigation and determined that there were no additional instances of SERC_URE1 failing to update the access lists of individuals with access to CCAs within seven days of a change in the access rights of such individuals. This issue lasted from eight days after the first individual no longer needed physical access to CCAs, through approximately seven weeks later, when SERC_URE1 updated the CCA access list to remove physical access for the last of the involved individuals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to update the access lists within seven days of a change in access rights could have permitted personnel who no longer required authorized access the opportunity to re-obtain physical access to CCAs and potentially damage, degrade, or obtain data that could be detrimental to the BPS or SERC_URE1 operations. However, the four individuals noted were in good standing with SERC_URE1 prior to their voluntary departure and had valid Personnel Risk Assessments and cyber security training prior to gaining physical access to CCAs. The access permissions involved physical access to areas containing CCAs, and did not include remote electronic access. SERC_URE1 collected the access badges at the time individuals involved left their positions, and badge access reports showed no use of the badge past the date of departure. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-004 R4 compliance history in determining the disposition track. SERC_URE1 timely self-reported the issue after discovery and had internal controls in place that detected the issue. Each year, a SERC_URE1 HR representative uses a list of interns to ensure all steps have been completed to terminate the internship, including removing access and updating access lists. SERC_URE1 also reviews access lists quarterly to ensure that the access lists are updated. In addition, the most recent prior noncompliances ended almost two years before this issue occurred. The length of time between the prior noncompliances and the instant issue indicates that the instant issue was an isolated occurrence. | To mitigate the first issue, SERC_URE1: 1) removed the intern from the list of personnel with physical access to substation CCAs; 2) held three meetings where attendance at one of the sessions was mandatory and staff discussed current NERC regulations & HR’s role, an overview of recent incidents, an overview of past incidents, and terminations under new NERC CIP V5 Requirements; 3) updated the current process to address the internal communication breakdown within the HR team identified in the root cause for issue 1; and 4) trained and implemented new process to appropriate HR personnel on outcome from step 3. To mitigate the second issue, SERC_URE1: 1) removed the contractors from the list of personnel with physical access to substation CCAs; 2) sent an off-boarding expectations email to all individuals who have direct reports with access to CCAs and did not receive an executive communication describing the off-boarding process; 3) established access revocation training for new managers; and 4) established annual, recurring access revocation training for managers.
2015-07-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014562 | CIP-007-3a | R1 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-007-3a R1. SERC_URE2 failed to ensure that significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. There were energy management system (EMS) workstations, all Critical Cyber Assets (CCAs), which were loaded with an untested software client. SERC_URE2 opened a work order to install a software product on servers within the ESP. SERC_URE2 tested and approved this change, as required by CIP-007 R1, eight days later and started deployment on the day after testing and approval. This effort concluded a day after deployment. In order to implement the server software, SERC_URE2 also had to install an associated software client on the EMS workstations. During a post-installation meeting on the day following the deployment, SERC_URE2 discovered that, although it tested the server software for cyber security impacts as required, SERC_URE2 did not test the software client installed on the EMS workstations. SERC_URE2 had functionally tested the software client for the EMS workstations, but did not conduct cyber security controls testing. Upon discovery of this issue during a post-installation debrief meeting, SERC_URE2 halted any further installations beyond the EMS workstations on which SERC_URE2 had already installed the software client. SERC_URE2 completed testing the software client on the EMS workstations on the same day, showing no impacts to existing cyber security controls from this software client being installed. SERC_URE2 resumed deployment of the software client and completed installation of the software client on the remaining workstations five days after the issue was discovered. This issue affected less than half of the EMS workstations, all of which were CCAs. The root cause of this issue was a lack of training for the operations personnel, and a failure to understand that when performing a related change on different classes of Cyber Assets (in this case, the installation of server software on the servers and an associated software client on the EMS workstations), each class of Cyber Asset modified must undergo CIP-007 R1 security testing prior to implementation. This issue lasted from when SERC_URE2 deployed the untested software client on the EMS workstations, through the following day, when SERC_URE2 completed the testing of the software client showing no impact on existing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to properly test significant changes to Cyber Assets within the ESP could result in changes to existing cyber security controls that SERC_URE2 would not be aware of, potentially making specific vulnerabilities available for exploit. However, SERC_URE2 tested the server software on the servers prior to deployment with no cyber security impacts. The associated software client for the EMS workstations was functionally tested, but did not include a review for impacts to existing cyber security controls. Subsequent testing by SERC_URE2 found the software client had no impact on existing cyber security controls. The time between the untested deployment of the software client and the cyber security testing was one day. All Cyber Assets are protected within a secured ESP and Physical Security Perimeter. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-007 R1 compliance history in determining the disposition track. SERC determined that SERC_URE2's compliance history should not serve as a basis for applying a penalty. Although the issues involved the same Standard and Requirement, the underlying conduct of the two instances was different than the instant issue. When determining that compliance exception treatment was appropriate, SERC also considered the fact that SERC_URE2’s internal controls in the form of the post-installation debrief meeting led to a prompt identification and mitigation of the issue. | To mitigate this issue, SERC_URE2: 1) completed CIP-007 R1 testing on the client at issue; 2) completed installation of the client software on the remaining production workstations; 3) updated the work procedures used when completing an request for change (RFC) to require that configuration items be attached to the RFC; and 4) circulated an email to affected personnel describing the updated RFC work procedure document.
2015-07-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014456 | CIP-007-3a | R2; R2.1 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-007-3a R2 and R2.1. TRE_URE1 failed to implement its documented process to ensure that only those ports and services required for normal and emergency operations were enabled (R2). Specifically, TRE_URE1 enabled a port on multiple switches that reside within the Electronic Security Perimeter (ESP). However, the port was not listed in the baseline of enabled ports for the switches. Additionally, TRE_URE1 attested that the port was not required for normal and emergency operations. Therefore, TRE_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled. The root cause of the issue was that TRE_URE1 did not have adequate processes in place to ensure that only those ports and services required for normal and emergency operations were enabled. TRE_URE1 used switch commands to check for enabled ports, but the command only identified UDP ports. Texas RE determined the duration of the issue to be for over ten months, from the time when the CVA was performed and the open port was discovered until the port on the affected switches was determined to be disabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE1's failure to implement its documented process to ensure that only those ports and services required for normal and emergency operations are enabled could create an opportunity for unauthorized access through an open communication channel. The risk to the BPS was mitigated by the following factors. The devices are protected by TRE_URE1’s layered security approach. These Cyber Assets are kept within both physical and electronic security perimeters. In addition, TRE_URE1 deploys network-based intrusion prevention (IPS) and/or detection (IDS) devices. Furthermore, TRE_URE1’s security monitoring system would have received an alert if any unauthorized electronic access attempts were made. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) disabled the port at issue for the affected switches; and 2) revised the procedure to clarify how ports and services are identified for TCP and UDP ports. Texas RE has verified the completion of all mitigation activity.
2015-07-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015014550 | CIP-003-3 | R6 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-003-3 R6. TRE_URE1 failed to follow its change control and configuration management process for replacing Critical Cyber Asset (CCA) hardware components. Specifically, TRE_URE1 did not request, test, and approve an emergency change within three days of implementation. A loss of power to its Physical Security Perimeter (PSP) centralized monitoring system caused a CIP server component to fail, prompting a repair that was documented as an incident in its system. The repair was considered an emergency change and understood to be related to the incident, but a unique change request documenting the repair was not submitted. TRE_URE1 failed to document the emergency change within three days of implementation, which is required by its change management process. The root cause of the issue was a failure to document an emergency change request. Texas RE determined the duration of the issue to be for approximately seven months, from the day after the change and configuration management process was to be followed until the day after the change control and management process was implemented. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE1's failure to follow its change control process for 210 days could have resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets and an attendant remote possibility of loss of load. However, the risk to the reliability of the BPS was reduced by the following factors. First, TRE_URE1 employs a defense-in-depth approach for 24x7 cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, host intrusion prevention and antivirus was operational. Third, two-factor authentication to access network devices was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) performed a business impact analysis risk assessment in order to improve organization response; 2) installed a temporary generator which was also relocated, rewired, and made operational; and 3) issued business impact analysis final recommendations. TRE_URE1 will complete the following mitigation activities within six months: 1) complete switchgear breaker installations; 2) implement visual management techniques during team huddles to identify events requiring follow-up; and 3) install a 3MW Generator.
2015-07-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014551 | CIP-003-3 | R6 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-003-3 R6. TRE_URE2 failed to follow its change control and configuration management process for replacing Critical Cyber Asset (CCA) hardware components. Specifically, TRE_URE2 did not request, test, and approve an emergency change within three days of implementation. A loss of power to its Physical Security Perimeter (PSP) centralized monitoring system caused a CIP server component to fail, prompting a repair that was documented as an incident in its system. The repair was considered an emergency change and understood to be related to the incident, but a unique change request documenting the repair was not submitted. TRE_URE2 failed to document the emergency change within three days of implementation, which is required by its change management process. The root cause of the issue was a failure to document an emergency change request. Texas RE determined the duration of the issue to be for approximately seven months, from the day after the change and configuration management process was to be followed until the day after the change control and management process was implemented. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE2's failure to follow its change control process for 210 days could have resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets and an attendant remote possibility of loss of load. However, the risk to the reliability of the BPS was reduced by the following factors. First, TRE_URE2 employs a defense-in-depth approach for 24x7 cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, host intrusion prevention and antivirus was operational. Third, two-factor authentication to access network devices was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) performed a business impact analysis risk assessment in order to improve organization response; 2) installed a temporary generator which was also relocated, rewired, and made operational; and 3) issued business impact analysis final recommendations. TRE_URE2 will complete the following mitigation activities within six months: 1) complete switchgear breaker installations; 2) implement visual management techniques during team huddles to identify events requiring follow-up; and 3) install a 3MW Generator.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014545 | CIP-004-3a | R4.1 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4.1. A WECC_URE1 employee retired early. The employee’s official retirement date was recorded as such, WECC_URE1’s internal personnel system. The employee in scope had physical access to WECC_URE1’s substations all containing PSPs . The employee in scope also had physical, but not logical, access to ESPs. WECC_URE1’s Human Resources (“HR”) sent an early retirement notification to WECC_URE1’s Physical Access Security Team. However, HR did not include the internal “HR Training” email address in the notification. The HR Training email is monitored by WECC_URE1 employees responsible for revoking eligibility and sending notification to update the CCA access list. HR did collect the employee’s CIP key and badge and then deactivated the employee’s badge. The employee in scope no longer had physical access to WECC_URE1’s CCAs. The employee did not have cyber access permissions to any WECC_URE1 CCAs. HR sent the auto-generated notification regarding the employee’s change in status. A member of WECC_URE1’s team responded to the notification and discovered the employee’s early retirement notification had not trigger WECC_URE1’s normal CIP process. As a result, the employee’s access account in WECC_URE1’s system had not been updated and WECC_URE1’s CCA access list was not updated within seven calendar days of the employee’s change in access. Previously, a primary and secondary employee monitored WECC_URE1’s access revocations and ensured all CIP processes were timely completed. During the time of the employee’s early retirement, the primary employee was no longer working at WECC_URE1, and the secondary employee was not in the habit of monitoring for revocations. WECC_URE1 completed the retired employee’s account removal and updated the CCA access list. The compliance exception start date was eight calendar days after the WECC_URE1 employee in scope no longer required access. The compliance exception end date was when WECC_URE1 completed the revocation process by removing the account from WECC_URE1’s system and updating the Critical Cyber Asset access list. The root cause of this compliance exception was less than adequate communication between WECC_URE1's HR department and the employees responsible for revoking access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not update its Critical Cyber Asset access list within seven calendar days of one employee’s retirement. This failure could have potentially resulted in the retired employee gaining access to WECC_URE1’s CCAs. WECC_URE1’s controls did reduce the potential risks. Although WECC_URE1’s CCA access list was not updated within seven calendar days of the employee’s retirement, WECC_URE1 did collect the employee’s CIP key and badge on the employee’s last day. WECC_URE1 also deactivated the badge on the employee’s last day. Even if the employee was somehow able to temporarily access the substations in scope using a temporary badge or some other means, the employee would not have physical access to the ESPs because the employee’s CIP key was revoked. Any unauthorized access also likely would have been detected during WECC_URE1’s quarterly access control list review. | To mitigate this issue, WECC_URE1: 1) updated its Access Control Master List; and 2) hired an additional employee to assist with revocation process. WECC has verified completion of all mitigation activity.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014882 | CIP-006-3c | R2 | WECC_URE2 submitted a Self-Certification stating that it had an issue of CIP-006-3c R2. WECC_URE2 commissioned a new logging server. The old server was decommissioned, but 3 workstations and 8 servers, totaling 11 Physical Access Control System (“PACS”) devices continued to send logs to the old IP address. All other devices sent logs to the new server. WECC_URE2 discovered the issue and began manually collecting and reviewing logs, which it will continue doing until the 11 PACS devices are configured to forward logs to the central server. WECC_URE2's failure to provide PACS all the protective measures specified in the Standard is a compliance exception of CIP-006-3c R2.2. Specifically, WECC_URE2 failed to collect logs for account use and system events related to cyber security for at least 90 days and review logs for system events related to cyber security, as required by CIP-007 R5.1.2, CIP-007 R5.2.3, and CIP-007 R6, and as referenced in CIP-006-3c R2.2. The root cause of this issue was WECC_URE2's failure to identify the impact of a system change outside or the PACS secured network. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because WECC_URE2 implemented preventative and detective controls. As preventative controls, WECC_URE2 uses malware prevention on its devices, which look for known attack signatures and could have prevented a malware attack from being successful. WECC_URE2 has personnel in the control center 24x7, who would have prevented an unknown person from physically damaging CCAs. WECC_URE2 applied quarterly security patches, which could have closed security gaps in the PACS devices. As detective controls, WECC_URE2 performed security testing during quarterly patch updates. This testing compares a previous baseline of settings with the baseline after the patch. As such, any unapproved changes would have been discovered at that time. WECC_URE2 also performs quarterly reviews of its access list. | To mitigate this issue, WECC_URE2 is manually collecting, reviewing and retaining logs as required by the Standard.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014515 | CIP-004-3 | R3 | WECC_URE3 submitted a Self-Report stating that it had an issue with CIP-004-3 R3. WECC_URE3 failed to update its Personnel Risk Assessments (“PRA”) for employees with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (“CCAs”) every seven years. WECC_URE3's failure to update PRAs at least every seven years after the initial PRA for two employees is a compliance exception of CIP-004-3 R3.2. The compliance exception start date was when WECC_URE3 failed to renew or update the first PRA after seven years, and terminated when WECC_URE3 completed the PRA for the second employee in scope. The root cause of this issue was errors with the manual entry of dates into the system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to renew PRAs for two employees. The employees in scope had access to WECC_URE3's primary control center, which contains WECC_URE3 CCAs, including WECC_URE3's SCADA and EMS systems. Access to these systems could have allowed the employees to perform any SCADA function, including intentionally shedding load or affecting BES elements controlled by this system at the control center. However, WECC_URE3 implemented preventive, detective, and corrective controls. As preventive controls, WECC_URE3 trains employees to prevent tailgating and to report suspicious activities. Also, the control center is manned with system operators around the clock, and would have noticed malicious behavior being attempted on the CCAs. As an additional preventive control, WECC_URE3 restricts logical access to CCAs, and neither of the two employees had logical access. As detective and corrective controls, the control center is within the PSP, which is monitored around the clock via a live CCTV system and contact alarms. As a corrective control, WECC_URE3 hired an investigator after it first discovered the issue with the first employee to determine the full scope of the violation. Upon discovery of the incorrect dates, WECC_URE3 immediately disabled those employees’ access until after a new PRA had been completed. WECC determined that WECC_URE3's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, WECC_URE3: 1) revoked access of the two employees; and 2) completed PRAs for both employees.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014654 | CIP-006-3c | R1 | WECC_URE3 submitted a Self-Report stating that it had an issue with CIP-004-3a R2. WECC determined that the contractors in scope did not have authorized unescorted access to the Physical Security Perimeter (“PSP”), and as such the contractors should be considered as visitors to the PSP, and covered under CIP-006-3a R1.6. WECC issued a dismissal for CIP-004-3a R2. A new Self-Report was created under CIP-006-3c R1. WECC_URE3's failure to log the contractor’s entry and exit with date and time is a compliance exception of CIP-006-3c R1.6.1. WECC_URE3 failure to continuously escort the two contractors is a compliance exception of CIP-006-3c R1.6.2. The compliance exception began when the employees were given unescorted access to the PSP, and terminated when the employee’s unescorted access was revoked. The root cause was the ommission of a step due to the distraction of the outage and the need to have security personnel onsite. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to continuously escort two employees without unescorted physical access within a PSP and failed to log the employees’ entry and exit into the PSP. The PSP contained WECC_URE3 primary control center, which houses both Critical Cyber Assets (“CCAs”) and the Energy Management System (“EMS”). Had the contractors caused physical damage to these devices, it could have disrupted the SCADA environment. However, WECC_URE3 implemented both preventive and detective controls. The PSP was manned with system operators 24x7, which would have noticed and prevented malicious behavior toward the control center CCAs and EMS. WECC determined that WECC_URE3 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, WECC_URE3 revoked the unauthorized CIP access of the two contractors.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014512 | CIP-006-3c | R8 | WECC_URE3 submitted a Self-Report stating that it had an issue with CIP-006-3c R8. WECC_URE3 failed to conduct maintenance and testing of some security systems at least every three years. At certain facilities, WECC_URE3 missed the three year maintenance cycle for its security mechanisms. WECC_URE3's failure to test and maintain all physical security mechanisms on a cycle no longer than three years is a compliance exception of CIP-006-3c R8.1. The compliance exception began when WECC_URE3 should have tested and maintained security mechanisms at one of its facilities, and continued until WECC_URE3 completed maintenance and testing of security mechanisms at all seven facilities. The root cause was that WECC_URE3's testing schedules were on varying three year cycles, rather than on a uniform cycle. This varience caused confusion. The cycles are now uniform. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to perform testing and maintenance for its security systems in seven facilities. Failing to perform testing and maintenance could potentially cause its Physical Access Control (“PAC”) system to malfunction or could lead to an unknown hardware failure. This could create a physical denial of service to authorized WECC_URE3 operators with access to the facilities and prevent them from managing the Energy Management System and associated workstations. However, WECC_URE3 implemented detective and compensating controls. WECC_URE3's security system generates alarms, inclusive of failed hardware, at monitored locations and provides the ability to log and review alarm response messages. As compensating controls, WECC_URE3 deploys security personnel in response to failed hardware at PSP access points and implements 24x7 monitoring and alarm procedures including intrusion alarms, motion detectors and electronic logs for access control and/or monitoring. | To mitigate this issue, WECC_URE3 completed maintenance and testing of physical security mechanisms at the seven facilities.
2015-06-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2015014958 | CIP-005-3a | R2 | MRO-URE1 submitted a self-log stating that it had an issue of CIP-005-3a, R2. Specifically, MRO-URE1 failed to implement its internal policy when one of its control centers was only requiring single factor authentication (password) in violation of its internal policy that required two-factor authentication (password and RSA token). This occurred because an analyst assumed that the two-factor authentication policy was no longer in effect. The root cause of this instance of noncompliance is human error. The instance of noncompliance began on November 7, 2013, when the analyst first logged in using single factor authentication, and ended on April 25, 2014. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability to the bulk power system (BPS). MRO-URE1's single-factor authentication (password) was a strong technical control that reduced the risk posed by one analyst's failure to follow MRO-URE1's documented internal policy requiring two-factor authentication. The instance of noncompliance is based on MRO-URE1 not following its own internal policy of utilizing two factor authentication. MRO-URE1 submitted evidence that this instance of noncompliance was limited to a single control center. No harm is known to have occurred. This is MRO-URE1's first instant of noncompliance with CIP-005-3a R2. | To mitigate this issue, MRO-URE1: 1) Changed the firewall rules to require two-factor authorization to access the devices within NERC CIP Electric Security Perimeters (ESPs); and 2) Reviewed the interal procedure with the IT Security, Windows Server, and Data Networks teams to make sure they understand the internal two-factor authorization requirement.
2015-06-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014985 | CIP-004-3 | R4. | NPCC_URE1 had an issue of CIP-004-3 R4. NPCC_URE1 identified a compliance concern related to the quarterly review of the list of personnel who have unescorted physical access to Critical Cyber Assets (CCAs). NPCC_URE1 performed a reconciliation between the physical security system database and the access lists being produced. It was determined that the specific physical access rights for one employee was incomplete. The root cause of the error was the wrong access approver was entered into the physical security database when additional access was granted. The error caused the employee's additional physical access rights to not appear on the list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee that had specific physical access rights missing from the list had an up-to-date Personnel Risk Assessment, CIP Training, and a continued business need for authorized unescorted physical access to CCAs. | To mitigate this issue, NPCC_URE1: 1) Re-authorized specific physical access rights for the employee. The physical security database record for the employee was corrected. 2) Developed a reconciliation process that will compare the physical security system active access records to the physical security database to ensure the physical access lists that are created are complete.
2015-06-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015014988 | CIP-004-3 | R4. | NPCC_URE2 had an issue of CIP-004-3 R4. NPCC_URE2 identified a compliance concern related to the quarterly review of the list of personnel who have unescorted physical access to Critical Cyber Assets (CCAs). NPCC_URE2 performed a reconciliation between the physical security system database and the access lists being produced. An access list is generated for each approver for their quarterly review. It was determined that one employee was missing from the physical access list being produced for substation access. The root cause of the error was the wrong access approver was entered into the physical security database when access was granted. The error caused the employee to not appear on any list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee that was missing from the physical access list had an up-to-date Personnel Risk Assessment, CIP Training, and a continued business need for authorized unescorted physical access to CCAs. The issue was strictly a review of the documented access. | To mitigate this issue, NPCC_URE2: 1) Performed the Q1 2015 review of the list of personnel who have authorized unescorted physical assess to CCAs. The report included the employee that was previously missing from the list. The physical security database record for the employee was corrected. 2) Developed a reconciliation process that will compare the physical security system active access records to the physical security database to ensure the physical access lists that are created are complete.
2015-06-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015014987 | CIP-004-3a | R4. | NPCC_URE3 had an issue of CIP-004-3 R4. NPCC_URE3 identified a compliance concern related to the quarterly review of the list of personnel who have unescorted physical access to Critical Cyber Assets (CCAs). NPCC_URE3 performed a reconciliation between the physical security system database and the access lists being produced. An access list is generated for each approver for their quarterly review. It was determined that one employee was missing from the physical access list being produced for substation access. The root cause of the error was the wrong access approver was entered into the physical security database when access was granted. The error caused the employee to not appear on any list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee that was missing from the physical access list had an up-to-date Personnel Risk Assessment, CIP Training, and a continued business need for authorized unescorted physical access to CCAs. The issue was strictly a review of the documented access. | To mitigate this issue, NPCC_URE3: 1) Performed the Q1 2015 review of the list of personnel who have authorized unescorted physical assess to CCAs. The report included the employee that was previously missing from the list. The physical security database record for the employee was corrected. 2) Developed a reconciliation process that will compare the physical security system active access records to the physical security database to ensure the physical access lists that are created are complete.
2015-06-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015014986 | CIP-003-3 | R5. | NPCC_URE3 had an issue of CIP-003-1 R5. During an annual assessment of protected information controls, NPCC_URE3 identified a compliance concern involving the annual review of access privileges to protected information. An incident analysis was conducted and it was determined that two employees access privileges to the Physical Security Perimeter (PSP) diagrams for the primary, back-up, and regional control centers were not reviewed annually. The cause of the error was a lack of understanding that the two employees access privileges were not being reviewed annually as part of an overall access review for documents. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Only two long-term employees have access privileges (one with read/write and one with read only access) to control center PSP diagrams. The PSP diagrams depict locations of doors, card readers, and cameras, however, it does not provide access codes needed to gain access to the PSP or IP Addresses of the Physical Access System equipment installed. | To mitigate this issue, NPCC_URE3: 1) Completed and documented a review of the two employees access privileges to the protected information (control room PSP diagrams) and confirmed that the their access privileges are correct and that they correspond with needs and appropriate personnel roles and responsibilities. 2) Updated document regarding the custodian who is responsible for controlling access to the control center PSP diagrams.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014473 | CIP-006-3c | R5 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R5. While performing a complete upgrade to the Physical Access Control System (PACS) software, RFC_URE1 took the PACS system offline for a short period of time on two separate days, for a total of 76 minutes. During the time that the PACS system was offline, responsible personnel utilized closed circuit television (CCTV) cameras to monitor the Physical Security Perimeter (PSP) access points. However a RFC_URE1 security officer on patrol discovered that a large tool crib was positioned in such a way that it could have blocked the CCTV view of one of the two PSP access points during the time that the PACS system was offline. The security officer immediately relocated the tool crib. RFC_URE1 reviewed this incident and determined that that tool crib had, in fact, been blocking the CCTV view of the PSP access point during the two planned outages. The root cause of this noncompliance was human error. Specifically, the security guard who was responsible for monitoring the PSP access points through the CCTV cameras during the two planned outages failed to identify the fact that the tool crib was blocking the view of the PSP access point. The duration of this noncompliance is five days, from the date on which the PACS system was first taken offline to the date RFC_URE1 relocated the tool crib. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the PSP access point at issue had other access control devices in place during the period of noncompliance, including, but not limited to, the card key lock, which would have prevented an unauthorized person from gaining access to the PSP. Second, the PSP access points are inside the generating plant that is well patrolled by both security guards and plant employees. Accordingly, it was unlikely that an unauthorized person with malicious intentions could have gained unnoticed entry to this access point despite the lack of visibility caused by the tool crib. | To mitigate this issue, RFC_URE1: 1) relocated the tool crib so that the access point can be clearly seen through the CCTV camera; 2) updated the daily checklist for security guards to require them to review camera views each day at the beginning of their shift and report anything out of the ordinary; 3) installed at each access point an additional camera that is closer to the access point and relocate the existing camera so that each access point has two separate CCTV cameras monitoring it; 4) developed a checklist for each access point that will contain a picture of what the security guards should see when they are monitoring the access point. This checklist will be completed by anyone monitoring the cameras during an outage and will be incorporated into applicable procedures/job aids for monitoring; 5) replaced the existing 19-inch monitors at the monitoring station with two 42-inch LED monitors; and 6) reviewed all access points to ensure that a similar event could not occur and installed additional CCTV cameras as needed to mitigate any potential issues. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014538 | CIP-004-3a | R3 | RFC_URE3 and RFC_URE2 submitted Self-Reports to ReliabilityFirst stating that they were noncompliant with CIP-004-3a R3. RFC_URE3 and RFC_URE2 identified two Personnel Risk Assessment (PRA) date inconsistencies in the compliance management system. RFC_URE3 and RFC_URE2 discovered that a total of two employees, one from RFC_URE3 and one from RFC_URE2, with active NERC CIP access had incorrect PRA dates in the compliance management system. Based on these incorrect PRA dates, RFC_URE3 and RFC_URE2 did not renew the two employees’ PRAs on time. The root cause of these noncompliances was ineffective technical controls within the HR system during the posting and updating of PRA information. RFC_URE3 and RFC_URE2 had previously discovered (and reported to ReliabilityFirst) that the HR system contained incorrect PRA dates for a number of employees and contractors. In the context of resolving these prior violations, it was learned that the administrators entering the data into the HR system had transposed PRA completion dates with the PRA data entry dates. The mitigation for the prior violations addressed all individuals with current NERC CIP Access and was completed prior to the discovery of the instant noncompliances. The individuals that are the subject of the instant noncompliances did not have NERC CIP Access at the time the prior issues were being mitigated. RFC_URE3 and RFC_URE2 actually discovered the instant issues as a result of the effective controls implemented, combined with the decision to conduct additional checks beyond the scope of the prior mitigation. The duration of these noncompliances is approximately six months, from the date the employees’ PRAs were not timely renewed as required by CIP-004-3a R3 to the date the employees’ access was removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The two individuals that are the subject of these noncompliances had prior PRAs, current training, justified business needs for access, and were trusted employees that had been with the company for at least 7 years. Once identified, RFC_URE3 and RFC_URE2 immediately removed the access for the two employees, requested new PRAs, and completed the PRAs with no adverse findings. RFC_URE3 and RFC_URE2 also maintain a robust network of monitoring and detective controls which monitors for any changes to the baselines for ports and services on a large number of assets, and a system which immediately detect suspicious network activity based on defined signatures. Tools such as these would allow RFC_URE3 and RFC_URE2 to timely detect any malicious conduct by the two individuals with expired PRAs while they had access. RFC_URE3 and RFC_URE2 did not identify any inappropriate activity for the duration of this noncompliance. | To mitigate this issue, RFC_URE3 and RFC_URE2: 1) removed access for the two employees and completed new PRAs for both employees; 2) established and implemented a manual PRA validation process prior to an individual being granted CIP access. This ensures that when requests for new access to NERC Assets are made for individuals who do not have current access, an additional check is now performed to validate the correct PRA date; and 3) modified the method for tracking and updating CIP PRA dates within the HR system and trained relevant employees on the new method. The HR system now includes a new field for the posting of CIP PRA dates only and employees in the services group will have the exclusive ability to update this field.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014014539 | CIP-004-3a | R3 | RFC_URE3 and RFC_URE2 submitted Self-Reports to ReliabilityFirst stating that they were noncompliant with CIP-004-3a R3. RFC_URE3 and RFC_URE2 identified two Personnel Risk Assessment (PRA) date inconsistencies in the compliance management system. RFC_URE3 and RFC_URE2 discovered that a total of two employees, one from RFC_URE3 and one from RFC_URE2, with active NERC CIP access had incorrect PRA dates in the compliance management system. Based on these incorrect PRA dates, RFC_URE3 and RFC_URE2 did not renew the two employees’ PRAs on time. The root cause of these noncompliances was ineffective technical controls within the HR system during the posting and updating of PRA information. RFC_URE3 and RFC_URE2 had previously discovered (and reported to ReliabilityFirst) that the HR system contained incorrect PRA dates for a number of employees and contractors. In the context of resolving these prior violations, it was learned that the administrators entering the data into the HR system had transposed PRA completion dates with the PRA data entry dates. The mitigation for the prior violations addressed all individuals with current NERC CIP Access and was completed prior to the discovery of the instant noncompliances. The individuals that are the subject of the instant noncompliances did not have NERC CIP Access at the time the prior issues were being mitigated. RFC_URE3 and RFC_URE2 actually discovered the instant issues as a result of the effective controls implemented, combined with the decision to conduct additional checks beyond the scope of the prior mitigation. The duration of these noncompliances is approximately six months, from the date the employees’ PRAs were not timely renewed as required by CIP-004-3a R3 to the date the employees’ access was removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The two individuals that are the subject of these noncompliances had prior PRAs, current training, justified business needs for access, and were trusted employees that had been with the company for at least 7 years. Once identified, RFC_URE3 and RFC_URE2 immediately removed the access for the two employees, requested new PRAs, and completed the PRAs with no adverse findings. RFC_URE3 and RFC_URE2 also maintain a robust network of monitoring and detective controls which monitors for any changes to the baselines for ports and services on a large number of assets, and a system which immediately detect suspicious network activity based on defined signatures. Tools such as these would allow RFC_URE3 and RFC_URE2 to timely detect any malicious conduct by the two individuals with expired PRAs while they had access. RFC_URE3 and RFC_URE2 did not identify any inappropriate activity for the duration of this noncompliance. | To mitigate this issue, RFC_URE3 and RFC_URE2: 1) removed access for the two employees and completed new PRAs for both employees; 2) established and implemented a manual PRA validation process prior to an individual being granted CIP access. This ensures that when requests for new access to NERC Assets are made for individuals who do not have current access, an additional check is now performed to validate the correct PRA date; and 3) modified the method for tracking and updating CIP PRA dates within the HR system and trained relevant employees on the new method. The HR system now includes a new field for the posting of CIP PRA dates only and employees in the services group will have the exclusive ability to update this field.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014014543 | CIP-004-3a | R3.2 | RFC_URE4 submitted a Self-Report stating that it was noncompliant with CIP-004-3a R3. RFC_URE4 determined that a contractor’s personnel risk assessment (PRA) had expired while the contractor was still included on an access list for a Critical Cyber Asset. Specifically, while completing a quarterly review of its access list, RFC_URE4 identified that a relay testing contractor’s PRA had expired during the previous quarter but the contractor was still included on the access list. The contractor’s access, without subsequent demonstration of an updated PRA, should have been revoked prior to the quarterly review. The contractor used an identification card to comply with the PRA requirement, which RFC_URE4 permitted as proof of a background check. When RFC_URE4 initially identified this issue, RFC_URE4 incorrectly believed that identification cards are valid for seven years, which would have meant that it should have requested an updated identification card or conducted a new PRA for the contractor to retain his access. RFC_URE4 subsequently discovered that identification cards are only valid for five years. However, upon further investigating this noncompliance, RFC_URE4 also discovered that the contractor’s identification card was actually issued two years later. A typographical error had incorrectly listed the identification card issue date in the system RFC_URE4 uses to track PRA information. Therefore, the contractor’s access should have been revoked when the contractor’s identification card truly expired in the absence of a new PRA or an updated indentification card. The root cause of this violation was ineffective training and lack of oversight. RFC_URE4 employees were not aware that identification cards are valid for only five years, not seven years as they incorrectly believed, and no one discovered that the contractor’s identification card issued date in RFC_URE4's list was incorrect, and off by two years, until after the contractor’s identification card expired. The duration of this noncompliance is approximately three months, from the date the contractor’s identification card expired, to the date RFC_URE4 removed the contractor’s access. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliablity of the bulk power system based on the following factors. At the time of the violation, the contractor was a service provider and all service providers are required to coordinate and receive approval for onsite presence prior to appearing onsite and do not receive any access privileges until onsite. This is an additional check that ensures access privileges are given only to appropriate contractors and employees. The contractor with the expired identification card never applied for or received approval for onsite presence, was never onsite, and did not actually enter any Physical Security Perimeters during the three month time frame after his identification card was expired and before RFC_URE4 discovered the issue. | To mitigate this issue, RFC_URE4 will complete the following mitigation activities by June 30 2015. 1) update RFC_URE4’ access list by removing the contractor’s access. The contractor’s access will be restored once he can document that his identification card has been renewed or a new PRA is provided to RFC_URE4; 2) add a formula to its access list spreadsheets that flags and informs the owner of the list when an employee or contractor’s PRA is set to expire during the upcoming quarterly cycle; 3) will update its procedure document to reflect that identification cards expire after five years and that a new identification card or other PRA is required in order to maintain access privileges. RFC_URE4 will also update its compliance procedures to address expectations and the process for revoking access privileges for an out of date PRA. This update will also inform employees and contractors that it is required for employees and vendors to notify RFC_URE4 when an event occurs that would be considered a PRA revocable issue per its procedure document; 4) amend its existing workflow for CIP-004 R3 to include a step for RFC_URE4's Human Resources to update PRAs for all those with access privileges set to expire in the upcoming year; and 5) will perform training to ensure that all personnel involved in the review process are aware of the CIP access requirements in CIP-004, especially pertaining to identification cards. RFC_URE4 needs until June 30, 2015 to complete this final milestone because the training must be given to all personnel involved in the review process.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013926 | CIP-002-1 | R1; R1.1 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-002-1 R1, R1.1. SPPRE_URE1 had identified and documented a risk-based assessment methodology (RBAM) used to identify Critical Assets; however SPPRE_URE1 did not describe its RBAM procedures. Specifically, although SPPRE_URE1 included evaluation criteria in a flow chart, within its RBAM, to identify whether it owned any critical assets or critical cyber assets, SPPRE_URE1 did not include procedural steps to apply the evaluation criteria. The root cause of this issue was SPPRE_URE1’s lack of internal controls to ensure that: its RBAM would sufficiently identify Critical Assets, if applicable; its subsequent documentation would accurately reflect its CIP-002 evaluation; and its senior manager would review such procedures to ensure any and all necessary changes to its RBAM and/or asset lists would be updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to fully document an RBAM and asset lists, and annually review such documents could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. Although SPPRE_URE1 did not include procedural steps within its RBAM, it did have an identified and documented RBAM, and the lack of such steps did not change SPPRE_URE1’s determination that it does not own any Critical Assets. Further, because SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets, this is a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No prior violation history. | To mitigate this issue, SPPRE_URE1 will adopt the CIP-002-5 bright-line criteria and will rely on this criteria to determine whether or not it owns assets that require CIP protections. SPPRE_URE1's procedure will be revised to include the bright-line criteria of CIP-002-5.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013927 | CIP-002-1 | R2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-002-1 R2. SPPRE_URE1 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE1 does not own any Critical Assets. The root cause of this issue was SPPRE_URE1’s lack of internal controls to ensure that: its RBAM would sufficiently identify Critical Assets, if applicable; its subsequent documentation would accurately reflect its CIP-002 evaluation; and its senior manager would review such procedures to ensure any and all necessary changes to its RBAM and/or asset lists would be updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to fully document an RBAM and asset lists, and annually review such documents could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. Although SPPRE_URE1 did not include procedural steps within its RBAM, it did have an identified and documented RBAM, and the lack of such steps did not change SPPRE_URE1’s determination that it does not own any Critical Assets. Further, because SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets, this is a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No prior violation history. | To mitigate this issue, SPPRE_URE1 will adopt the CIP-002-5 bright-line criteria and will rely on this criteria to determine whether or not it owns assets that require CIP protections. As required a list of critical assets will be generated, if no critical assets are identified a null list will be generated.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013928 | CIP-002-1 | R3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-002-1 R3. SPPRE_URE1 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE1 does not own any Critical Cyber Assets. The root cause of this issue was SPPRE_URE1’s lack of internal controls to ensure that: its RBAM would sufficiently identify Critical Assets, if applicable; its subsequent documentation would accurately reflect its CIP-002 evaluation; and its senior manager would review such procedures to ensure any and all necessary changes to its RBAM and/or asset lists would be updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to fully document an RBAM and asset lists, and annually review such documents could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. Although SPPRE_URE1 did not include procedural steps within its RBAM, it did have an identified and documented RBAM, and the lack of such steps did not change SPPRE_URE1’s determination that it does not own any Critical Assets. Further, because SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets, this is a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No prior violation history. | To mitigate this issue, SPPRE_URE1 will adopt the CIP-002-5 bright-line criteria and will rely on this criteria to determine whether or not it owns assets that require CIP protections. As required a list of critical assets will be generated, if no critical assets are identified a null list will be generated.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013929 | CIP-002-1 | R4 | During a Compliance Audit conducted on June 5, 2014, SPP RE determined that SPPRE_URE1, as a Generator Owner and Generator Operator, had an issue of noncompliance with CIP-002-1 R4. SPPRE_URE1’s senior manager did not annually approve SPPRE_URE1’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. This instance of non-compliance began on January 1, 2010, the first day Standard CIP-002-1 became enforceable for Generation Owners and Generation Operators, and will end once SPPRE_URE1 successfully completes the mitigating activities. The root cause of this issue was SPPRE_URE1’s lack of internal controls to ensure that: its RBAM would sufficiently identify Critical Assets, if applicable; its subsequent documentation would accurately reflect its CIP-002 evaluation; and its senior manager would review such procedures to ensure any and all necessary changes to its RBAM and/or asset lists would be updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to fully document an RBAM and asset lists, and annually review such documents could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. Although SPPRE_URE1 did not include procedural steps within its RBAM, it did have an identified and documented RBAM, and the lack of such steps did not change SPPRE_URE1’s determination that it does not own any Critical Assets. Further, because SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets, this is a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No prior violation history. | To mitigate this issue, SPPRE_URE1 will adopt the CIP-002-5 bright-line criteria and will rely on this criteria to determine whether or not it owns assets that require CIP protections. As required, a Senior Manager or delegate will approve the identifications required by requirement R1 at least once every fifteen months, even if no items are identified in Requirement R1.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014088 | CIP-003-1 | R2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-003-1 R2. Specifically, SPPRE_URE1 did not properly assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. SPPRE_URE1 did assign certain roles to its Vice President, such as signing certifications, applications, and/or reports regarding environmental and health and safety matters for any and all federal, state, or local governmental agencies; however, this assignment was not specific to addressing NERC CIP Standards. Furthermore, the document that described SPPRE_URE1’s Vice President’s authorizing privileges did not name the Vice President by title; instead it designated him by name only. The root cause of this issue was SPPRE_URE1’s lack of internal controls to ensure that its documents fully adhered to the Standard and Requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failure to assign a senior manager for leading and managing SPPRE_URE1’s implementation of CIP Standards increases the risk that the protective measures required by CIP standards may not be adequately implemented for the Critical Assets and Critical Cyber Assets essential to the operation of the BPS, which could negatively impact the reliability of the BPS. Notwithstanding, SPPRE_URE1 does not have any Critical Assets or Critical Cyber Assets. Moreover, although SPPRE_URE1 did not assign a senior manager in accordance with the NERC CIP Standards, SPPRE_URE1 did assign its Vice President to authorize, lead, and manage all other aspects of SPPRE_URE1’s operations, and the Vice President did have the same authority to lead and manage the implementation of SPPRE_URE1’s CIP program. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No prior violation history. | To mitigate this issue, SPPRE_URE1 will revise its assignment documentation to assign the Senior Manager overall responsibility and authority of the NERC CIP Standards.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014310 | CIP-007-3a | R5; R5.1 | TRE_URE1 submitted a Self-Report after receiving notice of an upcoming Compliance Audit, stating that it had an issue with CIP-007-3a R5.1. TRE_URE1 failed to ensure that an individual had access permission on a shared account consistent with the concept of "need to know" with respect to work functions performed. Specifically, access to a restricted password list was granted by a provisioner to the wrong user for approximately 15 hours. After discovering the issue the next morning via an automated process, access was promptly revoked. The password list was for all TRE_URE1 substation Critical Cyber Assets (CCAs) that have passwords. The root cause of the issue was human error. Texas RE determined the duration of the issue to be for one day, from the time access permission was granted to the wrong user until access permission was revoked from the wrong user. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). The issue was discovered promptly via an automated process and remedied quickly. Although the likelihood is remote, TRE_URE1 's granting access to the password list for all CCAs inside the ESPs to the wrong user could possibly have resulted in a user gaining access to Critical Cyber Assets utilized for substation relay control. The risk to the reliability of the BPS was reduced by the following factors. First, the issue duration was brief, approximately 15 hours. Second, the wrong user was unaware that access had been granted to the password list. Third, the wrong user did not have physical or electronic access to Critical Cyber Assets. Fourth, TRE_URE1 has an automated process in place to catch such errors quickly. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) revoked access permission from the wrong user; and 2) developed a list of NERC CIP Access Provisioners' FAQ's and Answers and delivered this list as training to Provisioners in IT. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014327 | CIP-007-3a | R5; R5.1 | TRE_URE2 submitted a Self-Report after receiving notice of an upcoming Compliance Audit, stating that it had an issue with CIP-007-3a R5.1. TRE_URE2 failed to ensure that an individual had access permission on a shared account consistent with the concept of "need to know" with respect to work functions performed. Specifically, access to a restricted password list was granted by a provisioner to the wrong user for approximately 15 hours. After discovering the issue the next morning via an automated process, access was promptly revoked. The password list was for all TRE_URE2 substation Critical Cyber Assets (CCAs) that have passwords. The root cause of the issue was human error. Texas RE determined the duration of the issue to be for one day, from the time access permission was granted to the wrong user until access permission was revoked from the wrong user. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). The issue was discovered promptly via an automated process and remedied quickly. Although the likelihood is remote, TRE_URE2's granting access to the password list for all CCAs inside the ESPs to the wrong user could possibly have resulted in a user gaining access to Critical Cyber Assets utilized for substation relay control. The risk to the reliability of the BPS was reduced by the following factors. First, the issue duration was brief, approximately 15 hours. Second, the wrong user was unaware that access had been granted to the password list. Third, the wrong user did not have physical or electronic access to Critical Cyber Assets. Fourth, TRE_URE2 has an automated process in place to catch such errors quickly. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) revoked access permission from the wrong user; and 2) developed a list of NERC CIP Access Provisioners' FAQ's and Answers and delivered this list as training to Provisioners in IT. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014013892 | CIP-007-3a | R3; R3.1 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-007-3a R3.1. Specifically, TRE_URE2 failed to document the assessment of a security patch that addressed a vendor software DHCP server vulnerability until 131 days after its availability. Although TRE_URE2 had a security patch management document that explained the process for assessing patches and security updates, TRE_URE2 did not have a process that explained how to check for new releases pertaining to security patches and upgrades. According to TRE_URE2, an assigned group typically reviewed security patch management evidence during planned events such as self-certifications or unplanned events such as ad hoc requests. Texas RE determined the root cause of this issue to be a lack of procedures and management controls to ensure that new security patches and upgrades were identified and assessed timely. Texas RE determined the duration of the issue to be over four months, from the thirty-first day after the patch became available until the vendor patch was documented and assessed. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). Although the failure to document assessment of security patches for applicability could potentially allow a vulnerability to be exploited, creating access to any part of the system and compromising the reliability of the BPS. The risk to the BPS was reduced due to the following factors. After TRE_URE2 assessed the vendor patch, TRE_URE2 found it was not applicable to the router. Specifically, the security patch would fix a vulnerability in a feature set (DHCP Server) which is not used by the router supporting TRE_URE2. Additionally, TRE_URE2 uses a intrusion protection system that protects all critical environments. At the external perimeter (Internet), TRE_URE2 uses multiple Advanced Threat tools, in addition to its IPS and Firewalls. Furthermore, devices are monitored 24x7 with an TRE_URE2 staffed operations center. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2 completed the missed security patch assessment. Additionally, TRE_URE2 will complete the following mitigation activities within seven months: 1) assign an IT Manager to ensure that all future security patch assessments are conducted and the results are documented; 2) develop a project plan to identify resources and tasks needed to implement process improvements, including increased automation through the use of an electronic tool, and all following milestones; 3) review all of the IT security patch management processes and controls to determine the current state of the processes, including compliance gaps. This is an “extent of condition” review that will ensure this mitigation plan is addressing all shortcomings in the IT process; 4) implement a new electronic tool to monitor security patch assessments, which includes: a. automated notification processes, new dashboards, and reports, b. tracking of assessments within this tool, c. evaluating installed software/firmware detection methods and processes, and d. address any inconsistencies found by enforcing a consistent approach for all methods and processes; and 5) include a process for creating and revising mitigation plans when applicable patches are unable to be applied within 35 days of evaluation completion.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014298 | CIP-005-3a | R3 | TRE_URE2 submitted a Self-Report after receiving notice of an upcoming Compliance Audit, stating that it had an issue with CIP-005-3a R3. After a loss of power to its security monitoring system, TRE_URE2 failed to implement and document an electronic or manual process for monitoring and logging access at access points to the Electronic Security Perimeter(s) for approximately 15 hours. The root cause of the issue was the loss of power to the data center. The age and insulation type of the underground secondary cables were contributing factors to the loss of power. Additionally, long term heating from high loading accelerated aging of cable insulation, caused embrittlement, shrinking, cracking, and exposed conductors. Texas RE determined the duration of the issue to be for 15 hours, from the time the ESP access point monitoring system lost power and stopped working until access point monitoring was fully functional. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE2's failure to monitor and log access at ESP access points for 15 hours could have possibly resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets and compromise the BES. However, the risk to the reliability of the BPS was reduced by the following factors. First, TRE_URE2 employs a defense-in-depth approach for 24x7 cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, host intrusion prevention and antivirus was operational. Third, two-factor authentication to access network devices was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) performed a business impact analysis risk assessment in order to improve organization response; 2) installed a temporary generator which was also relocated, rewired, and made operational; and 3) issued business impact analysis final recommendations. Additionally, TRE_URE2 will complete the following mitigation activities within seven months: 1) complete switchgear breaker installations; and 2) install a new generator.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014299 | CIP-007-3a | R6; R6.3; R6.4; R6.5 | TRE_URE2 submitted a Self-Report after receiving notice of an upcoming Compliance Audit, stating that it had an issue with CIP-007-3a R6. After a loss of power to its Security Monitoring system, TRE_URE2 implemented its automated process controls to monitor system events; however, TRE_URE2 failed to maintain (R6.3), retain (R6.4), and review (R6.5) all logs of system events that are related to cyber security. All TRE_URE2 Electronic Security Perimeters (ESPs) were affected. The root cause of the issue was the loss of power to the data center. The age and insulation type of the underground secondary cables were contributing factors to the loss of power. Additionally, long term heating from high loading accelerated aging of cable insulation, caused embrittlement, shrinking, cracking, and exposed conductors. Texas RE determined the duration of the issue to be for 15 hours, from the time the ESP security status monitoring system lost power and stopped working until the security status monitoring was fully functional again. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE2’s failure to monitor security status at multiple ESPs for 15 hours could have resulted in a failure to detect an intruder gaining access to Critical Cyber Assets and Critical Assets and an attendant remote possibility of loss of load. However, the risk to the reliability of the BPS was reduced by the following factors. First, TRE_URE2 employs a defense-in-depth approach for 24x7 cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Second, host intrusion prevention and antivirus was operational. Third, two-factor authentication to access network devices was functioning. Fourth, firewall and other malicious software prevention tools were operational. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) performed a business impact analysis risk assessment in order to improve organization response; 2) installed a temporary generator which was also relocated, rewired, and made operational; and 3) issued business impact analysis final recommendations. Additionally, TRE_URE2 will complete the following mitigation activities within seven months: 1) complete switchgear breaker installations; and 2) install a new generator.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014300 | CIP-006-3c | R5 | TRE_URE2 submitted a Self-Report after receiving notice of an upcoming Compliance Audit, stating that it had an issue with CIP-006-3c R5. After a loss of power to its Physical Security Perimeter (PSP) centralized monitoring system, TRE_URE2 failed to implement the technical and procedural controls for monitoring physical access at all access points to the PSP(s) for approximately four and a half hours. All TRE_URE2 PSP access points were affected. The root cause of the issue was the loss of power to the data center during a weather event. The age and insulation type of the underground secondary cables were contributing factors to the loss of power. Additionally, long term heating from high loading accelerated aging of cable insulation, caused embrittlement, shrinking, cracking, and exposed conductors. The issue duration was for approximately four and a half hours, from the time when monitoring was lost and staff evacuated the monitoring premises until TRE_URE2 recovered the ability to monitor sites in real time through contingency monitoring. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE2's failure to monitor and log access at ESP access points for four and a half hours could have possibly resulted in an intruder gaining access to Critical Cyber Assets and Critical Assets and compromise the BES. However, the risk to the reliability of the BPS was reduced by the following factors. Local alarms and strobe lights remained functional during the outage. Additionally, TRE_URE2 dispatched security personnel to all TRE_URE2 PSPs and found no signs of forced entry. After the incident, TRE_URE2 reviewed local cellemetry logs and found no alarms. Furthermore, TRE_URE2 employs a defense-in-depth approach for 24x7 cyber monitoring, including a backup distributed intrusion detection system to monitor access points for security events. Lastly, two-factor authentication to access network devices was functioning. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) performed a business impact analysis risk assessment in order to improve organization response; 2) installed a temporary generator which was also relocated, rewired, and made operational; and 3) issued business impact analysis final recommendations. Additionally, TRE_URE2 will complete the following mitigation activities within seven months: 1) complete switchgear breaker installations; and 2) install a new generator.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2015014770 | CIP-006-3c | R1; R1.6.2 | TRE_URE3 submitted a Self-Log stating that it had an issue with CIP-006-3c R1.6.2. Specifically, TRE_URE3 failed to continuously escort a visitor who had not been granted authorized unescorted access privileges to a Physical Security Perimeter (PSP). A contractor without unescorted PSP access privileges accessed a PSP unaccompanied for ten minutes. The security officer assigned to control and monitor the PSP for the TRE_URE3 PSP security post issued a visitor badge and logged the entry in the visitor log, as required by CIP-006-3c, R1.6.1. However, the security officer allowed the contractor to enter the PSP without an escort. At 14:33 hours, the security officer notified the supervisor by phone that access to the PSP was given to an unauthorized contractor with Personal Risk Assessment (PRA) clearance. The supervisor instructed the officer to pursue and remove the contractor from the floor. At 14:35 hours, the second security officer returned to the security post and was advised of the situation. At 14:36 hours, the second security officer entered the PSP in pursuit of the contractor. The contractor was located and escorted out of the PSP at 14:36 hours and logged out in the visitor’s log. The contractor remained unescorted in the PSP for ten minutes. When examining the root cause of the reported issue, TRE_URE3 identified that the security officer who granted physical access to the PSP did not follow the TRE_URE3 PSP manual, which instructs security personnel how to process visitor access to the PSP. However, the security officer had received training on the visitor access requirements seven weeks prior to the incident. TRE_URE3’s investigation into the incident also revealed that the security officer, who was the only officer on duty at the time, was confused on how to handle the visitor. The officer did not want to leave the desk unmanned and made the incorrect decision to allow the visitor to enter unescorted. The officer did call the supervisor to discuss the decision, thereby mitigating the duration of the incident. TRE_URE3 had an issue with CIP-006-3c R1.6.2 for ten minutes, from when the visitor was unescorted in the PSP until the unescorted visitor left the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to continuously escort a visitor without authorized unescorted access in a PSP could have resulted in the detrimental tampering of Cyber Assets, access to confidential and proprietary operational information, and access to the organization’s computer network and Cyber Assets, collectively compromising the security of important systems. The risk to the BPS was reduced due to the following factors. First, the unescorted visitor having successfully completed a PRA and been approved for physical access to the building. Second, TRE_URE3 had an established and implemented protocol in place addressing the subject issue. Third, the issue was mitigated within ten minutes. Fourth, the in-scope Critical Cyber Assets within this PSP used for operation are located in an area that was continuously occupied by authorized support staff at the time the contractor was inside the PSP. Furthermore, the Critical Cyber Assets in the control center are in an open office environment and an attempt by an unknown individual to access any of those assets during normal business hours would quickly be noted, challenged and curtailed. Lastly, in the unlikely event such activity was not noted or such activity occurred outside normal business hours, the electronic defense-in-depth deployed to protect CCAs has multiple mechanisms by which inappropriate activity would be detected and notifications would be automatically sent to the support team. No harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue: 1) TRE_URE3 immediately removed the security officer from the TRE_URE3 contract; 2) the security vendor modified post orders so that visitor badges will be handed directly to the authorized escort and not to the visitor. The escort will be responsible for the handoff of the badge to the visitor. Security vendor management counseled and obtained signatures from every security officer assigned to the TRE_URE3 PSPs that they understood this change in the post orders; 3) the security vendor implemented required quarterly training program for security officers. Security officers that do not complete the required training will not be assigned to duty; 4) TRE_URE3 cross-trained the night and weekend security officers on the post with the day shift officers. This training will continue with any future personnel changes and will be conducted with existing staff periodically. The purpose of the training is to expose the security officers to both day and night shift post activities; and 5) the contractor was relieved of all duties related to the PSP area. The applicable department manager department will follow protocol for requesting access to TRE_URE3 PSP areas and demonstrate the proper procedure was followed by completing a checklist and placing it in the personnel record of the employee/contractors that request access to PSP areas. One-on-one training for all staff needing to access PSP areas will be conducted by management in addition to the cyber security training completed by all contractors and employees prior to access being granted to the PSP. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014849 | CIP-004-3a | R3 | WECC_URE1 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R3. The personnel risk assessment (PRA) expired for one WECC_URE1 employee who had physical access to a Physical Security Perimeter (PSP), but did not have access to WECC_URE1’s Bulk Electric System (BES) Cyber Assets. The employee badged into the PSP, and badged out three minutes later. WECC_URE1 identified the expired PRA during a routine quarterly audit and revoked access. At the time the PRA should have been renewed, WECC_URE1 was in the process of changing to a new PRA vendor. WECC_URE1 decided to wait and use the new vendor for PRAs, but the change process took longer than expected, and the WECC_URE1 compliance group failed to timely initiate a PRA for the employee. The first quarter, 2015 scheduled quarterly review was completed six days after the employee’s PRA expired. Enforcement determined WECC_URE1 had a compliance exception for CIP-004-3a R3, for its failure to ensure that one employee’s PRA was timely updated at least every seven years. The root cause of this compliance exception was a human performance error, and a lack of compliance process to ensure that PRAs were not allowed to expire during the vendor change process. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, the employee in question was a long-term respected employee, who had physical access to the PSP, but did not have any BES Cyber Asset access, and would not have been able to login to any equipment within the PSP. WECC_URE1 implemented preventative controls to restrict USB ports and CD drives on the devices, to prevent unauthorized personnel gaining access by using malicious software. WECC_URE1 also has processes in place to verify PRA status before granting initial or escalated access to an individual, reducing the likelihood of someone gaining physical access to the PSP. WECC_URE1 implemented detective controls by implementing a policy to have the PSP manned by at least two people 24x7. These personnel have been trained to know who should be working on the devices within the PSP and would detect any physical damage. Additionally, WECC_URE1 logs invalid login attempts and alerts designated personnel of such attempts. As additional compensating controls, WECC_URE1 implemented a process for CIP training, and verified that those who had access to CIP-related devices were trained before granting access. | To mitigate this issue, WECC_URE1 revoked the employee’s access and began the PRA renewal process.
2015-05-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014870 | CIP-006-3c | R1; R1.1 | NPCC_URE1 had an issue of CIP-006-3c R1. During an internal audit, NPCC_URE1 discovered a closet within their physical security perimeter (PSP) did not have full 6-wall protection. Specifically, a conference room had access to a closet defined to be a PSP using overhead plenum space. The condition existed since the original construction of the closet and ended upon sealing the top of the closet space. The root cause was an oversight when the closet was first established as a PSP and evaluated for compliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 set aside a badged entry closet in a conference room which serves as the PSP for certain Critical Cyber Assets. The conference room contained a hole (approximately 4' x 8') in the ceiling that was able to access a closet within the PSP. The closet can serve as a temporary network location so that operations could be reestablished if the building is evacuated. If unauthorized operation from the network were attempted, the on-shift operators would see the activity and be able to identify and stop it. The opening in the closet wall was only visible above the ceiling tiles and from inside the closet. The closet door is managed by a badge reader and a camera. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) installed a sheetrock ceiling in place after discovery 2) sealed the closet space at the level of the start of the plenum NPCC has verified the completion of all mitigation activity.
2015-05-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015014916 | CIP-007-3a | R5; R5.3 | NPCC_URE2 had an issue of CIP-007-3a R5. During an internal review, it was discovered that passwords for one of four types of passwords within their Energy Management System had not been changed in 2013. NPCC_URE2 has processes and procedures in place to ensure annual password changes are made but relies on human intervention to complete the process. The root cause of the issue was due to an individual's failure to change the passwords as per their assignment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The passwords in question are for individual system operator accounts that can only be accessed within the physical security perimeter (PSP). Remote access is not possible. To gain access to the network manager, an operator must first enter the PSP and use login credentials that were CIP compliant during the time of the non compliance. No system operator account has been compromised due to the failure to change the passwords. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) validated the password changes 2) created a CIP late task report that can highlight when CIP Compliance tasks are due 3) added a recurring evidence task to their compliance tool to track activity.
2015-05-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2015014918 | CIP-009-3 | R3 | NPCC_URE3 had an issue of CIP-009-3 R3. NPCC_URE3 performed various updates to their disaster recovery plan but did not notify one person responsible for the activation and implementation of the recovery plan within thirty calendar days of the change being completed in all cases. In this case, two people needed communication of the update, but NPCC_URE3 only has evidence that one person received the communication within thirty days. The matter was resolved when the remaining person was notified of the changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to communicate updates to the recovery plan to one individual could potentially result in those responsible for activating the plan to be unaware of key changes necessary for a successful recovery in an emergency situation. This could cause a delay in the recovery of critical cyber assets. NPCC_URE3 implemented preventive controls. Specifically, NPCC_URE3 regularly published its recovery plan updates on its internal site. NPCC_URE3 employees responsible for implementation of the plan are trained to review the internal site for latest versions of the plan in case the plan is activated. Additionally, the person in scope of this violation works closely with the team responsible for the recovery plan. As such, this person likely knew of the update to the plan and how to use the updates. NPCC_URE3 utilized a team to develop and update the recovery plan. As a result, the team would have been aware if one of the team members was using an outdated version of the recovery plan. | To mitigate this issue, NPCC_URE3: 1) communicated the updates to the disaster recovery plan to the remaining person. 2) hired a compliance manager and a CIP compliance specialist to coordinate, organize, and ensure compliance activities including those surrounding CIP-009. NPCC has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014805 | CIP-006-3c | R1 | RFC_URE1 and RFC_URE2 submitted a Self-Certification and a self-log stating that they had an issue of CIP-006-3c R1. RFC_URE1, RFC_URE2, and RFC_URE4 determined that a possible violation had occurred involving CIP-006-3c R1. Specifically, following a fire alarm at a facility, personnel began to re-enter the facility en-masse through various points of entry. In this particular instance, nine (9) individuals proceeded to follow the crowd, and re-entered the facility through a back doorway leading to a Physical Security Perimeter (PSP) area. In the process of doing so, these individuals failed to follow certain physical security program protocols as outlined below: • Four (4) individuals were authorized to be in the PSP area, but did not swipe their ID access card at the doorway card reader upon re-entry; • Three (3) individuals were not authorized to be in the PSP area and were escorted through the area by authorized personnel, but were not formally logged in as visitors; and • Two (2) individuals were neither authorized to be in the PSP area nor escorted by authorized personnel. With regard to the five (5) individuals that were not authorized to be in the PSP area, access was limited in all cases to a secure hallway within the PSP. This hallway leads to several badge controlled rooms in which Cyber Assets reside. Given the badge controlled doors, none of the individuals in question were able to enter the secure rooms and gain access to the Cyber Assets therein. Further investigation of the incident determined that the five (5) unauthorized personnel were unaware that they had entered a restricted area, and were simply “following the crowd” of personnel returning to the facility after the fire alarm was cleared. The root cause of the identified issue was lack of personnel awareness. The personnel at issue were not paying attention and did not realize that they were re-entering the facility through a doorway that led into a PSP area, and as a result failed to follow appropriate protocols. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This particular PSP is comprised of a secure hallway from which various enclosed, badge-controlled rooms can be accessed. It is within these secure rooms that protected Cyber Assets reside. In this particular instance, personnel returning to the facility only accessed and walked through the PSP secure hallway, and did not gain access to the PSP secure rooms, which off-shoot from the hallway. In addition, as two (2) of the unauthorized personnel exited the PSP, they realized they had passed through a protected area and immediately notified Compliance personnel, who immediately engaged the Manager of Control Room Operations to conduct a thorough security search of the PSP area. No additional unauthorized personnel were identified within the area. | To mitigate this issue, RFC_URE1 and RFC_URE2: 1) escorted all unauthorized personnel out of the PSP hallway immediately; and 2) conducted a thorough search of the PSP to ensure no additional unauthorized personnel were in the area. No additional unauthorized personnel were identified. To mitigate this issue, RFC_URE1 and RFC_URE2 will also complete the following mitigation activities: 1) will issue awareness communications to heighten personnel awareness around facility exit and re-entry procedures; 2) will implement a 2-factor authentication under CIP version 5; 3) will now require both a badge swipe as well as key pad code entry, and will display large red and green LEDs indicating access status for exterior doors that lead into High Impact BES Cyber System PSP areas (like the one at issue here). With 2-factor authentication and LED display, it will be even more obvious to personnel that these doorways are restricted, and without a key pad code, they should not enter.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014807 | CIP-003-3 | R6 | RFC_URE1 and RFC_URE2 submitted Self-Certifications and a self-log stating that they had an issue of CIP-003-3 R6. Having completed a compliance investigation of the issue, RFC_URE1 and RFC_URE2 determined that a possible violation had occurred involving CIP-003 R6 as applied to RFC_URE1 and RFC_URE2's maintenance laptops. Maintenance laptops are used by authorized personnel to conduct routine maintenance tasks at RFC_URE1 and RFC_URE2 substations. On a monthly basis, new images are installed on each maintenance laptop to ensure that the latest security and configuration updates are consistently applied (e.g., security patches, anti-virus signatures, etc.). All updated images are tested in a lab environment prior to installation on the maintenance laptopss. However, RFC_URE1 and RFC_URE2 determined that the requisite change control documentation associated with these installations was being initiated after the new image was installed on the maintenance laptop as opposed to before. In all cases, the necessary documentation and approvals were completed, but the order in which this documentation was initiated and captured was inconsistent with their processes, which require that the change control review and approvals be completed prior to the image being installed. Our investigation identified a total of six (6) individuals who are involved from testing to implementation of the updated maintenance laptop images: one (1) administrator is responsible for testing the changes to the maintenance laptop configurations; three (3) administrators are responsible for installing the updated images to the maintenance laptops on a monthly basis; and two (2) maintenance managers are responsible for ensuring that the changes have been implemented as captured within the request. Particularly during the implementation phase, there was an inconsistent understanding amongst the implementation administrators and maintenance managers as to the order by which change control documentation needs to be captured for these maintenance laptop image updates. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The images were tested in a lab environment prior to installation, and all approvals were ultimately obtained and change documentation completed. Additionally, the images are installed on the maintence laptops external to the substation Electronic and Physical Security Perimeters (ESP and PSP) without risk to Critical Cyber Assets. This issue involved an inconsistency in the order in which the documentation was completed in the process. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 and RFC_URE2: 1) clarified each individual’s respective roles and reinforced the order of the CIP change control process, such that change control documentation is initiated and approved in advance of the maintenance laptop image updates being installed. Note: In terms of CIP tasks, maintenance laptop image updates are the only CIP tasks that require the administrators who are responsible for installing the updated images to execute on the CIP change control process. Accordingly, there are no similar performance concerns with regard to change control documentation and other CIP tasks; and 2) enhanced the change control documentation used by the maintenance laptop administrators to provide greater clarity around who the appropriate reviewers and approvers are in the process. Since the implementation of the improved change control document, the final approver has engaged in a quality assurance review of all maintence laptop change control documentation (and the information documented therein) before an approval is granted.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014806 | CIP-003-3 | R5 | RFC_URE1, RFC_URE2, and RFC_URE4 submitted Self-Certifications and a self-log stating that they had an issue of CIP-003-3 R5. Having completed a compliance investigation of the issue, RFC_URE4, RFC_URE1, and RFC_URE2 determined that a possible violation had occurred involving CIP-003 R5 as applied to the Critical Asset (CA) List. Specifically, the CA List was reviewed annually as required under CIP-002 R2. What was not reviewed was the list of personnel with authorized access to the restricted file share where the CA List resides. The failure to review the access list in 2013 was identified by personnel who were implementing new evidence management process controls for such annual reviews. Beginning in 2011-2012, the CA List was maintained by a single employee, who had sole access to and sole access authorization responsibility for the CA List. Accordingly, the CA List was stored in a secure information repository to which no one other than the authorized employee had access. The employee conducted annual reviews in 2011 and 2012 verifying his sole authorization and access rights to the CA List as appropriate. However, given the singular nature by which the CA List was being maintained and protected, formal “lists” identifying the employee as the designated CA List access authorizer and as the sole personnel with authorized access were never created. Thereafter, in 2013, responsibility for the CA List was transitioned to another employee/team. During this transition, the CA List was moved to another secure information repository. However, no formal designated authorizer or personnel access lists were created/updated during this transition. Moreover, with no such lists in existence, the annual review of access authorizers and personnel with access to the CA List was not performed in 2013. The above issues were identified while implementing new evidence management process controls for annuals reviews. In addition to discovering that formal access authorizer and personal access lists were never established for the CA List from 2011-2013, and the that annual access reviews for the CA List were not performed in 2013, it was also identified that the CA List had been incorrectly classified as “NERC Restricted” and should have been classified as “NERC Secret” pursuant to the Information Protection Program (IPP). Classifying a document as “NERC Secret” as opposed to “NERC Restricted” provides for additional protections/restrictions. In particular, documents marked “NERC Secret” may not be transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except as required to facilitate compliance audits, investigations and the like. Although the CA List was marked as “NERC Restricted” during the time frame of the reported issue, the document was at no time transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except for those instances outlined above. Since identifying these issues, formal lists of designated access authorizers and personnel with authorized access to the CA List have been developed and reviewed during the 2014 annual review cycle. The CA List has also been relabeled as “NERC Secret” documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. While formal access lists were not established, the CA List was stringently controlled by a very small number of employees, who all had completed requisite trainings, personnel risk assessment (PRAs), and a valid business need for their access. In addition, the CA List was always stored in a secure information repository to which a very limited number of personnel would have access. There were no identified instances in which the CA List was accessed by personnel who did not have the requisite training, PRA or business need. | To mitigate this issue, RFC_URE4, RFC_URE1, and RFC_URE2: 1) immediately relabeled the CA List as “NERC Secret” documentation in accordance with the IPP; 2) created a designated authorized approver list and personnel access list for the CA List; and 3) developed a uniform procedure/process for managing access to the CA List moving forward. Note: Although the CIP Senior Manager does not have access to the restricted file share where the CA List is stored, it is made available for his review upon request at any time.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014812 | CIP-006-3c | R1 | RFC_URE1 and RFC_URE2 submitted a Self-Certification and a self-log stating that they had an issue of CIP-006-3c R1. RFC_URE1, RFC_URE2, and RFC_URE4 determined that a possible violation had occurred involving CIP-006-3c R1. Specifically, following a fire alarm at a facility, personnel began to re-enter the facility en-masse through various points of entry. In this particular instance, nine (9) individuals proceeded to follow the crowd, and re-entered the facility through a back doorway leading to a Physical Security Perimeter (PSP) area. In the process of doing so, these individuals failed to follow certain physical security program protocols as outlined below: • Four (4) individuals were authorized to be in the PSP area, but did not swipe their ID access card at the doorway card reader upon re-entry; • Three (3) individuals were not authorized to be in the PSP area and were escorted through the area by authorized personnel, but were not formally logged in as visitors; and • Two (2) individuals were neither authorized to be in the PSP area nor escorted by authorized personnel. With regard to the five (5) individuals that were not authorized to be in the PSP area, access was limited in all cases to a secure hallway within the PSP. This hallway leads to several badge controlled rooms in which Cyber Assets reside. Given the badge controlled doors, none of the individuals in question were able to enter the secure rooms and gain access to the Cyber Assets therein. Further investigation of the incident determined that the five (5) unauthorized personnel were unaware that they had entered a restricted area, and were simply “following the crowd” of personnel returning to the facility after the fire alarm was cleared. The root cause of the identified issue was lack of personnel awareness. The personnel at issue were not paying attention and did not realize that they were re-entering the facility through a doorway that led into a PSP area, and as a result failed to follow appropriate protocols. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This particular PSP is comprised of a secure hallway from which various enclosed, badge-controlled rooms can be accessed. It is within these secure rooms that protected Cyber Assets reside. In this particular instance, personnel returning to the facility only accessed and walked through the PSP secure hallway, and did not gain access to the PSP secure rooms, which off-shoot from the hallway. In addition, as two (2) of the unauthorized personnel exited the PSP, they realized they had passed through a protected area and immediately notified Compliance personnel, who immediately engaged the Manager of Control Room Operations to conduct a thorough security search of the PSP area. No additional unauthorized personnel were identified within the area. | To mitigate this issue, RFC_URE1 and RFC_URE2: 1) escorted all unauthorized personnel out of the PSP hallway immediately; and 2) conducted a thorough search of the PSP to ensure no additional unauthorized personnel were in the area. No additional unauthorized personnel were identified. To mitigate this issue, RFC_URE1 and RFC_URE2 will also complete the following mitigation activities: 1) will issue awareness communications to heighten personnel awareness around facility exit and re-entry procedures; 2) will implement a 2-factor authentication under CIP version 5; 3) will now require both a badge swipe as well as key pad code entry, and will display large red and green LEDs indicating access status for exterior doors that lead into High Impact BES Cyber System PSP areas (like the one at issue here). With 2-factor authentication and LED display, it will be even more obvious to personnel that these doorways are restricted, and without a key pad code, they should not enter.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014811 | CIP-003-3 | R6 | RFC_URE1 and RFC_URE2 submitted Self-Certifications and a self-log stating that they had an issue of CIP-003-3 R6. Having completed a compliance investigation of the issue, RFC_URE1 and RFC_URE2 determined that a possible violation had occurred involving CIP-003 R6 as applied to RFC_URE1 and RFC_URE2's maintenance laptops. Maintenance laptops are used by authorized personnel to conduct routine maintenance tasks at RFC_URE1 and RFC_URE2 substations. On a monthly basis, new images are installed on each maintenance laptop to ensure that the latest security and configuration updates are consistently applied (e.g., security patches, anti-virus signatures, etc.). All updated images are tested in a lab environment prior to installation on the maintenance laptopss. However, RFC_URE1 and RFC_URE2 determined that the requisite change control documentation associated with these installations was being initiated after the new image was installed on the maintenance laptop as opposed to before. In all cases, the necessary documentation and approvals were completed, but the order in which this documentation was initiated and captured was inconsistent with their processes, which require that the change control review and approvals be completed prior to the image being installed. Our investigation identified a total of six (6) individuals who are involved from testing to implementation of the updated maintenance laptop images: one (1) administrator is responsible for testing the changes to the maintenance laptop configurations; three (3) administrators are responsible for installing the updated images to the maintenance laptops on a monthly basis; and two (2) maintenance managers are responsible for ensuring that the changes have been implemented as captured within the request. Particularly during the implementation phase, there was an inconsistent understanding amongst the implementation administrators and maintenance managers as to the order by which change control documentation needs to be captured for these maintenance laptop image updates. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The images were tested in a lab environment prior to installation, and all approvals were ultimately obtained and change documentation completed. Additionally, the images are installed on the maintence laptops external to the substation Electronic and Physical Security Perimeters (ESP and PSP) without risk to Critical Cyber Assets. This issue involved an inconsistency in the order in which the documentation was completed in the process. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 and RFC_URE2: 1) clarified each individual’s respective roles and reinforced the order of the CIP change control process, such that change control documentation is initiated and approved in advance of the maintenance laptop image updates being installed. Note: In terms of CIP tasks, maintenance laptop image updates are the only CIP tasks that require the administrators who are responsible for installing the updated images to execute on the CIP change control process. Accordingly, there are no similar performance concerns with regard to change control documentation and other CIP tasks; and 2) enhanced the change control documentation used by the maintenance laptop administrators to provide greater clarity around who the appropriate reviewers and approvers are in the process. Since the implementation of the improved change control document, the final approver has engaged in a quality assurance review of all maintence laptop change control documentation (and the information documented therein) before an approval is granted.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014810 | CIP-003-3 | R5 | RFC_URE1, RFC_URE2, and RFC_URE4 submitted Self-Certifications and a self-log stating that they had an issue of CIP-003-3 R5. Having completed a compliance investigation of the issue, RFC_URE4, RFC_URE1, and RFC_URE2 determined that a possible violation had occurred involving CIP-003 R5 as applied to the Critical Asset (CA) List. Specifically, the CA List was reviewed annually as required under CIP-002 R2. What was not reviewed was the list of personnel with authorized access to the restricted file share where the CA List resides. The failure to review the access list in 2013 was identified by personnel who were implementing new evidence management process controls for such annual reviews. Beginning in 2011-2012, the CA List was maintained by a single employee, who had sole access to and sole access authorization responsibility for the CA List. Accordingly, the CA List was stored in a secure information repository to which no one other than the authorized employee had access. The employee conducted annual reviews in 2011 and 2012 verifying his sole authorization and access rights to the CA List as appropriate. However, given the singular nature by which the CA List was being maintained and protected, formal “lists” identifying the employee as the designated CA List access authorizer and as the sole personnel with authorized access were never created. Thereafter, in 2013, responsibility for the CA List was transitioned to another employee/team. During this transition, the CA List was moved to another secure information repository. However, no formal designated authorizer or personnel access lists were created/updated during this transition. Moreover, with no such lists in existence, the annual review of access authorizers and personnel with access to the CA List was not performed in 2013. The above issues were identified while implementing new evidence management process controls for annuals reviews. In addition to discovering that formal access authorizer and personal access lists were never established for the CA List from 2011-2013, and the that annual access reviews for the CA List were not performed in 2013, it was also identified that the CA List had been incorrectly classified as “NERC Restricted” and should have been classified as “NERC Secret” pursuant to the Information Protection Program (IPP). Classifying a document as “NERC Secret” as opposed to “NERC Restricted” provides for additional protections/restrictions. In particular, documents marked “NERC Secret” may not be transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except as required to facilitate compliance audits, investigations and the like. Although the CA List was marked as “NERC Restricted” during the time frame of the reported issue, the document was at no time transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except for those instances outlined above. Since identifying these issues, formal lists of designated access authorizers and personnel with authorized access to the CA List have been developed and reviewed during the 2014 annual review cycle. The CA List has also been relabeled as “NERC Secret” documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. While formal access lists were not established, the CA List was stringently controlled by a very small number of employees, who all had completed requisite trainings, personnel risk assessment (PRAs), and a valid business need for their access. In addition, the CA List was always stored in a secure information repository to which a very limited number of personnel would have access. There were no identified instances in which the CA List was accessed by personnel who did not have the requisite training, PRA or business need. | To mitigate this issue, RFC_URE4, RFC_URE1, and RFC_URE2: 1) immediately relabeled the CA List as “NERC Secret” documentation in accordance with the IPP; 2) created a designated authorized approver list and personnel access list for the CA List; and 3) developed a uniform procedure/process for managing access to the CA List moving forward. Note: Although the CIP Senior Manager does not have access to the restricted file share where the CA List is stored, it is made available for his review upon request at any time.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013788 | CIP-003-3 | R5 R5.1.2 R5.2 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-003-3 R5. Specifically, RFC_URE3 identified three discrete instances of noncompliance during a regularly scheduled internal compliance review. First, RFC_URE3 discovered that it failed to verify a list of designated personnel who are responsible for authorizing logical or physical access to protected information at least annually, in violation of R5.1.2. Second, RFC_URE3 discovered that an annual review of personnel access privileges was not conducted for a cabinet where printed drawings containing Critical Cyber Asset Information (CCAI) were stored. Third, RFC_URE3 discovered that access privileges to one information technology helpdesk system containing electronic CCAI had not been reviewed annually. The root cause for all three instances of noncompliance was human error. With respect to the first instance, the individual who was responsible for conducting the annual verification accepted a new position, but failed to effectively communicate the need to conduct the list verification to his or her successor. As to the second instance, the cabinet at issue had previously been included within a Physical Security Perimeter (PSP) boundary established for the office that contained the cabinet. However, RFC_URE3 subsequently reduced that PSP boundary, excluding the cabinet from the PSP. Consequently, the individual responsible for maintaining the information within the cabinet did not know that access privileges associated with the cabinet needed to be reviewed annually in addition to the annual review of the access privileges for the PSP located within the office. As to the third instance, the information technology helpdesk system had not initially been used to store CCAI. When RFC_URE3 modified it for this purpose, the individuals responsible for conducting the annual review did not recognize that an annual access privilege review was required for it. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-003-3 R5, to the date RFC_URE3 completed the last of the three required reviews explained above. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. As to the first instance of noncompliance, although RFC_URE3 failed to perform an annual verification of the list of designated personnel responsible for authorizing logical or physical access to protected information, RFC_URE3 nevertheless issued a memorandum which identified the designated personnel by name, title and information for which each was responsible to protect. Each of the identified individuals signed this memorandum acknowledging acceptance of responsibility. Accordingly, all of these responsible individuals had a clear understanding that they were responsible for authorizing logical and physical access to protected information. Furthermore, after performing the required verification, RFC_URE3 indicated that only a few minor revisions were required, so the actual impact was minimal. As to the second instance of noncompliance, although RFC_URE3 failed to perform an annual review of personnel access privileges for a cabinet where printed drawings containing CCAI were stored, access to the office containing the cabinet at issue was restricted to only a limited number of RFC_URE3 authorized personnel with CIP qualifications. Furthermore, as part of RFC_URE3’s layered approach to security, the cabinet was separately secured by a keyed lock. Only a small subset of those individuals with access to the office had also been issued keys to the cabinet. Thus, the likelihood of an unauthorized individual obtaining the physical CCAI within the cabinet was remote. As to the third instance of noncompliance, although RFC_URE3 failed to review access privileges to one system containing electronic CCAI, the individuals accessing this particular work station were appropriately qualified to do so per RFC_URE3's Policy. ReliabilityFirst considered RFC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RFC_URE3: 1) verified and approved the RFC_URE3 Authority list for the missed verification period in 2013, which accurately reflects the designated personnel who were responsible for authorizing logical or physical access to protected information; 2) updated the RFC_URE3 Database to include the annual verification of the Authority list, which will ensure that email reminders are issued when the annual verifications are required; 3) reviewed the list of personnel with access privileges to the restricted area where the cabinet containing physical CCAI is located and confirmed that access privileges are correct and correspond with RFC_URE3’s needs and appropriate personnel roles and responsibilities; 4) added the office location (and the cabinet) containing physical CCAI to the RFC_URE3 tracking system that schedules, initiates and records completion of reviews on a quarterly basis to confirm that access privileges are correct and correspond with RFC_URE3’s needs and appropriate personnel roles and responsibilities, which will ensure that the access privileges for the office and cabinet are reviewed at least annually; 5) reviewed the list of personnel with access privileges to the specific helpdesk system containing electronic CCAI and confirmed that access privileges are correct and correspond with RFC_URE3’s needs and appropriate personnel roles and responsibilities; and 6) added the helpdesk system containing electronic CCAI to the RFC_URE3 tracking system that schedules, initiates and records completion of reviews on a quarterly basis to confirm that access privileges are correct and correspond with RFC_URE3’s needs and appropriate personnel roles and responsibilities, which will ensure that the access privileges for the office and cabinet are reviewed at least annually. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013994 | CIP-005-3a | R5 R5.1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-005-3a R5. During an effort to compile compliance documentation associated with this Standard following the annual self-certification, RFC_URE3 discovered that multiple documents needed to support compliance with the Requirements of CIP-005-3 had not been annually reviewed in accordance with RFC_URE3’s definition of “annual” in its Policy. Specifically, RFC_URE3 reviewed twelve documents of the thirteen affected documents within the calendar year as required; however, the interval between the last and the current annual reviews was greater than the 16 month interval set by RFC_URE3’s Policy by as much as three months. The one additional document was not reviewed within the calendar year nor within the 16 month interval. The root cause of this noncompliance was human error resulting from three factors: (1) RFC_URE3 was using a manual process to track the required annual reviews of documents and to notify individuals responsible for performing the annual reviews; (2) RFC_URE3 had no independent monitoring process in place to ensure the annual review of documents was performed as required; and, (3) without independent monitoring, there was no escalation process that would have alerted management and/or compliance personnel of pending deadlines or missed annual reviews of documents. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-005-3a R5, to the date RFC_URE3 completed the required review of all documentation required by CIP-005-3 to ensure that it reflected current configurations and processes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, twelve of the thirteen affected documents had been annually reviewed within the calendar year; however, the interval between the last and current annual reviews was greater than the 16 month interval set by RFC_URE3’s Policy by no more than three months. Second, the one document that did not undergo an annual review was a high level policy document that simply states RFC_URE3’s commitment to the requirements of the CIP-005 Standard. Third, this noncompliance was an administrative oversight that was corrected by the implementation of an automated notification system. ReliabilityFirst considered RFC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RFC_URE3: 1) conducted a complete review of all documents required for compliance with the CIP standards in order to confirm that all had received an annual review per the RFC_URE3 Policy (if required); 2) entered all documents required for compliance with CIP standards that require an annual review into an electronic system that will track the required annual reviews and automatically notify by email the individual responsible for completing the annual reviews 60 days in advance of the targeted completion date. Targeted completion dates have been established that will allow a sufficient grace period following the date, without exceeding the calendar year or 16 month requirement. After being notified 60 days in advance, the individual responsible will receive an automatic reminder via email until the annual review is completed; 3) assigned responsibility to a compliance team to update and maintain the electronic system used to track the required annual reviews of CIP compliance documents. This same team developed a documented procedure that will ensure independent monitoring of the annual review process. This procedure includes a scheduled monthly meeting to review the status of all pending annual reviews with the responsible individuals; and 4) configured the electronic system used to track the required annual reviews to automatically provide email notifications to management and compliance personnel whenever the targeted completion date is reached and the annual review has not been completed. This escalation process will ensure that the proper attention and resources are focused on completing the annual reviews before the grace period has expired. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013995 | CIP-007-3a | R9 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R9. During an effort to compile compliance documentation associated with this Standard following the annual self-certification, RFC_URE3 discovered that multiple documents specified in Standard CIP-007-3 had not been annually reviewed in accordance with RFC_URE3’s definition of “annual” in its Policy. Specifically three procedures had been annually reviewed within the calendar year as required; however, the interval between the last and current annual reviews was greater than the 16 month interval by as much as three months. The root cause of this noncompliance was human error resulting from three factors: (1) RFC_URE3 was using a manual process to track the required annual reviews of documents and to notify individuals responsible for performing the annual reviews; (2) RFC_URE3 had no independent monitoring process in place to ensure the annual review of documents was performed as required; and, (3) without independent monitoring, there was no escalation process that would have alerted management and/or compliance personnel of pending deadlines or missed annual reviews of documents. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-007-3a R9, to the date RFC_URE3 completed the required review of all documentation required by CIP-007-3a. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, these three procedures were reviewed within the calendar year, but just not within the 16 month interval set by RFC_URE3’s Policy. Second, this noncompliance was an administrative oversight that was corrected by the implementation of an automated notification system. ReliabilityFirst considered RFC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RFC_URE3: 1) conducted a complete review of all documents required for compliance with the CIP standards in order to confirm that all had received an annual review per the RFC_URE3 Policy (if required); 2) entered all documents required for compliance with CIP standards that require an annual review into an electronic system that will track the required annual reviews and automatically notify by email the individual responsible for completing the annual reviews 60 days in advance of the targeted completion date. Targeted completion dates have been established that will allow a sufficient grace period following the date, without exceeding the calendar year or 16 month requirement. After being notified 60 days in advance, the individual responsible will receive an automatic reminder via email until the annual review is completed; 3) assigned responsibility to a compliance team to update and maintain the electronic system used to track the required annual reviews of CIP compliance documents. This same team developed a documented procedure that will ensure independent monitoring of the annual review process. This procedure includes a scheduled monthly meeting to review the status of all pending annual reviews with the responsible individuals; and 4) configured the electronic system used to track the required annual reviews to automatically provide email notifications to management and compliance personnel whenever the targeted completion date is reached and the annual review has not been completed. This escalation process will ensure that the proper attention and resources are focused on completing the annual reviews before the grace period has expired. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013996 | CIP-009-3 | R1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-009-3 R1. During an effort to compile compliance documentation associated with this Standard following the annual self-certification, RFC_URE3 discovered that multiple recovery plans that had not been annually reviewed in accordance with the RFC_URE3 definition of “annual” in RFC_URE3’s Policy. Specifically five recovery plans had been annually reviewed within the calendar year as required; however, the interval between the last and current annual reviews was greater than the 16 month interval by as much as four months. The root cause of this noncompliance was human error resulting from three factors: (1) RFC_URE3 was using a manual process to track the required annual reviews of documents and to notify individuals responsible for performing the annual reviews; (2) RFC_URE3 had no independent monitoring process in place to ensure the annual review of documents was performed as required; and, (3) without independent monitoring, there was no escalation process that would have alerted management and/or compliance personnel of pending deadlines or missed annual reviews of documents. The duration of this noncompliance is from the date RFC_URE3 was required to comply with CIP-009-3 R1, to the date RFC_URE3 completed the required review of all documentation required by CIP-009-3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, these five recovery plans were reviewed within the calendar year, but just not within the 16 month interval set by RFC_URE3’s Policy. Second, this noncompliance was an administrative oversight that was corrected by the implementation of an automated notification system. ReliabiltyFirst considered RFC_URE3's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because although RFC_URE3 previously had a possible violation related to CIP-009 R1 (RFC2011001239), that previous violation of CIP-009 R1 related to the adequacy of the content of RFC_URE3’s recovery plan(s) for CCAs. The present issue, on the other hand, relates to RFC_URE3’s annual review of those recovery plans. Accordingly, ReliabilityFirst did not consider RFC_URE3’s violation history as a factor warranting an alternative disposition method. | To mitigate this issue, RFC_URE3: 1) conducted a complete review of all documents required for compliance with the CIP standards in order to confirm that all had received an annual review per the RFC_URE3 Policy (if required); 2) entered all documents required for compliance with CIP standards that require an annual review into an electronic system that will track the required annual reviews and automatically notify by email the individual responsible for completing the annual reviews 60 days in advance of the targeted completion date. Targeted completion dates have been established that will allow a sufficient grace period following the date, without exceeding the calendar year or 16 month requirement. After being notified 60 days in advance, the individual responsible will receive an automatic reminder via email until the annual review is completed; 3) assigned responsibility to a compliance team to update and maintain the electronic system used to track the required annual reviews of CIP compliance documents. This same team developed a documented procedure that will ensure independent monitoring of the annual review process. This procedure includes a scheduled monthly meeting to review the status of all pending annual reviews with the responsible individuals; and 4) configured the electronic system used to track the required annual reviews to automatically provide email notifications to management and compliance personnel whenever the targeted completion date is reached and the annual review has not been completed. This escalation process will ensure that the proper attention and resources are focused on completing the annual reviews before the grace period has expired. ReliabilityFirst has verified the completion of all mitigation activity
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014816 | CIP-005-3a | R1.4 | RFC_URE4 submitted a Self-Certification and submitted a self-log stating that it had an issue of CIP-005-3a R1.4. Having completed a compliance investigation of the issue, RFC_URE4 determined that a possible violation had occurred involving CIP-005-3a R1.4. Specifically, Energy Management System (EMS) staff identified a remote terminal unit (RTU) test set that was connected via an Ethernet cable to a Switch (a Critical Cyber Asset) located in the backup control center. The RTU test set is routinely connected (every two weeks) to make sure that RTU communications are operating as intended to the backup control center in the event of a system cutover. Normal protocols require that the test set be connected only when needed/in use and via a non-routable serial connection. When not in use, the test set is separately maintained and securely stored within the backup control center Physical Security Perimeter (PSP). In this case, when last required, the personnel tasked with connecting the test set incorrectly connected it to the Switch using an Ethernet cable (as opposed to the serial connection), and then failed to remove the cable after the test was complete. Our analysis indicates that the Ethernet cable was connected from the RTU test set to the Switch on the date of the last known test prior to issue discovery, and the connection was inadvertently left in place until discovered during a walk down of the backup control center associated with a re-cabling project. The root cause of the identified issue was attributed to personnel error due to lack of awareness. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The device involved is a test set used to poll RTUs in the field, and ensure that they can communicate with the backup network. The RTU test set only has a single network interface, and therefore cannot be connected to both the Switch inside the EMS and another network at the same time. The only other simultaneous connection is serial to test communications between the backup control center and RTUs in the field. In its current configuration, the test set cannot be used to access devices within the Electronic Security Perimeter (ESP), or make any changes to the ESP environment or the devices therein. Moreover, connectivity from the RTU test set to the switch cannot be established without requisite security configuration information (e.g., IP Addresses within the environment, Default Gateway, etc.). Finally, the device is securely maintained within the backup control center PSP, thus restricting access to only those authorized and ensuring that the device does not introduce a security risk (e.g., malware) when connected to the system. | To mitigate this issue, RFC_URE4: 1) removed the Ethernet cable and disconnected the RTU test set from the Switch, immediately upon identifying the connection; 2) disabled the Ethernet port used to connect to the Switch so as to prevent connections via Ethernet entirely and limit connections to non-routable serial only, to address this root cause and prevent future recurrence; 3) put in place configuration monitoring controls to alert when the port interface status is changed for the networking switches and firewalls in the EMS and EBS environments; and 4) administered additional training to further reinforce applicable procedures and protocols regarding the connection of test/maintenance devices to ensure that they are properly followed.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014819 | CIP-007-3a | R5.2 | RFC_URE4 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-3a R5.2. Having completed a compliance review of two separately identified but similar issues, RFC_URE4 determined that a possible violation had occurred involving CIP-007-3a R5.2. Specifically, while conducting a rule configuration review, RFC_URE4 identified two (2) new shared accounts that were inadvertently created on certain Energy Management System (EMS) network switches. Similarly, RFC_URE4 also identified two (2) new administrator accounts that were inadvertently created on certain EMS workstations. In the first instance, the two (2) new shared accounts were created as a result of a password change script that was run in the EMS environment. Specifically, a script was run to change the passwords associated with certain shared accounts due to changes in personnel access. In running the script, a duplicate shared account was inadvertently created on two network switches. To clarify, the creation of the two new shared accounts was not the result of a flaw or failure in the script. The script was run as intended to change the passwords for all EMS/EMS Backup System (EBS) Switches with shared accounts named “DoNotUse.” In this particular instance, two of the Switches did not have their local shared accounts configured with the name “DoNotUse,” and as a result, the script created a duplicate shared account named “DoNotUse” on each device. If the shared accounts on the two Switches at issue had been configured with the name “DoNotUse” (consistent with all the other EMS/EBS Switch shared accounts), the duplicate accounts would not have been created. Immediately upon discovery, the duplications were eliminated and a single shared account was retained on each switch. In the second instance two (2) new administrator accounts were inadvertently created as a result of a Windows 7 migration. Immediately upon discovery, the accounts were removed from the impacted EMS workstations. The reports show that no one made any unauthorized changes from the time the accounts were added through the date on which RFC_URE4 EMS deleted the accounts from the two workstations. The root cause of the issues identified is attributed to personnel error. In both cases, personnel performing the change should have subsequently audited all accounts on the impacted devices to ensure that the changes were completed successfully and that there were no inadvertent accounts created. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Both the shared accounts and administrator accounts involved were subject to several layers of protections commensurate with such accounts on devices located within a CIP protected environment. Specifically, the EMS network switches and workstations reside within an ESP that is further protected by a Physical Security Perimeter. In order for an individual to gain access to accounts on these devices, he/she would have to pass through several layers of electronic security controls (e.g., firewalls, user authentication, etc.) and/or physical security controls before reaching the accounts at issue. Moreover, default passwords were automatically implemented on the accounts upon their creation. Finally, further review of the reports have confirmed that the accounts were never accessed and no unauthorized changes were made to the impacted devices from the time the accounts were created to when they were deleted. | To mitigate this issue, RFC_URE4: 1) immediately removed the shared accounts and administrator accounts at issue from the EMS environment after concluding that they were not necessary to operations; 2) configured a technical control to alert when a change is made to a system account, to address the root cause and prevent future recurrence; 3) further developed technical procedures to clearly define the performer’s role and process for ensuring that system accounts are audited post-change; and 4) administered training on these improved procedures to all applicable personnel.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014818 | CIP-007-3a | R4.2 | RFC_URE4 submitted a Self-Certification and a self-log stating that it had an issue of CIP-007-3a R4.2. The below issue was identified and immediately communicated to a separate entity. Thereafter, an investigation was conducted, which upon completion, resulted in a determination of potential noncompliance. Specifically, RFC_URE4 determined that a possible violation had occurred involving CIP-007-3 R4.2. While conducting a rule configuration review, RFC_URE4 identified two (2) instances in which antivirus signatures were not installed within the separate entity's procedural timeframe of “at least once every 30 calendar days.” In the first instance, RFC_URE4 completed a transfer of client machines to a dedicated server. During the course of this transfer, one of the Energy Management System (EMS) workstations did not successfully transfer. Accordingly, when the updated antivirus definitions were installed 30 calendar days following the previous antivirus, the workstation was not updated. In the second instance, the antivirus client on the EMS Backup System (EBS) server was inadvertently uninstalled. Accordingly, when the updated antivirus definitions were installed 30 calendar days following the previous antivirus update, the server was similarly not updated. Upon discovering the above issues, RFC_URE4 immediately scheduled both the workstation and the server for antivirus definition updates. The workstation was updated 28 calendar days overdue, and the server was updated 32 calendar days overdue. The root cause of the identified issues was attributed to personnel error. In both cases, personnel performing the impacting system change should have verified (1) that the change was applied successfully across all applicable devices, and (2) that there were no unintended consequences. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. In particular, the RFC_URE4 EMS and EBS have no internet connectivity. As a result, the only way malware might be introduced to the EMS and EBS environments is by USB, CD, or other storage media. In order to mitigate this risk, RFC_URE4 employs an endpoint encryption technology, which prohibits the transfer of data by any means (including USB, CD, and other storage media) to assets within the EMS and EBS by anyone other than authorized EMS maintenance personnel. Moreover, when the EMS maintenance team installs maintenance data (e.g., patches or antivirus updates) on the EMS and EBS, they do so from computers that are protected by active, anti-virus scanning technology with regularly updated signatures. The EMS maintenance team also tests all new data in a test environment prior to deployment within the EMS and EBS. Finally, both the test and production environments use a hash-based change detection system so that unauthorized changes introduced by any malware would be quickly detected and alerted. | To mitigate this issue, RFC_URE4: 1) immediately scheduled both workstation and server for antivirus updates; 2) EMS, in its unified procedure with RFC_URE1 and RFC_URE2, implemented controls to verify that AV definitions are consistently installed on all EMS client systems, and updated its malicious software prevention procedure accordingly; and 3) trained the EMS Support Team on the updated controls and procedure.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014814 | CIP-003-3 | R5 | RFC_URE1, RFC_URE2, and RFC_URE4 submitted Self-Certifications and a self-log stating that they had an issue of CIP-003-3 R5. Having completed a compliance investigation of the issue, RFC_URE4, RFC_URE1, and RFC_URE2 determined that a possible violation had occurred involving CIP-003 R5 as applied to the Critical Asset (CA) List. Specifically, the CA List was reviewed annually as required under CIP-002 R2. What was not reviewed was the list of personnel with authorized access to the restricted file share where the CA List resides. The failure to review the access list in 2013 was identified by personnel who were implementing new evidence management process controls for such annual reviews. Beginning in 2011-2012, the CA List was maintained by a single employee, who had sole access to and sole access authorization responsibility for the CA List. Accordingly, the CA List was stored in a secure information repository to which no one other than the authorized employee had access. The employee conducted annual reviews in 2011 and 2012 verifying his sole authorization and access rights to the CA List as appropriate. However, given the singular nature by which the CA List was being maintained and protected, formal “lists” identifying the employee as the designated CA List access authorizer and as the sole personnel with authorized access were never created. Thereafter, in 2013, responsibility for the CA List was transitioned to another employee/team. During this transition, the CA List was moved to another secure information repository. However, no formal designated authorizer or personnel access lists were created/updated during this transition. Moreover, with no such lists in existence, the annual review of access authorizers and personnel with access to the CA List was not performed in 2013. The above issues were identified while implementing new evidence management process controls for annuals reviews. In addition to discovering that formal access authorizer and personal access lists were never established for the CA List from 2011-2013, and the that annual access reviews for the CA List were not performed in 2013, it was also identified that the CA List had been incorrectly classified as “NERC Restricted” and should have been classified as “NERC Secret” pursuant to the Information Protection Program (IPP). Classifying a document as “NERC Secret” as opposed to “NERC Restricted” provides for additional protections/restrictions. In particular, documents marked “NERC Secret” may not be transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except as required to facilitate compliance audits, investigations and the like. Although the CA List was marked as “NERC Restricted” during the time frame of the reported issue, the document was at no time transmitted outside of RFC_URE4, RFC_URE1, and RFC_URE2 except for those instances outlined above. Since identifying these issues, formal lists of designated access authorizers and personnel with authorized access to the CA List have been developed and reviewed during the 2014 annual review cycle. The CA List has also been relabeled as “NERC Secret” documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. While formal access lists were not established, the CA List was stringently controlled by a very small number of employees, who all had completed requisite trainings, personnel risk assessment (PRAs), and a valid business need for their access. In addition, the CA List was always stored in a secure information repository to which a very limited number of personnel would have access. There were no identified instances in which the CA List was accessed by personnel who did not have the requisite training, PRA or business need. | To mitigate this issue, RFC_URE4, RFC_URE1, and RFC_URE2: 1) immediately relabeled the CA List as “NERC Secret” documentation in accordance with the IPP; 2) created a designated authorized approver list and personnel access list for the CA List; and 3) developed a uniform procedure/process for managing access to the CA List moving forward. Note: Although the CIP Senior Manager does not have access to the restricted file share where the CA List is stored, it is made available for his review upon request at any time.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014342 | CIP-004-3a | R4 | RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. As described in the Self-Report, a RFC_URE5 supervisor failed to remove physical access for a staff augmentation contractor to two Physical Security Perimeters (PSPs) after the contractor changed job functions within the same Responsibility Center. The supervisor failed to review the contractor’s NERC CIP accesses and revoke those that did not apply to the new job function. The contractor’s new supervisor became aware that the contractor’s access to two PSPs was still active during RFC_URE5’s quarterly access validation review. The contractor’s change in job function did not trigger the automated controls which are in place for access removal when individuals transfer to different Responsibility Centers within RFC_URE5. The contractor’s new job responsibilities also required NERC CIP access but to different assets than those protected by the two affected PSPs. The contractor’s additional NERC CIP access in the new job function had been approved in accordance with RFC_URE5’s access control program. The root cause of this noncompliance was human error and control failure as the supervisor failed to remove the contractor’s physical access rights to two PSPs after the contractor changed job functions within the same Responsibility Center. The contractor’s change in job function did not trigger the automated controls which are in place for access removal when individuals transfer to different Responsibility Centers within RFC_URE5. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-004-3a R4, to the date RFC_URE5 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The contractor only had access to two PSPs that were not necessary for his job function for thirty (30) days. Additionally, the contractor was NERC CIP cleared and did not access the PSPs after the change in job function. The contractor also had a current Personnel Risk Assessment and NERC cybersecurity training at all relevant times: before the job change, during the one month period when he inadvertently retained authorized access rights to the subject PSPs, and after the unauthorized access was revoked. RFC_URE5 also reviewed the CCURE log files to confirm that the contractor did not access either of the PSPs after his job function changed. ReliabilityFirst considered RFC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RFC_URE5: 1) submitted a ticket to remove the contractor’s access that was no longer required. This request was processed and completed on that same day, thereby removing the contractor’s access to both affected PSPs; 2) counseled both the old supervisor and the contractor's on-site representative on the importance of checking on an individual’s NERC CIP access when contemplating reassignments; 3) took measures to prevent future recurrences of this violation by adding a standing agenda item to the weekly status meeting between the staff augmentation contract firm and RFC_URE5 supervisors to review any proposed role changes of contractor resources. Any identified planned role changes will trigger review of physical and logical access to better assure unneeded access in the new role is revoked in a timelier manner; and 4) created a daily automatically generated report that is auto-emailed each day to the contract representative and relevant RFC_URE5 supervisor. This report shows any person that has a supervisor change. The report is sent out immediately after the process has recorded a change in supervisors and allows for review of physical and logical access and submission of appropriate and timely tickets. Both the daily report and the weekly meeting agenda item will increase awareness of job changes that require changes in NERC access. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2014014343 | CIP-006-3c | R7 | RFC_URE5 submitted a Self-Report stating that it had an issue with CIP-006-3c R7. As described in the Self-Report, the System hard drive experienced disk errors that resulted in partial file corruption of the logs recording Physical Security Perimeter (PSP) access on three different dates. On each of these three dates, journal files that were produced in accordance with CIP-006-3c R6 were inadvertently corrupted and only partially recoverable. Therefore, RFC_URE5 did not meet the retention requirements of CIP-006-3c R7 for the corrupted logs on these three dates. The first occurrence of journal file corruptions lasted for 47 minutes, the second lasted for 17 hours and 15 minutes, and the third lasted for 24 hours. RFC_URE5 believes the loss of the journal files is related to disk errors or locked record/delayed writes associated with anti-virus scanning. The root cause of this noncompliance was hardware failure as RFC_URE5 failed to retain physical access logs recording PSP access on three different dates after the system experienced hard drive disk errors. The duration of this noncompliance is from the date RFC_URE5 was required to comply with CIP-006-3c R7, to the date RFC_URE5 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The scope of the noncompliance was limited to the damaged journal files on the three specified dates. RFC_URE5 was able to partially recover readable information for logging physical access to the various PSPs during the second occurrence. Physical security measures such as monitoring by RFC_URE5 personnel, door locks and alarms, and access card readers remained active during these periods when the files were damaged and thus the PSPs remained protected. ReliabilityFirst considered RFC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RFC_URE5: 1) ran programs on the affected servers to fix disk errors; 2) increased the memory on the affected servers from 1 gigabyte to 4 gigabytes; 3) modified how antivirus scans were performed on specific folders; 4) replaced the hard drives on both affected servers; and 5) implemented hardware changes to allow the Support Team to perform “Emergency Reboots” of the servers. This ability to reboot will decrease the lead time to troubleshoot technology issues because system reboots can be performed in the event of memory issues or system unresponsiveness; resulting in improved issue resolution time. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011823 | CIP-004-3 | R4 | This determination addresses multiple incidents regarding SERC_URE1’s issue with CIP-004 R4. Therefore, each incident is discussed separately. SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-3 R4. SERC_URE1’s access list included two employees, who should not have been on the list. SERC_URE1 discovered that two employees had been granted electronic access to Critical Cyber Assets (CCA). After further assessment, SERC determined that the issue was applicable to only one employee, who had been mistakenly included on SERC_URE1’s authorized cyber access list. SERC determined that SERC_URE1 failed to maintain a list of personnel with authorized cyber access to CCAs, as required. While SERC was performing its assessment and determining the scope of the issue, the following additional issue was found: 1. SERC_URE1 self-reported that it granted an employee, who already had authorized unescorted physical access, electronic access to CCAs. However, SERC_URE1 did not update the CCA access list to reflect the employee’s electronic access until 134 days later. SERC determined that SERC_URE1 failed to update its access list within seven days of any change in the access rights of such personnel, as required. This issue lasted from when the Standard became mandatory and enforceable for SERC_URE1 through when SERC_URE1 updated its CCA access list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to maintain lists of personnel with authorized cyber access to CCAs could have allowed unauthorized persons to access CCAs, which greatly increased the risk of the CCAs being compromised and/or rendered inoperable. However, the inclusion of the individual in the initiating event was a clerical error and the individual did not have access to CCAs. In addition, all of the other individuals involved had valid personnel risk assessments and cyber security training. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) updated the respective access lists; 2) improved instructions regarding processing access request forms and retrained its staff on procedures; and 3) instituted quality control steps to confirm accuracy in updating the access list and to ensure that both the primary and secondary subject matter expert responsible for updating the access list are made aware of the dates access is granted.
2015-05-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012859 | CIP-006-3c | R6 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-006-3c R6. SERC_URE1 failed to log sufficient information to uniquely identify individuals and the time of access 24 hours a day, seven days a week at all access points to the Physical Security Perimeter (PSP). SERC_URE1 failed to log all physical access into a PSP during a malfunction of the Physical Access Control Systems (PACS) monitoring equipment. According to SERC_URE1, five maintenance personnel accessed the PSP during the outage to work on a door. Because the door was held open, the individuals did not utilize the card reader to gain access and SERC_URE1 did not manually log their access. This issue lasted from when the PACS system communications went offline, through approximately two hours later, when the PACS communications was restored. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to capture physical access logs would diminish its ability to perform forensics or evaluate possible security breaches during the investigative stage of possible misoperations and/or malicious activity. However, all personnel, who accessed the PSP, were authorized for unescorted physical access and there were no visitors. The PSP was located within a secure building. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) began manually logging access as soon as the situation was identified; 2) established more effective indoctrination of maintenance personnel on these procedures and providing for more flexibility to respond in these situations; 3) announced verbally at morning staff meetings with security personnel that any personnel that have NERC access to that PSP may start logging personnel until security personnel take over; 4) issued an e-mail to formally remind technicians and security employees that they are to notify the security dispatcher and manually log all access during maintenance or malfunction of the PACs; and 5) revised SERC_URE1's physical security plan to expand the types of personnel authorized to log access during these events.
2015-05-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2014014371 | CIP-004-3a | R4 | SERC_URE2 submitted a Self-Report stating that, it had an issue with CIP-004-3a R4.2. SERC_URE2 reported that it failed to revoke electronic access to Critical Cyber Assets (CCAs) within seven calendar days for two individuals who no longer required such access. SERC_URE2 approved a security access request (SAR) to revoke physical access rights for two individuals who transferred positions within SERC_URE2 and no longer required access to CCAs. SERC_URE2 revoked the individuals’ physical access rights to CCAs on the next day. At the time of physical access revocation, SERC_URE2 noted that both the individuals had electronic access rights to the CCAs. Therefore, SERC_URE2 approved a SAR several days later to revoke the electronic access. However, SERC_URE2 failed to revoke electronic access until 25 days after the approval of the SAR to revoke electronic access. SERC_URE2 utilizes the management approval date in the SAR as the date that access in no longer required. SERC_URE2’s SAR system worked correctly and notified the individual responsible for revoking access via email that the individual needed to revoke electronic access rights for the two individuals. However, the individual overlooked the email and failed to take action until 25 days later. This issue lasted from eight days after the individuals no longer required electronic access, until when SERC_URE2 revoked the individuals' electronic access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). SERC_URE2’s failure to revoke electronic access to CCAs could lead to unauthorized personnel tampering with CCAs, which may have rendered CCAs inoperable, resulting in the loss of monitoring and control of the BPS. However, the employees in question were in good standing and were transferring to new positions within SERC_URE2. In addition, the individuals had completed the required cyber security training and personnel risk assessment. The CCAs did not have remote access capability. Therefore, upon revocation of the physical access rights, SERC_URE2 effectively revoked the ability for the individuals to electronically access the CCAs. The individuals had electronic access to only 10% of the Cyber Assets inside the Physical Security Perimeter. No harm is known to have occurred. SERC considered SERC_URE2’s CIP-004 R4 compliance history in determining the disposition track. SERC determined that SERC_URE2's compliance history should not serve as a basis for applying a penalty. Both issues appear to be isolated failures. SERC_URE2 identified and corrected both issues within less than three weeks, and the individuals involved in the instant issue were in good standing with SERC_URE2 and would not be able to use their electronic access without first gaining physical access to the CCAs, but SERC_URE2 had previously removed their physical access rights. Finally, SERC_URE2’s mitigating activities provide the notice to remove access to multiple personnel, reducing the likelihood of future failures to remove access in time. | To mitigate this issue, SERC_URE2: 1) modified its SAR system to provide multiple e-mail reminders to revoke electronic access rights to SERC_URE2’s CCAs; and 2) changed its process so that electronic access rights are managed by a functional group rather than an individual.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013242 | CIP 004-2 | R4 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP 004-2 R4.1. A WECC Subject Matter Expert discussed the self-report with WECC_URE1. During WECC_URE1’s quarterly review, it found that it failed to maintain an accurate list of its personnel who have access to Critical Cyber Assets (CCAs) and that it failed to document and update its list. WECC_URE1 uses a program to generate a current list of personnel with authorized cyber or authorized unescorted physical access to CCAs. In eight instances, the access was not revoked. The program WECC_URE1 was using to generate a current list of personnel with authorized cyber or authorized unescorted physical access to CCAs incorrectly indicated access had been revoked for eight individuals, when in fact; access had not changed when it should have for these eight individuals. As a result, WECC_URE1 failed to maintain an accurate list of its personnel who have access to CCAs per CIP 004 R4. The root cause of this issue was an inadequate process and system to obtain the the level of documentation that was required by data custodian when performing quarterly reviews. The root cause of this issue was a lack of technology management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 implemented good preventive controls to prevent the loss of visibility into its transmission SCADA system. Specifically, WECC_URE1 stated that access rights in its system were correct and that personnel's job functions were not impacted by the report inconsistencies. Further, WECC_URE1 implemented good detective and corrective controls to detect and correct the loss of visibility into its transmission SCADA system. In these eight instances, the access was not revoked; it was incorrectly reported as revoked as a result of an error in the report. The assessment team identified that the quarterly report contained false positive errors that indicated access had been removed for individuals; however, the access had not changed and these individuals still required access. WECC_URE1 further stated that during its quarterly reviews, it reviews PRA dates, training dates, and business need. It also ensures that this information was correct for all personnel on the list. | To mitigate this issue, WECC_URE1: 1) pulled the access list reports directly from the source systems; 2) updated its Quarterly Electronic and Physical Access Review Procedures to reflect the changes in this process due to the change in the reports; and 3) communicated the changes to the CCA/ACM data custodians. WECC has verified the completion of all mitigation activity.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013508 | CIP-007-3a | R4 | WECC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R4. WECC_URE2 failed to update its existing TFEs with newly added devices that were technically incapable of having malicious software prevention tools installed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As preventive controls, WECC_URE2 implemented a separate network environment for operation and management of control systems. WECC_URE2 uses Intrusion Detection and Intrusion Prevention systems to monitor and alert known threats and it's firewalls are configured to deny all access to downstream devices. WECC_URE2 ensured that all network device activity is monitored via real-time logging, and equipment logs are monitored and reviewed in real time. Also annual port scans are performed across all CCA networks to identify vulnerabilities via open ports and services. | To mitigate this issue, WECC_URE2: 1) standardized its cyber asset inventory to include TFE requirements for each cyber asset; 2) coordinated SMEs to update each cyber asset with any new TFE requests and populate the cyber asset inventory; 3) provided tailboard and training for cyber asset inventory maintenance and management; 4) implemented awareness meetings and training for Standard Leads, SME's and associated Asset Areas regarding new standardized cyber asset and TFE inventory; and 5) scheduled bi-annual ECTS task to each asset area to review and update cyber asset TFE information prior to TFE compliance due date. WECC has verified the completion of all mitigation activity.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014645 | CIP-005-3a | R2 | During a Compliance Audit, WECC determined that WECC_URE3 was in possible non-compliance with CIP-005-3a R2. WECC determined that WECC_URE3 failed to implement strong controls for remote interactive access to ESP devices. Specifically, WECC_URE3 did not have two-factor authentication at the firewalls related to its ESP access. In a previous Compliance Audit, WECC did not find WECC_URE3 in possible non-compliance with CIP-005-3a R2. Subsequent to that Audit, WECC modified its audit approach to require two-factor authentication for all remote (external to ESP) interactive access into an ESP, to ensure that Entities implemented the “strong” controls required by R2.4. The root cause for this compliance exception is WECC_URE3’s lack of compliance understanding, and its failure to establish two-factor authentication at the electronic access point to its ESP. Although WECC_URE3 has already implemented two-factor authentication in some areas, it did not want to make changes to its ESP access before the upcoming audit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk electric system. Specifically, WECC_URE3 did not implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party. This compliance exception posed a potential risk to WECC_URE3, because failing to implement access controls to the ESPs could increase the risk of unauthorized access to devices within the ESP. As preventive controls, the WECC_URE3 access workstations reside within a PSP, WECC_URE3 requires three separate authentication verification steps, and the workstations are restricted by IP addresses and ports. WECC_URE3 also employees PSP access cards and appropriate remote access approvals. WECC_URE3’s firewalls employ multilayer firewall technology, have specific access controls for VPN and all other access using source, destination and ports. As detective controls, WECC_URE3 implemented monitoring and alerting of all access through firewalls and at destination devices, to ensure access is authorized. | To mitigate this issue, WECC_URE3: 1) created a DMZ on the ESP firewall, 2) implement an intermediate host terminal server in the ESP firewall DMZ (R2.1), 3) implement a two-factor authentication server (R2.3), 4) configure the existing interactive VPN access to use two-factor authentication (R2.2), and 5) document the new interactive access configuration.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013568 | CIP-004-3a | R3 | WECC_URE4 submitted a Self-Certification stating it was in possible non-compliance with CIP-004-3a R3. A WECC SME reviewed the Self-Certification and conducted interviews with WECC_URE4 compliance staff, and determined that WECC_URE4 had a compliance exception of CIP-004-3a R3, for its failure to ensure one individual’s personnel risk assessment (PRA) was updated within seven years. The individual in question had physical access to all WECC_URE4’s Physical Security Perimeters (PSPs) that house WECC_URE4’s Energy Management System Critical Cyber Assets (CCAs). Specifically, the PRA for one employee expired. The vendor in charge of conducting PRAs for WECC_URE4 had completed the results of the PRA prior to the employee’s seven year expiration date. However, the vendor failed to appropriately notify WECC_URE4’s Human Resources department that the PRA was complete and available for review; thus WECC_URE4’s Human Resources department did not review the updated background check and timely complete its assessment. The root cause of the issue was a lack of compliance understanding, related to the miscommunication between the vendor responsible for conducting PRAs, and WECC_URE4’s HR personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 updated one individual’s personnel risk assessment 31 days after the initial personnel risk assessment, instead of the 7 years required by the standard. This issue could cause potential harm to WECC_URE4, because failing to timely update and review a PRA could cause WECC_URE4 to miss changes in an individual’s criminal history, an element of potential risk for safety and security. WECC_URE4 implemented detective controls by conducting quarterly reviews of access privileges that included a review of training and PRAs. WECC_URE4 implemented compensating controls, including the initial PRA for the individual; ensuring WECC_URE4 knew the identity of the individual, that the individual had no criminal history that was identified as severe enough to cause any risk. The individual was currently in good standing with WECC_URE4, and was appropriately trained on CCA security, reducing the likelihood of accidental misuse or damage of CCAs. No harm is know to have occured. In consideration of WECC_URE4’s compliance history, WECC notes that WECC_URE4 has provided documentation of its internal compliance program. For these reasons, WECC considers WECC_URE4’s compliance history as a factor in its designation of these remediated issues for CE treatment. | To mitigate this issue, WECC_URE4; (1) reviewed the individual’s PRA, and (2) re-certified that individual for CIP-restricted access seven years and 29 days after the individual’s initial PRA. WECC has verified all mitigating activity. To prevent recurrence, WECC_URE4 will simplify the PRA review by minimizing the number of parties involved and decreasing the possibility for similar miscommunication.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014135 | CIP-004-3a | R4 | WECC_URE4 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R4. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE4’s compliance staff and determined that WECC_URE4 had a compliance exception with CIP-004-3a R4, for its failure to revoke physical access and timely update the access list within seven business days, for one employee who had retired. WECC_URE4 reported that the employee retired but had not been removed from WECC_URE4’s Access Control Matrix within seven days, as required by WECC_URE4’s Cyber/Unescorted Physical Access Control Procedure. WECC_URE4 revoked access 34 days after the employee’s retirement date. The root cause was human error and administrative oversight, because although WECC_URE4 personnel had sent an email related to the employee’s retirement and revocation of access rights, and the supervisor had taken possession of the access card, the access card remained programmed. WECC_URE4’s facility access history shows no further activity associated with this ID card after the employee’s supervisor collected the card. | This remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to revoke physical access rights for one employee who had physical access to its PSPs and update the physical access list within seven (7) days of the employee no longer needing access. This issue of non-compliance posed potential harm to WECC_URE4, because by failing to timely revoke access and update the access list, an unauthorized person could potentially gain access to a PSP, and any associated CCAs. WECC_URE4 implemented preventative controls by taking possession of the employee's card, preventing an unauthorized person from using the card to gain access to the PSP. Also, the facility has a security gate, and the guards were aware of the employee's retirement, so the employee would not have been able enter the PSP. WECC_URE4 implemented detective controls by installing CCTV cameras outside of every door into a PSP, allowing WECC_URE4 security to see if an unauthorized person attempted to access the PSPs. Additionally, WECC_URE4 logs entry and exit into PSPs, and generates alarms as necessary, alerting WECC_URE4 when unauthorized access is detected. As further compensating measures, the employee retired in good standing at WECC_URE4, thus reducing the likelihood of any malicious activity by the employee. No harm is known to have occured. In consideration of WECC_URE4’s compliance history, WECC notes that WECC_URE4 has identified and self-reported the issues of non-compliance addressed herein, and has provided documentation of its internal compliance program. For these reasons, WECC considers WECC_URE4’s compliance history as a factor in its designation of these remediated issues for CE treatment. | To mitigate this issue, WECC_URE4; (1) revoked access for the retired employee; (2) updated its access list; (3) reviewed and clarified language for revocation responsibilities; and (4) updated its revocation process to alert two people for future revocation requests. WECC will not require further formal mitigation activities for this compliance exception. To prevent recurrence, WECC_URE4 has incorporated an audit process by peer review of access changes and documentation. .
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015014854 | CIP-007-1 | R6 | WECC_URE4 submitted a Self-Certification stating that it was in possible noncompliance with CIP-007-1 R6. A WECC SME reviewed the Self-Certification and conducted interviews with WECC_URE4’s compliance staff and determined that WECC_URE4 failed to retain all logs for certain Windows workstations for ninety calendar days, and failed to review logs in compliance with CIP-007 R6.5 guidelines. As background, WECC_URE4 uses a logging system to monitor system events that are related to cyber security. The logging system collects system logs from servers, workstations, and network devices on WECC_URE4’s EMS and Backup Energy Management System. The logging system collects logs from Unix servers and network devices. To collect logs from WECC_URE4’s Microsoft Windows servers and workstations, WECC_URE4 installed an agent program on each EMS. The agent program forwards events from the native Windows system event logs and log files to the logging system server. However, in an internal review, WECC_URE4 discovered that some workstations were logged locally, but were not logged within the logging system. WECC_URE4’s systems administration supervisor, working together with an EMS Engineer, determined that on the other systems within the EBS ESP, the local logs were not being forwarded to the logging system server, because the agent program was terminating inconsistently and for unknown reasons. The local logs of some Windows systems showed that the agent program had terminated unexpectedly. The service was restored during routine system re-starts. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to retain and review 90 days of logs for certain Windows workstations. This issue of non-compliance posed potential harm to WECC_URE4, because failing to review 90 days’ worth of logs could lead to undetected security incidents. WECC_URE4 implemented preventative controls with physical security controls to protect the PSPs, by restricting access to the CCAs to only a limited number of individuals who have cyber security training and valid PRAs. In other words, WECC_URE4 restricts access to the PSPs based on need and job function or duties. WECC_URE4 implemented detective controls using technical and procedural mechanisms for control of electronic access at all access points, enabling only those ports and services necessary at the access points and on the cyber assets within the ESP, and requiring username and passwords to access the devices. Also, WECC_URE4 stated that all devices are located within a PSP and therefore have technical and procedural controls to manage physical access to the PSPs including 24 x 7 logging and monitoring of physical access. Additionally, if any of the devices within the ESP were to lose connectivity, WECC_URE4 would be alerted immediately. WECC_URE4's current detective controls, specifically the practice of enabling only the necessary ports and services, could help prevent a malicious user from implementing a distributed denial of service attack via the devices, because the electronic access points (e.g. firewalls) would have blocked the unauthorized ports and services. WECC_URE4 implemented corrective controls to ensure software consistency and configuration across its test and production environments. In other words, all devices have the same OS configuration; thus, WECC_URE4 would know what ports and services were currently allowed to run on each device. This would minimize the malicious attempt to enable unauthorized TCP/IP ports and services, because the on-call system administrator would be able to disable the unauthorized ports fairly quickly if they happen to by-pass the firewall(s). No harm is known to have occured. | WECC_URE4 submitted a mitigation plan to address this compliance exception. To mitigate this issue, WECC_URE4 will complete the following mitigation activities: 1. Install and test logging system agent program software; 2. Set the logging system agent program service to automatically restart in the event of a failure on all Windows systems within the EMS and EBS ESPs; 4. Configure syslog.conf on all EMS UNIX assets to forward messages to the logging system server and reconfigure the logging system server application to ingest messages from EMS UNIX assets via syslog; 5. Remove terminal server connections to EMS UNIX assets and decommission and dispose terminal servers; 6. Complete a manual review of the CIP-007-3 R6 controls and system event logs for all assets within the EMS and EBS ESPs. To prevent recurrence, WECC_URE4 will include a formal Security Log Review on a 90-day cycle to eliminate the potential for auto-alert log-gaps spanning greater than 90 days.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013841 | CIP-007-3a | R5 R5.1.1 | RFC_URE1 submitted a Self-Certification stating that it had an issue of CIP-004-3a R4. Additionally, RFC_URE1 submitted Self-Reports to the Regions identifying two instances of noncompliance with CIP-004-3a R4. The Regions subsequently determined that the instances of noncompliance should have been submitted as instances of noncompliance with CIP-007-3a R5 rather than CIP-004-3a R4. (As a result, SPP dismissed the CIP-004-3a R4 violation, and RFC_URE1 submitted a new Self-Report to SPP identifying the noncompliance with CIP-007-3a R5. ReliabilityFirst and Texas RE noted the change to CIP-007-3a R5, but did not require RFC_URE1 to submit new Self-Reports identifying the noncompliance with CIP-007-3a R5.) As a result, the Regions are processing the instances of noncompliance under CIP-007-3a R5. RFC_URE1 failed to ensure that shared user accounts and authorized access permissions were implemented consistent with the concept of “need to know” with respect to work functions performed. In addition, RFC_URE1 failed to limit access to systems to those with authorization. The Self-Report contained two instances. With regard to the first incident, RFC_URE1 discovered that an employee shared the password list to all of its Critical Cyber Assets (CCAs) with two individuals who had not been granted authorized electronic access. One of the individuals was an RFC_URE1 employee, and the other individual was an RFC_URE1 contractor. The issue was initially discovered via a software reporting tool on the same day that the RFC_URE1 employee copied the password list from a company laptop to an unencrypted USB drive and provided the passwords list to the two individuals. At the time of the noncompliance, neither co-worker had an active request for this access. Since this instance of noncompliance, RFC_URE1 has authorized the employee’s cyber access but not the contractor’s cyber access. However, the contractor attested that he deleted the password list from his electronic devices. In addition, RFC_URE1 has since changed all the passwords. The RFC_URE1 employee was granted authorized electronic access. RFC_URE1 changed the affected passwords during its normal annual password change process. Regarding the second incident, RFC_URE1 discovered that an employee shared the password list to all of its CCAs with an RFC_URE1 employee who had not been granted authorized electronic access. The issue was initially discovered via a software reporting tool on the same day that an RFC_URE1 employee authorized to access the document provided the USB thumb drive to a co-worker who then copied the list to the co-worker’s computer. The co-worker, who is a RFC_URE1 employee, did not have authorized cyber access at the time of the incident. The RFC_URE1 employee was granted authorized electronic access. The duration of this noncompliance is from the date of the first instance of noncompliance to the date the RFC_URE1 employee in the second instance of noncompliance was granted authorized electronic access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. RFC_URE1 failed to minimize the risk of unauthorized system access which could lead to the introduction of exploitable vulnerabilities in RFC_URE1’s Cyber Assets without its knowledge. RFC_URE1 employees on two different occasions shared passwords to all CCAs with individuals that had not been granted electronic access to CCAs. In addition, the passwords were copied onto an unencrypted USB drive which increased the risk because the data was not protected, and RFC_URE1 would not have been able to track the information in the event it was further copied or shared. Although RFC_URE1 was alerted immediately of the noncompliance, at least in the first instance RFC_URE1 failed to change the affected passwords for almost two months. Furthermore, while RFC_URE1 indicated on the self-report that after the incident it obtained the contractor’s verbal confirmation that he deleted the passwords, RFC_URE1 waited nine months to obtain a formal attestation from the contractor confirming that the password list was deleted from any devices. However, the risk was mitigated by the following factors. First, RFC_URE1 immediately discovered the noncompliances through its Data Loss Prevention tool. Second, the employees and contractor to whom the other RFC_URE1 employees gave the protected information had properly authorized access to the PSP, and they had the same job duties and responsibilities as the authorized employees. Thus, it was less likely that the unauthorized employees and contractor would use the information in a way that would put the Bulk Electric System at risk. Third, in the first instance of noncompliance, it took RFC_URE1 only eight days from the date of the incident to grant the employee authorized access to the CCAs. In the second instance of noncompliance, it took RFC_URE1 only two days to grant the employee authorized access to the CCAs. Finally, the contractor attested that the password list was deleted from all devices, acknowledging that there were no attempts to gain access to CCAs. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) had its supervisors review their employees’ access for Protection and Control personnel, which is the group involved in the instances of noncompliance, and request access where necessary; 2) updated its current field training relating to the appropriate access that supervisors must request; 3) had its Protection and Control employees take the updated training, which includes a complete review of the basic responsibilities relating to CIP processes and procedures; and ReliabilityFirst has verified the completion of all mitigation activity in the Mitigation Plan. Additionally, RFC_URE1 indicated in its self-report that it built a report that monitors field personnel with physical access and no cyber access to ensure that RFC_URE1 gives appropriate access to personnel who require both sets of access rights.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014742 | CIP-003-3 | R6 | RFC_URE1 submitted a Log stating that it had an issue of CIP-003-3 R6. IT Defense team was onboarding a new intrusion detection system (IDS) device. IT network switch ports are enabled by default and converted to monitoring ports upon request via planned change. This installation requires two change requests: one to be completed as a standard change request and the other as a compliance task to lock it down. This appliance was discovered connected to a network port that had not been set to monitoring as that change had not been completed yet. This discovery was made during RFC_URE1's site survey of unresolved connections. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, according to the device vendors, routing through and utilizing an IDS device as an access point is an unlikely scenario, due to design of the security devices. Second, there are additional layers of protection in place to prevent against the realization of any potential harm. For example, RFC_URE1 limits the number of internet connections into its business and control networks and the internet access points are firewalled and continuously monitored. An extensive, dedicated skilled cyber security staff monitors RFC_URE1’s network and systems for malware infections; maintains industry leading anti-virus, threat, anti-malware capabilities, dedicated advanced reverse malware engineering capabilities, a multi-platform suite of advanced persistent threat (APT) monitor and blocking tools, an advanced intrusion detection/intrusion prevention platform, an industry leading security event and alerting platform, and maintains an in house dedicated 24x7 Operations Desk which is staffed to respond to any real-time cyber events. As a result, while there was a remote possibility of compromise, the likelihood of compromise occurring was low due to the existence of the compensating measures listed above. | To mitigate this issue, RFC_URE1: 1) completed the change request; 2) collected vendor documentation proving Sourcefire infrastructure does not allow traffic injection into the switch port; 3) documented a process for Installing a new IDS sensor in the appropriate sequence; and 4) implemented a process for installing a new IDS sensor. RFC_URE1 recognized that it has recently experienced several issues related to change control/configuration management/testing of significant changes. As stated above, RFC_URE1 took certain actions to remediate the issues and prevent reoccurrence under CIP Version 3 to the extent practicable. RFC_URE1 will continue to work to prevent reoccurrence of these types of issues by focusing on them when undertaking its transition to CIP Version 5 throughout 2015. To address change control issues in Version 5, RFC_URE1 will identify Version 5 obligations, conduct a gap analysis, develop a project plan, and implement that project plan. RFC_URE1 will focus on areas where an enterprise-wide approach is practicable, and implement business unit-specific approaches only where necessary.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014743 | CIP-006-3c | R1 | RFC_URE1 submitted a Log stating that it had an issue of CIP-006-3c R1. While pulling Physical Security Perimeter (PSP) Drawings for an Audit, it was discovered there was not a folder for a RTU Cabinet, which is the only PSP located at that site. Upon further investigation, a drawing existed for the Plant Control room, which is not a PSP and does not fall under CIP-006. This drawing was complete after the commissioning. The RTU Cabinets were commissioned and no record of drawing could be found. There was no initial drawing provided by the vendor, so this drawing was not created into an official RFC_URE1 PSP Drawing. After discovery of this issue, it was requested that pictures be taken of the cabinets so a drawing could be produced. Even though the drawing did not exist, the initial identification of all physical access points through each PSP was already established and entered into the Monitoring system. The PSP drawing was created and added to the file share. This oversight is no longer a concern moving forward because the vendor requires a Design drawing prior to approval of the work. This drawing which is saved in the File share is the first record of the site before it is turned into the official RFC_URE1 PSP drawing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the physical access points were clearly identified in the system and monitored even though they were not identified on the drawing. As a result, this is a documentation issue with no impact on Bulk Power System reliability. | To mitigate this issue, RFC_URE1 created and added the PSP drawing to the file share. This oversight is no longer a concern moving forward since the vendor now requires a Design drawing prior to approval of the work. This drawing which is saved in the File share is the first record of the site before it is turned into the official RFC_URE1 PSP drawing.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014275 | CIP-006-3c | R1 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-3c R1. RFC_URE2 determined that there was a failure by personnel to follow its applicable Visitor Access Control Program. Specifically, while on site completing work for a project, two individuals (a RFC_URE2 employee and a contractor) required access to an area within a Physical Security Perimeter (PSP) in order to complete their work. Because neither had access to this area, they contacted another contractor known to have access to the area for assistance. This authorized contractor escorted both individuals into the area and began filling out a visitor log, but then became distracted and did not complete the entries. In a subsequent interview, the authorized contractor indicated that although he knew the area was secured, he did not realize that the area was a protected area. The authorized contractor did provide escorted access throughout the visitors’ access period to the area. RFC_URE2’s subsequent investigation determined that the authorized contractor failed to realize the status of the area due in part to the deterioration of signage outside the area. The duration of this noncompliance is from the date the individuals entered the secured area without following RFC_URE2’s Visitor Access Control Program, to the date RFC_URE2 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The secured area in question resides inside a PSP with access control and perimeter detection. The authorized contractor appropriately escorted the unauthorized contractor and employee into the PSP surrounding the secured area in question. Moreover, all three individuals (the authorized contractor and the unauthorized employee and contractor) had valid Personnel Risk Assessments on file. In addition, the RFC_URE2 employee involved in this noncompliance also had current authorized access to another protected area. Although ReliabilityFirst recognizes the potential risk posed by the authorized contractor’s lack of awareness of the criticality of an area to which he was providing access (due at least in part to the signage deterioration), because the contractor at issue still afforded most of the protections required by the Standard (escorted access and visitor log entry, albeit incomplete), ReliabilityFirst viewed this particular noncompliance as more of a documentation issue based on the incomplete log entry. | To mitigate this issue, RFC_URE2: 1) assessed and installed permanent signage indicating the security level of the area; 2) included additional material in annual training related to responsibilities for access, including awareness and proper visitor logging procedures; and 3) communicated the changes incorporated in the training material to all who have Physical Access. ReliabilityFirst has verified the completion of all mitigation activity.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013721 | CIP-007-3a | R3 R3.1 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R3. RFC_URE3 did not assess a patch within thirty days of availability. While migrating from a spreadsheet-based patch management system to a patch management database system to improve patch management tracking and reporting capabilities, the patch was unintentionally omitted from the upload process. Because the patch was not uploaded, it was not assessed on the scheduled date. The root cause of this violation was human error, which occurred during the one-time migration process from the spreadsheet-based patch management system to the patch management database system. The duration of this noncompliance is from the date on which the patch was required to be assessed to the date RFC_URE3 actually assessed the patch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the systems that required the patch at issue do not directly impact the Bulk Electric System (BES), and the impacted Critical Cyber Asset is located at the backup site. Second, the upload process during migration was a one-time occurrence and this one patch was simply an oversight. Third, although the assessment was completed more than 30 days after the patch was available, RFC_URE3 still installed the patch within its internal deadline for installing patches with a Common Vulnerability Scoring System (CVSS) rating of “Medium.” | To mitigate this issue, RFC_URE3: 1) committed to enter all future patches through the application interface, which will eliminate the potential for reoccurrence; 2) committed to ensuring that a process is followed to verify the accuracy of information uploaded to the patch management database; and 3) committed to continue to research and apply opportunities to improve compliance and security controls where they are found to improve the reliability of the BES.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014014023 | CIP-007-3a | R5 R5.3.2 | RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. A visual inspection of a shared privilege account revealed that the password did not contain a numeric value. The root cause of this violation was human error. Specifically, the vendor-supplied technology for this particular device did not provide the means of enforcing complex passwords, so RFC_URE3 requested and obtained a Technical Feasibility Exception (TFE) as to the requirement that a technical control be in place. However, RFC_URE3 was not exempt from meeting the complexity requirement through other means, which it addressed by implementing a manual process. In this case, the individual responsible for creating the password failed to follow the documented, manual procedure for creating passwords. The duration of this noncompliance is from the date on which the password was created without a numeric character, to the date on which RFC_URE3 changed the password to include a numeric character. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, access to the control network is limited to physical on-site connection points that are within physical security perimeters (PSPs), which means that additional credentials are required to gain access to these devices. Second, the site is also manned 24 hours per day, 7 days per week, further restricting physical access. Third, RFC_URE3 logs and monitors permitted traffic flowing from the corporate network to this device to track any inadvertent activity. | To mitigate this issue, RFC_URE3: 1) committed to install software, which will ensure password complexity for domain accounts; 2) committed to implementing complexity requirement controls for shared accounts; and 3) committed to train applicable personnel on utilization of said software, and retrain on password requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2015-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014248 | CIP-007-3a | R4 | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R4.2. SERC_URE1 reported that it failed to implement its process for anti-virus and malware prevention signatures and properly update the anti-virus signatures on a single Critical Cyber Asset (CCA) server. In preparation for the upcoming SERC Compliance Audit, SERC_URE1 discovered that one CCA server in use had failed to receive updated antivirus signatures as required in CIP-007-3a R4.2. SERC_URE1 inadvertently modified a command on the individual server causing the failure. This modification stopped communications between the single server at issue and the administrative server which housed and disseminated the approved and updated antivirus signatures. Upon review of the logs on all servers in service, SERC_URE1 determined that this problem was limited to just the single server. The issue lasted for approximately 16 months when SERC_URE1 corrected the command and antivirus signatures began updating on the single server at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to maintain updated antivirus signatures on Cyber Assets within the Electronic Security Perimeter (ESP) could have permitted a known virus to impact the single device and cause potential problems with EMS data and actions. However, this issue affected one CCAs in service, so any impacts to the single CCA would have been limited in its ability to propagate and affect other Cyber Assets. There are no connections from the SERC_URE1 protected network to the internet and email is not permitted within the ESP network. SERC_URE1 also utilizes an intrusion detection system, which monitors for any abnormalities within the protected network. After updating the antivirus signatures, SERC_URE1 found no viruses or malware on the affected CCA. No harm is known to have occurred. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) corrected the issue with the signature update process and updated the signature; and 2) updated its automatic notification system used to verify that the signatures are being updated and installed to include this device.
2015-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014249 | CIP-007-3a | R5 | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R5.3. SERC_URE1 reported that it failed to change passwords annually for five accounts. In preparation for the upcoming SERC Compliance Audit, SERC_URE1 discovered five administrative account passwords that SERC_URE1 had not changed annually as required in CIP-007-3a R5.3.3. The administrative accounts consisted of one individual user account and four shared accounts. SERC_URE1 defines annual as within the calendar year (beginning on January 1 and ending on December 31). For the single user account, SERC_URE1 administrative staff alerted the owner of the account that the password was due to be changed annually prior to the end of the year. This alert process is an internal manual tracking and alerting process implemented by SERC_URE1 for required annual user account password changes. The account owner failed to follow-up on the alert email, and the password went past the annual change requirement unchanged. The four shared accounts are not part of the manual alert process, but in all five cases, SERC_URE1 had established technical controls within the domain security settings to lock any accounts if the password is not changed within the required annual timeframe. Thus, in all five instances, once the password went past the 365 day mark since the last password change, the account was locked pending the required change. Also, in the case of the single user account, a different administrator would have to reset the password. This issue lasted approximately eight months, from the first day past the required annual change window until SERC_URE1 finished changing the passwords on the administrative accounts and disabled one of the accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to change passwords on an annual basis permitted passwords to remain on Cyber Assets longer than permitted, thereby increasing the amount of time an attacker would have to discover the passwords. However, SERC_URE1 had technical controls in place to lock the accounts at issue that had a password that was over 365 days in age and force a password change. In the case of the single user account, a different administrator would have to rest the password. The accounts in question are on Cyber Assets within an Electronic Security Perimeter behind a firewall that requires two-factor authentication to access and are in a Physical Security Perimeter. SERC_URE1 conducted an internal review of access records and confirmed that no access was made using these accounts during the issue. No harm is known to have occurred. SERC considered SERC_URE1's compliance history and determined that the instant issue was appropriate for compliance exception treatment. Although, the previous instances were of the same Standard and Requirement, the underlying conduct of the two instances was different than the instant issue and SERC_URE1 had controls in place that reduced the likelihood that the accounts could be compromised. | To mitigate this issue, SERC_URE1: 1) disabled the individual user account and one shared account; 2) changed the passwords for the other three administrative accounts; 3) determined the solution to prevent a recurrence is to refine existing scripts and develop new scripts to list the dates that all account passwords were last changed; and 4) developed, tested, reviewed, and implemented the scripts from item three above.
2015-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014250 | CIP-005-3a | R1; R1.5 | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-005-3a R1.5. SERC_URE1 did not provide Electronic Access Control and Monitoring (EACM) devices the protections specified in CIP-007 R5.3 when it failed to change three application account passwords on its EACM servers annually. In preparation for the upcoming SERC Compliance Audit, SERC_URE1 discovered that it did not change the passwords annually on three application accounts used in its EACM program. These three accounts reside on two dedicated servers within a de-militarized zone network segment off the established SERC_URE1 Electronic Security Perimeter (ESP). During upgrades to the SERC_URE1 EACM program, two new servers were introduced into the environment. The three accounts at issue were a part of the upgrade. SERC_URE1 identified the three default accounts at the time of installation and confirmed they could not be disabled or modified. The purpose of the accounts was to permit the application administrator account to be unlocked or reset if needed. The accounts were not used or required by SERC_URE1, but because they could not be disabled, SERC_URE1 set-up the accounts per the vendor instructions and changed the passwords upon initial installation. In order to track these accounts and manage them for compliance purposes, the technician who originally performed the work added them to an internal tracking tool which would annually alert administrators to their presence within the secured network and the requirement to change the associated passwords. However, the technician did not properly classify the accounts as CIP accounts in the tracking tool when they were added. Because of this error, SERC_URE1 did not receive the annual change reminder and did not annually change the passwords for the three accounts. SERC_URE1 defines annual as within the calendar year (beginning on January 1 and ending on December 31). SERC_URE1 utilizes a template developed to address the requirements specified within CIP-005 R1.5, and a review of that template and the assessments conducted demonstrated that no other requirements specified in CIP-005 R1.5 were missed for these new EACM servers. This issue lasted approximately eight months, from the first day past the required annual change window until SERC_URE1 changed the passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to change EACM passwords on an annual basis permitted passwords to remain on Cyber Assets longer than permitted, increasing the amount of time that an attacker would have to discover the passwords. However, the accounts in question are on Cyber Assets within an ESP behind a firewall that requires two-factor authentication to access and the passwords to the accounts met the complexity requirements of CIP-007 R5.3. The Cyber Assets with the affected accounts are in a Physical Security Perimeter and there was not remote access to the accounts in question. Thus, an attacker would have to gain physical access to the relevant Cyber Assets to use the accounts. SERC_URE1 conducted an internal review of access records and confirmed that no access was made using these accounts during the issue. No harm is known to have occurred. SERC considered SERC_URE1's compliance history and determined that the instant issue was appropriate for compliance exception treatment. Although, the previous instances were of the same Standard and Requirement, the underlying conduct of the two instances was different than the instant issue. | To mitigate this issue, SERC_URE1: 1) conducted a review of the CIP-related systems; 2) validated proper application of the “CIP” classification in the application for all shared, default, generic, disabled, or active accounts; and 3) scheduled and performed activities to change account passwords for their annual update.
2015-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014351 | CIP-004-3a | R4 | SERC sent SERC_URE1 an initial notice of a compliance audit. SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4.2. SERC_URE1 failed to revoke cyber access to a single Critical Cyber Assets (CCAs) within seven calendar days for an individual who no longer required such access. In preparation for the upcoming SERC Compliance Audit, SERC_URE1 discovered a single SERC_URE1 employee that no longer required authorized cyber or authorized unescorted physical access to CCAs due to a job re-assignment but retained cyber access to a single CCA in error. This employee was integral to a major SERC_URE1 project, its energy management system (EMS) upgrade, and just prior to completion of the project, the employee accepted a position in another SERC_URE1 department. Management decided and documented that the employee would retain access to CCAs for the remainder of the project and the individual would be shared between the new role and the previous role until work was completed on the project. A workflow was generated to remove the employee’s cyber access due to the job change. On the same day, management decided to retain access for the employee due to the project, and the revoke access ticket was placed on hold. Approximately four months later, SERC_URE1 completed the project, and the manager initiated a workflow to have the employee’s access to CCAs revoked and the employee was released in full to the new position. The administrator completed the revocations in the workflow indicating that all access was revoked. However, the administrator mistakenly failed to revoke cyber access to a single CCA, but filled in the form that it was completed as required. Upon discovery of this issue on, the employee’s access was immediately removed. In order to ensure the scope of this issue was limited to just this one instance, SERC_URE1 reviewed the historical logs of all CIP related assets against all the previous workflows, and this was the only instance found where SERC_URE1 did not revoke access as required. This issue lasted approximately seven months, from eight days after the individual no longer needed cyber access to the CCA until SERC_URE1 revoked the individual’s cyber access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to revoke individual access to CCAs once the need for access was eliminated could permit individuals to mistakenly or maliciously access and modify or corrupt CCAs and potentially impact the EMS or the BPS. However, the employee in question was and remains in good standing with SERC_URE1, had access to CIP network devices through the new position, was current on training, and had a current Personnel Risk Assessment. For the duration of this issue, the employee retained remote access to only one CCA, and the employee had no knowledge that this access capability remained intact. The employee did not attempt any accesses for the duration of this issue. No harm is known to have occurred. SERC considered SERC_URE1’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the prior and instant issues were isolated instances that each involved a single individual. The instant issue involved a single employee that retained cyber access to a single CCA after accepting a different position within SERC_URE1 that required cyber access to other Cyber Assets. Upon discovering the issue, SERC_URE1 immediately removed the employee’s cyber access to the CCA and promptly self-reported the issue to SERC. | To mitigate this issue, SERC_URE1: 1) fully document the Access Revocation Procedure, including requirements for complete and timely verification of access removals; 2) provided subsequent reinforcement training on the procedure for all administrators; and 3) completed an investigation into the use of active directory for assigning users to the server management module. To mitigate this issue, SERC_URE1 will implement the use of the active directory.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014666 | CIP-002-3 | R1 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE1 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014679 | CIP-002-3 | R2 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE1 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE1 does not own any Critical Assets. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014684 | CIP-002-3 | R3 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE1 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014699 | CIP-002-3 | R4 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE1’s senior manager did not annually approve SPPRE_URE1’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE1 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014669 | CIP-002-3 | R1 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE2 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014682 | CIP-002-3 | R2 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE2 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE2 does not own any Critical Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014687 | CIP-002-3 | R3 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE2 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE2 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014694 | CIP-002-3 | R4 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE2’s senior manager did not annually approve SPPRE_URE2’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE2 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE2 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014670 | CIP-002-3 | R1 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE3 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014683 | CIP-002-3 | R2 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE3 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE3 does not own any Critical Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014688 | CIP-002-3 | R3 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE3 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE3 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014696 | CIP-002-3 | R4 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE3’s senior manager did not annually approve SPPRE_URE3’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE3 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE3 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014667 | CIP-002-3 | R1 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE4 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014680 | CIP-002-3 | R2 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE4 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE4 does not own any Critical Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014685 | CIP-002-3 | R3 | SPPRE_URE4 submitted a Self-Certification stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE4 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE4 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014700 | CIP-002-3 | R4 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE4’s senior manager did not annually approve SPPRE_URE4’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE4 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE4 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014668 | CIP-002-3 | R1 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE5 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014681 | CIP-002-3 | R2 | SPPRE_URE5 submitted a Self-Certification stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE5 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE5 does not own any Critical Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014686 | CIP-002-3 | R3 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE5 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE5 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014695 | CIP-002-3 | R4 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE5’s senior manager did not annually approve SPPRE_URE5’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE5 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE5 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 6 (SPPRE_URE6) | NCRXXXXX | SPP2015014697 | CIP-002-3 | R4 | SPPRE_URE6 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE6’s senior manager did not annually approve SPPRE_URE6’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. The root cause of this issue was SPPRE_URE6’s misinterpretation of CIP-002-3. SPPRE_URE6’s Planning Coordinator had informed SPPRE_URE6 that it did not consider SPPRE_URE6, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE6 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to continue maintaining an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review an RBAM and Critical Asset and Critical Cyber Asset lists could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE6 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE6 will: 1.) Review RBAM and apply methodology. 2.) Have Company Officer sign list of critical assets (should be a null list). 3.) Have Company Officer sign list of critical cyber assets (should be a null list). 4.) Repeat above 1 to 3 for February 2016. In preparation for CIP version 5, a document management tool (Sharepoint) and calendar notification tool (Archer) is being implemented. A notification that this process will need to be repeated in 2016 will be entered into both of these tools.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 7 (SPPRE_URE7) | NCRXXXXX | SPP2015014698 | CIP-002-3 | R4 | SPPRE_URE7 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE7’s senior manager did not annually approve SPPRE_URE7’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. The root cause of this issue was SPPRE_URE7’s misinterpretation of CIP-002-3. SPPRE_URE7’s Planning Coordinator had informed SPPRE_URE7 that it did not consider SPPRE_URE7, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE7 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to continue maintaining an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review an RBAM and Critical Asset and Critical Cyber Asset lists could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE7 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE7 will: 1.) Review RBAM and apply methodology. 2.) Have Company Officer sign list of critical assets (should be a null list). 3.) Have Company Officer sign list of critical cyber assets (should be a null list). 4.) Repeat above 1 to 3 for February 2016. In preparation for CIP version 5, a document management tool (Sharepoint) and calendar notification tool (Archer) is being implemented. A notification that this process will need to be repeated in 2016 will be entered into both of these tools.
2015-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014107 | CIP-007-3a | R5; R5.2.1 | TRE_URE1 submitted a Self-Report to Texas RE and SPP RE stating that it had an issue with CIP-007-3a R5.2.1. Specifically, TRE_URE1 did not change shared account passwords for 17 of its machines prior to placing the machines into service. The root cause of the issue was that TRE_URE1 did not have a documented process to check for a password change before deployment of a computer that was newly imaged. TRE_URE1 had an issue with CIP-007-3a R5.2.1 for approximately nine months. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE1’s failure to change passwords on the accounts of the 17 computers prior to deployment could have resulted in a vulnerability that may be exploited to access any part of the system and compromise the reliability of the BPS. However, the risk was mitigated due to the following factors. First, TRE_URE1 has multiple layers of physical security in place to prevent unauthorized access. Second, the systems involved were non-administrator accounts, and the local accounts require direct local access. Also, the shared accounts did not include administrator access. Furthermore, the passwords for the shared accounts are secured and provided to authorized personnel. No actual harm is known to have occurred. Although TRE_URE1 has had previous noncompliance for failing to change passwords on systems before deployment, the instances involved different systems that were deployed by different groups. While the circumstances of the issues are similar, Texas RE and SPP RE determined that it does not warrant an alternative disposition method because TRE_URE1 has implemented measures to prevent future recurrence of this specific issue. | To mitigate this issue, TRE_URE1: 1) changed passwords on the affected machines; 2) updated the procedure and deployment checklist to include a step that confirms passwords have the current year date; and 3) provided refresher training in processes and procedures regarding deploying devices to the ESP. Texas RE has verified the completion of all mitigation activity.
2015-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014306 | CIP-007-3a | R5 | TRE_URE2 submitted a Self-Report stating that it had identified two instances of noncompliance with CIP-004-3a R4. Texas RE subsequently determined that the instances of noncompliance should have been submitted as instances of noncompliance with CIP-007-3a R5 rather than CIP-004-3a R4. As a result, Texas RE dismissed the CIP-004-3a R4 issue and a new Self-Report identifying the noncompliance with CIP-007-3a R5 was submitted. TRE_URE2 failed to ensure that shared user accounts and authorized access permissions were implemented consistent with the concept of “need to know” with respect to work functions performed. In addition, TRE_URE2 failed to limit access to systems to those with authorization. The Self-Report contained two instances. With regard to the first incident, TRE_URE2 discovered that an employee shared the password list to all of its Critical Cyber Assets (CCAs) with two individuals who had not been granted authorized electronic access. One of the individuals was a TRE_URE2 employee, and the other individual was a TRE_URE2 contractor. The issue was initially discovered via a software reporting tool on the same day that the TRE_URE2 employee copied the password list from a company laptop to an unencrypted USB drive and provided the passwords list to the two individuals. At the time of the noncompliance, neither co-worker had an active request for this access. Since this instance of noncompliance, TRE_URE2 has authorized the employee’s cyber access but not the contractor’s cyber access. However, the contractor attested that he deleted the password list from his electronic devices. In addition, TRE_URE2 has since changed all the passwords. The TRE_URE2 employee was granted authorized electronic access. TRE_URE2 changed the affected passwords during its normal annual password change process. Regarding the second incident, TRE_URE2 discovered that an employee shared the password list to all of its CCAs with a TRE_URE2 employee who had not been granted authorized electronic access. The issue was initially discovered via a software reporting tool on the same day that a TRE_URE2 employee authorized to access the document provided the USB thumb drive to a co-worker who then copied the list to the co-worker’s computer. The co-worker, who is a TRE_URE2 employee, did not have authorized cyber access at the time of the incident. The TRE_URE2 employee was granted authorized electronic access. TRE_URE2 had an issue with CIP-007-3a R5 for approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. TRE_URE2 failed to minimize the risk of unauthorized system access which could lead to the introduction of exploitable vulnerabilities in TRE_URE2’s Cyber Assets without its knowledge. TRE_URE2 employees on two different occasions shared passwords to all CCAs with individuals that had not been granted electronic access to CCAs. In addition, the passwords were copied onto an unencrypted USB drive which increased the risk because the data was not protected, and TRE_URE2 would not have been able to track the information in the event it was further copied or shared. Although TRE_URE2 was alerted immediately of the noncompliance, at least in the first instance TRE_URE2 failed to change the affected passwords for almost two months. Furthermore, while TRE_URE2 indicated on the self-report that after the incident it obtained the contractor’s verbal confirmation that he deleted the passwords, TRE_URE2 waited nine months to obtain a formal attestation from the contractor confirming that the password list was deleted from any devices. However, the risk was mitigated by the following factors. First, TRE_URE2 immediately discovered the noncompliances through its Data Loss Prevention tool. Second, the employees and contractor to whom the other TRE_URE2 employees gave the protected information had properly authorized access to the PSP, and they had the same job duties and responsibilities as the authorized employees. Thus, it was less likely that the unauthorized employees and contractor would use the information in a way that would put the BES at risk. Third, in the first instance of noncompliance, it took TRE_URE2 only eight days from the date of the incident to grant the employee authorized access to the CCAs. In the second instance of noncompliance, it took TRE_URE2 only two days to grant the employee authorized access to the CCAs. Finally, the contractor attested that the password list was deleted from all devices, acknowledging that there were no attempts to gain access to CCAs. No harm is known to have occurred. The compliance history for CIP-007 R5 is distinguishable from the noncompliance here. However, unlike the subject noncompliances, most of the previous violations related to failure to change passwords under CIP-007 R5.2 and 5.3. Several issues in one of the previous violations related to TRE_URE2’s failure to conduct reviews of access privileges to local user accounts, but those issues are distinguishable from the instant noncompliances, which relate to individuals improperly sharing information with unauthorized individuals. As a result, Texas RE did not consider TRE_URE2’s CIP-007 R5 violation history as a factor warranting an alternative disposition method. | To mitigate this issue, TRE_URE2: 1) had its supervisors review their employees’ access for protection and control personnel, which is the group involved in the instances of noncompliance, and request access where necessary; 2) updated its current field training relating to the appropriate access that supervisors must request; and 3) had its protection and control employees take the updated training, which includes a complete review of the basic responsibilities relating to CIP processes and procedures. Texas RE has verified the completion of all mitigation activity.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014263 | CIP-006-3c | R1; R1.1 | WECC_URE1 submitted a Self-Certification stating that, it had a possible instance of noncompliance with CIP-006-3c R1.1. Later, WECC_URE1 reported an additional instance of noncompliance with CIP-006-3c R1.1. The first instance of noncompliance occurred in early 2013, when WECC_URE1 remodeled a Physical Security Perimeter (PSP). During the remodel, WECC_URE1 omitted from the six-wall border two rectangular sections in the north wall mesh above the drop ceiling. The omitted sections measure 16.5” by 7.5” and 16” by 6.5”. The PSP contains non-critical Cyber Assets, consisting of energy management system (EMS) workstations and desk phones. The PSP does not contain Critical Cyber Assets (CCAs). WECC_URE1 discovered the two omitted sections of the PSP. Regarding the other instance of noncompliance, WECC_URE1 added a new PSP. While implementing the six-wall border, WECC_URE1 omitted one rectangular section of the PSP where the ceiling meets the wall. Within this PSP, an iron beam runs along the ceiling 18” away from the wall. The iron beam obstructed the view behind the beam, leading to WECC_URE1’s omission of the rectangular section from the six-wall border. The omitted section measured 18” by 48”. The PSP contains over non-critical Cyber Assets, consisting of EMS workstations and desk phones. The PSP does not contain CCAs. WECC_URE1 discovered the omitted section from the PSP. The root cause of this instance of noncompliance was WECC_URE1's failure to thoroughly inspect before remodeling or building PSPs. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to ensure that all Cyber Assets within an Electronic Security Perimeter resided within an identified PSP. This occurred because WECC_URE1 implemented six-wall borders, but omitted two sections from the six-wall border in one PSP and one section from the six-wall border in a second PSP. This could have allowed malicious individuals to gain physical access to non-critical Cyber Assets. However, WECC_URE1 implemented internal controls to prevent a malicious individual from gaining access and causing damage. The devices in scope were protected by username and password authentication and a separate level of authentication for the EMS application used to view the real-time information. Access points were used to restrict communication into and out of the ESPs. WECC_URE1 also implemented antivirus that likely would have prevented malicious code from being installed. WECC_URE1’s internal controls also included software designed to detect and alert to any changes in the configuration of the devices. Additionally, the devices in scope were not used to give directives to other entities, but were only used for application and tech support. In order to gain physical access to either of the PSPs in scope, a malicious individual would need to enter the main entrance of the building, access the ceiling space through a ceiling hatch in the hall, crawl in the ceiling to the PSP, enter the PSP through one of the holes in the six-wall border, and then drop nine feet from the ceiling to the ground. WECC_URE1 did not discover any access attempts through the PSP holes. As a result, no harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) Updated the physical security plan to require approval of a PSP boundary change prior to the PSP effective date; and 2) Patched the PSP holes.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013902 | CIP-004-3a | R4.1, R4.2 | WECC_URE2 submitted a Self-Certification stating that, as a Responsible Entity, it had noncompliance of CIP-004-3a R4. WECC_URE2 transitioned to a new contract security service company. As part of the transition, WECC_URE2 compiled a roster of existing contract security officers with access rights to WECC_URE2’s Critical Cyber Assets (CCAs). WECC_URE2 provided the roster to the new contract security company to validate that all security officers on the roster had been hired by the new security company and thus would require continued access to WECC_URE2’s CCAs. If security officers appeared on the roster, but were not hired by the new security provider, WECC_URE2 would remove their physical access rights to WECC_URE2’s CCAs. While compiling the roster of existing contract security officers, WECC_URE2 omitted the name of one security officer. The security officer had physical access rights to Physical Security Perimeters (PSPs). The one security officer in scope was not hired by the new security company and no longer required physical access to WECC_URE2’s CCAs. However, because the name of the security officer in scope was omitted from the roster, the new security company was unable to inform WECC_URE2 that the security officer had not been hired and that their physical access rights should be removed. The new contract security company began providing security for WECC_URE2 and as a result, the security officer in scope no longer required physical access to WECC_URE2’s CCAs. Later, WECC_URE2 conducted a quality control review of its security officer roster and discovered the name of the security officer in scope was omitted from the roster WECC_URE2 sent to the new contract security company. WECC_URE2 revoked the security officer’s physical access rights and updated the CCA physical access list. The root cause of this noncompliance was an individual oversight during the original roster compilation. The noncompliance start date was the eighth calendar day after the change of personnel with access to WECC_URE2’s CCAs. The noncompliance end date was when WECC_URE2 revoked the physical access rights and updated the CCA physical access list. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 did not revoke access and update its list of personnel who have access to CCAs within seven calendar days of a change in personnel. This noncompliance involved one security officer who was not retained by WECC_URE2’s new contract security company. This noncompliance could have resulted in the individual in scope gaining physical access to CCAs and non-CCAs. The individual in scope could have used physical access to the PSPs to cause damage to the devices or install malicious software. However, the noncompliance and associated potential consequences were limited due to the controls implemented by WECC_URE2. WECC_URE2 did not grant electronic access to the personnel in scope. The devices in the PSPs in scope each had its own username and password. The personnel in scope did not have access to any of the device’s usernames or passwords. The PSPs are monitored twenty-four hours a day seven days a week by the other WECC_URE2 personnel working at the PSPs. This reduces the likelihood that an unauthorized individual would be able to successfully gain logical access and cause damage to the devices within the PSPs. For these reasons, and because no harm is known to have occurred from this compliance exception, WECC determined this noncompliance poses a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE2 revoked the security officer's physical access rights and updated the list of personnel who have access to the CCAs.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014547 | CIP-007-3a | R4. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R4. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before the TFE was submitted. The Cyber Assets are not architected to run antivirus software and were therefore required to be added to a TFE. The original plan was to add the Cyber Assets to the antivirus TFE because the technology, basis and compensating measures are the same. Based on previous FRCC guidance and internal discussions, there was confusion about whether or not there needed to be a separate TFE for these Cyber Assets because one device configuration is different from the other devices, which added to the delayed submittal. The TFE was submitted approximately three months after the Cyber Assets went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets are not designed to run antivirus software. The Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), and do not have access to the Internet. They are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the Bulk Electric System (BES) and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because malicious code prevention exists at the system level, active directory (AD), at which there is the ability to deter, detect, or prevent malicious code. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014548 | CIP-007-3a | R6. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R6. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before the TFE was submitted. The Cyber Assets are not designed to produce security event logs and were therefore required to be added to a TFE. The TFE was submitted approximately three months after the Cyber Asset went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets are not designed to produce security event logs. The Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), do not have access to the Internet, are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the BES and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because Security Event Monitoring (logging) exists at the system level, active directory (AD). No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014549 | CIP-007-3a | R5. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R5.3. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before a TFE was filed. These Cyber Assets do not have accounts in which to change passwords and were therefore required to be added to a TFE. The TFE was submitted approximately three months after the Cyber Asset went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets do not have accounts in which to change passwords. However, the Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), do not have access to the Internet, are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the BES and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because System Access Control exists at the system level, active directory (AD). No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014744 | CIP-007-3a | R2; R2.1; R2.2 | NPCC_URE1 submitted a self-report stating that it had an issue with CIP-007-3a R2. Two devices had documentation that indicated associated ports and services should be closed. NPCC_URE1 devices do not have the functionality that allows its services to be disabled. The root cause of the non-compliance was NPCC_URE1's failure to submit a Technical Feasibility Exception for the devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). NPCC_URE1 has a number of mitigation measures to reduce exploitation that include the following; firewalls, host-based firewalls, physical security, local syslogging and intrusion detection. E-Mail and internet access by CCAs (including protected cyber assets) is not permitted by firewall rules, minimizing compromise opportunity. In addition, NPCC_URE1 contracts with a third-party to log and monitor access to the Electronic Security Perimeter (ESP) and provides alerting 24 hours a day, 7 days a week. In addition to the managed monitoring service, NPCC_URE1 employs an intrusion detection system. This system passively monitor NPCC_URE1 network traffic and generate alerts on suspicious activity. The Security Event Manager (SEM) monitors activity and protects from threats and vulnerabilities by collecting and correlating event logs. The SEM provides a console for viewing alerts by the NPCC_URE1 staff. | To mitigate this issue, NPCC_URE1: 1) completed a verification of all ports and services on all Protected Cyber Assets. The current running configuration was compared against the baseline documented in CIP-007 R2 Ports and Services documentation. 2) filed a TFE describing and justifying why NPCC_URE1 cannot achieve strict compliance with the applicable requirement. NPCC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015014747 | CIP-002-3 | R4 | NPCC_URE2 submitted a self-report stating that it had an issue of CIP-002-3 R4. NPCC_URE2 failed to have their senior manager approve their documentation for CIP-002-3 R4. NPCC_URE2 prepared the documents for signature in but the senior manager was unavailable for signature and the documents were left in a file ready for signature. During the course of the end of the year responsibilities, the documents were misplaced and the senior manager was unable to sign before the end of the year. The root cause of the violation was due to human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The failure to develop a list of Critical Assets and CCAs and have it approved by senior management could potentially result in non-identification and protection of Critical Assets and CCAs. Therefore, critical systems may not be afforded all the CIP protections. NPCC_URE2 is a Generator Owner and based on its RBAM does not have any Critical Assets or CCAs, therefore the entity has no impact to the BPS based upon the application of their RBAM to its assets. NPCC_URE2 has documented and updated their RBAM annually. It has also identified its potential assets and demonstrated its application of the RBAM against all of NPCC_URE2’s assets. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) provided a signed and dated record of senior manager or delegate approval of the necessary documents NPCC has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014370 | CIP-004-3a | R4 | RF_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. RF_URE1 failed to revoke access to Critical Cyber Assets for two students who worked as summer interns within seven days of the end of their internships. RF_URE1 did not submit Out of Service Notification forms and revoke access for these students until 11 days after each of the student’s internships ended. Upon investigation, RF_URE1 determined that there were no access attempts made by either student, or anyone else using their credentials, during the time that the students’ access badges were still active. The root cause of this noncompliance was the failure to follow established company procedures for revoking access to Critical Cyber Assets. The duration of the first instance of noncompliance is from the seventh day following the end of the first student’s internship, to the date on which RF_URE1 revoked that student’s access to the Critical Cyber Assets. The duration of the second instance of noncompliance is from the seventh day following the end of the second student’s internship, to the date on which RF_URE1 revoked that student’s access to the Critical Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the two students had physical access only to a small subset of areas containing Critical Cyber Assets, and never had electronic access to them. Furthermore, the areas in which the student interns were assigned are occupied 24 hours a day by operations personnel. Second, neither of the student’s departures was for cause and each had undergone personnel risk assessments and cyber security training in accordance with the CIP Reliability Standards. | To mitigate this issue, RF_URE1: 1) Counseled the two submitters of the Out of Service Notification requests on the importance of initiating the employee Out of Service request as soon as a firm date is determined so that access can be cancelled within seven calendar days for access to NERC assets; 2) Counseled Corporate Security’s contract security officer on the importance of properly and promptly handing ID cards requiring deactivation; 3) Updated its Out of Service Checklist form to emphasize that Corporate Security should be contacted in addition to sending the employee’s ID card to Corporate Security on the same day the employee separation occurs; and, 4) Issued an awareness notification to all Company supervisors of employees with access to NERC assets reminding them of their responsibility to coordinate with Corporate Security to ensure timely cancellation of access, within 24 hours for personnel terminated for cause and within seven calendar days for any other changes. RF_URE1 also issued similar informational notifications to the employees themselves as well as the supervisory chain of command up through and including Directors. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014345 | CIP-004-3a | R4 | RF_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. RF_URE2 indicated that a RF_URE2 supervisor failed to remove physical access for a staff augmentation contractor to two Physical Security Perimeters (PSPs) after the contractor changed job functions within the same Responsibility Center. The supervisor failed to review the contractor’s NERC CIP accesses and revoke those that did not apply to the new job function. The contractor’s new supervisor learned that the contractor’s access to two PSPs was still active during RF_URE2’s access validation review. The contractor’s change in job function did not trigger the automated controls which are in place for access removal when individuals transfer to different Responsibility Centers within RF_URE2. The contractor’s new job responsibilities also required NERC CIP access but to different assets than those protected by the two affected PSPs. The duration of this noncompliance is from the date RF_URE2 was required to comply with CIP-004-3a R4 to the date RF_URE2 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The contractor only had access to two PSPs that were not necessary for his job function. Additionally, the contractor was NERC CIP cleared and did not access the PSPs after the change in job function. The contractor also had a current Personnel Risk Assessment and NERC cybersecurity training at all relevant times: before the job change, during the one month period when he inadvertently retained authorized access rights to the subject PSPs, and after the unauthorized access was revoked. RF_URE2 Corporate Security also reviewed the log files to confirm that the contractor did not access either of the PSPs after his job function changed. ReliabilityFirst considered RF_URE2's compliance history and determined there were no relevant instances of noncompliance | To mitigate this issue, RF_URE2: 1) submitted an SRS ticket to remove the contractor’s access that was no longer required. This request was processed and completed on that same day, thereby removing the contractor’s access to both affected PSPs; 2) counseled both the old supervisor and the contractor’s on-site representative on the importance of checking on an individual’s NERC CIP access when contemplating reassignments; 3) took measures to prevent future recurrences of this issue. These measures included adding a standing agenda item to the weekly status meeting between the staff augmentation contract firm and RF_URE2 supervisors to review any proposed role changes of contractor resources. Any identified planned role changes will trigger review of physical and logical access to better assure unneeded access in the new role is revoked in a timelier manner; and 4) created a daily automatically generated report that is auto-emailed each day to the contract representative and relevant RF_URE2 supervisor. This report shows any person that has a supervisor change. The report is sent out immediately after the Personnel Action Notice process has recorded a change in supervisors and allows for review of physical and logical access and submission of appropriate and timely tickets. Both the daily report and the weekly meeting agenda item will increase awareness of job changes that require changes in NERC access. ReliabilityFirst has verified the completion of all mitigtion activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014348 | CIP-006-3c | R7 | RF_URE2 submitted a Self-Report stating that it had an issue of CIP-006-3c R7. RF_URE2 stated that, on three different dates, the Physical Access Control System hard drive experienced disk errors that resulted in partial file corruption of the logs recording PSP access. On each of these three dates, journal files that were produced in accordance with CIP-006-3c R6 were inadvertently corrupted and only partially recoverable. Therefore, RF_URE2 failed to meet the retention requirement of CIP-006-3c R7 for these three dates. RF_URE2 believes the loss of the journal files is related to disk errors or locked record/delayed writes associated with anti-virus scanning. The duration of this noncompliance is from the date RF_URE2 was required to comply with CIP-006-3c R7, to the date RF_URE2 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The scope of the noncompliance was limited to the damaged journal files on the three specified dates. RF_URE2 was able to partially recover readable information for logging physical access to the various PSPs during the second occurrence. Physical security measures such as monitoring by RF_URE2 Corporate Security Command Center personnel, door locks and alarms, and access card readers remained active during these periods when the files were damaged and thus the PSPs remained protected. ReliabilityFirst considered RF_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE2: 1) ran programs on the affected servers to fix disk errors; 2) increased the memory on the affected servers from 1 gigabyte to 4 gigabytes; 3) modified how antivirus scans were performed on specific folders; 4) replaced the hard drives on both affected servers; and 5) implemented hardware changes to allow the Support Team to perform “Emergency Reboots” of the servers. This ability to reboot will decrease the lead time to troubleshoot technology issues because system reboots can be performed in the event of memory issues or system unresponsiveness; resulting in improved issue resolution time. ReliabilityFirst has verified the completion of all mitigtion activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013993 | CIP-003-3 | R6 | RF_URE3 submitted a Self-Report stating that it had an issue with CIP-003-3 R6. RF_URE3 determined that patches were automatically installed without approved change control requests or cyber security testing being completed between two devices. Specifically, a machine reboot was initiated on a device while the device was being fixed. When the device restarted, device patches began automatically installing on that device. On six different dates in 2014, patches were automatically installed without proper change control between the two devices. The patches were supposed to be installed on the devices, but were installed prematurely via an automated process that should have been disabled prior to the device being used. When the patches were installed, neither the approved change control request nor cyber security testing for the patches had been completed. The devices were configured without effective group policy controls that traditionally prevent automated patching. The root cause of this noncompliance was ineffective controls. The duration of this noncompliance is from the date RF_URE3 was required to comply with CIP-003-3 R6, to the date RF_URE3 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RF_URE3 has been highly cooperative throughout the enforcement process and has been proactive in ensuring future compliance and reliability; and RF_URE3’s mitigation was effective and comprehensive. RF_URE3’s mitigation actions will prevent further issues by ensuring updated processes are in place that prevent automatic patching without proper authorization. Appropriate RF_URE3 staff have been trained on these updated processes to prevent recurrence. ReliabilityFirst considered RF_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE3: 1) disabled Windows Update Service, the process that caused the automated patching to prevent any additional patches from being installed without proper change control. The patches were also removed; 2) ran a vulnerability scan as part of cyber security testing and revalidation to assess whether the installation adversely impacted the devices in any way. The scan showed that all patches, except one, were successfully uninstalled. Per Microsoft, there is no mechanism to remove the remaining patch; 3) researched other technical controls, such as whether a group policy object can be applied to the vendor supplied Windows workstations, in an attempt to prevent recurrence; 4) updated process documentation to ensure the process reflects the necessary steps to properly patch a RF_URE3 device; and 5) conducted reeducation and reinforcement training of the roles, responsibilities, and processes for updating patches for the individuals at RF_URE3 that support these devices. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014013789 | CIP-002-3 | R4 | RF_URE4 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. RF_URE4 failed to keep a signed and dated record of the senior manager or delegate’s approval of its risk-based assessment methodology (RBAM). RF_URE4 performed its RBAM, however, the senior manager did not approve the RBAM, the list of Critical Assets (null), and the list of Critical Cyber Assets (null) until a later date. The duration of this noncompliance is from the earliest date the senior manager could have approved the RBAM, to the date RF_URE4 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This issue was purely a documentation issue, as RF_URE4 timely completed its RBAM, but failed only to create and retain a written record of its approval. In addition, both the lists of Critical Assets and Critical Cyber Assets were null, reducing the potential harm from a delayed approval of the RBAM. ReliabilityFirst considered RF_URE4's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE4: 1) approved the RBAM, the null list of Critical Assets, and the null list of Critical Cyber Assets; 2) implemented a second tier of internal controls to ensure that plant personnel will be able to maintain and demonstrate compliance with all CIP-002 requirements; and 3) implemented compliance tracking system software that provides notifications to plant personnel to perform annual reviews and complete signatures for CIP-002. If the tasks are not completed and entered into the system by a programmed date, the tasks are escalated to compliance personnel.
2015-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013985 | CIP-002-3 | R1; R1.2 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R1.2. SERC_URE1 did not correctly follow its risk-based assessment methodology (RBAM) that is used to identify its Critical Assets. Some of SERC_URE1’s control centers contained assets with the capability to manipulate breakers within two substations through relaying software. SERC_URE1 had relay specific software loaded onto control room workstations designed to provide remote support to the substations at issue. This relay software allowed manipulation of breakers in the substations. SERC_URE1 failed to accurately consider these control centers within its RBAM for multiple years because it incorrectly believed it had removed all control capabilities of all breakers greater than 200kV from its control centers. In reality, some of the control centers retained the ability to manipulate breakers at several substations greater than 200 kV. SERC reviewed SERC_URE1’s RBAMs from the period and found that in each year, the first question of each RBAM was whether the control center controlled any breakers of 100 kV or higher. SERC_URE1 answered ‘no’ to this first question because it believed it had eliminated the ability to control breakers at the affected substations from the control centers. SERC_URE1’s RBAM only required it to further analyze the control centers for Critical Asset consideration if it answered this first question in the affirmative. As such, SERC_URE1 incorrectly excluded the control centers from further Critical Asset consideration after answering ‘no’ to the first question. Because the affected control centers had the ability to manipulate breakers of 100 kV or above, SERC_URE1 should have answered ‘yes’ to the first question of its RBAM for the control centers that contained assets with this relay software. Despite this failure, SERC_URE1’s responses to the remaining questions in its RBAM posed for control centers would not have changed, resulting in the determination that the control centers were not Critical Assets. Thus, the final Critical Asset list would not have changed. SERC determined that SERC_URE1 has an issue with CIP-002-3 R1.2 because it did not correctly follow its RBAM as written. This issue lasted from the day after SERC_URE1 failed to follow its RBAM correctly in one year through when SERC_URE1 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to follow its RBAM as written could lead it to overlook or fail to properly consider some assets for inclusion as Critical Assets, which could lead to a failure to identify and protect associated Critical Cyber Assets. However, if SERC_URE1 had considered the control centers beyond the first question, SERC_URE1 would have determined that they were not Critical Assets and the list of Critical Assets would not have changed. SERC_URE1 had conducted planning studies in which it removed all 100 kV and above transmission and those studies determined that the bulk electric system would remain stable. The software within the control centers that could be used to manipulate the relays at the affected substations was used by SERC_URE1 for remote engineering support purposes and not for control purposes. The software could only be used to manipulate three total breakers. Lastly, the software resided within control centers that SERC_URE1 staffed with trained system operators 24 hours a day, seven days a week. No harm is known to have occurred. SERC considered SERC_URE1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) removed the ability to manipulate breakers at several substations from within one of the control centers at issue; and 2) formally transitioned to the CIP-002 version 5 standard. As a result the RBAM assessment is no longer completed.
2015-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2014014546 | CIP-002-3 | R4 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. SERC_URE2 reported that the senior manager failed to approve annually the risk-based assessment methodology (RBAM), the list of Critical Assets, and the list of Critical Cyber Assets (CCAs) in one year. During an internal audit conducted as part of its Internal Compliance Program, SERC_URE2 determined that it had not conducted its annual review and approval of the RBAM and null list of Critical Assets and CCAs in one year. SERC_URE2 conducted its prior annual review and approval, but did not conduct the next review and approval until a month after the next annual review and approval should have been conducted, which is outside of both a rolling twelve month period and a calendar year period. The primary cause of this issue was a turnover in personnel responsible for ensuring the annual reviews and approvals occur and a lack of internal controls. When the employee who was responsible for ensuring the annual review and approval changed roles at the company, that employee cancelled the annual calendar reminder that was part of the previous mitigation plan actions and sent the cancellation to the employee who would be taking over that role. The incoming employee failed to create a calendar reminder for the annual review. This issue lasted from the day after SERC_URE2 failed to conduct the annual review and approval, through when SERC_URE2 reviewed and approved the RBAM, Critical Asset list, and CCA list. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to conduct its annual review and approval of the RBAM could have led to recent changes in the entities asset list to be overlooked or omitted from consideration. However, SERC_URE2 does not have Critical Assets. It applied its RBAM in the years prior to and after the missed year, resulting in null lists for Critical Assets. In addition, SERC_URE2 is a minimal size utility that owns a co-generation plant. No harm is known to have occurred. SERC considered SERC_URE2's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the prior and instant issues were of the same Standard and Requirement, SERC_URE2 discovered the instant issue during an internal audit, whereas the prior issue was discovered by a SERC audit team, indicating that SERC_URE2 has strengthened its detective internal controls. In addition, SERC_URE2 was approximately one month late in approving the necessary documents, whereas in the prior issue, SERC_URE2 took over a year to fully resolve the issue. SERC also considered that SERC_URE2 has implemented preventative internal controls as part of its mitigating activities when determining that Compliance Exception treatment was appropriate. | To mitigate this issue, SERC_URE2: 1) had its designated CIP senior manager sign its RBAM, Critical Asset, and Critical Cyber Asset list; and 2) set its annual calendar reminders through the next decade for two separate dates (November and December) for the Primary Compliance Officer, Primary Compliance Contact and Alternate Compliance Contact.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014465 | CIP-004-3a | R4; R4.1 | TRE_URE1 submitted a Self-Log to Texas RE stating that it had an issue with CIP-004-3a R4.1. TRE_URE1 failed to update the list(s) for a single contractor within seven days of a change in personnel with unescorted physical access to two Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs). The issue was discovered as part of a routine quarterly access review conducted by TRE_URE1 pursuant to CIP-004-3a R4.1. A segment of that review compares records in the TRE_URE1 corporate badging system for authorized unescorted physical access to the records in the internal list of personnel for authorized unescorted physical access and identifies discrepancies. Specifically, a contractor was granted physical access in the corporate badging system to two PSPs; however, the list of personnel who have authorized cyber or authorized unescorted physical access rights to CCAs was not updated until eleven days after access was granted. When examining the root cause of this issue, TRE_URE1 identified that the CIP administrator who granted authorized unescorted physical access in the corporate badging system did not recall the seven-day internal list update requirement and made an incorrect decision about how to complete the internal list record upon encountering an atypical issue in the internal list record entry process. TRE_URE1 had an issue with CIP-004-3a R4.1 for three days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. • The contractor had been properly approved by the contractor's management and a TRE_URE1 CIP administrator for the unescorted physical access to the two PSPs. o The Personal Risk Assessment (PRA) for the contractor was recently cleared. o The contractor had recently completed both the CIP training and policy acknowledgement. • This incident is not indicative of a systemic flaw in the TRE_URE1 CIP access granting process. • As part of the Risk Assessment, TRE_URE1 identified what threat could occur as a result of not updating the internal list as necessary. • Such access would pose a very minimal threat because of the following mitigating factors: o The CCAs in the Control Center are in an open office environment and an attempt by an unknown individual to access any of those assets during normal business hours would quickly be noted, challenged and curtailed. o In the unlikely event such activity was not noted or such activity occurred outside normal business hours, the electronic defense-in-depth deployed to protect CCAs has multiple mechanisms by which inappropriate activity would be detected and notifications would be automatically sent to the support team. o The above defense-in-depth mechanisms would also mitigate any comparable access attempts from the Control Center. Texas determined that the instant issue was appropriate for CE treatment. Although TRE_URE1 and its affiliates had prior noncompliance issues with CIP-004, the root causes were different. Additionally, TRE_URE1 has implemented several measures to address the root cause and to prevent recurrence of this specific issue. | To mitigate this issue, TRE_URE1: 1) updated the list of personnel who have authorized cyber or authorized unescorted physical access rights to CCAs; 2) retrained the individual who delayed the internal list update; 3) added an additional flag drop-down box to the internal list in order to prevent delays in completing the process; 4) added a new required comment field to the internal list to allow the entry of follow-up notes or other specifics around access; 5) modified the process document for access additions to add the following: a. On any occasion where the new flag option is selected, the responsible CIP administrator shall create a task reminder in the applicable mailbox for all CIP administrators so follow-up can be pursued if needed; that task reminder is to be set 5 days after the internal list entry was created or modified. b. Once the circumstances are resolved, the flag will be adjusted accordingly; and 6) revised the access request checklist to include setting up the reminder noted above. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014648 | CIP-002-3 | R4 | TRE_URE2 submitted a Self-Report to Texas RE stating that it had an issue with CIP-002-3 R4. Specifically, TRE_URE2 cannot produce documentation that the senior manager or delegate approved the risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs). The root cause was the lack of a backup that assured that the annual approval and documentation preservation was completed. Texas RE determined that TRE_URE2 had an issue with CIP-002-3 R4 for approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to produce a document showing and approving the RBAM, list of Critical Assets, and CCAs could potentially result in a lack of identification and protection of Critical Assets and CCAs. Therefore, critical systems would not be afforded all the CIP protections and could have allowed TRE_URE2’s peak load to be lost or misused. The risk to the reliability of the BPS was reduced by the following four mitigating factors. First, in the prior year, TRE_URE2 identified and documented that they had no Critical Assets or CCAs. Second, TRE_URE2 applied and approved its risk-based assessment methodology, ending the issue period, and stated that it did not have any Critical Assets or CCAs during the issue period. Third, TRE_URE2’s smaller size minimizes the risk to the BES. Specifically, TRE_URE2’s peak demand was less than 140 MW. Fourth, TRE_URE2 had no Special Protection Systems. No actual harm is known to have occurred due to this noncompliance. Texas RE considered TRE_URE2’S compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) approved its RBAM and null CA/CCA lists; 2) instituted a three step process that occurs annually in Outlook directing the delegated person to complete the following actions: • perform annual standard requirements; • obtain annual signatures; • save/file signature pages electronically; and 3) included the above steps in its plans for its new work order system. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012558 | CIP-006-3a | R2 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue with CIP-006-3a R2. During the audit, the WECC Auditors discovered eight (8) Physical Access Control System (PACS) devices or Intelligent Controller (IC) Board Controllers that were incapable of logging system events related to Cyber Security. The auditors verified that there WECC_URE1 did not file Technical Feasibility Exceptions (TFEs) for these 8 Cyber Assets (CAs). Per CIP-006 R2, CAs that authorize and/or log access to the Physical Security Perimeter must be protected from unauthorized physical access and shall be afforded the protective measures specified in CIP-007-3. WECC_URE1 failed to file TFEs per CIP-007 R6.3 for the eight PACS devices. The auditor forwarded this information to Enforcement for review. Enforcement reviewed the information provided by the WECC Auditor. Enforcement determined that WECC_URE1 failed to file TFE’s for 8 PACS devices which were incapable of logging system events related to Cyber Security. This issue began January 31, 2010, the date which WECC_URE1 should have filed its initial TFE for those 8 devices and ended on July 8, 2013, the date WECC_URE1’s TFE’s for those 8 devices were approved. The root cause was lack of internal controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to file TFE’s for 8 Cyber Assets which were incapable of logging system events related to Cyber Security. Failing to file a TFE report for devices that are incapable of monitoring system events related to cyber security implies that WECC_URE1 is unaware of a technical deficiency of these 8 CAs. WECC_URE1 has compensating measures in place to prevent the compromise of the ESP. Specifically, WECC_URE1 implemented a defense-in-depth architecture of physical and logical Cyber Security controls, including internal and external physical security mechanisms with guards, special locks, Close Circuit Television (CCTV), and logical network perimeter and internal Cyber Security control including firewalls, vulnerability scanning tools, Intrusion Detection Systems and a Security Events Management (SEM) system. Thus, even if a potential attacker obtained information from the devices in scope, the attacker would still have to penetrate WECC_URE1’s defenses to utilize the information gained. For these reasons, and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE1: 1) WECC_URE1 submitted TFE # 2013-WECC-TFE02330 for the 8 PACS devices in scope that are technically infeasible of logging system events related to cyber security. The TFE was approved July 8, 2013; WECC has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014454 | CIP-004-3 | R3 | WECC_URE2 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R3. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2 compliance staff, and determined that WECC_URE2 granted unescorted physical access to an employee without first performing and documenting the results of a PRA for that employee. WECC_URE2 performed a PRA for one employee (“first employee”). Subsequently, WECC_URE2 granted physical access to CCAs, and used the PRA information for another employee (“second employee”) with a similar name as the first employee. When access was granted, WECC_URE2 performed a name search to verify the PRA status, but did not check the unique ID number for a match. At the time, WECC_URE2 did not have a full step-by-step procedure to grant access and verify that the PRA information matched the employee getting access. WECC_URE2 subsequently finished this procedure, but did not discover this issue until later, when WECC_URE2 reviewed the PRA history for the first employee for renewal after seven years. After discovering the error, WECC_URE2 revoked access for the second employee with the similar name. The root cause of this issue of non-compliance is WECC_URE2’s lack of a compliance process, leading to its failure to verify that PRA information matched the employee. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to perform a PRA and document the results for one employee prior to granting that employee unescorted physical access to WECC_URE2 Critical Cyber Assets. The employee had access to various CCAs. This issue of non-compliance posed potential harm to WECC_URE2, because failing to perform a PRA prior to granting unescorted physical access could lead to WECC_URE2 failing to know of an employee's criminal or malicious history. If WECC_URE2 granted physical access to CCAs to an employee with malicious intentions, he/she could physically damage the devices, unplug cables, or attempt to use malware on a USB stick or other device to attempt to gain logical access and control of the devices. WECC_URE2 implements preventative controls that require a user name and password for logical access to the devices, which only employees with authorized logical access would know. The person in this case was only granted physical access. Without logical access, a person with physical access only would require a certain amount of time to gain logical access, if at all. WECC_URE2’s facilities are staffed with authorized personnel 24/7, who would most likely know which employees had authorized physical and/or logical access, and could possibly prevent an unauthorized person from gaining logical access, once inside the facility. WECC_URE2 also uses a subnet system for its devices, separating devices into distinct groups, which would require someone who wanted to inflict maximum damage to compromise multiple devices in order to affect all subnets. WECC_URE2 also uses port plugs on its devices, which could delay/prevent a malware attack using a USB device. WECC_URE2 implements detective controls that would alert WECC_URE2's transmission control center (via alarms) if load changed. Also, if there were any unauthorized logical access attempts into the ESP, an email would be sent to alert personnel, and personnel could have corrected a problem. These alarm controls are tested on a bi-monthly basis to ensure that they are working properly, alerting WECC_URE2 of any unauthorized logical access attempts. As further compensation, WECC_URE2 implements compensating controls, because thefacilities in question are logically separated from one another, so if a malicious person wanted to affect load, it would require compromising either the Control Center, to which the employee in this case did not have access, or each facility individually, which takes time; allowing WECC_URE2 to discover the attack. | To mitigate this compliance exception, WECC_URE2: 1) Revoked unescorted physical access to its Critical Cyber Assets for one employee; 2) Defined steps for reviewing, conducting and reporting CIP PRAs. The steps include searching the human resources database to confirm identity and employment status and also the security screening database, as well as historical files to confirm the CIP PRA elements are complete; and 3) implemented a two-step review process for CIP PRAs. When there are two Personnel Security Consultants (PSC) present, both will review the CIP PRA to ensure it meets the standard requirement and sign off on the file. In the event both PSCs are not available, the Sr. Manager, EEO & Employee Relations will provide the secondary review. The new process has been instituted and documented.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014325 | CIP-006-3c | R7 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-006-3c R7. In the Self-Report, WECC_URE3 reported that it failed to retain physical access logs for at least 90 days. Specifically, WECC_URE3’s hard drive experienced disk errors that resulted in partial file corruption of the logs recording Physical Security Perimeter (“PSP”) access on three different dates. In each of these instances, the journal files that were produced in accordance with CIP-006-3c R6 were inadvertently corrupted and only partially recoverable resulting in WECC_URE3 failing to meet the retention requirements of CIP-006-3c R7 for the corrupted logs on these three dates. WECC_URE3 believes the loss of the files is related to disk errors or locked record/delayed writes associated with anti-virus scanning. As a result, WECC_URE3 reported that it had a possible issue with CIP-006-3c R7. A WECC Subject Matter Expert (SME) began a review of WECC_URE3’s Self-Report and spoke with WECC_URE3 personnel. As a result of the examination, the SME determined that WECC_URE3 had an issue with CIP-006-3c R7. Specifically, the SME determined that WECC_URE3 failed to retain physical access logs for at least 90 days, as required by CIP-006-3c R7. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE3 had an issue with CIP-006-3c R7 for failing to retain physical access logs for at least 90 days. Enforcement determined that the issue began the first day that it failed to retain logs for at least 90 days. Enforcement also determined that the issue ended on the date that WECC_URE3 completed its Mitigating Activities. Additionally, Enforcement determined that the root cause of this noncompliance was hardware failure. WECC_URE3 failed to retain physical access logs that recorded the PSP access on three different dates due to the system experiencing hard drive disk errors. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to retain physical access logs for at least 90 days. Failure to retain physical access logs for the required time could potentially result in WECC_URE3 not having an accurate account of who accessed the Electronic Security Perimeters (ESP) via the PSPs during the three occurrences of lost data. This could assist unauthorized personnel in gaining unauthorized access to the PSPs and the ESPs. This could lead to an individual being able to physically damage the EMS workstations and other hardware equipment. WECC_URE3 implemented strong preventative controls to prevent any unauthorized access. Specifically, WECC_URE3 implemented independent local control panels to manage the local doors and badge access readers whether the systems are fully functional or not. This maintained the physical access control list even during the three instances where the hard drives experienced disk errors. Additionally, the scope of the issue was limited to the damaged journal files on the three specified dates. WECC_URE3 was also able to partially recover readable information for logging physical access to the various PSPs during the second occurrence. No harm is known to have occurred. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3: 1) personnel ran programs on the affected servers to fix disk errors; 2) increased the memory on the affected servers; 3) modified how antivirus scans were performed on specific folders; 4) replaced the hard drives on both affected servers; and 5) implemented hardware changes to allow the Support Team to perform “Emergency Reboots” of the servers. WECC has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014180 | CIP-002-3 | R4 | WECC_URE4 submitted a Self-Report stating that its CIP senior manager did not sign and date its Risk-Based Assessment Methodology (RBAM) for calendar year 2013. WECC_URE4 had records for two approval dates for its RBAM; one for 2012 and one for 2014, but no review date or approval document for 2013. WECC_URE4’s lists for its Critical Assets (CA) and Critical Cyber Assets (CCAs) are null lists, and have been approved by WECC_URE4’s CIP senior manager. According to WECC_URE4, it applied the procedures set forth in its RBAM when its new Backup Control Center was commissioned in 2013, but failed to conduct a review and acquire approval for the RBAM at that time. The root cause of this compliance exception was human error, and WECC_URE4’s failure to review its RBAM and have it approved by WECC_URE4’s CIP senior manager for calendar year 2013. | This compliance exeption posed a minimal risk, but did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to ensure that its risk-based assessment methodology (RBAM) was approved by its CIP senior manager for calendar year 2013. This instance of non-compliance could have posed a potential risk to WECC_URE4 because failing to approve its RBAM during the 2013 calendar year could potentially result in an RBAM that may not accurately identify facilities, Critical Assets, or Critical Cyber Assets. However, in this case, WECC_URE4’s lists of CAs and CCAs are null, and were appropriately approved by a CIP senior manager for 2012, 2013, and 2014. WECC_URE4 implemented compensating controls, because WECC_URE4 reviewed and approved the Critical Asset (CA) and CCA lists and verified that each list was null. Since the lists of CAs and CCAs did not identify any assets as critical,WECC_URE4 would likely know that it had no CCAs and therefore no devices needed to be protected. | WECC_URE4 remediated this compliance exception when its CIP senior manager approved its RBAM for calendar year 2014. WECC will not require further mitigation activities for this instance of non-compliance.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014527 | CIP-006-2 | R2 | WECC Compliance Auditors conducted an onsite audit of WECC_URE5 to determine WECC_URE5’s compliance with the Standard. The Audit Team reviewed submitted evidence, conducted on-site audit tours, interviews, and data request submittals. The Audit Team submitted a Data Request to obtain a list of WECC_URE5’s approved ports and services on its Physical Access Control System (“PACS”), as well as a list of currently enabled ports and services on those devices. WECC_URE5 responded that its PACS devices do not have any open ports and services, and as such, WECC_URE5 did not have a baseline list. However, while doing site tours the auditors observed a PACS control panel that was connected using an Ethernet LAN connection. To verify that the PACs panel was not using any TCP/IP ports in its communication to the server, the auditors reviewed the device configuration instructions. The auditors found that the PACS type used by WECC_URE5 are configured by default to use a port when using the LAN interface. The Audit Team then issued another Data Request, inquiring into whether WECC_URE5 was aware of the open port, and to provide the business justification for the open port. WECC_URE5 responded to the Data Request and stated the devices do not communicate via the identified port and that the manufacturer had configured the device on site to use a different port. WECC_URE5 provided evidence that the devices were communicating using a routable protocol over the different port. Because WECC_URE5 did not have a baseline of open ports and services for their PACS devices, the Audit Team determined WECC_URE5 had a possible issue with CIP-006-3c R2.2, and forwarded the findings to Enforcement for review. Enforcement reviewed the Audit Teams findings, the audit report, and Data Request responses. Enforcement determined that WECC_URE5 had an open port on certain PACS devices protecting Critical Cyber Assets that was not listed on its baseline. As such, WECC_URE5 has an issue of noncompliance with CIP-006-3c R2.2. | WECC_URE5 failed to properly enumerate and document open ports or services for certain PACS devices protecting CCAs. The root cause of the issue of noncompliance was a failure of technology management. Such failure could result in the improper or lack of protection to those devices not properly documented. Further, having undocumented ports or services results in an inadequate annual cyber vulnerability assessment. However, WECC_URE5 implemented several compensating measures. First, WECC_URE5 implemented an “Electronic Security Perimeter (“ESP”) like” environment that restricts user access to Cyber Assets. WECC_URE5 also implemented an anti-malware product to monitor and protect PACS Cyber assets. Finally, due to the nature of the devices themselves, the likelihood a malicious user having the ability to alter the devices is very low. For these reasons, and because no harm is known to have occurred, WECC determined this issue posed minimal risk to the reliability of the BES. | To mitigate this violation, WECC_URE5 will complete by April 30, 2015: 1) Review its PACS documentation to identify the scope of the existing references to the ACUs within the PACS, as well the existing identification of ACUs on PACS diagrams; 2) Draft additional text for inclusion within its physical security documentation; 3) Identify the ACUs within WECC_URE5s Cyber Vulnerability Assessment documentation; 4) Create a new document focused exclusively on the identification of ACUs and their associated port, so that ACUs benefit from their own separate listing; and 5) Review other relevant documents that support the PACS to confirm that no additional modifications were warranted.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013297 | CIP-004-1 | R3 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1, had an issue of CIP-004-1 R3. RF_URE1 failed to provide evidence of complete personnel risk assessments (PRAs), including seven year background checks and identity verifications for three contractors. Specifically, although RF_URE1 provided redacted PRAs for all sampled vendors and contractors, the records for three contractors failed to show either a seven year criminal check or identity verification. One contractor only showed records going back five years for the criminal check, another had a PRA without an identity check, and the last was believed to have been completed, but the vendor was not able to provide the 2009 records. The duration of this noncompliance is from the start date of the Compliance Audit assessment period, to the date RF_URE1 remediated the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All three contractors had a lengthy work history with RF_URE1, and RF_URE1 took immediate action, removing access for all contractors involved in the noncompliance until new PRAs or additional evidence could be provided to RF_URE1 by the vendor, to mitigate the risk of the noncompliance and prevent recurrence. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided evidence that it had removed all access for all contractors involved in the noncompliance until new PRAs or additional evidence could be provided to RF_URE1 by the vendor; and 2) revised its PRA process to require that any contractors and vendors provide redacted PRA results before access is granted, a requirement that did not exist prior to the Compliance Audit. ReliabilityFirst verified that these mitigating actions were complete during the Compliance Audit.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013303 | CIP-006-1 | R6 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1, had an issue of CIP-006-1 R6. ReliabilityFirst discovered that several Manual Log Books used as Visitor Logs for access to Physical Security Perimeters (PSPs) contained incomplete information regarding escort and/or visitor names. Specifically, although RF_URE1 provided manual visitor logging records from PSP access points, some of the entries in those logs were missing either the escorting personnels’ signatures or the visitors’ names. The duration of this noncompliance is from the start date of the Compliance Audit assessment period, to the date RF_URE1 remediated the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the manual logs were incomplete, they were in place and being used. Second, RF_URE1 was able to view video of the PSP access points to confirm the visitors and escorts in question on the incomplete logs, reducing uncertainty about the security of those physical access points even without proper logging. Third, RF_URE1 took immediate action, described in detail in the following paragraph, to mitigate the noncompliance when it was discovered. During the Compliance Audit, RF_URE1 provided evidence demonstrating it identified all missing log information through camera footage at each access point, and provided re-training through emails, meeting, and reminder posters to make employees aware of the importance of completing visitor logs and escorting visitors at all times. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided evidence demonstrating it identified all missing log information through camera footage at each access point; and 2) provided re-training through emails, meeting, and reminder posters to make employees aware of the importance of completing visitor logs and escorting visitors at all times. ReliabilityFirst verified these mitigating activities during the Compliance Audit, including a review of the current manual visitor logs.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013304 | CIP-007-1 | R2 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1 had an issue of CIP-007-1 R2. RF_URE1 provided only a high-level process to ensure only those ports and services required for normal and emergency operations are enabled. Although RF_URE1 provided additional detail to the audit team for the purposes of explanation, its internal process document failed to provide sufficient detail to ensure only needed ports and services are enabled. In addition, RF_URE1 failed to provide sufficient evidence that only needed ports and services are enabled for all Cyber Assets inside Electronic Security Perimeters (ESPs). Although RF_URE1 provided evidence demonstrating that it uses ports and services baseline documents to compare against configuration files, baselines were not available for all Cyber Assets until the second quarter. The duration of this noncompliance is from the start date of the Compliance Audit period, to the date RF_URE1 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although RF_URE1 failed to provide sufficient evidence of its ports and services processes to demonstrate compliance with CIP-007 R2, RF_URE1 did maintain some documentation of configurations and ports and services, and provided sufficient detail to the audit team, although this detail was not documented for the use of RF_URE1 personnel. Second, RF_URE1 had remediated the noncompliance prior to the Compliance Audit, based on results of its Cyber Vulnerability Assessment, indicating that some internal controls are in place to identify and manage risks related to ports and services. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided greater detail of how it ensures only needed ports and services are enabled, and committed to revise its process to include these additional details; 2) created ports and services baselines for all Cyber Assets prior to the Compliance Audit; and 3) formed a Configuration Management Working Group to facilitate the development of more comprehensive baseline documentation with enhanced descriptions of the operational need for an open port or service.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014377 | CIP-006-3c | R2.2 | RF_URE2 submitted a Log stating it had an issue of CIP-006-3c R2.2. An internal audit indicated that micro panels (to which card readers, doors, inputs and outputs are physically wired) and workstations should be considered part of the Physical Access Control System (PACS). RF_URE2 has not considered micros or workstations as part of PACS and therefore have not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3 as defined in CIP-006 R2.2 for workstations, and have not afforded the protective measures specified above excluding CIP-006-3 R4 and R5 for micros. PACS are defined as Cyber Assets that control, alert, or log access to the Physical Security Perimeter(s), exclusive of locally mounted hardware or devices at the Physical Security Perimeter such as motion sensors, electronic lock control mechanisms, and badge readers. RF_URE2's sever has been identified as PACS, but RF_URE2 has not included micros and workstations as PACS. Workstations were not considered PACS because the workstation itself does not control, alert or log access but is a means to access a web-based application that has the ability to remote unlock doors. Because it is a web-based application, every workstation on the wide area network (WAN) could access the application if the user is able to get through the following layers of security: 1. Must be on the RF_URE2 network (If not, must have two-factor authentication) 2. Two-factor authentication to access the firewall 3. Must have an account on the application 4. Must have a specific role within the application to perform remote control. The servers on which the application is hosted follow all requirements detailed in CIP-006-3 R2.2. Micros were not considered PACS because although they have the ability to store logs, there is no mechanism or interface to change badge holder permissions or pull badge access logs directly from a micro panel. The only way to communicate card holder permissions from server-to-micro-to reader is with the corresponding application system. All changes to access permissions must be initiated in the application database. For the micros, there are offices/service centers and substations. For the workstations, the issue implicated all workstations (since the application is web-based). | RF_URE2 determined that this issue posed a minimal risk to Bulk Power System reliability based on the following factors. First, the web-based application can only be accessed through the following layers of security: (1) Must be on the RF_URE2 network (If not, must have two-factor authentication); (2) Two-factor authentication to access the firewall ; (3) Must have an account on the application; (4) Must have a specific role within the application to perform remote control. Second, the only way to communicate card holder permissions from server-to-micro-to reader is with the corresponding application system. All changes to access permissions must be initiated in the application database. As a result of the foregoing, RF_URE2 determined that while the potential existed for compromise to its system, the likelihood of compromise through the micros or workstations was low. | For the workstations, RF_URE2 implemented remote desktop access to the application, changed firewall access rules to only allow virtual machines to connect to server, changed firewall authentication of all users to require SecurID for everyone, and remove request and workflow system from the PACS server. For the substation micros, RF_URE2 put them on the current critical network or collaborated with the group for a separate solution. For the control centers and data centers, RF_URE2 ran ethernet cable from each panel to the server. RF_URE2 will complete the following mitigation activities by December 31, 2015.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012422 | CIP-007-3a | R5 | RF_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. Specifically, RF_URE3 failed to develop and manage five shared accounts that monitor their system in accordance with CIP-007-3a R.5.1.3, 5.2 and 5.2.2. The shared accounts provide logging functions within the RF_URE3 CIP environment. Internal review of the issue that a change management checklist completed during system implementation identified three (3) accounts and personnel with access, but in a subsequent review, RF_URE3 discovered that there were five (5) accounts not listed. This issue was identified as a result of continued extent-of-condition analysis associated with affiliate entity reported issues and mitigation. The duration of this issue is from the date by which RF_URE3 had five shared accounts for which it failed to comply with CIP-007-3a R5, to the date by which RF_URE3 will complete the Mitigation Plan that will remedy this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The implicated accounts are shared accounts utilized for support to the logging program. Access to the account does not allow for access to the actual assets being logged; the account only provides access to the logs for review of unusual activity. ReliabilityFirst discovered that RF_URE3’s current corporate affiliates, have violations of CIP-007-3a R5. However, the start date for each of the violations began when RF_URE3 was not a corporate affiliate. RF_URE3 has not previously violated CIP-007-3a R5 and therefore ReliabilityFirst did not consider RF_URE3’s violation history to constitute an aggravating factor for penalty and disposition determination. | To mitigate this issue, RF_URE3 will complete the following mitigation activities by June 29, 2015: 1) enable logging on the shared accounts; 2) define process improvements: 3) conduct training on revised processes; and 4) transition to corporate affiliate’s significant change testing program. Mitigtion will take until June 2015 to accommodate quality assurance assessments of the change testing program and conduct training and awareness activities.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014264 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report stating that it had an issue of non-compliance with CIP-004-3a R4. For three separate individuals, WECC_URE1 did not revoke access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. WECC_URE1 terminated the first individual and the supervisor locked the identification badge, electronic physical access key card key card and keys in his desk. WECC_URE1 disabled physical access permissions to WECC_URE1’s general office buildings on the key card. WECC_URE1 discovered that physical access permissions to WECC_URE1’s Physical Security Perimeter (PSP) and an additional PSP, both of which are controlled by the the security management system, were still enabled on the key card, and WECC_URE1 disabled the access on the key card. WECC_URE1 updated the list of personnel who have authorized unescorted access to generation CCAs, and removed the individual from the list. WECC_URE1 terminated a second individual, but did not revoke the associated electronic access card until 53 days later. WECC_URE1 removed the physical access permissions to WECC_URE1’s headquarters for a third individual who was an employee of an WECC_URE1 subsidiary, but the physical access permission to the Data Center was not revoked until 24 days later. (However, it should be noted that when WECC_URE1 revoked physical access to the WECC_URE1 headquarters, access was also revoked to the access doors to the Data Center). The root cause of these issues was a lack of compliance understanding, leading to WECC_URE1’s failure to timely revoke access and update its access lists. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to update the access list to the PSP within seven calendar days of a change in personnel per CIP-004 R4.1 and R4.2, for three separate individuals. This issue poses potential harm to WECC_URE1, because failing to revoke access promptly increases the likelihood of a malicious person utilizing the inaccurate access list to gain physical access to CCAs. Specifically an outside individual could steal or gain the WECC_URE1 employee's access badge and use it to gain unauthorized access. Additionally, the formal employee in scope could have used the inaccurate list to lie to the appropriate personnel (Security Guard or HR) and state that the badge was lost to gain a duplicate temporary badge and gain access to the two PSPs. WECC_URE1 implemented preventative controls. Specifically, the individual’s supervisor collected and locked in his desk the identification badge, electronic physical access key card and keys, which would reduce the likelihood of any employee or an outside malicious individual using the former employee's badge to gain access to the two PSPs. In addition, WECC_URE1 also has operators within each PSP who operate the Management System and could have stopped the former employee, or other unauthorized individuals. No harm is known to have occurred from WECC_URE1's failure to control access to its PSPs. | To mitigate this issue, WECC_URE1: (1) revoked access for the first individual, (2) revoked access for the second individual; and (3) revoked access for the third individual.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013489 | CIP-004-1 R3 | R3 | WECC_URE2 submitted a Self-Certification stating that it was in possible non-compliance with CIP-004-3 R3. A WECC SME reviewed the Self-Certification and conducted interviews with WECC_URE2 compliance staff, and determined that WECC_URE2 failed to accurately verify the identity of one janitorial contractor, prior to granting access for that individual to one WECC_URE2 Physical Security Perimeter (PSP). Specifically, the contractor worked for a vendor that conducted an initial clearance for the contractor, and WECC_URE2 granted CIP access to that contractor to WECC_URE2’s PSP. WECC_URE2 compliance staff identified the issue when the individual's existing PRA was nearing expiration and required an update. As part of the update, WECC_URE2 staff noticed a discrepancy between the existing Social Security number and the updated Social Security number for the contractor. After further investigation,WECC_URE2 discovered the contractor intentionally gave a false Social Security number, and immediately revoked access. The root cause of this issue is WECC_URE2’s lack of a compliance process for verifying the accuracy of personnel risk assessment information from its contractors and vendors. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to accurately identify the identity of one contractor prior to granting the contractor access to one PSP. Specifically, the contractor fraudulently submitted an incorrect Social Security number when hired, and was then granted physical access to WECC_URE2's primary transmission control center. This issue of non-compliance posed potential harm to WECC_URE2, because failing to accurately verify a contractor’s identity prior to granting access could lead to WECC_URE2 being unaware of the contractor’s actual identity and criminal background history. However, WECC_URE2 implemented controls to prevent an unverified contractor from causing actual harm to WECC_URE2’s CCAs in the PSP. Specifically, the WECC_URE2 PSP in question is staffed 24 hours a day 7 days a week and thus personnel would have likely detected any attempted logical and physical malicious activity. Also, the contractor did not have logical access to CCAs or any devices within the ESP, thus making it difficult to compromise the CCAs or the associated Critical Asset since user credentials are required to gain access. And, WECC_URE2 implemented AV and malware prevention tools on the devices to mitigate the likelihood of a contractor implanting a virus to gain control of or harm the CCAs. WECC_URE2 implemented detective controls for logging and alerting for detected bad password attempts on the assets within the ESP. Thus, if the contractor attempted to gain logical access to the CCA by guessing passwords, WECC_URE2's logging would have detected it and alerted personnel responsible for responding to the alert. | To mitigate this issue of non-compliance, WECC_URE2: (1) revoked the contractor’s access to its PSP, and (2) worked with the contractor to review its corrective action plan related to Social Security re-verification and criminal background checks. WECC verified WECC_URE2’s mitigation plan was complete.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013992 | CIP-005-3a R1 | R1 | WECC_URE2 submitted a Self-Report stating that it was not compliant with CIP-005-3a R1. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2's compliance staff and determined that WECC_URE2 had failed to follow its change control process for four rule set changes (all unauthorized changes) on one logical access point (two redundant devices) that control logical access into WECC_URE2's control center ESP. The ESP contains approximately 50 to 60 cyber assets of which 20 to 30 are classified as CCAs, including SCADA workstations, operator consoles, test workstations, primary SCADA servers, and AGC and training simulator devices. The rule set changes did not follow the WECC_URE2 change management process nor have proper approval for implementation. An EMS infrastructure firewall administrator enabled changes to a firewall rule set on a ESP electronic access control point, to work around a non-emergency issue on an interface on the firewall. The firewall administrator needed the rule enabled to correct an issue with his VPN profile in order to support on-call remote access into the ESP. The VPN connection allowed remote users to gain remote access into the corporate network and gain access into the ESP after two-factor authentication was performed. WECC_URE2 enabled two more rules. These rule sets only impacted interfaces that do not have interactive access to any ESP and only impacted traffic between DMZs. WECC_URE2 enable a rule on the same ESP access point that controls the DMZ between the WECC cloud access to WECC_URE2, only impacting traffic between the DMZ and the WECC cloud. The root cause of this issue was WECC_URE2’s lack of a compliance process, and its failure to timely implement its access management procedures. | This instance of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to follow its change control process for four rule set changes for one access point that controls logical access into WECC_URE2's control center ESP. This non-compliance poses potential harm to WECC_URE2, because its failure to follow established change control procedures on an access point to the primary control center ESP could allow unauthorized, inappropriate, and incorrect changes, introducing vulnerabilities and unrestricted access into the ESP. WECC_URE2 implemented preventative controls, using two-factor authentication at the access point, for any communication from the corporate network into the ESP, preventing an unauthorized user from gaining access into the ESP. WECC_URE2 implemented user credential controls on the devices within the ESP and an additional layer of credentials to access the EMS application on the SCADA devices. It is unlikely that an unauthorized user would know both layers of credentials, and therefore, would not be able to access the CCAs and EMS application within the ESP. WECC_URE2 implemented detective controls, using an IDS sensor on the access point which would detect anomalous activity, and scans originating from the cooperate side of the access point going into the ESP interface of the access point. Also, WECC_URE2's control center is manned 24 hours a day 7 days a week by operators who are stationed on the SCADA devices, and has 24 hours a day 7 days a week logging and monitoring of the access point and devices within the ESP. The operators would likely detect any generation or transmission value changes and would be able to react to and correct changes. The devices would also detect login attempts and generate invalid login attempt alerts to EMS support personnel 24 hours a day 7 days a week. | To mitigate this issue of non-compliance, WECC_URE2 will: (1) review CIP-005 with its EMS personnel; (2) reviewing the current WECC_URE2 Change Control Process for all EMS CIP Cyber Assets; and (3) identify improvements to the current EMS Change Control Process.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013990 | CIP-006-3c R1 | R1 | WECC_URE2 submitted a Self-Report stating that it was in possible non-compliance with CIP-006 R1. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2 compliance personnel, and determined that WECC_URE2 failed to ensure that one janitorial contractor was provided unauthorized access by a second janitorial contractor, and did not sign the manual log for entry and exit into one PSP in the control center. Upon discovery of the issue, both janitorial contractors were terminated from the WECC_URE2 account, and all access was revoked. In addition, WECC_URE2 identified another issue of CIP-006 R1. A janitorial contractor entered a WECC_URE2 control center, but did not sign in. A review of the door force alarms via camera showed that the contractor was provided access by a second contractor. Upon discovery of the issue, both janitorial contractors were terminated from the WECC_URE2 account, and all access was revoked. The root cause of this issue is human error, and a lack of understanding by WECC_URE2’s janitorial contractors of WECC_URE2’s security processes at physical access points. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In two instances, janitorial contractors did not comply with WECC_URE2’s physical security plan, did not sign in, and allowed unauthorized access for other janitorial contractors. This issue of non-compliance poses potential harm to WECC_URE2 because failing to follow log-in procedures to the WECC_URE2 control center could potentially result in WECC_URE2 being unaware for a short period of time when contractors are entering and leaving the control center containing WECC_URE2's most important CCAs. WECC_URE2 implemented preventive and detective controls, because the control center was staffed 24 hours a day 7 days a week, and in each case, the contractor was in the line of sight of WECC_URE2 personnel the entire time. Additionally, the CCAs were password-protected and WECC_URE2 had trained the contractors in the proper way to handle CCAs. These controls would likely prevent the visitor from physically damaging the CCAs and also prevent the visitor from gaining logical access and thereby preventing misuse of the AGC. | To mitigate this issue of non-compliance, WECC_URE2: (1) revoked access and terminated the contractors involved; and (2) worked with its janitorial contractor to remove PAC access for the contractors in question; (3) updated the PAC master list; (4) provided compliance training; and (5) submitted a compliance training sign-in sheet as proof of training.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014405 | CIP-004-3a | R4 | WECC_URE3 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R4. The WECC Enforcement Department (Enforcement) determined that on WECC_URE3 granted physical access to one individual, but did not update the access list, as required by the Standard. WECC_URE3 discovered the oversight during a quarterly review of the Physical Access Rights List (who should have access), and the PACS list (who currently has access in the system). WECC_URE3 revoked access for the individual in question, and updated the list. The root cause of these issues of CIP-004-3a R4 is access management, leading to WECC_URE3’s failure to monitor and control access to its Critical Cyber Assets. | This issue posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to maintain its access lists to reflect a change in access for two personnel. Specifically, for one individual, WECC_URE3 failed to update the access list(s) within seven days; and for the second individual, WECC_URE3 failed to revoke physical access within seven days after such access was no longer required. These individuals had access to 3 PSPs, 20 ESPs, 55 CCAs, 16 ACMs, 22 PACs devices, and 2 Cyber Assets. This issue poses potential harm to WECC_URE3, because failing to revoke physical access when such access is no longer necessary could lead to unauthorized use of devices to cause harm to the BES. In this instance, the individuals had physical access to devices in the EMS ESP. With physical access to the EMS devices, a malicious person could plug a USB or CD containing malicious software (malware) into an EMS device that controls WECC_URE3's transmission to attempt to gain logical control of the device. WECC_URE3 implemented preventative controls. Specifically, an individual needs to pass a guard with the access list at the gate, before gaining access to the PSP that contains the EMS ESP. Although one individual still had physical access on his card, he was not on the access list and could not have been able to get past the guard. WECC_URE3 also uses anti-virus software on its devices, which could prevent a malware attack. WECC_URE3 implemented detective controls. Specifically, WECC_URE3 has personnel on site 24 hours a day 7 days a week, and the personnel would detect a malicious attempt to gain logical access to an EMS device through a malware attack. WECC_URE3 also uses anti-virus software to detect a malware attack. Further, WECC_URE3 has video surveillance, which could also detect an attempt to gain unauthorized logical access to an EMS device. Finally, WECC_URE3 uses an Intrusion Detection System (IDS), which, like the anti-virus, could detect a malware attack. WECC_URE3 implemented compensating controls. Specifically, both individuals in question were in good standing at WECC_URE3. WECC_URE3 also has a policy in place that employees cannot plug in any removable media (i.e., USB or CD) to any device. Both employees were up-to-date on training, and as they were both in good standing, there is a low likelihood that either would attempt any malicious activity. | To mitigate this issue, WECC_URE; 1) revoked access for both individuals; and 2) implemented a process to have one person make access right change and a different person to validate changes. WECC has verified the completion of all mitigation activity.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013591 | CIP-003-3 | R4 | WECC issued an Annual Notice of Requirement to Self-Certify. WECC_URE4 self-certified its possible non-compliance with CIP-003-3 R4. A WECC SME reviewed the Self-Certification, issued data requests, and conducted an interview with WECC_URE4 personnel. According to the SME findings, WECC_URE4 failed to assess its adherence to its Critical Cyber Asset (CCA) information protection program, document the results, and implement an action plan to remediate deficiencies identified during the assessment, as required by CIP-003-3 R4. Specifically, WECC_URE4 did not have sufficient evidence to show it had performed a review of its adherence to its CCA information protection program for the 2012 calendar year. WECC_URE4 stated that it had appropriate evidence for all other calendar years including 2013. WECC_URE4 stated that the possible cause of the issue was confusion about responsibilities resulting from a new manager over CIP-003. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the self-certification information and the SME’s findings and determined that WECC_URE4 had an issue with CIP-003-3 R4 for its failure to assess its adherence to its CCA information protection program, document the results, and implement an action plan to remediate deficiencies identified during the assessment. Enforcement determined that the issue began the first day of the year that WECC_URE4 did not have sufficient evidence to show it had performed a review of its adherence to its Critical Cyber Asset information protection program. Enforcement also notes that WECC_URE4 submitted a mitigation plan for this issue and WECC_URE4 completed the mitigating activities. WECC verified completion of mitigating activities. | In this instance, WECC_URE4 failed to assess its adherence to its CCA information protection program during the calendar year. WECC_URE4’s failure to assess its adherence to its CCA information protection program could lead to WECC_URE4 not knowing if its personnel understood and were following its program to protect sensitive information associated with CCAs. If WECC_URE4 personnel were not following its program, unauthorized individuals would have the potential to gain access to sensitive information and could use that information to attack WECC_URE4's controls. WECC_URE4 implemented good preventive controls to prevent unauthorized individuals from gaining access. Specifically, WECC_URE4 stated that its process ensures sensitive information is classified and has the confidential watermarking. WECC_URE4 also stated that its process ensures that all hard copy sensitive data is stored under lock and key. WECC_URE4’s process ensures that all soft copy sensitive data is stored on secure drives, for which access is only given to individuals with proper approval. Additionally, WECC_URE4 requires that a written form be filled out and approved if an individual needs to gain access to sensitive information. WECC_URE4 also requires individuals to meet PRA and CIP Training requirements prior to gaining access to sensitive information and for contractors to have a non-disclosure agreement. WECC_URE4 also implemented good detective controls to detect unauthorized individuals from gaining access. Specifically, WECC_URE4 tracks individuals that have access to sensitive information in its CIP PI Database. WECC_URE4 generates quarterly reports from its CIP PI Database and reviews the information to ensure that only necessary individuals maintain access. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities: Establishment of a notification to the Process Owner of the Standard, reminding them of the requirement to document the adherence to the CCA information protection program. This was done using task management software. Notification will be recurring and has an attached escalation feature to notify others if not completed in advance end of the year. Review of adherence to the program will be integrated into WECC_URE4's routine CIP Process Owner meetings that occur monthly throughout the year. WECC has verified completion of WECC_URE4’s mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014121 | CIP-006-3c | R1 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-006-3c Requirement 1. In the Self-Report, WECC_URE4 reported that it failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. Specifically, WECC_URE4 granted physical access to the Backup Control Center (BUCC) that contained ten Energy Management System (EMS) workstations to four contractors. The individual granting access to this Physical Security Perimeter (PSP) accidentally gave physical access to an entire group instead of only the appropriate individuals within the group. This allowed four unauthorized contractors to have unescorted physical access to the BUCC. As a result, WECC_URE4 reported that it had a possible issue with CIP-006-3c R1. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-006-3c R1.4. Specifically, the SME determined that WECC_URE4 failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R1.4. Specifically, Enforcement determined that WECC_URE4 failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. Enforcement also notes that WECC_URE4 submitted a mitigation plan and WECC_URE4 completed the mitigating activities. | WECC_URE4 failed to grant access to only authorized individuals. Specifically, WECC_URE4 granted four contractors physical access to the BUCC that contained ten EMS workstations. The unauthorized access of the four contractors had the potential to be used to gain physical access to the BUCC and damage or destroy the 10 EMS workstations. The unauthorized access could also allow the four contractors to log into the EMS workstations and attempt to insert a worm or virus that could impact the network or functionality of the workstations. The four contractors also could potentially work with a disgruntled employee who had access to the BUCC and was willing to share his or her account information to gain logical access and attempt to remotely access the EMS workstations within the Primary Control Center (PCC). WECC_URE4 implemented good preventative controls to prevent the physical access from occurring. Specifically, WECC_URE4 never granted logical user access to the ten EMS workstations within the BUCC to the four contractors. WECC_URE4 also implemented redundant EMS workstations in the PCC to reduce the negative impact of one or all of the EMS workstations being damaged or destroyed within the BUCC. Additionally, WECC_URE4 also maintains the PCC and BUCC in an active and passive state respectively, meaning the BUCC could not become the PCC until the PCC was either shut down or unavailable. WECC_URE4 disabled the ability to run mass storage devices on the EMS workstations to prevent the installation of malicious software. WECC_URE4 also implemented detective controls to detect the unauthorized physical access from occurring. Specifically, WECC_URE4 implemented processes to investigate suspicious activity on the EMS workstations. If a contractor was given a valid user account and password, the account logs would track the valid user's activity on a daily basis. WECC_URE4 also implemented anti-virus software that would send an alert message to the appropriate personnel if malicious software was detected. Additionally, WECC_URE4 has quarterly reviews of employees and contractors that have full access to the BUCC to limit the likelihood that unauthorized access to the EMS workstations is undetected. WECC_URE4 discovered this issue during one of these quarterly reviews. As another detective control, WECC_URE4's badges are color coded based on several factors, including whether the individual is an employee or contractor and whether the individual has full or restricted access. Employees can detect whether someone should be in the BUCC based on the color code. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities: WECC_URE4 removed the PSP doors from the four contractor’s access profile. WECC_URE4 parsed the existing physical control system into two separate physical systems, one for CIP (PACM) operation and the other for business operation. This will in turn separate the administrative tasks/entries which will prevent or minimize the potential for future access modification errors. WECC has verified completion of WECC_URE4's mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014391 | CIP-006-3c | R2 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-006-3c R2. In the Self-Report, WECC_URE4 reported that it failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a Technical Feasibility Exception (TFE) for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. As a result, WECC_URE4 reported that it had a possible issue with CIP-006-3C R2. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-006-3c R2. Specifically, this possible issue was originally part of NERC Violation ID WECC2014013931. The original scope of NERC Violation ID WECC2014013931 consisted of 27 devices: 24 EACM devices and 3 PACS devices. The WECC SME determined that the PACS devices should be removed from the scope of NERC Violation ID WECC2014013931 and should be a separate possible issue under CIP-006-3C R2. The SME determined that WECC_URE4 failed file a TFE for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R2. Specifically, Enforcement determined that WECC_URE4 failed to file TFEs for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. Enforcement determined that the issue began on the day that CAN-0017 was issued, verifying that a TFE needs to be filed to show compliance in enforcing password complexity for devices that cannot fully meet all requirements. WECC_URE4 is currently in the process of submitting a Mitigation Plan; however, prior to creating the new possible issue, WECC_URE4 had submitted a Mitigation Plan for NERC Violation ID WECC2014013931, stating mitigation was completed on or before September 30, 2014. The mitigation plan was accepted. At the time the Mitigation Plan was submitted, the three PACS devices were still within scope of NERC Violation ID WECC2014013931. | In this instance, WECC_URE4 failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a TFE for three PACS servers that are incapable of enforcing the password complexity requirements. The servers manage door operations. Failing to file a TFE for devices not technically capable of enforcing password complexity requirements could lead to WECC_URE4 not knowing of vulnerabilities on those devices. As compensation for any vulnerability with these devices, WECC_URE4 implemented strong compensating controls. Specifically, WECC_URE4 has a manual procedure by which the changing and validation of password complexity is observed and signed off on by the appropriate supervisor. WECC_URE4 also has a procedure written that defines the requirement of CIP-007 R5.3.1 and CIP-007 R5.3.2. Utilizing the Vendor Firmware, and HP iLo to proctor the requirements with the manual procedure ensures compliance. In addition, WECC_URE4 has logging, monitoring, and alarming on all account activity within the systems affected. WECC_URE4 also controls access through authorization and accounting and provide appropriate ports and services controls, patch management, and malicious software prevention tools. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 has not yet submitted a Mitigation Plan to address this issue. WECC_URE4 is required to submit a plan for mitigating this issue. However, prior to creating the current possible issue, WECC_URE4 had submitted a Mitigation Plan for NERC Violation ID WECC2014013931 and at the time the Mitigation Plan was submitted, the three PACS devices were still within scope of NERC Violation ID WECC2014013931. In that mitigation plan, WECC_URE4 stated it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the CAN-0017 TFE submitted to cover the assets not capable of the Technical Controls. WECC_URE4 also submitted evidence of password change and account renaming where applicable. WECC verified completion of the mitigating activities associated with WECC2014013931.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013935 | CIP-007-3a | R4 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-007-3a R4. In the Self-Report, WECC_URE4 reported that it failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter (ESP) by failing to file Technical Feasibility Exceptions (TFEs) on or before the date the devices were installed. Specifically, WECC_URE4 failed to amend its original TFEs when adding three new devices to an ESP. The three devices that WECC_URE4 failed to file TFEs for are Cisco switches that are used to manage WECC_URE4’s ESP. As a result, WECC_URE4 reported that it had a possible issue with CIP-007-3a R4. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-007-3a R4. Specifically, the SME determined that WECC_URE4 failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the ESP by failing to file TFEs on or before the date the devices were installed. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-007-3a R4. Specifically, Enforcement determined that WECC_URE4 failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the ESP by failing to file TFEs on or before the date the devices were installed. Enforcement determined that the issue began the day that WECC_URE4 installed the switches without filing the TFEs. | WECC_URE4 failed to amend its original TFEs when adding three new Cisco switches to an ESP. Failing to submit TFEs for new devices could result in misidentifying the critical role or function that these devices serve to the ESP. The two ESPs in scope contain devices that are essential for WECC_URE4 to reliably operate its EMS, which manages WECC_URE4's area load peaking, with 19 interconnections to neighboring BAs. WECC_URE4 implemented strong preventative controls to prevent the weakening of the ESP security. Specifically, WECC_URE4 implemented two primary and one backup Cisco switches that have an embedded layer of security within the operating system (IOS). The Cisco switches also have intelligence within the IOS to prevent unknown Media Access Control (MAC) addresses from connecting to the network preventing an unauthorized user with a laptop to connect to the switches. WECC_URE4 also implemented strong detective controls to detect the weakening of the ESP security. Specifically, WECC_URE4 implemented a Security Information and Event Management (SIEM) that is used to monitor various network devices, such as firewalls, switches, and routers within the ESP. If an unauthorized user installed a virus into the ESP, the current detective and preventive measures would likely block the virus or other malicious code from causing harm. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 stated that it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the vulnerability assessment in 2013 as well as provided a current “baseline” of authorized ports and services for the three switches. WECC_URE4 staggered deployment by using standby/testing systems for testing of new AV signatures. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013931 | CIP-007-3a | R5 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-007-3a R5. In the Self-Report, WECC_URE4 reported that it failed to file a Technical Feasibility Exception (TFE) for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3. As a result, WECC_URE4 reported that it had a possible issue with CIP-007-3a R5. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-007 R5.3. Specifically, the SME determined that WECC_URE4 failed to file a TFE for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. WECC_URE4 failed to file the TFEs for 24 Electronic Access Control and Monitoring (EACM) devices that are incapable of enforcing the password complexity requirements required by CIP-007 R5.3. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-007 R5.3. Specifically, Enforcement determined that WECC_URE4 failed to file a TFE for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Enforcement determined that the issue began on the day that WECC_URE4 failed to file a TFE to show compliance in enforcing password complexity for devices that cannot fully meet all requirements. | WECC_URE4 failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a TFE for 24 EACM devices that are incapable of enforcing the password complexity requirements. Failing to file a TFE for devices not technically capable of enforcing password complexity requirements could lead to WECC_URE4 not knowing about vulnerabilities on those devices. WECC_URE4 implemented strong compensating controls to compensate for these devices. Specifically, WECC_URE4 has a manual procedure to observe and obtain approval by the appropriate supervisor the change and validation of password complexity. WECC_URE4 also has a procedure that defines the requirement of CIP-007 R5.3.1 and R5.3.2. Utilizing the vendor firmware to proctor the requirements with the manual procedure ensures compliance. WECC_URE4 also has logging, monitoring, and alarming on all account activity within the systems affected. Additionally, WECC_URE4 controls access through authorization, accounting, providing appropriate ports and service controls, patch management, and malicious software prevention tools. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 stated that it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the CAN-0017 TFE submitted to cover the assets not capable of the Technical Controls. WECC_URE4 also submitted evidence of password change and account renaming where applicable. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014000 | CIP-009-3 | R1 | WECC conducted on Combo On-site Audit of WECC_URE4’s facilities. At the Audit, the WECC Audit Team identified a possible issue of CIP 009-3 R1. The WECC Audit Team determined that WECC_URE4 failed to annually review the recovery plan. Specifically, WECC_URE4 created a recovery plan for Critical Cyber Assets. The recovery plan addressed the minimum criteria outlined in each sub-requirement of Requirement 1, but WECC_URE4 did not review the plan. WECC_URE4 changed its process from including annual reviews in the revision history to using the DocMinder system. WECC_URE4 had one DocMinder task for both annual review of the plan and annual exercise of the plan. WECC_URE4 separated those processes into two separate tasks within DocMinder. Based on a review of an audio file of the exercise of the plan and the DocMinder output, the WECC audit team determined that there is no evidence that the plan was appropriately reviewed. This resulted in WECC_URE4 having a possible issue of CIP 009-3 R1 for failing to annually review the recovery plan. The Audit Team forwarded its findings to Enforcement for review. Enforcement reviewed the Audit Team’s findings and determined that WECC_URE4 had an issue with CIP 009-3 R1. Specifically, Enforcement determined that WECC_URE4 failed to annually review the recovery plan. Enforcement determined that the issue began the day that after one year from the last review of the plan. Enforcement also determined that the issue ended the date that WECC_URE4 annually reviewed the plan. | WECC_URE4 failed to annually review the recovery plan. Specifically, WECC_URE4 created a recovery plan for Critical Cyber Assets. The recovery plan addressed the minimum criteria outlined in each sub-requirement of Requirement 1, but WECC_URE4 did not review the plan. WECC_URE4 owns and operates two Hydro Electric facilities with 10 generators at each facility, with an aggregate capacity of about 2000 MW. Additionally, WECC_URE4 operates two hydro units off irrigation canals. Despite WECC_URE4’s failure to review the recovery plan, WECC_URE4’s recovery plan is well documented and there were no substantial changes impacting the plan during the noncompliance time frame. Annual exercises of the plan were also conducted each year, even though the plan was not reviewed. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities on: A task notification that details the recovery plan sections under review and confirms the performance of the review will be dispatched as a recurring reminder on an annual basis. A Review block will be incorporated to the Recovery Plan showing the date of annual review. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014097 | CIP 007-1 | R2 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R2. During this time,WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R2. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert also reviewed WECC_URE5’s self-report and found that it failed to enable only those ports and services required for normal and emergency operations. Specifically, WECC_URE5 failed to submit a complete list of TFE’s for 5 devices in scope. These devices are SCADA workstations and logical controllers. The WECC SME forwarded this information to Enforcement for review. Enforcement reviewed the self-report and the SME findings. Enforcement determined WECC_URE5 failed to enable only those ports and services necessary for normal and emergency operations. Further, WECC_URE5 failed to submit a complete list of TFE’s that include the 5 devices in scope. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to enable only those ports and services necessary for normal and emergency operations. Specifically, WECC_URE5 failed to submit a complete list of TFE’s for 5 devices in scope. Failing to submit TFEs in a timely manner could result in the proper compensating measures not being applied to the SCADA system. Since these devices cannot disable unnecessary ports, WECC_URE5 may be unaware of all the ports the devices use and which ports may be vulnerable to attack. Also, the access point may not be setup correctly to compensate for the unnecessary ports and allow unnecessary communication into the Electronic Security Perimeter (ESP). On the other hand, WECC_URE5 implemented some compensation controls such as placing these devices in a physically secure location. Only authorized personnel have access. The network containing these devices is monitored by the WECC_URE5 IDS system and network services provided to these devices are controlled by a role-based policy system. Further, WECC_URE5 developed, documented, and implemented procedures to address ports and services from both a physical network port perspective and from a TCP and UDP ports and services perspective. This procedure is contained in the “CIP-007 System Security Management Program” document, Section 8.2. It is WECC_URE5’s commitment to ensure that only those ports and services required for normal and emergency operations are enabled when an asset is in service within the Electronic Security Perimeter. The procedures contained in Section 8.2 is provided to WECC_URE5 staff to guide their actions based on a “locked-down” approach that does not compromise necessary functionality or system availability. Also, per CIP-007 R2.1, it is WECC_URE5’s intent that all Secure Networks role assignments be made in such a way that they deny access by default, so that explicit permissions must be specified. The default role for each physical port in WECC_URE5’s network shall be “New User Lockdown”, unless it is a purpose-specific port (not a regular user port) and authentication must be enabled. To the extent that it is technically feasible, the assignment of default roles for ports shall be made prior to the deployment of the equipment for production use. When setting up new Critical Cyber Asset software or hardware at WECC_URE5, it is required that all unused services and ports are disabled. Starting from a complete locked-down approach allows for only the required services and ports to be enabled. For computer-based assets, WECC_URE5 personnel evaluate the necessary ports and services required for operations (with Vendor input), and disable those who do not meet criteria for the application. For non-computer-based assets, staff assesses what ports and services must remain enabled based on their review of the configuration screens on the device. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted a request for TFE #2014-WECC-TFE02513 on 6/26/2014 to cover three devices and 2014-WECC-TFE02507 on 6/25/2014 to cover two devices; 2) implemented a tracking spreadsheet showing all requirements for which a device might have a technical infeasibility, and all devices will be evaluated before deployment, and; 3) involved more of its personnel in the compliance procedure development process to further enhance a culture of compliance. WECC has verified the completion of all mitigation activity.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014013956 | CIP 007-1 | R3 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R3. During this time, WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R3. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert (SME) also reviewed WECC_URE5’s self-report and issued a data request to further clarify information about the devices in scope. The WECC SME found that WECC_URE5 failed to file a TFE for (4) devices consisting of an RTU, two plant voltage control and monitor devices, and a workstation that can control the total plant load. The entity also failed to document applicability of security patches for six devices, consisting of two control room interface devices for plant status, control, and alarming; one interface development device, one PACS server, and two PACS workstations. The entity also failed to check for security patches for 17 devices, consisting of two control room interface devices for plant status, control, and alarming; one interface development device, one PACS server, two PACS workstations, nine PACS panels, one device that controls breaker status, relay alarms, and other plant statuses; and one device that controls transformer status and alarms, station service status and alarms, and other plant statuses. As a result of these findings, the WECC SME found that WECC_URE5 failed to document and implement a security path management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). The WECC SME forwarded these findings to Enforcement for review. Enforcement reviewed the information provided in the self-report and from the WECC SME and determined that WECC_URE5 failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP either separately or as a component of the documented configuration management process specified in CIP 006 R6. Further, WECC_URE5 failed to file a TFE for four devices, failed to document applicability of security patches for 6 devices, and failed to check for security patches for 17 devices. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP either separately or as a component of the documented configuration management process specified in CIP 006 R6. Failing to document and implement a security patch management program could lead to vulnerabilities on devices because patches were not applied. If a malicious person knew of new patches that fixed vulnerabilities (something that can be deduced by looking at the patch information), he or she could scan devices on the network in order to obtain information about the device, specifically the version of software on the device (what is updated by a patch or upgrade). If the person is able to obtain this information, he or she could know if a patch or upgrade has been applied. If a scanned device is discovered to not have had the latest patch or upgrade applied, the person could use malicious software to exploit that vulnerability in attempt to take control of the device. In this case, two of the devices in scope are sources for the Plant Load Set Point. WECC_URE5 implemented strong preventative controls to prevent the above consequence from occurring. Specifically, it implemented MAC-based authentication, where any device with an unknown MAC address is locked down to prevent it from communicating with any of the devices on the network until the MAC address is authenticated. This would prevent someone from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. Furthermore, WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically,WECC_URE5 has operators manning the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 would likely correct the condition as WECC_URE5 implemented strong corrective controls. Specifically, WECC_URE5 operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set Point sources (see above) to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted the following TFE's 2014-WECC-TFE02514 and 2014-WECC-TFE02512 to cover the four (4) devices consisting of an RTU, two plant voltage control and monitor devices, and a workstation that can control the total plant load; 2) created documentation to track assessment of patch for IBM compatible devices and train employees on compliance standards and what is expected of them; 3) used a third-party software to track patch assessment tracks to remind technicians when to assess patches, which paperwork is required, and what approval is needed; and 4) trained its personnel to address the root cause of lack of compliance understanding.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014098 | CIP 007-1 | R4 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R4. During this time, WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R4. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert discussed this possible noncompliance with WECC_URE5. WECC_URE5 stated that it had 29 devices that were technically not capable of implementing AV/malware prevention tool and were not included in a TFE. After reviewing the self-report and speaking with WECC_URE5, the WECC SME found that WECC_URE5 failed to submit a complete list of TFEs that included 29 devices in scope. The WECC SME forwarded this information to Enforcement for review. Enforcement reviewed the information from the self-report and the WECC SME and determined that WECC_URE5 failed to submit a complete list of TFEs per CIP 007-1 R4 for 29 devices which included GMS workstations, PLCs, PACM control panels, firewalls, and a Firewall Management server. Therefore, WECC_URE5 has an issue with CIP 007-1 R4. This issue began the initial date when the TFE’s were supposed to be filed to the day WECC_URE5 completed its filing for the 29 devices. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to submit a complete list of TFEs per CIP 007-1 R4 for 29 devices which included GMS workstations, PLCs, PACM control panels, firewalls, and a Firewall Management server. Failing to submit a complete list of TFEs that included the 29 devices in scope could result in misidentifying the critical role or function that devices serve in the ESP. Mis-identifying the role or function of these devices could result in adding incorrect compensating measures that would adequately address the weakness posed by the device not being technically capable of implementing malware prevention tools. The 29 devices in scope are CCAs that are vital for the management of the SCADA systems. WECC_URE5 implemented strong preventative controls to prevent consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication, which prevents any unauthorized device with an unrecognized MAC address from communicating with any of the devices on the network. This would prevent personnel from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 implemented strong detective controls to detect the above consequence. Specifically, the entity has operators manning the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, the entity would have likely corrected the condition as the entity implemented strong corrective controls. Specifically, the entity's operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. The entity also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set point sources to be independent of one another. Therefore, if one device were to be compromised, the entity could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1);submitted TFEs for the 29 devices in scope under the following ID’s: 2010-WECC-TFE00694-4, 2014-WECC-TFE02506, 2014-WECC-TFE02511, 2014-WECC-TFE02516, 2014-WECC-TFE02517, and 2014-WECC-TFE02518 WECC has verified completion.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014099 | CIP 007-1 | R5 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R5. During this time, WECC Auditors were conducting a review of WECC_URE5's compliance with CIP-007-1 R5. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert (SME) reviewed WECC_URE5's self-report and discussed this possible noncompliance with WECC_URE5. WECC_URE5 stated that it had 9 Critical Cyber Assets (CCAs) that were technically not capable of implementing technical and procedural controls that enforce access authentication of, and accountability for, all user activity and were not included in the original Technically Feasible Exceptions (TFEs) filed. Therefore WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters as required by CIP 007 R5. The WECC SME forwarded this information to Enforcement. Enforcement reviewed the SME’s and WECC_URE5's information and determined that WECC_URE5 failed to implement and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. Further, WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters. Specifically, WECC_URE5 did not file TFEs for 9 devices incapable of enforcing the password complexity requirements of CIP-007 R5. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters. Specifically, WECC_URE5 did not file TFEs for 9 devices incapable of enforcing the password complexity requirements of CIP-007 R5. Failing to submit a complete list of TFEs could result in misidentifying the critical role or function that devices serve within the Electronic Security Perimeter (ESP). Misidentifying the role or function of these devices could result in adding incorrect compensating measures such as basic input and output system (BIOS) updates then the Kernel of the Operating System (OS) may become corrupted or incompatible, thus rendering the OS incapable of booting. On the other hand, WECC_URE5 did implement strong preventative controls to prevent the above consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication, which prevents any unauthorized device with an unrecognized MAC address from communicating with any of the devices on the network. This could prevent personnel from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which could help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically, WECC_URE5 has operators inside the Physical Security Perimeters (PSPs) 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 could have likely corrected the condition as it implemented strong corrective controls. Specifically, WECC_URE5's operators have the ability to switch the plant into 'Manual' mode, which could prevent any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, it set up the two Plant Load Set point sources to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. | To mitigate this issue, WECC_URE5: 1) submitted requests for TFEs #2014-WECC-TFE02506 and TFE02511. WECC has verified completion.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014006 | CIP 007-1 | R6 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R6. During this time, WECC Auditors were conducting a review of WECC_URE5's compliance with CIP-007-1 R6. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. Further, a WECC Subject Matter Expert (SME) also reviewed WECC_URE5's self-report and found that it failed to fully implement automated tools or organizational controls to monitor system events related to cyber security, as technically feasible. Specifically, WECC_URE5 failed to file a TFE for 16 devices consisting of, nine (9) PACS panels, three PACS interfaces, two controllers that provide breaker status, relay alarms, and other plant statuses; one device that provides communication between the SCADA master and substation end point-devices, and a RTU. WECC_URE5 also failed to review logs for nine (9) devices, consisting of two interface devices for plant status, control, and alarming; one interface development station, one PACS server, two PACS workstations, and three workstations that can control plant load. The WECC SME forwarded these findings to Enforcement for review. Enforcement reviewed the self-report and the SME’s findings and determined that WECC_URE5 failed to ensure that all Cyber Assets within the ESP implement tools or process controls for monitoring cyber security-related system events. Specifically, WECC_URE5 failed to file a TFE for 16 devices consisting of, nine (9) PACS panels, three PACS interfaces, two controllers that provide breaker status, relay alarms, and other plant statuses; one device that provides communication between the SCADA master and substation end point-devices, and a RTU. WECC_URE5 also failed to review logs for nine (9) devices, consisting of two interface devices for plant status, control, and alarming; one interface development station, one PACS server, two PACS workstations, and three workstations that can control plant load. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to ensure that all Cyber Assets within the ESP implement tools or process controls for monitoring cyber security-related system events, as technically feasible. Specifically, WECC_URE5 failed to file TFE for 16 devices. The root cause of the TFE portion of the issue was a lack of communication between those that file the TFEs and those that work with the devices requiring the TFEs. WECC_URE5 also stated that there was not one person designated to see the TFE-filing process from start to finish, adding to the lack of communication. For the log review portion of the issue, the entity stated that the root cause was a lack of compliance understanding due to a lack of training. Failing to ensure that, where technically feasible, CAs in the ESP has tools or processes to monitor cyber security-related system events and review these logs could lead to malicious activity on the network being undetected. Someone could scan devices on the network to look for vulnerabilities on the device. If vulnerabilities are discovered, the person could use malware to launch an attack and possibly exploit the vulnerability. If the attack succeeds, the person could take control of the devices. This unknown person could also scan other devices in scope to look for vulnerabilities and launch an attack with malware to attempt to take control of the device. If the attack was successful and the person able to take control of the device, he/she could use the device to scan other devices connected to it to look for vulnerabilities. If vulnerabilities are discovered, the person could launch an attack to try to get control of the device. If successful, the person could repeat the process of scanning for vulnerabilities, launching an attack against the device, and taking control of the device until a device controlling the generation is compromised. WECC_URE5 implemented strong preventative controls to prevent the above consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication. With this authentication, any device with an unknown MAC address is locked down to prevent it from communicating with any of the devices on the network until the MAC address is authenticated. This would prevent someone from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically, the entity has operators at the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 would likely correct the condition as WECC_URE5 implemented strong corrective controls. Specifically, WECC_URE5's operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set Point sources to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 could also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) filed TFEs for the 16 devices in scope under TFE Requests 2014-WECC-TFE02503, 2014-WECC-TFE02504 and 2014-WECC-TFE02505 and on June 26, 2014 under TFE Requests 2014-WECC-TFE02508 and 2014-WECC-TFE02515; 2) installed Adaptive Log Exporter on devices in scope that are capable using automated logging, configured SIEM to accept logs from these devices in scope, developed processes for manually reviewing logs for devices not capable of using automated logging, and trained staff on changes.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012480 | CIP-002-3 | R1 | During a Compliance Audit, WECC determined that WECC_URE6 was in non-compliance with CIP-002-3 R1, because WECC_URE6 failed to consider all asset types listed in R1.2.1 through R1.2.7 in its risk-based assessment of Critical Asset Identification. According to the Audit Team, WECC_URE6 changed its Critical Asset identification methodology from a risk-based assessment methodology (“RBAM”) consistent with Version 3 of the Standard, to the bright line criteria methodology set out in Version 4, while Version 3 was still in effect. Specifically, WECC_URE6 changed its criteria in section 5.1.1.2 of its RBAM from a threshold of 300 MW to 1500 MV or 1000 MVAR. Both methodologies determined that WECC_URE6 did not have any Critical Assets. Enforcement reviewed the Audit Team’s findings and the evidence WECC_URE6 produced at the Audit, and determined that WECC_URE6 had an issue with CIP-002-3 R1 for failing to identify and document a risk-based assessment methodology to identify its Critical Assets, compliant with Version 3 of the CIP Standards. However, because WECC_URE6'S generation capacity is 56 MW, the criteria adjustment did not change the determination that WECC_URE6 did not have any Critical Assets. The root cause of the non-compliance was WECC_URE6's lack of compliance understanding leading to its failure to monitor the CIP Version changes through the NERC and FERC processes. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. When WECC_URE6 changed its methodology from its initial Critical Asset Identification Procedure approach to a methodology based on CIP-002-4 Attachment 1 criteria, it failed to identify its Cyber Assets, as required by Version 3 of the Standard. This issue of non-compliance posed potential harm to WECC_URE6, because if its Cyber Assets were not correctly identified, they may not be protected. However, the WECC Audit Team confirmed that either methodology returned null lists for Cyber Assets and associated Critical Cyber Assets. | WECC_URE6 submitted a mitigation plan addressing this issue of non-compliance. To mitigate this issue, WECC_URE6 revised its RBAM to reflect the 300 MW threshold referenced in CIP-002-3 R1.2.5 (Version 3). By revising its RBAM, WECC_URE6 is minimizing the probability of further violations of CIP-002-3 R1.