## Public CIP SNOP Posting
Date | Regulatory Authority | Docket No. | Region | Registered Entity Name | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation (For purposes of this document, each violation at issue is described as a “violation,” regardless of its procedural posture and whether it was a possible, or confirmed violation.) | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
2017-11-30 | FERC | NP18-4-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016016649 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-6 R2 Part 2.3. Specifically, for the first instance, WECC_URE1 reported that on September 6 one of its CIP Leads reviewed the security patch status and notified the System Administrator they had reached the final day of a 35-day requirement to install applicable security patches. The CIP Lead evaluated the security patch in question on August 2. The Systems Administrator opened a change control ticket to install the applicable patch, and on September 6 completed the installation through automated means, which was within the 35-calendar day requirement. However, six days later when closing out the change control ticket, the System Administrator discovered that the applicable security patch was not installed on one Protected Cyber Asset (PCA) server associated with WECC_URE1's Medium Impact Bulk Electric System (BES) Cyber System (MIBCS) located within its Control Center. The System Administrator immediately installed the applicable security patch. The automated process that deployed security patches relies on a list regarding configuration analysis. Prior to this security patch deployment, a server that was scheduled for decommissioning was deleted from the list, but was not physically removed from the Electronic Security Perimeter (ESP). Therefore, when the automated process was launched, the server in scope was not updated. For the second instance, while a WECC_URE1 internal auditor was investigating the first instance, it was discovered that another applicable security patch was not installed within the 35-calendar day requirement. The CIP Lead assessed a firmware update for five Physical Access Control Systems (PACS) for applicability. One PACS was associated with WECC_URE1's MIBCS located within its Control Center, and four were associated with a MIBCS located within another Control Center. The technician responsible for installing the firmware update should have completed the install within 35 days; however, the update was not installed until two days after the deadline. The tracking log used to track security patch evaluation and installation, initially listed the wrong individual assigned to install the security patch. The individual did not notify anyone or take action because it was outside their area of responsibility. WECC determined that WECC_URE1, in two separate instances for the assets in scope, failed to take action to apply the applicable patches, create a dated mitigation plan, or revise an existing mitigation plan pursuant to CIP-007-6 R2 Part 2.3. The root cause of both instances was a less than adequate process or procedure for ensuring that compliance is maintained during security patching and change management. | CIP-007-6 | R2; Part 2.3 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The server in scope had no BES control capability; was located in WECC_URE1's Control Center; was scheduled for decommissioning; and the security update in question was for a portable application that is not activated at system startup, as a result, there were no open ports or services. The five PACS in scope reside within secure locations with defense-in-depth controls to prevent access. Three of the PACS were serial devices and not capable of remote access. | For the first instance - when WECC_URE1 should have taken action for a security patch assessed as applicable For the second instance - when WECC_URE1 should have taken action for a security patch assessed as applicable | For the first instance - when WECC_URE1 applied the security patch For the second instance - when WECC_URE1 applied the security patch | $22,000 (for WECC2016016649 and WECC2017016930) | Self-Report | To mitigate both instances in this violation, WECC_URE1: 1) applied the security patches; 2) revised its procedures to include formal decommissioning steps and timelines, and instructions not to remove assets from the configuration tools asset list until they are completely decommissioned and inactive; 3) provided formal training on the revised procedures and re-training on the security patch and change management processes; 4) implemented an automated workflow to provide security patch information and status to personnel and management; and 5) implemented a change management peer review to act as a control for ensuring changes are reviewed and accurate prior to the change. | 2017-04-19 | 2017-06-27 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's CIP-007 compliance history in determining the penalty and disposition track. WECC considered WECC_URE1's CIP-007 compliance history to be an aggravating factor in the penalty determination.
2017-11-30 | FERC | NP18-4-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017016930 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5.2.3. Specifically, WECC_URE1 reported that there was a communication system failure between two CIP Cyber Assets. The System Administrator assigned to resolve this issue contacted the vendor for support. Several of the vendor’s employees were authorized for remote CIP access under WECC_URE1's access management program. This authorization allowed approved vendor employees to provide support to WECC_URE1 as needed. WECC_URE1 determined that an unauthorized vendor employee gained remote access to a single Non-Critical Cyber Asset (NCCA) by using the remote access credentials of another employee from the same vendor who was authorized to have said access. The unauthorized vendor employee had access to CIP Cyber Assets for six days. WECC_URE1 determined that the unauthorized vendor employee asked for a shared account password, for which he was not authorized, and which a WECC_URE1 System Administrator sent him via email to gain access to the same NCCA. Additionally, on the same day, this same vendor employee notified the System Administrator via email that he had used this access to create a system account, and uninstalled and reinstalled software on the NCCA. WECC determined that WECC_URE1 failed to manage user account access to only those individuals who were authorized. The root cause of this issue was a less than adequate policy for managing user account access and a failure to follow documented internal procedures. | CIP-007-3a | R5; R5.2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The system accessed by the unauthorized vendor employee has no control capability of any BES-related system. The vendor and the vendor employee are known resources for the system and under contract for system support. WECC_URE1 had implemented controls to reduce the likelihood of harm. These controls consisted of two-factor token authentication; encrypted sessions controls; and ingress/egress protocol traffic controls. WECC_URE1 had terminal server access portal controls to prevent unauthorized source systems from accessing Cyber Assets; control sessions to Cyber Assets; controls to protect the confidentiality of the data streams; and controls to limit unauthorized sessions from occurring. WECC_URE1 had documented policies, procedures, and training to manage electronic remote access and system accounts. Additionally, the duration of the issue of noncompliance was limited to five days and the third-party contractor employee did not have electronic remote access to any other Cyber Assets. | when WECC_URE1 granted to one vendor employee unauthorized electronic access to a NCCA server | when WECC_URE1 removed the unauthorized electronic access and the shared user account | $22,000 (for WECC2016016649 and WECC2017016930) | Self-Report | To mitigate this violation, WECC_URE1: 1) removed the unauthorized access from the third-party contractor employee; 2) removed the unapproved software and deleted the unapproved system account that was added; 3) removed physical and electronic CIP access from the employee who did not follow documented procedures and removed them as a System Administrator; and 4) updated its interactive remote access procedure to only allow managers to issue remote access tokens. | 2016-11-09 | 2017-07-18 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's CIP-007 R5 compliance history in determining the penalty and disposition track. WECC considered WECC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2017-10-31 | FERC | NP18-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002165 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it had a possible issue of noncompliance of CIP-006-1 R1. A WECC SME reviewed the supplemental data and conducted telephone interviews with WECC_URE1's compliance personnel. Based on the interviews with WECC_URE1, the WECC SME confirmed WECC_URE1 failed to create and maintain a Physical Security Plan, approved by a senior manager or delegate. Based on the investigation and available information, the SME determined WECC_URE1 was in possible violation of CIP-006-1 R1. The SME forwarded the findings to WECC Enforcement. WECC Enforcement reviewed the information submitted by WECC_URE1 and the SME’s findings, and determined WECC_URE1 was in violation of CIP-006-1 R1, due to WECC_URE1's failure to create and maintain a Physical Security Plan, approved by a senior manager or delegate. Additionally, WECC_URE1 submitted a Self-Report for CIP-004-3 R4. In this instance, a security guard clicked the wrong checkbox in the physical access management system and gave the contractor in scope inadvertent access to a Physical Security Perimeter (PSP). When the security guard updated WECC_URE1's CIP-004-3 R4 access list, they realized and corrected the error. A WECC SME discussed the violation with WECC_URE1 and determined that the instance of noncompliance was actually a violation of CIP-006-3 R1.4, instead of a CIP-004-3 R4 violation. WECC added this instance of noncompliance to the scope of the above open enforcement action. The duration of this violation was approximately 81 months. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to create and maintain a Physical Security Plan to ensure that all Cyber Assets in an identified Electronic Security Perimeter (ESP) are also located within a PSP. Failing to create and maintain a Physical Security Plan could allow Cyber Assets within that PSP to go unprotected, unmonitored, or unchecked. This could allow unauthorized physical access to Critical Cyber Assets (CCAs) within that PSP, which could be used to affect the operation of the BPS. As compensating measures, WECC_URE1 had security in place several years prior to the beginning of this violation at all WECC_URE1 projects. All security plans included significant attention to securing the powerhouses. Further, WECC_URE1 had standard operating procedures and processes that were compliant with other regulations at the time of the violation. For these reasons, WECC determined that this violation posed a moderate risk to the reliability of the BPS. | When the Standard became mandatory and enforceable on WECC_URE1 | When WECC_URE1 finished transitioning to CIP Version 5 | No Penalty | Self-Certification | To mitigate this violation, WECC_URE1: 1) updated its Physical Security Plan to include: i. defined operational or procedural controls to restrict physical access; ii. utilization of multiple different physical access controls to collectively allow unescorted physical access into PSPs to only those individuals who have authorized unescorted physical access; iii. monitoring for unauthorized access through a physical access point into a PSP; iv. an alarm or alert in response to detected unauthorized access through a physical access point into a PSP to the personnel identified in the Bulk Electric System (BES) Cyber Security Incident response plan within 15 minutes of detection; v. monitoring of each Physical Access Control Systems (PACS) for unauthorized physical access; vi. an alarm or alert in response to detected unauthorized physical access to a PACS to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection; vii. logged entries of each individual with authorized unescorted physical access into each PSP, with information to identify the individual and date and time of entry; viii. retaining of physical access logs of entry of individuals with authorized unescorted physical access into each PSP for at least 90 calendar days; and ix. restricted physical access to nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter (ESP) in those instances when such nonprogrammable communication components are located outside of a PSP; 2) implemented extensive modifications to the existing security systems at all of its Critical Assets; 3) updated the current Physical Security Plan documentation or created documents, where only informal procedures were in place; and 4) procured and developed a PACS test bench to evaluate new software and hardware and to test new components to the system. | 2016-07-01 | 2016-10-07 | Does Not Contest | WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-10-31 | FERC | NP18-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014941 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. Specifically, WECC_URE2 failed to test backup media to ensure information essential to recovery is available, as specified in CIP-009-3 R5, and required by CIP-005-3 R1.5 for Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). This issue affected 12 Cyber Assets. The cause of this issue was a lack of proper settings and procedures for the affected routers and switches. The data to successfully recover the affected assets was stored on a server that had been decommissioned and whose data was stored in a format that was irretrievable. WECC determined that this violation began when a server was decommissioned and the data to successfully recover the affected assets was no longer readily available, and ended when WECC_URE2 implemented changes to its settings so that configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to servers, which are themselves backed up, for a total of 1,371 days of noncompliance. | CIP-005-3a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 failed to provide evidence of testing back up media for network equipment. Failure to annually test backup media for Cyber Assets used in the access control and/or monitoring of the ESP could lead to recovery plans that are ineffective. Alternatively, WECC_URE2 may be forced to restore outdated information from a known good backup image in order to resume normal operations. However, WECC_URE2 had several controls in place to prevent and detect irrecoverable CCAs and their potential effect to the BPS. These controls include that there are redundant hardware and configurations in production and the Quality Assurance environment, so the proper configuration could be taken from the Quality Assurance environment, and Cyber Vulnerability Assessments were performed annually on the configuration. | When the server was decommissioned and the data to successfully recover the affected assets was no longer readily available | When WECC_URE2 implemented changes to its settings so that configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to servers, which are themselves backed up | No Penalty | Self-Report | To mitigate this violation, WECC_URE2: 1) implemented an archive command on switches and routers, so configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to server, which are themselves backed up; 2) ensured backup/configuration/compliance information is stored in a generic format that can be recovered without special software; and 3) revised backup processes to ensure backups are done consistently, so media testing can take place. | 6/9/2016 | 12/15/2016 | Does Not Contest | WECC did not give credit for WECC_URE2’s Internal Compliance Program (ICP). Although WECC_URE2does have a documented ICP that has been provided to WECC, WECC determined that, due to the length of the violation, WECC_URE2’s ICP failed, in this instance, to adequately detect the violation in a timely manner.
2017-10-31 | FERC | NP18-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014926 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. Specifically, WECC_URE2 failed to implement the protective measures specified in CIP-007-3 R5 and R6, needed to prevent unauthorized physical access to one Physical Security Perimeter (PSP). WECC_URE2 discovered that an employee, who was not authorized to grant access, was granting unauthorized personnel physical access to a PSP using other users’ Physical Access Control System (PACS) credentials to make the change. WECC_URE2 investigated the incident and determined that the accounts were not properly managed and that the monitoring was insufficient to timely discover the unauthorized activity. The cause of this issue was that the field controllers were not identified as being a PACS elements so they were not captured under the CIP management functions. Staff turnover and unclear roles and responsibilities between the maintenance, physical security, and IT groups led to this misidentification. Additionally, there was insufficient monitoring to discover the unauthorized activity due to inadequate procedures. The PACS application audit log for users was available, but not reviewed until a problem was discovered via direct observation. WECC determined that this violation began when WECC_URE2 first failed to implement various protective measures, required by CIP-006 R2.2, and ended when WECC_URE2 completed its mitigating activities for a total of 1,400 days of noncompliance. | CIP-006-3c | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 control measures needed to prevent unauthorized physical access to a PSP. Failure to control access to restricted areas, such as a PSP, could result in unauthorized access by adversaries, who could ultimately gain access to protected BPS Cyber Assets. However, WECC_URE2 had several controls in place to prevent and detect the unauthorized access to the BES Cyber Assets, including, monitoring of the PSP; regular maintenance and testing of the field controllers; Personnel Risk Assessments were completed for all people involved in the incident; the PACS monitoring was functioning; WECC_URE2’s access control process indicated the unauthorized access; PACS audit logs were functioning and upon review captured all unauthorized actions; appropriate patching was taking place for server/operating system and applications; and server/operating system user reviews were performed. | When WECC_URE2 first failed to implement various protective measures, required by CIP-006 R2.2 | Mitigation Plan completion | No penalty | Self-Report | To mitigate this violation, WECC_URE2: 1) either deleted the non-approved access or provided approval for access, depending on need; 2) implemented proper user account controls, according to CIP version 5; 3) clarified and documented roles and responsibilities for all parts of PACS management, including ensuring PACS roles and responsibilities were clear and communicated; 4) ensured user account controls are addressed in CIP version 5 transition; and 5) completed an administrative action for the employee who improperly granted access. | 7/1/2016 | 2016-12-09 | Does Not Contest | WECC did not give credit for WECC_URE2's Internal Compliance Program (ICP). Although WECC_URE2 does have a documented ICP that has been provided to WECC, WECC determined that, due to the length of the violation, WECC_URE2’s ICP failed, in this instance, to adequately detect the violation in a timely manner.
2017-09-28 | FERC | NP17-29-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015511 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R2. Specifically, MRO_URE1 stated that it only listed "listening" ports in its initial security reviews, but failed to list User Datagram Protocol (UDP) and ephemeral ports on Critical Cyber Assets (CCAs) and Non-CCAs. MRO_URE1 stated that it included these ports on security reviews in the past, but MRO_URE1 was unable to provide evidence of that claim. MRO_URE1 also stated that the issue ended in two years prior to the violation end date, but that assertion was contradicted by the findings of a Compliance Audit. Subsequently, during a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-007-3a R2. During the Compliance Audit, MRO discovered the documented ports and services required for one CCA did not include UDP ports or transmission control protocol (TCP) ephemeral ranges. An audit sample of CCAs and Non-CCAs was taken to see if listening or established processes, which were documented as required for operation, had their associated ports documented. The sample established that the required ports were not documented in some of the sampled CCAs and all of the sampled Non-CCAs. The cause of this violation was MRO_URE1's failure to understand the scope and requirements of the Standard and Requirement. MRO_URE1 considered it sufficient to only document required TCP "listening" ports. In addition, MRO_URE1 occasionally failed to document TCP ports because of its reliance on a change management ticket system to document ports required for operation, which lead to some TCP ports not being documented. The duration of the violation was approximately eight years and three months. | CIP-007-1 | R2 | Medium | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was not severe because MRO_URE1 does not allow Interactive Remote Access into either its Primary Control Center's or Back-Up Control Center's Electronic Security Perimeters (ESPs). Additionally, dial-up access to the ESP firewall is not enabled, and external interactive access to the firewalls is not permitted. This restricted electronic access is a strong and uncommon control for a registered entity of MRO_URE1's size. Although MRO_URE1 was generally documenting TCP "listening" ports required for operation, the risk was not minimal because the identification of all ports and services, including all TCP, UDP, and ephemeral ports, required for operation provides a fundamental information base needed to control the attack surface of Cyber Assets. Additionally, all Cyber Assets within the Primary Control Center and Back-Up Control Center were potentially affected. Further, the duration of the issue spanned several years. | When the Standard became enforceable on MRO_URE1 | Mitigation Plan completion date | No Penalty | Self-Report and Compliance Audit | To mitigate this violation, MRO_URE1 will: 1) implement a software security system that stores baseline ports and services data collected via the software security system's agents; 2) review processes for controlling ports and services per CIP Version 5; 3) identify the applicable systems that need to be assessed; 4) demonstrate that it has no Medium Impact Bulk Electric System Cyber Systems with External Routable Connectivity; 5) identify the network accessible ports on each of the applicable devices; and 6) document the business reason for each open network accessible port. | 10/16/2017 (approved completion date) | TBD | Does Not Contest | MRO reviewed MRO_URE1's internal compliance program and considered it a neutral factor in the penalty determination. MRO reviewed MRO_URE1's cooperation and considered it a mitigating factor in the penalty determination. MRO considered the Self-Report of the first instance a mitigating factor in the penalty determination. MRO_URE1 has no relevant history of noncompliance with CIP-007-1 R2.
2017-09-28 | FERC | NP17-29-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017016847 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it had a noncompliance with CIP-014-2 R4 Parts 4.1, 4.2, and 4.3. Specifically, WECC_URE1 reported that, after identifying the primary control center that operationally controls its substations in its R1 assessment, it inadvertently omitted the primary control center from its evaluation of potential threats and vulnerabilities of a physical attack pursuant to CIP-014-2 R4. WECC_URE1 discovered this issue while performing an internal compliance evaluation. During this evaluation, WECC_URE1 determined that when the individual previously responsible for CIP-014-2 left the company, WECC_URE1 did not have a good understanding of the tasks that needed to be performed and the time frame around performing those tasks. WECC determined that WECC_URE1 did fail to conduct an evaluation of the potential threats and vulnerabilities of a physical attack to its primary control center. The root cause of this noncompliance was less than adequate processes for transitioning CIP-014 compliance obligations when employees terminate their employment with WECC_URE. This led to an inadvertent omission of the primary control center from WECC_URE1's CIP-014 threat and vulnerability assessment. | CIP-014-2 | R4; P4.1; P4.2; P4.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE1 failed to conduct an evaluation of the potential threats and vulnerabilities of a physical attack to its primary control center. Such failure could result in WECC_URE1 having less than adequate mitigating measures in place to prevent a physical attack that could damage and/or render the primary control center inoperable; thereby potentially affecting the reliability of the BPS. However, the likelihood of the harm occurring was reduced by the controls WECC_URE1 had implemented. WECC_URE1's primary control center had mitigating measures that deter, detect, and defend against potential physical security threats. Specifically, the primary control center is primarily a brick construction multilevel facility located in a residential area where it is partially concealed behind existing foliage and has no signage indicating the type or function of the facility. The perimeter is protected with a brick wall, chain link, and rigid fence that is monitored with physical intrusion detection systems. Entry to the fenced perimeter is via two access-controlled gates. The main entry gate is a Class III crash-rated gate. All areas of the perimeter are monitored by cameras that are viewed and controlled locally and can be accessed remotely by corporate security operators. All ground-level windows on the public sides of the building are coated with blast and penetration coating. Intercom systems are used at all entry points. Each entry point has camera coverage to provide a view of the intercom and the entry point overall. WECC_URE1 has 24/7 security monitoring by physical security personnel located at the primary control center. Finally, WECC_URE1 has not discovered any unauthorized physical access or experienced or detected any potential physical security threats to the primary control center that could result in instability, uncontrolled separation, or cascading within an interconnection. No harm is known to have occurred. | when WECC_URE1 was required to demonstrate compliance with the Standard | when WECC_URE1 evaluated potential threats and vulnerabilities for its primary control center | $55,000 (for WECC2017016847 and WECC2017016848) | Self-Report | To mitigate this violation, WECC_URE1: 1) conducted an evaluation of the potential threats and vulnerabilities of a physical attack to its primary control center; and 2) created automatic task reminders utilizing a tool that assigns all necessary tasks associated with Requirement R4 to both an individual and a group responsible for performing the tasks; thereby ensuring the task is received by more than one individual. | 2017-01-12 | TBD | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-09-28 | FERC | NP17-29-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017016848 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it had a noncompliance with CIP-014-2 R5 Parts 5.1, 5.2, 5.3, and 5.4. Specifically, WECC_URE1 reported that, after identifying the primary control center that operationally controls its substations identified in its R1 assessment, WECC_URE1 inadvertently omitted the primary control center from its documented physical security plan pursuant to CIP-014-2 R5. WECC_URE1 discovered this issue while performing an internal compliance evaluation. During this evaluation, WECC_URE1 determined that when the individual responsible for CIP-014-2 left the company, WECC_URE1 did not have a good understanding of the tasks that needed to be performed and the time frame around performing those tasks. WECC determined that WECC_URE1 did fail to develop and document a physical security plan that included its primary control center identified in CIP-014-2 R1 Part 1.2. The root cause of this noncompliance was less than adequate processes for transitioning CIP-014 compliance obligations when employees terminate their employment with WECC_URE1. This led to WECC_URE1 inadvertently omitting the primary control center from its physical security plan development. | CIP-014-2 | R5; P5.1; P5.2; P5.3; P5.4 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE1 failed to develop and implement a documented physical security plan that included its primary control center identified in CIP-014-2 R1 Part 1.2. Such failure could result in WECC_URE1 having less than adequate mitigating measures in place to prevent a physical attack that could damage and/or render the primary control center inoperable; thereby potentially affecting the reliability of the BPS. However, the likelihood of the harm occurring was reduced by the controls WECC_URE1 had implemented. WECC_URE1's primary control center had mitigating measures to deter, detect, and defend against potential physical security threats. Specifically, the primary control center is primarily a brick construction multilevel facility located in a residential area where it is partially concealed behind existing foliage; and has no signage indicating the type or function of the facility. The perimeter is protected with a brick wall, chain link, and rigid fence that is monitored with physical intrusion detection systems. Entry to the fenced perimeter is via two access-controlled gates. The main entry gate is a Class III crash-rated gate. All areas of the perimeter are monitored by cameras that are viewed and controlled locally and can be accessed remotely by corporate security operators. All ground-level windows on the public sides of the building are coated with blast and penetration coating. Intercom systems are used at all entry points. Each entry point has camera coverage to provide a view of the intercom and the entry point overall. WECC_URE1 has 24/7 security monitoring by physical security personnel located at the primary control center. Finally, WECC_URE1 has not discovered any unauthorized physical access or experienced or detected any potential physical security threats to the primary control center that could result in instability, uncontrolled separation, or cascading within an interconnection. No harm is known to have occurred. | when WECC_URE1 was required to demonstrate compliance with the Standard | when WECC_URE1 developed a physical security plan that included its primary control center | $55,000 (for WECC2017016847 and WECC2017016848) | Self-Report | To mitigate this violation, WECC_URE1: 1) developed and implemented a documented physical security plan that includes its primary control center; and 2) created automatic task reminders utilizing a tool that assigns all necessary tasks associated with Requirement R5 to both an individual and a group responsible for performing the tasks; thereby ensuring the task is received by more than one individual. | 2017-05-19 | TBD | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016053 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-5.1 R1. RFC_URE1 self-identified that vendor-provided administrative tools contained the functionality (although never used) to read, change, and update the configurations on managed devices inside Electronic Security Perimeters (ESPs) for both High and Medium Impact locations. However, these devices were not on RFC_URE1's Bulk Electric System (BES) Asset List. Under CIP version 3, RFC_URE1 was not required to identify these types of administrative tools as Electronic Access Control or Monitoring Systems (EACMS), but under version 5, with the new definition of EACMS, RFC_URE1 was now required to include them on its BES Cyber Asset list. The cause of this violation was a lack of understanding of the need to identify and include devices that have the functionality to remotely configure BES Cyber Assets (BCAs). This cause involves the management practice of asset and configuration management. During the CIP version 5 transition, further review of detailed architecture diagrams and capabilities of the administrative tools led RFC_URE1 to conclude the servers with the administrative tools should be considered as EACMS, and therefore be included on the BES Cyber Asset list. The duration of the violation was approximately seven months. | CIP-002-5.1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although the violation could have affected the operation of RFC_URE1 BES assets due to their location at RFC_URE1's central data center, RFC_URE1 has numerous protections in place to reduce this risk. First, RFC_URE1 has security controls in place to monitor and prevent any changes within the corporate environment, up-to-date patch management of the devices hosting the administrative tools, and access control was enforced. Second, only a limited number of employees had access to the servers that had the administrative tools installed, and these individuals had proper NERC CIP training and updated personnel risk assessments, which mitigates the risk of possible vulnerabilities being exposed. Finally, RFC_URE1's internal control of an internal review of CIP-007 controls for routers and switches by its network operations team allowed RFC_URE1 to proactively detect the noncompliance. | When the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation, RFC_URE1: 1) held a planning meeting to obtain replacement servers and identify Physical Security Perimeter locations for replacement servers; 2) updated guidance for identifying assets for inclusion on the BES Cyber Asset List to ensure compliance with Version 5 CIP standards; 3) finalized the equipment list for administrative tools; 4) ordered new equipment identified and configured administrative equipment; and 5) deployed administrative equipment, retired remaining the relevant server and added equipment to its BES Cyber Asset List. | 2017-01-31 | TBD | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015502 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4. A security officer voluntarily left RFC_URE1's employment. The employee’s supervisor submitted the correct Human Resources (HR) electronic revocation request to remove the former employee’s physical and electronic remote access. However, the administrative manager responsible for approving the request (prior to HR processing the request) was on vacation when he received the revocation request and made a mistake when attempting to process the request remotely. Upon the administrative manager’s return from vacation, he realized the request had not been processed and was still active in the queue. He then immediately processed the request and the former employee’s access to all RFC_URE1 assets was revoked. The former employee did not use his physical or electronical access after he voluntarily left RFC_URE1's employment. The cause of this violation was lack of verification controls to ensure the access revocation request was properly processed. Additionally, the management practice of work management was involved in that additional personnel should have been designated to cover access tasks while the primary individual was out of the office. The duration of the violation was approximately one week. | CIP-004-3a | R4 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the employee was a trusted employee who left RFC_URE1's employment voluntarily, rather than being terminated for cause, thus reducing the likelihood that he would take any actions to compromise the BPS. Second, this was an isolated incident that RFC_URE1 self-identified within several days of the noncompliance occurring. Third, there were other security measures in place to limit access to authorized personnel, including 24/7 surveillance. Finally, upon identification, RFC_URE1 took immediate steps to correct the noncompliance. | The date RFC_URE1 was required to revoke the employee's access | When RFC_URE1 revoked the employee's access | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation, RFC_URE1: 1) revoked the former employee’s physical access; 2) created a process to verify that HR forms are completed; 3) trained corporate security employees on a new delegation process; 4) communicated the lessons learned from the violation to affected NERC stakeholders; and 5) developed programmatic monitoring of its deactivation queue and automatic escalation for pending deactivation requests. | 2016-05-12 | 2016-08-05 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015537 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. A RFC_URE1 employee attempted to gain access to the security operation data center Physical Security Perimeter (PSP) with his badge, but was unsuccessful. A supervisor, who was aware of the employee’s prior unescorted access privileges, allowed entry of the employee into the PSP, but did not enter him in the visitor log or escort him. After completing his work and exiting the PSP, the employee immediately self-identified and reported the noncompliance to his manager. The employee did not understand why his access privilege was denied. The manager immediately recognized this as a noncompliance and initiated an immediate walk-down of the PSP and a review of the visitor logs and badge reader. This review showed that this was an isolated incident and revealed no evidence of tampering or other malicious destruction of the NERC controlled assets or PSP. The cause of this violation was insufficient workforce management and verification practices, as the employee was not granted access to the PSP as a result of a clerical error in managing the access lists, and the supervisor failed to follow RFC_URE1's process regarding unauthorized access to its PSP without being properly logged or escorted. As RFC_URE1 continues to work to shift the cultural mindset of its employees to understand the connection between their day-to-day activities with overall security and reliability to the bulk power system (BPS), RF will continue to closely monitor the vigilance RFC_URE1's management shows when it comes to behaviors that affect culture. The duration of the violation was approximately one day. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. First, the system access controls RFC_URE1 had in place prevented the employee’s access as expected. Second, at the time of the noncompliance, the employee had current, valid NERC qualifications, including a current personnel risk assessment and up-to-date training. Third, the employee was supposed to have access to the PSP, but through a clerical error, his access was not approved. Fourth, the employee did not have electronic access to any of the NERC assets within the PSP, thus reducing the likelihood that the employee could compromise the BPS. Finally, the employee quickly self-identified and reported the noncompliance and RFC_URE1 took immediate action to investigate and ensure no malicious activity had occurred. | When the employee was permitted access to a PSP without being properly logged or escorted | When the employee exited the PSP | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation RFC_URE1: 1) requested access for the employee whose access was inadvertently not granted as intended 2) performed a formal walk-down on the security operation data center to confirm that no BPS Cyber Assets were damaged or tampered with during the period of unauthorized access; 3) revalidated the security operation data center access list to ensure that no other employees were inadvertently removed due to the PSP split; 4) communicated the NERC access policies to all security operation senior personnel to ensure the requirements are understood; 5) communicated to all personnel the intent and implication of splitting the security operation data center into two PSPs; and 6) developed a standardized methodology to validate access between periodic user access review cycles. | 2016-03-09 | 2016-05-03 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history to be an aggravating factor in the penalty determination.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015751 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. RFC_URE1 security performed a quarterly review of its escorted (visitor) access log for a Physical Security Perimeter (PSP), and identified three issues with the log. First, two individuals listed themselves as their own escort. Upon further investigation, RFC_URE1 determined that one individual had unescorted access to the PSP and was escorting the other but did not know how to appropriately fill out the visitor log. Second, an individual was found to have no escort listed in the log on two different dates. Although RFC_URE1 later granted this individual authorized unescorted access, he did not have authorized unescorted access at the time and thus should have had an escort. Third, an exit time was missing for a visitor. The cause of this noncompliance was RFC_URE1's lack of clearly defined escort responsibilities and training on how to complete the visitor log correctly. Workforce management is involved as RFC_URE1 did not adequately manage and monitor its execution of the organization’s visitor log process. The duration of the violation was approximately two weeks. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. While deficiencies in the accuracy of the log were identified, the individuals involved did log their access to the security operation center. Also, RFC_URE1's quarterly review caught the deficiencies which shows there is a control in place to confirm individuals are logging access and ensure compliance with the standard. | When the first visitor access issue began | When the last visitor access issue ended | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation RFC_URE1: 1) reviewed and reinforced escort responsibilities and visitor log maintenance at the team meeting; 2) followed employee relations process to determine if discipline is required; 3) updated corporate security to clarify that the escort is responsible for properly completing the visitor log; 4) disseminated updated corporate security to every NERC CIP compliance lead to share with Subject Matter Experts; and 5) granted authorized unescorted access to the person identified to have a business need to access the PSP on regular basis. | 2016-07-21 | 2016-11-14 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history to be an aggravating factor in the penalty determination.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016114 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-6 R1 in two instances, both of which concerned door hardware failures. First, an employee, without valid authorized unescorted access, swiped his badge at a Physical Security Perimeter (PSP) door, and was able to open the door due to a door hardware failure. An unauthorized access alarm was promptly generated and investigated immediately. RFC_URE1 confirmed there was no malicious intent and no cyber event. Second, at a different PSP, a contractor working outside the PSP opened the door without valid authorized access (by swiping the badge), due to a door hardware failure. An unauthorized access alarm was promptly generated and investigated immediately, and RFC_URE1 confirmed there was no malicious intent and no cyber event. On both occasions, RFC_URE1 deployed vendors onsite (the following business day after each event) to assess and correct the unexpected door hardware failures, which was the cause of the issues. As an additional security measure, RFC_URE1 employed security guards to monitor the malfunctioned doors while investigating both incidents. The duration of the violation was approximately one week. | CIP-006-6 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 immediately issued an alert to the appropriate personnel. Those personnel responded to the alert within minutes, identified the cause of the alert, and remediated the immediate noncompliance. The cause of each noncompliance was investigated on the next business day. Second, RFC_URE1 also had additional security measures in place such as 24/7 surveillance. Third, in both instances, the employee and contractor had valid needs to go into the rooms and the employee was later granted authorized unescorted access to the PSP. Finally, RFC_URE1 was unable to replicate similar hardware failures and therefore considered it an isolated issue. | When the hardware failure occurred in the first incident | When the hardware failure was resolved in the second incident | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation RFC_URE1: 1) deployed alternate measures to PSP doors while hardware was replaced and vendors assessed and tested hardware; and 2) granted authorized unescorted access to the employee, to the PSP. | 2016-09-01 | 2017-01-13 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history to be an aggravating factor in the penalty determination.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015594 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. RFC_URE1 enabled a temporary Physical Security Perimeter (PSP) to allow relocation and renovation of the permanent PSP. It enabled this temporary PSP using the existing device. During a routine document review, RFC_URE1 security realized security that the device was not on RFC_URE1's CIP Cyber Asset List. RFC_URE1 security submitted a request through its change control process to add this device to the list. The cause was inadequate communication and coordination between the information technology systems group and corporate security, which involves the management practices of workforce management and asset and configuration management. The duration of the violation was approximately seven months. | CIP-006-3c | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, per RFC_URE1 policy, all default passwords were changed prior to enabling the PSP to ensure that access was limited to those with access rights. Second, the device is physically located in a restricted access room, with 24/7 surveillance and layers of protection. Finally, due to RFC_URE1's continuous improvement to building a stronger cyber security and compliance program, it was able to detect the issue due to improved internal communication coordination and routine document review which demonstrates improved detective internal controls. | When the temporary PSP was enabled | When security submitted a request to add the device to the list | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation RFC_URE1: 1) formally requested a Technical Feasibility Exception (TFE) through its TFE change control process related to the device; 2) updated the TFE internal tracking spreadsheet; 3) created a process for commissioning and decommissioning PSPs; and 4) communicated the process to applicable NERC Corporate Security and NERC IT staff. | 2016-03-18 | 2016-04-11 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-08-31 | FERC | NP17-28-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015595 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R5. A RFC_URE1 employee attempted to gain access to a Physical Security Perimeter (PSP) door. The unsuccessful attempt created an alarm, which was acknowledged per written procedure by the access system operator. The employee unsuccessfully attempted to gain access to the same PSP door three additional times, however the employee had lost access to the data center PSP due to an administrative error. Each attempt created an alarm that was acknowledged by an access system operator per RFC_URE1's procedure. However, RFC_URE1 failed to produce a written report of the incident as required by its procedure. RFC_URE1 defines “unauthorized access” to include three or more “bad” badge swipes per person. Despite the fact that RFC_URE1's security procedure requires a written report of an unauthorized access attempt to be forwarded to RFC_URE1's security compliance, no such written report was forwarded. Upon discovery of the issue RFC_URE1 security conducted an investigation of logs for evidence of similar past occurrences, and identified one additional incident. The cause was that RFC_URE1 utilizes a manual monitoring process to track for three unsuccessful attempts by the same badge/PIN. The Physical Access Control System did not have a script built in to automatically alert for three unsuccessful attempts by the same badge/PIN. RFC_URE1's manual monitoring process failed to protect and ensure the availability of information assets to reduce risks to the bulk power system (BPS). The duration of the violation was approximately one day. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. First, RFC_URE1's security controls worked to prevent the individual from accessing the PSP. Second, security acknowledged each of the alarms individually, and thus had awareness that the individual had unsuccessful badge swipes. Third, even if the individual was able to gain access, which he wasn’t, RFC_URE1 has 24/7 surveillance and could have detected the unauthorized access. Finally, RFC_URE1's internal controls detected the issue, which demonstrates that RFC_URE1's current improved controls are being implemented. | When RFC_URE1 failed to follow its process for producing a written report of the incident | When RFC_URE1 failed to follow its process for producing a written report of the incident | $25,000 (for RFC2016016053, RFC2016015502, RFC2016015537, RFC2016015751, RFC2016016114, RFC2016015594, RFC2016015595) | Self-Report | To mitigate this violation RFC_URE1: 1) updated its processes directing the access system operator, based on alarm/alert to use various Physical Access Control Systems screens to determine and report unauthorized access attempts; 2) required access system operators to read the updated process; and 3) implemented a long-term automated solution. | 2016-05-30 | 2016-10-06 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF applied mitigating credit for RFC_URE1's submission of the Self-Report. RFC_URE1 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issue. RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-07-31 | FERC | NP17-25-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013072 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-3 R2. Specifically, WECC_URE1 failed to identity and document the configuration of ports and services for several access points to an Electronic Security Perimeter (ESP), as required by CIP-005-3 R2.2, and failed to implement strong procedural or technical controls at multiple access points, as required by CIP-005-3 R2.4. Specifically, for CIP-005-3 R2.2, WECC_URE1 failed to identify and document the configuration of ports and services for several access points to one ESP. The several devices in scope included multiple checkpoint firewalls and one router. The issue was caused by WECC_URE1's inability to identify or detect inconsistent rules applied to access point configurations, due to the lack of established access point configuration baselines to annotate the correlation of ports and services. For CIP-005-3 R2.4, WECC discovered WECC_URE1 had not implemented strong authentication mechanisms at multiple access points. The devices in scope included redundant pair checkpoint firewalls and one redundant pair router.WECC_URE1's documentation showed that only usernames and passwords were being used for external interactive access into the ESP for those access points. The access points were configured to only allow access from specific network locations, by subnet and specific network addresses; however, this does not equate to strong procedural or technical controls. The cause of this issue was an incorrect interpretation of the sub-requirement of the Standard. | CIP-005-3 | R2; R2.2; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to identity and document the configuration of ports and services for several access points to an ESP, and to implement strong procedural or technical controls at multiple access points. Failing to identity and document the configuration of ports and services for access points could result in the potential compromise of the ESP. If compromised, an adversary could access and disable a Critical Cyber Asset (CCA) jeopardizing the Bulk Electric System (BES). Additionally, failing to implement strong technical controls, such as two-factor authentication at access points to the ESP to ensure authenticity of the accessing party, could potentially result in the compromise of the ESP, by an adversary whom is able to compromise the password. If the single factor authentication was exploited to gain access to an ESP, an adversary could potentially misuse a CCA causing a cascading effect on local operations and ultimately the BES. However, as compensating measures, WECC_URE1 had implemented a defense-in-depth architecture of physical and logical cyber security controls. The controls included physical security mechanisms with guards, special locks, closed-circuit television, and a logical perimeter, as well as internal cyber security controls, such as firewalls, vulnerability scanning tools, and intrusion detection systems. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | No penalty | Compliance Audit | To mitigate this violation, WECC_URE1: 1) developed a firewall rule management system (application and database) to store firewall rules and the business justification metadata for each firewall rule; 2) created an annual firewall rule verification review process and procedures using the new firewall rule management system; 3) created an annual router rule verification review procedure for performing manual review of the rules and their business justification; 4) trained staff on the new processes and procedures; 5) put the firewall rule management system into production; 6) completed a full annual firewall rule verification; 7) completed a full annual router rule verification; 8) implemented a multi-factor authentication for remote access to control centers; 9) revised firewall rules; 10) implemented a device server requiring multi-factor authentication to access control servers' BES cyber systems and assets; and 11) implemented a device server at the CIP ESPs. | 11/4/2015 | 3/3/2017 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in evaluation of the case. WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be an aggravating factor.
2017-06-29 | FERC | NP17-24-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013842 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R3.1. Additionally, the Regions determined that RFC_URE1 had an issue of CIP-007-3a R3 as a result of a Compliance Audit. The violation at issue concerns RFC_URE1's execution and documentation of security patch assessments by a subset of RFC_URE1's Information Technology (IT) group. The subset of the IT group maintains a separate NERC CIP SCADA environment, which was the subject of the violation. The servers in this domain support the applications, including the the Energy Management System (EMS), used by the RFC_URE1 Dispatch groups to perform real-time dispatch functions for RFC_URE1's power plants. The total number of unique devices impacted was 3% of RFC_URE1's CIP devices (during the time period of the violation). During Self-Certification activities and the Compliance Audit, RFC_URE1 and the Regions identified three sets of missed patch assessments. First, as part of Self-Certification activities, RFC_URE1 discovered that it did not assess patches released on certain devices. RFC_URE1 determined that assessments for those months were overlooked at the time the patches were released and thus not timely assessed or implemented. After discovering the issue, RFC_URE1 assessed the security patches released and determined that 11 security patches were applicable to RFC_URE1's Cyber Assets. These 11 patches affected 88 devices that support SCADA and EMS functions in RFC_URE1's dispatch unit, which is responsible for dispatching power plants across RFC_URE1's entire footprint. Second, during the Compliance Audit, the Regions identified additional instances of RFC_URE1's IT group not timely documenting the assessment of patches and security upgrades on devices that support the dispatch systems. During the audit, the Regions requested evidence of assessments for security patches released by certain third-party vendors that were potentially applicable to devices that support dispatch systems. RFC_URE1 was unable to provide sufficient evidence that it assessed these patches in a timely manner. Instead, in some cases, RFC_URE1's documented assessments were incomplete, and in other cases, RFC_URE1 did not have sufficient documentation relating to its monthly checks for released patches and thus was unable to provide evidence to show whether or not patches were released by the vendors. After the audit, RFC_URE1 conducted a review of the patches released during those months to determine if RFC_URE1 missed patches that were applicable to its systems. As a result of that review, RFC_URE1 determined that the patches released by these third-party vendors during those months were not applicable to RFC_URE1 devices. The vendors at issue supplied software that RFC_URE1 ran on 64 devices. Third, during the Compliance Audit, RFC_URE1 provided evidence of an extent of condition review it conducted in response to the audit data request where it discovered 26 instances of late patches and missing or insufficient assessments for RFC_URE1's dispatch devices. The root cause of the violation was poor asset and configuration management controls, meaning that improved monitoring and oversight of the patch management process could have reduced the likelihood of occurrence. Oversight of this particular aspect of the process was inadequate, and there were inadequate documented patch management processes in place. Thus, as part of its mitigation, RFC_URE1 assigned an IT manager responsible for ensuring the successful completion of RFC_URE1's patch management program and created a formal documented process for patch management for these groups at issue. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The delay in or failure to assess, document, and implement security patches, especially relating to patches for RFC_URE1's EMS, could potentially allow a vulnerability to be exploited, which could affect the neighboring entities visibility into the system. Additionally, the violation occurred over a long duration and affected 93 devices that serve critical functions across RFC_URE1's entire footprint. And, because the Regions determined the root cause was a lack of management controls surrounding the patch management processes, the violation was widespread within the generation dispatch unit and there was a risk that the violation could have continued, thus potentially affecting the systems for a longer period. However, because of the facts and circumstances particular to this violation, including the multiple significant protections in place at the time of the violation, the Regions determined that the violation posed moderate risk to the reliability of the BPS. More specifically, the risks were partially mitigated by the following factors. First, RFC_URE1's security approach incorporates the traditional practices of layered firewalls, intrusion detection/prevention systems, security event monitoring and antivirus, but, importantly, also includes more sophisticated systems and protections going beyond traditional defense-in-depth techniques. Some of these significant protections include RFC_URE1's approach to host-based protections, network protections, and monitoring and proactive threat mitigation. RFC_URE1's monitoring includes end-point data and intelligence monitoring–including inbound and outbound anomalous network traffic. Across RFC_URE1's footprint, it operates a single network with very limited Internet connections. RFC_URE1 uses multiple industry leading advance persistent threat tools for both monitoring and auto-blocking cyber threats, ranging from common malware to near zero-day type attacks. Importantly, RFC_URE1 was able to demonstrate that, because of its approach, its system was protected against the specific vulnerabilities for which patches were released for the subject Cyber Assets throughout the duration of the violation. These combined protection and detection methods make it less likely that any vulnerability remediated by an identified patch would have been exploited. The Regions also note that the violation affected only one business unit, generation dispatch, and thus potential impact of a compromise would be limited to the function of that business unit. (RFC_URE1 indicated that with respect to the potential impact, in the event of compromise, the neighboring entities would redeploy any regulation service to other non-RFC_URE1 generators, and RFC_URE1 dispatchers would call the neighboring entities to ensure RFC_URE1 units were doing what the neighboring entities operators were requesting. These calls would occur periodically allowing the neighboring entities to have visibility into RFC_URE1 output and allow them to request loading adjustments.) | the first date RFC_URE1 was late in documenting the assessment of a security patch | when RFC_URE1 performed the final outstanding patch assessment | 150000 | Self-Report | To mitigate this violation, RFC_URE1: 1) conducted an investigation into patches for the months in question and a review of the sources for potential patches during that time indicated that none of the patches released were applicable to RFC_URE1's CIP environment; 2) assessed and implemented the latest versions of the patches at issue regarding the additional 26 instances identified during the Compliance Audit; 3) completed the missed security patch assessments; 4) assigned an IT Manager responsible for ensuring the successful completion of the IT security patch management program. This includes a documented process for conducting assessments and documenting assessment results; 5) developed a project plan to identify resources and tasks needed to implement process improvements, including increased automation through the use of an electronic tool; 6) reviewed all of the IT security patch management processes and controls to determine the current state of the processes, including compliance gaps. This included an extent of condition review; 7) implemented an electronic tool to monitor and track security patch assessments, including automated notification processes, new dashboards, and reports; and 8) included a process, within the electronic tool described above, for creating or revising mitigation plans when applicable patches are unable to be applied within 35 days of evaluation completion. | 2015-12-12 | 2016-11-09 | Neither Admits nor Denies | The Regions considered certain aspects of RFC_URE1's internal compliance program and awarded mitigating credit. Additionally, in response to the current violation, RFC_URE1 voluntarily implemented a mitigation strategy with strong overarching milestones, which is indicative of a strong compliance program. However, the Regions determined that full credit was not warranted because the current violation was indicative of a weakness in the patch management aspect of RFC_URE1's compliance program. The Regions considered RFC_URE1's cooperation during the Settlement Agreement process and awarded mitigating credit. Although RFC_URE1 struggled to provide the Regions with an accurate full scope of the violation and complete evidence of Mitigation Plan completion, RFC_URE1 attempted to cooperate with RF throughout the enforcement process. The difficulty in providing the Regions with accurate and useful evidence of mitigation plan completion made it difficult to verify that RFC_URE1 satisfactorily completed its mitigation plan. RFC_URE1 and the Regions have discussed this issue, and RFC_URE1 is aware that it must apply a higher standard in the future when certifying mitigation plans so that verification is not delayed. Since RFC_URE1 acted in good faith and intended to be cooperative throughout the duration of the Compliance Audit and enforcement action, the Regions applied some mitigating credit for RFC_URE1's cooperation. As above and beyond actions, RFC_URE1 has spent more than $1.7 million implementing a baseline monitoring software that scans selected assets nightly (including those associated with this violation) and reports any changes discovered. The tool will report any security patches that get applied in this nightly assessment. The tool also collects application versions and updates daily. Anything that the tool identifies as outside of the current baseline for a device is flagged as an exception and investigated by the asset owners. The Regions considered RFC_URE1's compliance history in determining the disposition track. The Regions determined that RFC_URE1's compliance history should not serve as a basis for aggravating the penalty because the prior noncompliance did not involve same or similar conduct.
2017-06-29 | FERC | NP17-24-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016130 | Settlement Agreement | WECC_URE_2 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-006-3c R2.1 and R2.2. For the first instance, during an upgrade to WECC_URE_2's Physical Access Control Systems (PACS), WECC_URE_2 failed to provide all the protections of CIP-006-3c R2.2 to 14 PACS workstations that were commissioned with software. WECC_URE_2 discovered this instance while performing an internal audit in preparation for the upcoming WECC audit. WECC_URE_2 hired a third-party company to further investigate the results of its internal audit. The results of the investigation determined that 1) WECC_URE_2 was noncompliant with CIP-006-3c R2.1 for not protecting all 14 workstations from unauthorized physical access, and 2) WECC_URE_2 failed to afford the protections, as described below, pursuant to CIP-006-3c R2.2, relating to the 14 workstations: a. CIP-003 R4: Not included in the information protection plan; b. CIP-003 R6: NERC change control procedures were not in place; c. CIP-004 R3: Initial and renewed Personnel Risk Assessments every 7 years were not validated for personnel with unescorted physical access; d. CIP-005 R2: The firewalls did not document and restrict ports/services with the same rigor as required in NERC CIP. Remote access to these workstations was allowed from corporate devices, and there is no CIP-compliant two-factor authentication for remote access; e. CIP-005 R3: Corporate networks and the corporate firewalls were monitoring for alerting for detected threats, but not with the scrutiny as required in this Standard; f. CIP-006 R4: Physical access controls were insufficient; g. CIP-006 R6: No logging records for three of the PACS workstations; h. CIP-007 R1: No testing conducted prior to commissioning; i. CIP-007-R2: Did not ensure only required ports and services were enabled; j. CIP-007 R3: Did not ensure patches were tracked, evaluated, tested, and installed; k. CIP-007 R4: Did not ensure anti-virus signature updates were tested prior to being installed; l. CIP-007 R5: Did not annually review user access rights; m. CIP-007 R7: Not included in appropriate disposal and redeployment policy; and n. CIP-007 R8: Did not perform annual cyber vulnerability assessments. The root cause of the first instance was an internal misunderstanding of the applicability of CIP-006-3c R2.1 and R2.2 to PACS workstations. For the second instance, WECC_URE_2 failed to provide all the protective measures of CIP-006-3c R2.2 when it did not change the password for one shared account on five PACS Internal Controller (IC) boards, annually. The shared account resided on all five IC boards. The root cause of the second instance was lack of an adequate process for transitioning compliance responsibilities when WECC_URE_2’s primary physical security personnel leave WECC_URE_2's employment. | CIP-006-3c | R2; R2.1; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In the first instance, WECC_URE_2 failed to provide the protective measures of CIP-006-3c R2.1 and R2.2 to 14 PACS workstations. In the second instance, WECC_URE_2 failed to provide the protective measures of CIP-006-3c R2.2 to five PACS IC boards. Failure to adequately protect cyber assets that provide, monitor, and log physical access to the Critical Cyber Assets (CCAs) integral to the reliable operation of the Bulk Electric System (BES) could compromise the CCAs or allow an unauthorized individual with malicious intent to have access to the CCAs; thus, potentially affecting the reliability of the Bulk Power System (BPS). The likelihood of these risks occurring were reduced by the controls implemented by WECC_URE_2. Specifically, WECC_URE_2 had 24 hour-a-day, 7 day-a-week access monitoring and security event monitoring on the CCAs with the PSPs. WECC_URE_2 had policies and procedures restricting access to only authorized personnel, as well as regular reviews of the personnel with electronic and/or unescorted physical access and their specific access privileges. WECC_URE_2’s corporate firewalls were restricted based on corporate policies. A "deny all" firewall rule was present. Ports and services to and through the access points were restricted. WECC_URE_2 had an active Intrusion Prevention System (IPS) monitoring and preventing any unknown or suspicious inbound traffic into the network. Corporate firewalls were monitored by a product which detects any changes made to the firewalls for investigation into whether the change was authorized. Physical access to any workstation required a valid WECC_URE_2 badge. All but four of the 14 workstations were within restricted rooms, where access to the building or room required individual badging. The four workstations not in restricted buildings or rooms still required a WECC_URE_2 badge and were monitored by employees during working hours. Changes to the workstations were limited to administrators only. WECC_URE_2 restricted ports on its corporate firewalls and had implemented a network-based IPS that could detect unexpected ports and services. The IC boards are naturally restrictive devices with limited functionality and no direct human interface capability. This reduced the potential that an unauthorized individual would be able to gain logical access to the IC boards. The IC boards are all within designated PSPs where access is restricted, logged, and monitored. Additionally, all personnel who were granted logical access to the PACS workstations and IC boards had training and current Personnel Risk Assessments. No harm is known to have occurred. | The first instance began when WECC_URE_2 did not provide protective measures to 14 PACS workstations | The first instance ended upon mitigation completion The second instance ended when WECC_URE_2 changed the password on one shared account. | 74000 | Self-Report | To mitigate this violation, WECC_URE_2: 1) Assessed whether all 14 workstations are needed; 2) Designated the remaining workstations as PACS devices; 3) Identified the most secure location for workstations assessed as being needed; 4) Designed a plan to ensure the remaining workstations have the physical and logical protections required by CIP Version 6; 5) Implemented the workstation CIP Version 6 plan; 6) Changed the passwords on the IC boards; 7) Identified and documented firmware versions on the IC boards; 8) Performed a comprehensive review of the IC boards to ensure compliance with applicable Standards; and 9) Documented ownership of the IC boards. | 6/26/2017 | TBD | Admits | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it a neutral factor in the penalty determination. Although WECC_URE_2 has a documented ICP that has been provided to WECC, WECC determined that because WECC_URE_2 did not implement their ICP with effective internal controls to identify this issue timely, the ICP does not qualify for credit. WECC_URE_2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit/during the self-certification period. WECC considered WECC_URE_2's CIP-006 R2 compliance history in determining the penalty. WECC_URE_2's relevant prior noncompliance with CIP-006 R2 includes two prior violations. WECC considered WECC_URE_2's CIP-006 R2 compliance history to be an aggravating factor in the penalty determination.
2017-05-31 | FERC | NP17-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015819 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. Specifically, WECC_URE1 contractors installed two Physical Access Control System (PACS) panels at two Physical Security Perimeters (PSPs), without going through WECC_URE1's change management process, therefore not applying all other applicable protective measures pursuant to CIP-006-3c R2.2. WECC_URE1 failed to afford the protective measures specified in Standard CIP-003-3 R6; Standard CIP-005-3 R2 and R3; Standard CIP-006-3 R5; and CIP-007-3 R1, R2, and R3. This work was being performed as part of WECC_URE1's transition to NERC CIP Standards Version 6 and the requirement for multi-factor authentication for unescorted physical access at High Impact BES Cyber Systems. The corporate security department identified a need to install new C-Cure panels, which are classified as PACS, at the two PSPs. In coordination with the operations department, corporate security and the contracting resources moved the door functionality from the existing C-Cure panels to the new C-Cure panels (with multi-factor authentication capability) at both control centers. Subject matter experts (SMEs) realized that the new panels had gone live without going through the proper change management process, as specified in CIP-003-3 R6. The responsible SME opened a change management ticket to initiate the CIP-003-3 R6 change management process after-the-fact. The root cause was a lack of utilizing established change management processes by those who are responsible for managing WECC_URE1's PAC devices. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to perform its change management process prior to the installation of two PACS at its critical asset PSP and therefore also failed to apply all other applicable CIP protections. Such failures could introduce unexpected vulnerabilities and disruption of operations to WECC_URE1's PACS, which could affect physical access points and allow unauthorized physical access to Critical Cyber Assets (CCAs), which could result in successful cyber attacks against CCAs essential to the operation of the bulk electric system (BES); thereby potentially affecting the reliability of the BPS. WECC_URE1 implemented controls to reduce the likelihood of these events occurring. These controls included administrative, technical, and physical access controls; personnel risk assessments for both role separation and function, as well as authentication systems controlling physical access to CCAs. WECC_URE1 implemented visitor controls and contractor screening processes. WECC_URE1 had 24 hour-a-day, seven days-a-week security monitoring of the PSPs, including video monitoring by the 24/7 security operations center and corporate security was on-site during the changes and no physical security issues were noted during this change. WECC_URE1's administrative controls include policies and procedures restricting access to only authorized personnel, as well as regular reviews of the list of personnel with electronic and unescorted physical access, and their specific access privileges. Further, corporate security was on-site during the changes so if there been a malfunction or any unintended consequences of the PACS change, immediate identification and action would have occurred. | when the first of the two PACS were put into production without going through WECC_URE1's change management process | when WECC_URE1 completed all protective measures required by CIP-006-3c R2.2 for both PACS panels | 54000 | Self-Report | To mitigate this violation, WECC_URE1: 1) completed the change management process on the two PACS panels; 2) updated documentation to clarify the change management initiator role for projects that cross multiple departments; 3) created a checklist for corporate security CIP-related projects to ensure all change management rules are followed; and 4) created and affixed labels on all existing PACS panels to alert personnel performing work on the panel to be aware of the change management requirements. | 12/21/2016 | 2017-05-11 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 discovered this violation and self-reported 290 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount for this violation. WECC considered WECC_URE1's compliance history in determining the penalty. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014013713 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-3 R5, R5.1, R5.2, and R5.3. Following its annual CIP Information Protection assessment, MRO_URE1 identified two locations where CIP-protected information classified as confidential and/or confidential-restricted did not meet the requirements of CIP-003-3 R5.1, R5.2, and R5.3. In the first instance of noncompliance, the location used to store the CIP Log manager configuration documents for MRO_URE1 was not identified as a CIP information repository, resulting in noncompliance with R5, R5.1, R5.2, and R5.3. As a result, the owner of the repository did not have documented access control procedures per R5, did not perform annual user access and permissions reviews per R5.2, and did not assess and document at least annually the processes for controlling access privileges to protect information per R5.3. Additionally, the designated approvers were not identified on the logical designated approver personnel list as required by R5.1. Because the CIP information protection program and CIP Access Control Program failed to include this location, the associated access control requirements (R5.1-R5.3) were not met. In the second instance of noncompliance, a document management application used to store and maintain CIP documents had a shared privileged account which was not covered by an access control procedure, resulting in noncompliance with R5, R5.1, R5.2, and R5.3. As a result, the shared privileged account was not identified on the designated approver personnel list per R5.1, and annual user access and permission and process reviews had not been conducted per R5.2 and R5.3, respectively. The account owner mistakenly thought that the required access control procedure and designated approver were covered by the application access control procedures. The root cause of the first instance of noncompliance was an oversight in the process that led to the failure to identify a CIP information repository in the MRO_URE1 CIP information protection program and CIP Access Control Program. The root cause of the second instance of noncompliance was the result of inadequate procedures, as this repository failed to have a clearly applicable written access control procedure. | CIP-003-3 | R5: R5.1; R5.2; R5.3 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-003-3 R5 has the potential to affect the reliable operation of the BPS by permitting unauthorized access to Critical Cyber Assets (CCAs), thus allowing potential compromise of confidential information. In the first instance, the data that was not stored in an identified CIP information repository was limited to the configuration files for the device, as opposed to the actual log data that tracked events for the CCAs. Additionally, the available evidence demonstrated that only non-CCAs were affected by this noncompliance. In the second instance, the data associated with the document management application was limited to the shared user account as opposed to each of the individual accounts. No improper access was discovered during mitigating activities, and the data identified for these instances of noncompliance could not be used to access CCAs. MRO_URE1 stated that access to Cyber Assets within the Electronic Security Perimeter (ESP) was limited to only those individuals with authorized physical and/or electronic access rights. The servers that house the applications are located in a data center with physical access restricted to authorized personnel. | When the standard became mandatory and enforceable on MRO_URE1 | When access control procedures and associated processes were implemented | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. created and implemented access control procedures and associated processes; 2. completed a gap assessment for the shared folders with CIP information; 3. remediated the compliance gaps by updating multiple existing procedures and creating one new procedure; and 4. trained any newly affected staff on CIP access controls. | 2014-08-06 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-003 R5 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013155 | Settlement Agreement | MRO_URE1 submitted Self-Reports stating that it was in violation of CIP-003-3 R6. The Self-Reports identified four instances of noncompliance with CIP-003-3 R6. 1. The change control process was not completed for work related to adding a devices and a control system. The work was completed properly, but the corresponding CIP-related documentation was not updated to reflect those changes within 90 days as required by MRO_URE1's procedures. The documentation was updated almost three weeks late. 2. An unsecured routable connection was discovered at an MRO_URE1 facility. 3. Serial communication changes were made when MRO_URE1 removed multiple communication connections to multiple MRO_URE1 substation devices. These changes did not have proper change control documentation completed within 90 days as required by MRO_URE1's change control and configuration management procedure. The documentation was updated approximately two months late. 4. A project which involved updating firmware at a MRO_URE1 substation did not have the necessary change control documentation submitted within 90 days as required by MRO_URE1's procedures. The documentation was updated almost two weeks late. The root cause of the violation was a failure to follow established procedures. | CIP-003-3 | R6 | Lower | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-003-3 R6 has the potential to affect the reliable operation of the BPS by providing the opportunity to exploit vulnerable Critical Cyber Assets (CCAs) after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs. While the first, third, and fourth instances were limited to documentation, and posed a minimal potential risk to the BPS, the second instance resulted in extending the ESP unintentionally to a distribution control house for nearly two years. The potential risk posed by the fourth instance was reduced because it did not involve a control center, was limited to a single substation, and was self-identified during MRO_URE1's annual substation inventory. | When MRO_URE1 first failed to follow its change management control procedures, resulting in an unsecured routable connection | When MRO_URE1 properly updated the documentation according to its change management and configuration procedure | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1 : 1. updated the CIP documentation for the instances where change control paperwork was completed but missed the 90-day timeline; 2. redesigned and implemented the substation network to address the non-compliant routable connection; 3. completed change controls forms for communication connections to a few MRO_URE1 substation devices that were disconnected; 4. evaluated and added additional program controls and monitoring practices to increase focus on change control processes; 5. completed change control forms for the firmware update project at one MRO_URE1 substation that had missed the 90-day timeline; and 6. added biweekly change control meetings to identify and review all change control activities occurring at Critical Asset substations. | 2014-03-05 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012800 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4.1 and R4.2. During a subsequent internal review, MRO_URE1 identified additional instances where the access list was not updated in the timeframe required by CIP-004-3a R4. MRO_URE1 self-identified seven instances of noncompliance with R4.1 and R4.2. In all seven instances of noncompliance, an employee or contractor retired, transferred, or resigned, thereby no longer requiring Physical Security Perimeter (PSP) access, but physical access was not removed from the access provisioning system in the required timeframe. The duration of the instances were: two days (three instances); three days (one instance); four days (one instance); seven days (one instance); and 11 days (one instance). The root cause of six instances was MRO_URE1 personnel's and contractors' failing to follow access policies, and the failure to execute access removal procedures. These instances were typically the result of the late submission of a personnel form. Instance number seven was caused by human error due to improper implementation of the revocation schedule by the administrator of the provisioning system. | CIP-004-3a | R4: R4.1; R4.2 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-004-3a R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for unauthorized personnel to access Critical Cyber Assets (CCAs), which could result in harm to the integrity of the CCAs. The overall number of errors was small (approximately half of a percent) in relation to the large number of access changes MRO_URE1 performs. Furthermore, none of the instances of noncompliance involved an individual who had been terminated, and MRO_URE1 had strong detective controls in place that limited the duration of the instances of noncompliance to less than two weeks. | When the first identified failure to revoke physical access occurred | When access was revoked and the access list was updated to accurately list physical access rights | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. contacted vendors that have CIP access and reiterated the current requirements for timely access removal; 2. updated the agreement for vendors to specifically identify responsibilities relating to CIP access; 3. updated all user access control documentation with any changes due to the new agreements; 4. provided coaching and counseling to responsible personnel; 5. revoked access for the retired employees and contractors; 6. created a joint access agreement entity distribution email list; 7. revised and distributed the access removal template; 8. reminded the joint access agreement entity to use the removal template for all access removal requests, to use the distribution email list, and to copy MRO_URE1 on that request; and 9. developed a monthly communication process for emailing each entity to share information on pending retirements. | 2014-10-16 | 2015-02-27 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-004 R4 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012366 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R1.5. MRO_URE1 subsequently discovered and reported 13 additional instances of noncompliance with CIP-005-1 R1.3 and R1.5. The identified instances include: 1. A security patch for an Access Point was not assessed within 30 days from its availability as required by CIP-007-1 R3.1. The duration of the instance was 12 days. 2. An Access Control Point at one substation was not configured to automatically alert for detected Cyber Security Incidents as required by CIP-007-1 R6.2. The duration of the instance was approximately three-and-a-half years. 3. Two shared passwords on servers used for authentication purposes were not changed within 90 days as required by MRO_URE1's policy. CIP-007-1 R5.3.3 requires that passwords be changed annually, or more frequently based on risk. The duration of the instance was approximately six months. 4. A failed hard drive used in the logging of dialup access was returned to the vendor without being erased as required by CIP-007-1 R7. The duration of the instance was approximately six months. 5. A dialup Access Point local default password was not changed as required by CIP-007-1 R5.2.1. The duration of the instance was approximately four-and-a-half years. 6. Alerts being generated by substation access points had not been consistently investigated according to MRO_URE1's documented procedures as required by CIP-007-1 R6. The duration of the instance was approximately four-and-a-half years. 7. The application that was provisioning control to substations was configured to use the corporate active directory servers but was not identified as a CIP-controlled Electronic Access Control or Monitoring System (EACMS) as required by R1.5. The duration of the instance was approximately one year. 8. MRO_URE1 failed to perform the scheduled evaluations for some security patches within 30 days as required by CIP-007-1 R3.1. The duration of the instance was approximately 14 months. 9. An undocumented Access Point was inadvertently established at a Critical Asset substation when a network connection was implemented in error in violation of R1.3. The duration of the instance was approximately seven months. 10. MRO_URE1 discovered additional instance where alerts being generated by substation access points were not consistently investigated according to MRO_URE1's documented procedures as required by CIP-007-1 R6. The duration of the instance was approximately four and a half years. 11. A logging device was not properly identified as an EACMS device and requirements associated with access control were not properly implemented as required by CIP-003-1 R5 and CIP-004-1 R4. The duration of the instance was approximately two-and-a-half years. 12. A system was not configured to alert on access or unauthorized login attempts as required by CIP-005-1 R3.2. Although the device was alerting for the devices it was monitoring, it was not monitoring itself or alerting for internal issues related to the system. The duration of the instance was approximately two and a half years. 13. A system did not implement documented processes for CIP significant changes as required by CIP-007-1 R1. Specifically, MRO_URE1 did not have any evidence of testing nor associated results. The duration of the instance was approximately ten months. 14. A system did not implement monitoring tools to monitor cyber security events as required by CIP-005-1 R3. The duration of the instance was approximately two-and-a-half years. 15. MRO_URE1 reported that a significant security patch was released but was not assessed until approximately five months later, which exceeded the 30 days allowed by CIP-007-1 R3.1. 16. MRO_URE1 reported that logging and alerting at ESP access points had become inactive at several substations after a firmware update was installed. This occurred even though the patch was tested in a lab environment prior to field implementation. The duration of the instance was approximately one month. The root cause of these instances was lack of sufficient processes. | CIP-005-1 | R1: R1.3; R1.5 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-005-1 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity for cyber intrusions to occur on Critical Cyber Assets (CCAs) located outside an established ESP. All but two of the issues (numbers four and eight) were limited to substations and not control centers. Two of the issues (numbers three and seven) were related to the implementation of a solution to provide an “Intermediate System” level of protection, which is a CIP V5 concept and exceeds the CIP V1 and V3 requirements. Finally, MRO_URE1 self-identified these issues, which is a strong indication of effective internal controls. | When the standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. developed security patch management, multiple failed authentication, firewall trafficking, and alarm tracking sheets; 2. created awareness of password checking and alarm verification through lists and bi-monthly meetings; 3. updated procedures and conducted testing to identify improvement opportunities for the patch management processes, change control processes; 4. disabled or removed some undocumented OS accounts, and other undocumented OS accounts were added to the current list of shared accounts; 5. configured a device to send user access attempts, including failed attempts, in the form of email alerts to the device's administrator; 6. formed a cross-functional team to review cross-departmental procedures used when a project involves remote connectivity; 7. reviewed and updated alert rules and cyber security protection documentation for the device; 8. completed physical security perimeter tasks; 9. applied CIP-005 R1.5 controls to the director, and implemented an application to new system; 10. setup and configured active directory in the EMS DMZ environment; 11. performed regular validation of the patch management process on a sampling of patches to determine that notifications and evaluations are being performed in a timely manner; and 12. incorporated a degaussing device, and maintained disk degaussing records to verify process compliance. | 2015-08-27 | 2015-12-28 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-005 R1 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014014472 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R3. In preparation for an upcoming audit, MRO_URE1 discovered the firewalls protecting the communication between the Electronic Security Perimeters (ESPs) for the primary and backup control centers were not sending the required logs to the centralized syslog environment. Upon conducting an investigation, MRO_URE1 determined that the firewalls were not properly configured to log events and send all the logs to the centralized EMS Syslog environment. MRO_URE1's review revealed that the devices were not logging because the configuration was set to detect only a limited amount of specific information across the logging environment for alarming and notification, such as unauthorized access attempts. The primary cause of the findings was a combination of the initial lack of focused adherence to CIP requirements and a lack of internal controls that would have confirmed and verified compliance that the firewall was logging the relevant information. | CIP-005-1 | R3: R3.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to log activity for an access point to the ESP at a control center represents a significant potential risk. Additionally, the violation existed for over five years, which increases the risk associated with the violation. In this case, the risk of this violation was reduced because the violation was limited to traffic between the primary and backup control centers. This communication path did not allow for interactive access from outside the ESP (i.e., the internet). All interactive access from outside the ESP was required to pass through the firewall at the primary control center. MRO did not detect any noncompliance associated with the firewall at the primary control center in the subsequent Compliance Audit. Additionally, the risk is limited because logging is a detective control to alert a registered entity of security events that have already occurred and is not intended to provide active security controls that prevent an adversary from obtaining access. | When the Standard became mandatory and enforceable on MRO_URE1 | When the firewalls were properly configured to send the required logs to the centralized syslog environment | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. configured the Firewall Logging environment on the applicable Electronic Access Point (EAP); 2. verified that logs were being correctly captured and sent to the appropriate location; 3. reviewed CIP-005-1 with EMS personnel to reinforce the criticality of following NERC Reliability Standards; 4. reviewed the process for all EMS CIP Cyber Assets and identified improvement opportunities; and 5. updated EMS process and documentation. | 2015-05-05 | 2016-01-04 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014013361 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. For the first instance of noncompliance, MRO_URE1 reported that a shared administrator password was not updated within 90 days per MRO_URE1's password security policy and as required by CIP-007-3 R5.3.3. The account owner who manages this account receives one password change email notification every 90 days from a password vault tool, which includes all passwords that need to be changed and the due date. The account owner overlooked this email notification and upon realizing it, changed the password. The duration of the instance was approximately one month. In the second instance of noncompliance, MRO_URE1 did not perform scheduled evaluations for the security patches within 30 days of availability for an access provisioning system as required by CIP-007-3 R3.1. The duration of the instance was approximately four months. In the third instance of noncompliance, MRO_URE1 identified a CIP-006-3c R2.2 issue related to CIP-007-3 R5.3.3. During the process of approving and creating a new badge administrator account, MRO_URE1 discovered that one temporary contractor badge administrator had shared his application login credentials with another temporary contractor badge administrator, who used the account to log into an application. Badge administrators are the personnel who issue staff and contract personnel badges for MRO_URE1 facilities. The badge administrators have access to the application but can only create and print badges. They do not have the ability to modify access privileges, to manipulate PSPs, or to log into servers. The duration of the instance was less than one week. The root cause was insufficient process, inadequate coordination, and a lack of preventive controls. | CIP-006-3c | R2: R2.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R2 has the potential to affect the reliable operation of the BPS, providing the opportunity for undetected compromise of Critical Cyber Assets (CCAs) to occur without the Responsible Entity’s knowledge. Notwithstanding, except for CIP-007 R3.1 and R5.3.3, all the other protective measures specified in CIP-006-3c R2.2 had been afforded. The risk associated with instance one was minimal because MRO_URE1's policy to change the password every 90 days is aggressive and well within the 365-day discretionary minimum allowed by CIP-007-1 R5.3.3, the duration was relatively brief, and MRO_URE1 timely detected and self-reported the noncompliance. However, MRO determined the overall combined risk of this violation was moderate. Failure to assess security patches (instance two) represents a significant two-fold potential risk. For instance, the device may have a vulnerability, which is the purpose of the patch, and by the nature of the release of the patch, the vulnerability is well-known to those who may have a malicious intent to exploit the vulnerability. For instance three, the sharing of personal passwords is an indicator of weakness in the effectiveness of a training program, and the issue increases the potential for unauthorized physical access to control centers. This violation would typically pose a serious risk, but the risk was mitigated because it was timely discovered and was self-reported, and the noncompliance was limited to a few days, which is an indication of strong secondary controls. Further, the contractor in question only had physical access, and did not have logical or interactive access. Finally, MRO_URE1 promptly terminated the contractor who shared the password and reassigned the contractor who used the shared password, which displays a commitment to ensuring security of its facilities and the BPS. | When the shared administrator password was due to be reset | When the badge administrator accounts were disabled | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. performed a CIP V3 and V5 assessment to determine what devices, if any, would be considered CIP Electronic Access Control Monitoring Systems (EACMS) or information repositories; 2. redesigned and procured needed hardware and software; 3. redesigned architecture to accommodate the Energy Management System environment; 4. installed systems and configured the environment; and 5. tested the functions of the specific system tool. | 2015-08-27 | 2016-01-03 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-006 R2 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011986 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R3.1. There were four instances of noncompliance: 1. MRO_URE1 reported that a security patch was released , but was not assessed for applicability for almost two months, which exceeded the 30 days allowed by R3.1. The duration of the instance was approximately 24 days. 2. MRO_URE1 reported that a significant security patch was released but was not assessed for over five months, which exceeded the 30 days allowed by R3.1. The duration of the instance was approximately 100 days. 3. MRO_URE1 reported that it was not receiving security patch notifications for a certain operating system The duration of the instance was approximately 5 years. 4. MRO_URE1 reported that a review of its Security Patch Management controls identified a security patch that had not been assessed within 30 days of availability as required by R3.1. The duration of the instance was approximately one day. The root cause for failing to assess the security patches for instances one and three was miscommunication regarding the lack of notification of released patches. The root cause for instances two and four was ineffective internal controls to ensure adherence to MRO_URE1's Security Patch Management Program. | CIP-007-1 | R3: R3.1 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-1 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for infiltration of unauthorized network traffic into the Electronic Security Perimeter (ESP) when security patches and upgrades are not installed on Cyber Assets within the ESP. Notwithstanding, all the issues were self-identified and self-reported, evidencing strong detective controls. Additionally, the noncompliance involving instances one and two were only applicable to substations, had a duration of less than 100 days, and were promptly mitigated. Further, instance three was merely a documentation error, and was mitigated by the submission of a Technical Feasibility Exception (TFE). Further, instance four had a duration of only one day. Additionally, MRO_URE1 states that the Critical Cyber Assets (CCAs) were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When the first security patch for the full operating system was not updated | When MRO_URE1 submitted a TFE for certain patches | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. conducted initial training and awareness regarding compliance instances to affected employees; 2. implemented an action tracking tool to assign due dates and completion dates; 3. evaluated use of a third party for notification to monitor alerts; 4. reviewed, enhanced, and communicated security patch management program and developed a security patch management tracking sheet; 5. evaluated the possibility of a TFE submission for SEL human-machine interface devices; 6. reviewed CIP-007 R3 Security Patch Management with Energy Management System (EMS) personnel to ensure they understand the criticality of Security Patch Management; 7. reviewed Security Patch Management process for all EMS team-controlled CIP Cyber Assets to ensure proper steps are fully documented; 8. identified and applied opportunities for improvement in the Security Patch Management process; 9. reviewed, trained, and reinforced new processes and evidence with MRO_URE1 staff in order to meet CIP requirements; and 10. performed regular Security Patch Management improvement validation on a sampling of patches to determine that evaluations are being performed in a timely manner. | 2014-05-28 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R3 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012126 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R4.2 because it failed to implement its process for the update of anti-virus and malware prevention signatures for certain Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). MRO_URE1 replaced its antivirus software, but failed to include all of the operating regions in the implementation. As a result, MRO_URE1 stopped receiving the automatic signature updates for certain CCAs. Signature updates of certain CCAs within the MRO_URE1 control center were not implemented, as required by R4.2. The duration of the instance was approximately 15 months. This violation occurred when MRO_URE1 stopped receiving automatic updates for the antivirus product and MRO_URE1 staff mistakenly believed that the first antivirus product was replaced company-wide by the second antivirus product. The root cause of the violation was lack of project oversight to ensure that the anti-virus product had been implemented on certain Cyber Assets within the ESP at MRO_URE1's primary and backup control centers. | CIP-007-3a | R4: R4.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-3a R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for the introduction, exposure, and propagation of malware on Cyber Assets within the ESP. The failure to update the anti-virus signatures for a large control center for over one year is a significant oversight and demonstrates a lack of attention to procedures. Notwithstanding, the violation was self-identified and self-reported, which is evidence of strong detective controls. Additionally, the anti-virus and malware prevention software was still running, albeit with outdated signatures. Further, MRO_URE1 installed an intrusion detection system (IDS) which was configured to detect the presence of viruses and malware at the access point to the ESP. IDS was not required at the time of the violation and is typically considered sufficient to meet the anti-malware requirements for CIP version 5. Finally, MRO_URE1 provided evidence that it provides training on the risks of removable media, which is the most common method for malware to infect control systems. This type of training is not required under CIP version 3. Additionally, MRO_URE1 stated that its CCAs and non-CCAs within the ESP were protected by pairs of firewalls running in an active/standby configuration, and configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. MRO_URE1 deployed intrusion prevention/detection systems on the outside of the ESP firewalls, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions to the control system ESP. MRO_URE1 implemented additional protective measures to protect Cyber Assets inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, host-based anti-malware systems, where technically feasible; password and lockout policies; and personnel physical and cyber access reviews and control processes. In addition, MRO_URE1's control system network had no direct Internet connectivity, no access to e-mail servers or clients, and auto-run/auto-play functions were disabled on certain devices. Finally, access to MRO_URE1's Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When MRO_URE1 failed to run the necessary antivirus signatures | When the signature updates were performed for certain CCAs in MRO_URE1's primary and backup control centers | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. installed anti-virus software, along with the most current anti-virus signature updates, on the MRO_URE1 EMS ESP Cyber Assets; 2. provided additional training to MRO_URE1 staff with security responsibilities; and 3. updated change management procedures to provide additional management oversight of anti-virus updates to ensure signatures remain current. | 2013-08-28 | 2014-10-31 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R4 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013054 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. During its annual Substation Cyber Vulnerability Assessment (CVA), MRO_URE1 identified the following issues: 1. Approximately 40 percent of MRO_URE1's Critical Asset substations were found to have at least one protective relay with a default password that had not been changed since installation. The duration of the instance was approximately three-and-a-half years. 2. Approximately eight percent of MRO_URE1's Critical Asset substations were found to have a “backdoor” default password on six Remote Terminal Units (RTUs) (that were designated as Critical Cyber Assets (CCAs)) that had not been changed since installation. The duration of the instance was over four years. 3. Approximately 18 percent of MRO_URE1's Critical Asset substations were found to have a “super-user” default password on the legacy tone communication equipment which was not capable of being changed as required. If this issue had been documented, it would not have been a violation under CIP V5. The duration of the instance was over one month. 4. Approximately 28 percent of MRO_URE1's CCAs had a default password that had not been changed. The duration of the instance was approximately three years. 5. During an internal MRO_URE1 review of account management, sufficient evidence was not available to assure that a thorough review of access privileges had been performed on time, as required by R5.1. Available evidence did not consistently list the authorized shared account users, the authorized shared account users that had no activity for that quarter, or that all authorized shared account users were reviewed to determine whether they had a continued business need to maintain their access, as required by R5.2.2, R5.2.3, and R5.1, respectively. The review revealed that the documentation provided as evidence of the shared account activity annual review did not match the dated attestation provided by the personnel who performed the review. The review also identified eight shared accounts which did not have an audit trail of account use, as required by R5.1.2. The duration of the instance was approximately five years. The primary cause of the findings was a lack of sufficient processes regarding adherence to CIP requirements. MRO_URE1 made aggressive changes to its internal substation policies and procedures, and has since aggressively looked for areas of noncompliance. These findings are a result of that effort. | CIP-007-1 | R5: R5.1; R5.1.2; R5.2; R5.2.2; R5.2.3; R5.3; R5.3.3 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The need to change default passwords on CCAs is fundamental. The accounts with default passwords present the most risk because they are typically “super-user” accounts that have broad capability to configure and/or operate the Cyber Assets. The risk is significant for these accounts with default passwords because the password can be easily obtained. However, for parts one through four of this violation, regarding the default password issues, the risk related to unchanged default passwords was reduced for the following reasons: 1. The issues were self-identified by MRO_URE1 and promptly mitigated. Additionally, MRO_URE1 initiated a comprehensive mitigation plan to ensure that all default passwords were discovered; 2. The issues were limited to substations and did not impact control centers; and 3. MRO_URE1 was conservative during the determination as to what substations constituted Critical Assets in its Risk-Based Assessment Methodology (RBAM). This is evidenced by the reduction in Version 3 Critical Asset substations compared to Version 5 Medium Impact substations after applying the bright-line impact rating criteria. The comprehensive review of access and approval is critical in ensuring the access approval and termination process is complete and accurate. For part number five of this violation, regarding the account management issue, the potential effectiveness of this critical management practice was reduced in the event that an adversary was utilizing a shared account. The potential risk was reduced by the following factors: 1. This issue was self-identified during an internal review which was not mandated by the requirements; 2. The review of shared accounts is performed quarterly as opposed to yearly, which is the maximum duration allowed by the Standard; and 3. The lack of an audit trail, which was identified during the review, is mitigated by the corporate policy of requiring two-factor authentication for remote access into an ESP. This was not mandated until Version 5 of the requirements. | When MRO_URE1 was required to be compliant with CIP-007-1 R5 | When the Mitigation Plan was completed | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. changed the default passwords on protective relay devices that were identified during the Cyber Vulnerability Assessment (CVA); 2. developed a list of devices that are known to have default passwords; 3. developed a Substation CVA procedure; 4. enhanced CVA process procedure and templates relating to default password and network community string checks; 5. changed the default passwords on RTU devices and disconnected devices with super-user passwords; 6. performed Quarterly Activity Report (QAR) validations; 7. reviewed manufacturer technical manuals to identify factory default accounts or passwords; and 8. developed a plan to change any newly identified default accounts and passwords. | 2016-03-25 | 2016-09-26 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R5 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012127 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R6. MRO_URE1 failed to implement security status monitoring for certain assets within the Electronic Security Perimeter (ESP). An application was installed to monitor an operating system, but did not adequately address the requirements of R6 for the certain assets. This noncompliance was uncovered during an internal Energy Management System (EMS) review of the software inventory list for all operating regions. Many assets were affected by this noncompliance, including multiple control centers and numerous Critical Cyber Assets (CCAs). The root cause was insufficient processes. | CIP-007-1 | R6: R6.1; R6.2; R6.3; R6.4; R6.5 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to monitor the security status of multiple large control centers is a significant oversight and can potentially cause significant risk in the system. A violation of CIP-007-1 R6 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of CCAs and other system events that are related to cyber security to occur without the Responsible Entity’s knowledge. Notwithstanding, the requirement for logging and the associated monitoring of logs is a detective control, as opposed to a preventive control. The requirement for the reporting of security status events can help limit the effect of attacks, but does not prevent them from occurring. Further, MRO_URE1 utilized an intrusion detection system (IDS), which was configured to detect the presence of viruses and malware at the access point to the ESP. IDS was not required at the time of the violation and is typically considered sufficient to meet the anti-malware requirements for CIP version 5. Moreover, MRO_URE1 provided evidence that it provides training on the risks of removable media, which is the most common method for malware to infect control systems. Additionally, this type of training is not under version 3 requirements of the standard. Further, the violation was self-identified, evidencing effective internal controls. MRO_URE1 also stated that its CCAs and non-CCAs within the ESP were protected by pairs of firewalls running in an active/standby configuration, and configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. MRO_URE1 deployed intrusion prevention/detection systems on the outside of the ESP firewalls, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions to the control system ESP. MRO_URE1 implemented additional protective measures to protect Cyber Assets inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, host-based anti-malware systems, where technically feasible; password and lockout policies; and personnel physical and cyber access reviews and control processes. In addition, MRO_URE1's control system network had no direct Internet connectivity, no access to e-mail servers or clients, and auto-run/auto-play functions were disabled on all Windows devices. Finally, access to MRO_URE1's Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When the Standard became mandatory and enforceable on MRO_URE1 | When MRO_URE1 completed the process of configuring and testing to ensure that all Cyber Assets within its ESPs were properly logging, monitoring, and alerting for events | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. reviewed monitoring and event alerting implementation plan and architecture; 2. implemented monitoring and event alerting on certain devices; 3. reviewed monitoring and event alerting of Cyber Assets in ESPs; and 4. updated Cyber Asset configuration documentation and validated that all Cyber Assets were properly configured. | 2013-10-29 | 2014-10-31 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-04-27 | FERC | NP17-22-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013116 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R6. While reviewing access logs and camera footage for the MRO_URE1 control center, MRO_URE1 identified that a cleaning contractor (contractor one) had entered the control center but did not sign in using the manual log. Contractor one was granted access by a second cleaning contractor (contractor two) who had badge access but also did not sign in using the manual log. MRO_URE1 further discovered that contractor two provided access to contractor one daily for approximately eight days. In each instance, contractor one was in the control center for up to thirty minutes performing cleaning duties. Personnel for the cleaning contractor had received training in CIP access requirements. Upon learning of the issue, MRO_URE1 promptly issued written and telephone notice to the contract vendor to take corrective action. The root cause of the violation was the contractor’s failure to fully understand MRO_URE1's escorted visitor policy. | CIP-006-3c | R6 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R6 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of Cyber Assets to occur without the Responsible Entity’s knowledge. Notwithstanding, the unauthorized visitor (contractor one) was properly escorted by the authorized contractor (contractor two). Additionally, the issue occurred at a manned distribution control center with limited BPS Critical Assets. Finally, the issue was self-identified and promptly mitigated, which is an indication of strong internal controls. | When contractor one first accessed the MRO_URE1 control center without following the access policy | When contractor one last accessed the MRO_URE1 control center without following the access policy | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. allowed only CIP-certified contract cleaners to enter the MRO_URE1 CIP-restricted areas, as MRO_URE1 no longer permits escorting of non-certified CIP personnel; 2. provided CIP certification training to contract cleaners whose job duties require CIP access, including building supervisor, primary cleaner, and one alternate, in their primary language; 3. reinforced the policy that only CIP-certified cleaners may clean the CIP spaces, and that if there are no CIP-certified cleaners available, the spaces should not be cleaned; and 4. requires quarterly CIP re-training for all contract cleaners with CIP access. Records will be kept in each individual's personnel folder, available upon request. | 2013-10-11 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-006 R6 was not considered an aggravating factor.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014836 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-004-3a R4. RFC_URE1 discovered that although it conducted reviews during the second and fourth quarters of a certain year of all lists of personnel who had authorized cyber access to Critical Cyber Assets (CCAs), it failed to include a particular segment of personnel in both cases. Additionally, RFC_URE1 also discovered that it failed to conduct the requisite review of personnel with authorized unescorted physical access to CCAs. The root cause of this violation was that RFC_URE1 relied on a manual process to conduct its personnel list reviews. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, developing a program to manage employee permissions and access to assets. | CIP-004-3a | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the quarterly review process is a redundancy and not the primary mechanism RFC_URE1 utilizes to identify personnel who no longer require access. RFC_URE1 primarily uses a personnel status change and access revocation procedure and software application to initiate the removal of an individual’s cyber or physical access when it is no longer required. This procedure requires RFC_URE1 supervisors and contractor sponsors to submit a personnel status change and access revocation ticket whenever access is no longer required. Second, RFC_URE1 properly followed the personnel status change and access revocation procedure in this case and identified and removed cyber access for one individual despite the fact that the individual remained on the access list, which RFC_URE1 failed to review on a quarterly basis. | the beginning of the third quarter | when RFC_URE1 completed all of the requisite reviews | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) removed from the list the one individual identified who no longer required authorized cyber access to CCAs; 2) entered quarterly reviews into an electronic system that will automatically notify by email the responsible departments. These notifications will be initiated at the beginning of each quarter and will continue weekly for 60 days and then daily until the electronic task is completed; 3) assigned responsibility to an IT compliance team to update and maintain the electronic system used to track the required quarterly reviews. This team will develop a procedure that will ensure independent monitoring of the quarterly review process, including a scheduled monthly meeting to review the status of all pending quarterly reviews; and 4) configured the electronic system used to track the required quarterly reviews to automatically provide daily email notifications to management and compliance personnel whenever the quarterly reviews are not completed 30 days prior to the end of the quarter. This escalation process is designed to ensure that the proper attention and resources are focused on completing the quarterly reviews. | 4/30/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014973 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-004-3a R4. RFC_URE1's internal control designed to monitor personnel status changes within the payroll system detected that ten days prior a RFC_URE1 employee with Critical Cyber Asset (CCA) access started a new job at a different facility and no longer required unescorted physical access to CCAs. Upon discovery, RFC_URE1 immediately removed authorized unescorted physical access to CCAs for this employee. The root cause of this first instance of the violation was the fact that the employee’s supervisor did not enter a ticket in the personnel status change and access revocation system to revoke access. The supervisor’s oversight was the result of the fact that he had been recently promoted to the position and had not received the annually provided training on using the personnel status change and access revocation system and the importance of entering tickets in the system. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, delivering training, education, and awareness to employees. During the course of mitigating this particular instance, RFC_URE1 discovered two additional instances involving access revocation for a college intern who planned to work when school was not in session. The intern did not require access to CCAs for a period of approximately three and a half months, and for a separate period of approximately one and a half months. However, the intern’s supervisor did not submit a formal request to remove the intern’s access via RFC_URE1's personnel status change and access revocation. Consequently, the intern’s name remained on the list of personnel with authorized cyber or authorized unescorted physical access to CCAs. Notably, prior to the intern’s departure on both occasions, the intern was required to surrender his access badge and electronic authentication device to his supervisor. Therefore, the intern did not have access during these periods of time. The root cause of this second instance of the violation was that RFC_URE1 had not made extensive use of interns in recent years and its personnel status change and access revocation policy did not specifically address interns who frequently return to the company to work every few months. Therefore, the intern’s supervisor was not aware of his responsibility to initiate a request via the personnel status change and access revocation system in order to have the intern’s name removed from the access list. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, developing a program to manage employee permissions and access to assets. | CIP-004-3a | R4 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. With respect to the first instance, RFC_URE1's internal controls quickly and effectively detected the issue and alerted the appropriate personnel to investigate and correct it. Although the employee no longer required access to CCAs, the employee remained properly qualified per the RFC_URE1 cyber security policy and remained a RFC_URE1 employee in good standing following the position change. With respect to the second instance, as stated earlier, the access list is a redundancy, and despite the fact that the intern’s supervisor did not follow RFC_URE1's personnel status change and access revocation policy, the supervisor collected the intern’s physical access badge and electronic authentication device. Moreover, the intern remained properly qualified per RFC_URE1's cyber security policy for access, meaning that he had undergone a current background check and annual training. | when the first employee should have had access revoked | when the employee should have had access again | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: With respect to the first instance: 1) revoked authorized unescorted physical access to CCAs for the employee involved; 2) provided training, both verbal and written, to the supervisor related to the personnel status change and access revocation process; 3) established a process to provide electronic training materials to newly hired or promoted supervisors and new sponsors concerning the personnel status change and access revocation procedure within 30 days of their assuming the position. The new supervisors and sponsors will confirm electronically that they have reviewed the training materials and understand the process; 4) implemented a quarterly awareness process that will remind supervisors and sponsors of the personnel status change and access revocation procedure and their obligation to submit a ticket whenever there is a personnel change. The awareness process will utilize various communication methods including, but not limited to, emails, newsletters, bulletin boards, RFC_URE1 intranet, and corporate video communication screens; and 5) conducted the annual personnel status change and access revocation procedure interactive training earlier in the year to communicate the new expectations for training new supervisors and sponsors, and the quarterly awareness program. With respect to the second instance: 1) modified the language of the personnel status change and access revocation and the associated training material to further define the term “Personnel” to include interns; and 2) communicated to supervisors and sponsors via an awareness email the recent change made to the personnel status change and access revocation policy that the definition of “Personnel” has been clarified to include interns. | 6/30/15 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the effective execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014832 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-005-3a R1. During its annual Cyber Vulnerability Assessment, RFC_URE1 discovered that an Electronic Access Control and Monitoring (EACM) device (i.e., a firewall), which was used for access control of an Electronic Security Perimeter, had a default Simple Network Management Protocol (SNMP) community string. (An SNMP is like a password and allows or denies access to a device. Most network vendors ship their equipment with a “default community string,” which is like a default password.) Upon further investigation, RFC_URE1 discovered that the SNMP default community string on this EACM device had been in use since the device was placed into service approximately three years earlier. This circumstance was scheduled to be corrected during the year being audited, along with a second redundant EACM device, when they were being upgraded to a newer SNMP version. However, during the scheduled work, the SNMP version upgrade was first applied to the secondary device, which resulted in the SNMP failing. The SNMP upgrade was backed out per the change control procedure, and a ticket was opened with the vendor to assist in the resolution of the issue. The RFC_URE1 subject matter expert performing the change did not upgrade the primary device until the issue with the SNMP upgrade on the secondary device had been resolved. However, because the issue had not been resolved, the primary EACM device was never removed from service to perform the SNMP upgrade and the default community string remained. The root cause of this violation was the fact that the device configuration checklist for this particular device type did not contain detailed instructions for configuration of SNMP. This major contributing factor relates to the management practice areas of asset and configuration management, which focuses on, inter alia, controlling changes to assets, and implementation, which focuses on, inter alia, identifying technical processes or technical areas associated with deployment of new designs or revisions to existing design critical to grid reliability. | CIP-005-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the firewall at issue was locked down and did not allow remote access such that only RFC_URE1's network team could access it by physically being present. Second, the information at risk was limited to information about the hardware itself (e.g., manufacturer, date of production, etc.) and not about the network. Third, the SNMP default community string only applied to this one specific device (primary and secondary). Therefore, an attacker could not use this information to glean any additional information from other servers. Fourth, the EACM device was protected behind corporate firewalls restricting access from networks external to RFC_URE1. | when RFC_URE1 put the primary EACM device into service | when RFC_URE1 changed the SNMP default community string on the EACM device | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) changed the SNMP default community string on the EACM device in addition to completing the SNMP version upgrade; 2) reviewed and strengthened all EACM configuration checklist documents to include the review and modification of the default SNMP community strings; and 3) changed the system used to monitor the health of cyber assets to deny access for connected cyber assets that have default SNMP community strings. This change will provide an additional control when new devices are placed into service. | 4/15/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-005 R1 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014714 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-006-1 R1. During planned monthly periodic testing of RFC_URE1's Physical Access Control System (PACS), RFC_URE1 discovered that access to a single Physical Security Perimeter (PSP) was not restricted to personnel who had been granted unescorted physical access. Security personnel were able to gain access to the PSP using a special “test” ID Card, which had been configured without unescorted physical access credentials. RFC_URE1 investigated the incident and discovered that the PACS Network Controller located within the PSP had failed to properly reboot following a configuration change initiated via a communication network from a centrally located PACS workstation. This configuration change was inadvertently attempted on this Controller five days earlier by a RFC_URE1 CIP-qualified contractor conducting maintenance on the PACS. The contractor failed to notify RFC_URE1 personnel that the Controller configuration change attempt had occurred, which resulted in RFC_URE1 personnel not performing the required Controller testing following a configuration change. This failed reboot left the Controller in an abnormal state, resulting in access to the specific PSP being granted to personnel with any RFC_URE1 ID Card, regardless of the individual’s specific access credentials. Additionally, the Controller failed to either internally or externally log access to the PSP during the five-day period. Upon further investigation, RFC_URE1 also discovered that although the PACS Controllers are part of the overall PACS, RFC_URE1 had not afforded the PACS Controllers the protective measures as required by CIP-006-3c R2. RFC_URE1 personnel did not initially believe that the PACS Controllers were within the scope of this Standard/Requirement because RFC_URE1 believed that they did not overtly perform the functions of granting or logging access. Rather, RFC_URE1 stated that these Controllers serve as intermediary devices that convert and communicate programmed instructions from centralized PACS servers to the physical security access devices as part of the authentication process necessary to gain access to PSPs. During normal operations, RFC_URE1 does not use these Controllers to independently authorize or log access to PSPs. The root cause of this violation was human error. With respect to the specific issue with the improper configuration of the PACS Controller, RFC_URE1 did not include the PACS Controllers in the same change control process used for PACS workstations and servers. This omission contributed to the miscommunication between the contractor performing the work and the responsible RFC_URE1 personnel. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, controlling changes to assets. With respect to the broader issue of including PACS Controllers under CIP-006 R2, RFC_URE1 personnel misinterpreted the Standard/Requirement, which resulted in a multi-year duration. (RF notes that the new CIP-006-5 R3 Part 3.1 explicitly brings this type of equipment into scope to avoid this type of misinterpretation. Specifically, CIP-006-5 R3 Part 3.1 provides: “Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly.”) The issue related to this specific Network controller being left in an abnormal state began when the configuration change was inadvertently attempted, and ended five days later, when RFC_URE1 conducted the successful reboot which restored the Network Controller to its normal operating state. The broader issue related to affording these Controllers the protective measures as required by CIP-006-3c R2 started on the date RFC_URE1 was required to comply with CIP-006-1 R1 and ended approximately five and a half years later on the date RFC_URE1 completed its Mitigation Plan. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during the five-day window when the PACS Controllers were left in an abnormal state, RFC_URE1 was vulnerable to the risk of insider threats because any RFC_URE1 personnel with an ID badge could have gained access to the PSP. Furthermore, RFC_URE1 would not have been able to identify who accessed the PSP during this five-day window because the PACS Controllers were not logging access. Second, in addition to this five-day window of vulnerability, RFC_URE1 failed to afford its PACS Controllers the other protections required by CIP-006 R2 for over five years. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 proactively identified this instance related to the abnormal state of the PACS Controllers through its internal detective controls. Specifically, RFC_URE1 security personnel discovered this abnormal condition during planned monthly PACS testing. However, RF notes that RFC_URE1 should have identified this condition more promptly by conducting this planned monthly PACS testing more frequently. Second, the PACS Controllers were within PSPs or locations which are monitored 24 hours per day, 7 days per week by security personnel. In fact, before an unauthorized person would have been able to gain access to this particular site, he or she would have been required to pass two outer check points at the facility. Third, the PACS Controllers are located within locked cabinets with tamper alarms such that only RFC_URE1 CIP-qualified personnel had access to them. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) conducted a forced reboot of the device using the proper configuration settings upon discovery of the abnormal Controller condition at the specific PSP location. After the Controller was rebooted, security personnel conducted a test using a special “test” ID Card to verify that the PACS was functioning properly and access to this specific PSP was not permitted for personnel not granted unescorted access. In addition, Security personnel verified that the remaining 14 PACS Controllers related to PSPs were functioning properly and in a normal state; 2) implemented new visual indicators and alarming on the PACS system displays to alert security personnel of Controllers in an abnormal operating condition; 3) revised the configuration of all 15 PACS Controllers related to PSPs to include a new, more secure default setting. This setting change will ensure that if a Controller enters an abnormal state for any reason, it will deny access for all access attempts. This new configuration will ensure access to a PSP is controlled and prompt an immediate investigation; 4) tested all 15 PACS Controllers related to PSPs, after implementation of the new Controller configuration described in Item 3 above, in an abnormal state to verify that the new setting denies access to the PSP as expected; 5) included the Controllers in the same change control process used for PACS workstations and servers in order to ensure that the configuration of all 15 PACS Controllers related to PSPs are properly maintained following required changes. Changes to Controllers could include but are not limited to: replacement, operating system upgrades, application revisions, patching, configuration changes, etc.; 6) reviewed and approved the personnel with authorized individual or shared account access to the Controllers, by the designated individual responsible for authorizing such access, to ensure their “need to know” with respect to work functions performed; 7) designated a person for the Controllers to be included on the RFC_URE1 list of designated personnel who are responsible for authorizing logical or physical access to protected information; 8) added the Controllers to the RFC_URE1 Asset Database that is used to track cyber assets within the scope of the RFC_URE1 CIP Cyber Security Policy. Inclusion of the devices in this database will ensure they are included in the RFC_URE1 change and configuration management program as well as covered by all associated RFC_URE1 Cyber Security Policy procedures and processes (i.e. cyber vulnerability assessments, incident response plans, etc); 9) developed and implemented a formal change and configuration management procedure that includes the Controllers; 10) verified and/or developed (where required) test procedures that outline testing security controls when significant changes are made to the Controllers; 11) established, documented, and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security patches for the Controllers; 12) developed a policy for managing the Controller shared account that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes; 13) established and implemented formal procedures for the disposal or redeployment of Controllers; 14) created recovery plans for the Controllers that will be reviewed at least annually; 15) documented and implemented the processes and procedures for managing ports and services associated with the Controllers to include documenting those ports and services enabled for operations and for monitoring the Controllers. A Technical Feasibility Exception (TFE) will be submitted for approval for the Controllers with respect to the unused ports and services that cannot be disabled due to technical limitations. In support of the TFE, RFC_URE1 is going to implement an additional layer of firewall protections as a mitigating measure due to the open Controller ports that are not required for operations and cannot be disabled. These firewalls will be configured to disable external access to all ports not needed for operation of the Controllers; 16) submitted a TFE for approval for the Controllers with respect to anti-virus software and malware prevention tools because it is not technically feasible for the Controllers to use anti-virus software and other malware prevention tools; 17) submitted a TFE for approval for the Controllers with respect to the inability to enforce required password complexity for the shared account. Although it is technically feasible for the Controller shared account passwords to consist of a minimum of six characters, and a combination of alpha, numeric and special characters which can be changed annually or more frequently, the Controller cannot enforce use of such password complexity; 18) submitted a TFE for approval for the Controllers with respect to monitoring system events because it is not technically feasible for the Controllers to implement automated tools or organizational process controls to monitor system events related to cyber security; 19) documented the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Controller protected network; and 20) included the devices (Controllers in the RFC_URE1 Asset Database (see Mitigation Action #8 above)) in the scope of all future Cyber Vulnerability Assessments (CVAs) conducted at least annually. However, in order to assess the vulnerability of the Controllers after completing the Mitigation Actions included in this Mitigation Plan, RFC_URE1 will conduct a limited scope CVA for the Controllers. | 2015-08-31 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-006 R1 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014834 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-007-3a R1. During an internal review of CIP-007 R1.3, RFC_URE1 discovered that documented test results could not be located from test procedures used to verify that certain patches did not adversely affect existing cyber security controls for Cyber Assets within the Electronic Security Perimeter. The missing test result documentation included five months of operating system patching, and an upgrade to the reporting tool for the enterprise storage device. RFC_URE1 Subject Matter Experts investigated the occurrence and determined that the requisite test procedures were completed, however the documented results were not available. The root cause of this violation was the fact that RFC_URE1: (a) relied on a manual process for collecting test results as the test procedures were being performed; and (b) lacked a coordinated tracking process. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, verifying the integrity of assets and configuration items by establishing and maintaining change records. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 initially tests patches in its Quality Assurance Program test environment, during which any problems with the patches would have been noted or flagged by the cyber security controls when the device was put into production. Second, this violation is a documentation issue. As explained earlier, RFC_URE1 had performed the requisite testing, but did not collect the test result documentation. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented a change to internal practices to track cyber testing progress and test result documentation; and 2) revised Cyber Security Test procedure to include notification when each phase of testing is completed. | 2015-05-06 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-007 R1 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014775 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-007-1 R2. Following its audit, RFC_URE1 brought in a consultant to help with CIP compliance. However, RFC_URE1 later discovered that it had a misunderstanding of what was required under the standard as a result of this engagement and therefore was not monitoring its UDP ports and services at the appropriate frequency per the Standard. RFC_URE1 had been performing periodic scans of its UDP ports and services. RFC_URE1 determined that it should have been monitoring these ports and services in real time to capture all relevant justifications in its baselines. The root cause of this violation was RFC_URE1's interaction with the contractor, the result of which was RFC_URE1's failure to monitor its UDP ports and services at the required frequency. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, establishing inventory and configuration baselines. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Incomplete or improper baselines make change control and configuration management difficult to perform properly because without proper baselines it is more difficult for an entity to detect and respond to malicious changes. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 was performing periodic scans of its UDP ports and services. Therefore, RFC_URE1 could, at any given time, have produced reports of all open UDP ports and services. Second, RFC_URE1 was protecting the cyber assets that use UDP ports behind corporate firewalls and EACM devices restricting access from the RFC_URE1 corporate network and networks external to RFC_URE1. Additionally, the devices were protected by antivirus and malware prevention software. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) prepared a documented baseline, prior to placing the rebuilt Cyber Assets in-service, for each asset that included the following: (a) Inventory of all Applications required for normal and emergency operations of the Cyber Asset, including the RFC_URE1 group assigned ownership of the Application, version and patching status, and supporting justification for the Application; and (b) Identification of all ports and services required for normal and emergency operation of the Cyber Asset, including supporting justification for the ports and services; 2) rebuilt and configured the Cyber Assets in scope by installing only those Applications that are identified and justified in the baseline documentation. The Applications will be installed at the most current applicable version and patch level; 3) developed, documented, and implemented, in support of the rebuilt Cyber Assets and in conjunction with RFC_URE1's CIPv5 implementation project, new processes and procedures concerning change control, configuration, and patch management. These new processes and procedures will ensure that the Cyber Assets (after being placed in service) continue to have only those Applications installed and ports and services enabled that are justified for normal and emergency operations; 4) enabled host-based firewalls on each of the Cyber Assets in scope to deny access to all ports and services that are not documented as required for normal and emergency operations of the Applications on the Cyber Asset. The host-based firewalls will be in addition to the existing perimeter-based firewalls that deny access to unjustified ports and services by default; and 5) tested each Cyber Asset to ensure that only it enables only those ports and services that are identified and justified in the baseline documentation. After each of the newly rebuilt Cyber Assets are tested, they will be placed in service in the new network environment. | 2016-03-18 | 2016-05-02 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-007 R2 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015015022 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-007-1 R3. RFC_URE1 conducted an investigation of recent industry threat intelligence and discovered that certain third-party applications installed on Cyber Assets within the Electronic Security Perimeter (ESP) did not have appropriate patches applied. These third-party applications did not include the operating systems or primary applications (such as the SCADA system, state estimator, etc.) on the Cyber Assets within the ESP. Additionally, while performing the mitigating actions, RFC_URE1 utilized a patch monitoring system to monitor operating systems for applications that require patching. This system leveraged a tool to assist in identifying missing patches and potential vulnerabilities. RFC_URE1 assessed the tool's reports daily as part of its normal process and analyzed them through its existing risk assessment process, which considers: (a) how the vulnerability is exploited; (b) if the vulnerability has an active exploit; (c) if the vulnerability can be exploited with the other controls in place; and (d) what the vulnerability might affect. Through this process, no new vulnerability was ranked as “critical” to the environment during this time period. However, the evaluation of each patch was not individually documented during this period, as the formalized process for patch management for third-party applications was not in place until required under the mitigation plan. The root cause of this violation was the fact that RFC_URE1 had not established, documented, or implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for these third-party applications. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, establishing inventory and configuration baselines. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that patching is a baseline compliance and security activity. The failure to install patches can result in computers and servers crashing, creating a reliability issue. This risk was mitigated by the following factors. First, the applications affected did not include the operating systems or primary applications (such as SCADA). Second, the Cyber Assets at issue were protected behind ESP Electronic Access Control and Monitoring devices and did not have access to the RFC_URE1 corporate network or the internet. Furthermore, these Cyber Assets were not used for corporate functions like email or internet access. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) prepared a documented baseline, prior to placing the rebuilt Cyber Assets in service, for each asset that will include the following: (a) Inventory of all Applications required for normal and emergency operations of the Cyber Asset, including the RFC_URE1 group assigned ownership of the Application, version and patching status, and supporting justification for the Application; and (b) Identification of all ports and services required for normal and emergency operation of the Cyber Asset, including supporting justification for the ports and services; 2) rebuilt and configured the Cyber Assets in scope by installing only those Applications that are identified and justified in the baseline documentation. The Applications will be installed at the most current applicable version and patch level; 3) developed, documented, and implemented, in support of the rebuilt Cyber Assets and in conjunction with RFC_URE1's CIPv5 implementation project, new processes and procedures concerning change control, configuration, and patch management. These new processes and procedures will ensure that the Cyber Assets (after being placed in service) continue to have only those Applications installed and ports and services enabled that are justified for normal and emergency operations; 4) enabled, as an above and beyond measure, host-based firewalls on each of the Cyber Assets in scope to deny access to all ports and services that are not documented as required for normal and emergency operations of the Applications on the Cyber Asset. The host-based firewalls will be in addition to the existing perimeter-based firewalls that deny access to unjustified ports and services by default; and 5) tested each Cyber Asset to ensure that it enabled only those ports and services that are identified and justified in the baseline documentation. After each of the newly rebuilt Cyber Assets are tested, they will be placed in service in the new network environment. | 2016-03-18 | 2016-04-29 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1’s response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF considered RFC_URE1’s CIP-007 R3 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014833 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-007-3a R5. During its annual Cyber Vulnerability Assessment, RFC_URE1 discovered that four Critical Cyber Assets and one non-critical Cyber Asset within the Electronic Security Perimeter had a default Simple Network Management Protocol (SNMP) community string. RFC_URE1 investigated and determined that the SNMP default community strings on these servers had been in use since the devices were placed into service. The root cause of this violation was the fact that the device configuration checklist for these devices did not contain detailed instructions for configuration of SNMP. This major contributing factor relates to the management practice areas of asset and configuration management, which focuses on, inter alia, controlling changes to assets, and implementation, which focuses on, inter alia, identifying technical processes or technical areas associated with deployment of new designs or revisions to existing design critical to grid reliability. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the information at risk was limited to information about the hardware itself (e.g., manufacturer, date of production, etc.). Second, each SNMP default community string only applied to the one specific device. Therefore, an attacker could not use this information to glean any additional information from other servers. Third, these devices were protected behind corporate firewalls restricting access from networks external to RFC_URE1. Furthermore, these devices are located within controlled access facilities, which include protection against unauthorized physical access with multiple layers of electronic and physical access controls, such as guards, account management, and access controls. | when RFC_URE1 placed the devices into service | Mitigating Activities completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) changed the SNMP default community strings on the five servers; 2) reviewed all server configuration checklist documents and strengthen the SNMP configuration section by including the review and modification of the default SNMP community strings; and 3) changed the system used to monitor the health of cyber assets to deny access for connected cyber assets that have default SNMP community strings. This change will provide an additional control when new devices are placed into service. | 4/15/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF did not consider RFC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014837 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF reporting it was in violation of CIP-007-1 R5. During its comprehensive internal review of its processes and procedures, RFC_URE1 discovered that it had not tracked shared database accounts until it determined that individual users had access to these shared accounts. Upon further investigation, RFC_URE1 also discovered that, although technical and procedural controls were in place to manage shared accounts, including limiting access to those with authorization and logging usage of shared accounts, RFC_URE1 failed to maintain an audit trail that associated the authorized user’s identity with each individual use of the shared account. Additionally, while performing the mitigating actions, RFC_URE1 discovered that it failed to include integrated access cards in its review of all shared accounts. Integrated access cards are remote access cards that provide administrators with the ability to remotely access physical servers in order to troubleshoot issues when a physical server is no longer responding. RFC_URE1 reviewed the use of these shared accounts and added them to the procedure controls put in place as part of the mitigating actions. The root cause of this violation was the fact that RFC_URE1 did not believe these particular accounts were covered by the Standard/Requirement because these accounts cannot provide interactive access to Cyber Assets. With respect to the audit trail issue, RFC_URE1 did not believe that it was required to track shared account usage down to the individual authorized user at the time of each use. | CIP-007-1 | R5 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 had processes and procedures in place to know who had access to the shared accounts and, where technically feasible, had maintained logs of shared account use. Second, access to all shared accounts associated with Critical Cyber Assets and non-critical Cyber Assets within the Electronic Security Perimeter required users to have either authorized cyber access or unescorted physical access, which included current background checks and annual training. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented a manual audit trail process to track the individual user when the shared account is used for the following shared accounts: administrative, system, application, and generic accounts which allow for interactive logons (excluding field devices). The manual process requires the individual user to send an email to a designated email account that includes the following information: (a) Shared Account Name; (b) Individual user of the shared account; and (c) Date and Time when access was required; 2) reviewed all shared database accounts to identify the owner and to create a list of authorized individual users of the accounts. An audit trail of when the shared database accounts are used and the individual authorized user will be retained by using the manual methods described in Mitigation Action #1 above; 3) configured the RFC_URE1 work management system with new device-specific work orders for field devices that are accessed via a shared account. When work activities are completed on these devices using the new work order, the user is forced to respond as to whether a shared account was used to access the device. The responses will be saved in the work management system, and a report will be produced to create an audit trail of the date the shared account was used and the individual authorized user; 4) formalized the manual audit trail process by including the procedure in the RFC_URE1 IT Technology Standards document. In addition, the account type definitions have been established and also inserted into the IT Technology Standards; 5) disabled, where possible, through verified testing, the interactive logon for the accounts identified in Mitigation Action #1 above, by enabling the following user rights assignments via Group Policy: Deny Logon Locally and Deny Logon Thru Terminal Services. This will remove the ability for an individual to use the account for interactive access; and 6) replaced, where possible, the accounts identified in mitigation action #1 (above) with individual accounts, which will then be tracked to the SMEs assigned to manage the identified devices. After testing, the account will be first disabled and then deleted. | 2015-07-30 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. RF observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. RF focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. RF chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. RF reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, RF seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided RF with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with RF regarding its Alleged Violations, processes, systems, and organization and this insight has allowed RF to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and RF awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which RF therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore RF viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. RF and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. RF considered RFC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2017-04-27 | FERC | NP17-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015861 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. WECC_URE1 reported that it inadvertently approved electronic access to one of its servers (Server A), which was a Physical Access Control System (PACS) server, to nine off-shore contractor personnel. WECC_URE1's Information Technology department (IT) engaged a contractor to obtain technical support for WECC_URE1's IT assets. To receive the technical support needed, an Active Directory group was created, so contractor personnel could electronically access a non-CIP document library, which resided in the same WECC_URE1 admin network as WECC_URE1's upgraded server (Server B). At the time, the upgraded server, Server B, was not a CIP Cyber Asset; however, WECC_URE1 was in the process of upgrading its PACS from one Server A to Server B, making the upgraded Server B a PACS. Upon learning that the contractors could access the upgraded server, Server B, the WECC_URE1 Domain Administrator immediately conducted an investigation of Server A, revealing the same misconfiguration. Once WECC_URE1 discovered this issue, it immediately revoked the electronic access for the nine contractors and promptly corrected the misconfiguration. The root cause was a failure to ensure the individual responsible for creating the Active Directory was aware of CIP standards during the onboarding of the contractors, resulting in a misconfiguration of permissions for a group on a PACS server. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to protect a PACS server from unauthorized electronic access as required by CIP-006-3c R2.2. Such failure could potentially result in fraudulent or errant activity on the CIP Cyber Asset by the parties given access. Depending on the access privileges granted, the potential harm could be significant in that this unauthorized electronic access could lead to access to a Physical Security Perimeter (PSP) which could affect operations, thus impacting the reliability of the bulk power system (BPS). WECC_URE1 had implemented controls to prevent the unauthorized access. The PACS server was actively monitored 24 hours a day, seven days a week; WECC_URE1's PSPs have alarms and alerting for unauthorized physical access. The nine contractors had only local administrative access privileges, which restricted their access to the PACS server software and, therefore, they were unable to change physical access rights; unlock doors to the PSPs; update any panels; or authorize local administrative rights to the server. During the issue, there were no alerts of unsuccessful, and/or failed, attempts to electronically access the Server A servers. Further, there were no configuration changes to the servers and/or attempts to shut down the servers. Finally, none of the nine contractors accessed the servers. | when WECC_URE1 misconfigured a PACS server permission group and provisioned unauthorized electronic access to PACS servers for nine off-shore contractors | Mitigation Plan completion | 26000 | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked the electronic access of the nine contractors; 2) reconfigured the group permissions on the PACS server; 3) created a separate NERC CIP domain for the access control and security management software system; 4) implemented multi-factor authentication to the new NERC CIP domain; and 5) required new access control and security management software IT Administrators be NERC CIP-certified. | 2015-01-22 | 2017-01-06 | Agrees/Stipulates | Credit was not given for WECC_URE1's internal compliance program (ICP). Although WECC_URE1 has a documented ICP that has been provided to WECC; WECC determined that WECC_URE1 did not implement its ICP with effective internal controls in place to identify this issue Credit was not given for self-reporting because the Self-Report was submitted 525 days after WECC_URE1 discovered this issue.
2017-04-27 | FERC | NP17-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014903 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R2. WECC_URE2 reported that it did not maintain technical mechanisms for control of electronic access at 40 Electronic Access Points (EAPs) to the Electronic Security Perimeters (ESPs) as required by CIP-005-3a R2.1. Specifically, during troubleshooting to resolve Energy Management System (EMS) application communication interruptions, WECC_URE2 disabled its Access Control Lists (ACLs) which specified which users or system processes were granted access to 40 EAP devices at several substations and control centers. WECC_URE2's control center reported a large number of red-border statuses on EMS workstations installed at several WECC_URE2 substations. The EMS issues a red-border status when there is a communication interruption between the workstation and the EMS server. The severity of these problems resulted in several EMS workstations becoming unusable. These red-border events happened intermittently, each interruption lasting between 4 to 10 seconds and did not happen daily. At its peak, WECC_URE2 estimated an operator probably experienced a red-border event approximately three times in an hour. WECC_URE2's priority was to stabilize the environment promptly and get workstations running properly. Initial troubleshooting efforts pointed to firewall or network-related issues. WECC_URE2's first attempt was to resolve network port mismatches, and second, WECC_URE2 sought to reduce switch ACL logging. These attempts did not resolve the red-border issues. WECC_URE2 then disabled ACLs on the switches between several substations and control centers to further eliminate variables. Disabling the switch ACLs appeared to reduce, but not eliminate, the number of red-border statuses. WECC_URE2 had previously transitioned operating systems. WECC_URE2, therefore, assessed the associated workstations, to determine whether any of the changes implemented during this transition contributed to the red-border issues. One of the changes implemented during the transition was a reduction of a specific Remote Procedure Call (RPC) dynamic port range. Once WECC_URE2 returned the RPC port range back to its original, pre-transition setting, the operational environment stabilized. WECC_URE2 performed security testing pursuant to CIP-007 as part of the upgrade; however, this issue was not identified during that testing. WECC determined the root cause of this violation to be WECC_URE2 failing to follow its documented processes for emergency deviations from compliance pursuant to CIP-003-3a R1.1, as described in NERC Violation ID WECC2016016705. | CIP-005-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, in this instance, WECC_URE2 failed to maintain ACLs on 40 EAPs at several substations and control centers, increasing the risk of a range of cyber security attacks, which could have resulted in system disruption or disablement, data loss or data theft, and/or remote seizure of WECC_URE2's computer systems. Such cyber security attacks could have directly affected WECC_URE2's ability to effectively control system load on its transmission system, which could be categorized as a potential for causing harm to the BPS, thereby potentially affecting the reliability of the BPS. However, in an effort to mitigate risk, WECC_URE2 maintained all other cyber security controls on its networks, and employed its automation system manager system to monitor for cyber security events on and through the affected EAPs. WECC_URE2 stated that a review of network traffic logs did not reveal any security related anomalies. Additionally, each switching center had multiple EMS workstations that could be used in place of those workstations that experienced red-border issues. As a standard practice, WECC_URE2's switching centers can share their Areas of Responsibility (AORs) with other WECC_URE2 switching centers. If needed, the control center could pass control of an AOR to another switching center without the risk or disruption of control, maintaining continuity of service. While these efforts did help to minimize risk, they were predominately cyber security monitoring actions, and thus could not effectively replace the preventive controls afforded by the ACLs on the EAPs. | when WECC_URE2 disabled the ACLs on the devices in scope | when WECC_URE2 re-enabled the last of the ACLs on the devices in scope | $87,000 (for WECC2015014903 and WECC2016016705) | Self-Report | To remediate and mitigate this violation, WECC_URE2: 1) returned the RPC port range back to its original pre-transition setting; 2) re-enabled the ACLs on 40 EAPs devices, which was coordinated with the staff; and 3) created a new procedure for subject matter experts to follow when a similar issue occurs that gives guidance on proper handling of CIP devices during an outage, and communicated this guidance to all applicable staff. | 7/14/2015 | 11/23/2015 | Admits | Credit was not given for WECC_URE2's internal compliance program (ICP). Although WECC_URE2 has a documented ICP that has been provided to WECC, it is WECC's belief that had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC_URE2 submitted its Mitigation Plan 145 days after self-reporting; therefore, WECC considered the tardiness of the Mitigation Plan as an aggravating factor. WECC_URE2 self-reported 457 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount.
2017-04-27 | FERC | NP17-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016705 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-003-3 R1.1. WECC_URE2 had a temporary deviation from compliance, in accordance with its cyber security policy, when it disabled 40 Access Control Lists (ACLs) in order to troubleshoot an Energy Management System (EMS) application communication interruption. Per WECC_URE2's CIP-003-3 R1 cyber security policy, prior to the deviation or immediately after the issue was resolved, WECC_URE2 was to obtain approval to deviate from compliance from the NERC CIP Senior Manager or delegate(s), which it did not. It was determined that WECC_URE2 did properly vet the change to disable the ACLs, it just failed to obtain the appropriate signature per its cyber security policy. The root cause of this violation was management policy guidance or expectations were not well-defined, understood, or enforced. | CIP-003-3 | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2 failed to implement its CIP cyber security policy. Specifically, failure to obtain NERC CIP Senior Manager approval on an emergency change could have resulted in implementing a change that had not been adequately planned or vetted. The change, which involved disabling 40 Electronic Access Point (EAP) devices, created the potential for a range of cyber security attacks that could have resulted in system disruption; disablement; data loss or data theft; and/or remote seizure of computer systems. Such cyber security attacks could have directly affected WECC_URE2's ability to effectively control system load, which could have had the potential for causing harm to the BPS. However, the likelihood of these situations occurring is low since this is an administrative control and the presence of the NERC CIP Senior Manager's signature does not directly reduce the likelihood of the above occurring. WECC_URE2 implemented controls that reduced the risk utilizing an automation system manager that detects changes to configurations and monitors for cyber security events on its EAPs. In addition, WECC_URE2 utilized physical access controls including, a defense-in-depth strategy, which would lower the likelihood that bad actors could physically access systems. | when WECC_URE2 failed to obtain NERC CIP Senior Manager or delegate(s) approval prior to or immediately after resolution of a temporary compliance deviation per its CIP-003-3 R1 cyber security policy | Mitigation Plan completion | $87,000 (for WECC2015014903 and WECC2016016705) | Self-Report | To remediate and mitigate this violation, WECC_URE2 sent an email to its IT managers instructing them to remind staff and reinforce the importance of following the directives outlined in WECC_URE2's NERC CIP cyber security policy relating to temporary compliance deviations, which indicates should a similar reliability/emergency event occur, a temporary deviation request will be submitted to the IT manager who will in turn communicate it to the WECC_URE2 NERC CIP Senior Manager or delegate for approval. | 2015-07-14 | 2017-01-13 | Admits | Credit was not given for WECC_URE2's internal compliance program (ICP). Although WECC_URE2 has a documented ICP that has been provided to WECC, it is WECC's belief that had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC_URE2 submitted its Mitigation Plan 145 days after self-reporting; therefore, WECC considered the tardiness of the Mitigation Plan as an aggravating factor. WECC_URE2 self-reported 457 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012260 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-1 R4. The initial Self-Report contained two instances of noncompliance. The scope of the violation was increased several times through the Mitigation Plan process, including an additional 17 instances of noncompliance through nine versions of the Mitigation Plan, resulting in a total of 19 instances of noncompliance. The first instance included 71 individuals, 69 students participating in a student work program and two contractors. WECC_URE1 reported that it failed to revoke authorized unescorted physical and/or authorized cyber access rights to Critical Cyber Assets (CCAs) within seven days the individuals who no longer required such access. Access should have been revoked within seven calendar days. However, access was not revoked until approximately three months later. The root cause of this issue was a failure of WECC_URE1's notification process used for revocation of access. The two contractors had been reassigned to other facilities not requiring unescorted physical access. The first contractor, a security guard, was reassigned and should have had his access revoked; however, WECC_URE1 did not revoke access until approximately a year later. The second contractor ceased employment with the contracting company, but that WECC_URE1 did not revoke the access until approximately six months later. The root cause of this issue was the failure to require and receive updated employment information from the contracting company. WECC_URE1 discovered the following instances while mitigating the self-reported violation. These instances included: 6 terminated contractors; 6 employee resignations; 5 terminated employees; 3 contractor resignations; 1 revocation for a current employee; 1 student; and 1 transferred employee. The instances occurred during a two year period. | CIP-004-1 | R4 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to update its list and to revoke access to CCAs for personnel no longer requiring such access within seven calendar days as required under CIP-004-1 R4. Such failures could allow the individuals with unauthorized access to cyber and/or unescorted physically access CCAs and act with maliciously, which would compromise the security of such assets essential to the operation of the Bulk Electric System (BES). However, WECC_URE1 had additional protections to help prevent CCAs from being compromised. All CCAs are located within both the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) and as such, all access is monitored and logged. Any changes to the CCAs trigger alarms to alert security personnel. The individuals in scope were not terminated for cause and the majority had completed Personnel Risk Assessments (PRAs) and Cyber Security Training. Nonetheless, WECC_URE1's poor control over its student program and over its contractors created a situation in which numerous individuals in 19 instances improperly had access to CCAs. Due to the multiple number of instances of noncompliance, the duration the instances were not internally discovered, and the size and potential impact of WECC_URE1's assets on the BPS, WECC determined this violation posed a moderate risk to the reliability of the BPS. | the date the Standard became enforceable on WECC_URE1 | when the last unauthorized access was revoked and the list updated for the nineteenth instance | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked all access for the affected employees that no longer needed access rights; 2) developed and implemented processes and procedures for notifying security privilege coordinators in a timely manner of changes in roles of personnel who have been granted authorized cyber and authorized unescorted physical access to CCAs so that the security privilege coordinators can revoke such authorized access for WECC_URE1 and contractor employees, students, apprentices, service contractors, etc.; 3) developed and implemented a policy for granting only temporary authorized access to CCAs to certain types of personnel, i.e., students, apprentices, service contractors, etc.; 4) approved and published the revised processes and procedures for notifying security privilege coordinators in a timely manner of all changes in authorized access to CCAs so that the security privilege coordinators can revoke authorized access to CCAs within the required timeframes, which should ensure that all managers and supervisors adhere to giving all the appropriate notifications regarding changes to employee access and are submitted within the required time frame for authorized access under CIP-004 R4; 5) approved and published the revised processes and procedures for updating the lists for authorized access to CCAs, as required by CIP-004, R1 to ensure that the lists for authorized access to CCAs are updated; 6) implemented the remedies identified in updating access lists to prevent future potential violations; 7) reviewed and revised, as necessary, the process(es) and procedures for quarterly review of access lists to ensure at a minimum that such quarterly reviews are conducted by designated staff and managers; 8) communicated to employees affected by the revised quarterly process and how it will impact them; 9) documented, approved and published the revised/new processes and procedures for quarterly review of authorized access to CCAs that ensures the reviews are completed on time and by the designated WECC_URE1 staff and managers; 10) develop access list, for each access area, with performance managers identified for each employee; 11) created user interfaces for reviewers; 12) developed an automated email notification system that notifies managers on a quarterly basis to verify the access list for their employee's is correct and access is still needed; 13) tested the revised quarterly access review process and procedures; 14) completed a quarterly access review; 15) implemented an awareness program whereby managers, supervisors, and other delegated WECC_URE1 personnel are routinely and regularly reminded of their responsibilities related to making appropriate notifications when there is a change in role for WECC_URE1 and contractor personnel, including students, apprentices, service contractors, and all others having authorized access to CCAs; 16) conducted a review of the access revocation process; any gaps identified through the review have been closed by clearly documenting access control roles and responsibilities, and adding a quality control check to ensure that the revocations have been implemented; 17) issued a directive to reply with what actions they will be taking in order to remedy their performance, specifically, (a) how they will comply with the termination clause of their contract, to include training appropriate personnel and establishing processes to ensure compliance; and (b) acknowledgement that the contract manager, any acting contract managers, and subcontracting nursing agency personnel for this contract have been advised of the process and will follow it; 18) discussed the incident at a team meeting where the team members agreed to track personnel actions on their shared calendars and sent a message to team members to direct them to begin using the calendar process; 19) reviewed the notification process which revealed that the personnel action report was excluding personnel actions that had an “Other” reason code. The HR system has since been updated to include the reason “Other” in the daily personnel action report; 20) improved the procedures for performing a quality control check by adding a weekly review of all notifications. Additionally, WECC_URE1 is adding staff to help perform quality control checks for the notification procedures; 21) provided more awareness information for dealing with contractors that are requesting unescorted physical access; 22) required proper contract language in subcontracts and verify that this language is in primary contracts; 23) improved procedures for tracking construction contractors and their subcontractors; 24) reviewed all contract clauses dealing with access requirements and consolidating them for inclusion into the proper contracts; and 25) copied all of the temporary access expiration date reminders and added another tab in the unescorted access list to include a chronological list of temporary access expiration dates so that WECC_URE1 staff can readily see whose access will be expiring and when. | 2015-05-15 | 2016-05-19 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). However, in this instance, WECC did not consider WECC_URE1's ICP a mitigating factor because the mechanisms in the ICP repeatedly failed to prevent the retention authorized cyber and/or authorized unescorted physical access. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013088 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-1 R4. WECC_URE1 failed to perform a review to verify that only ports and services required for operations at all access points were enabled, as required by CIP-005-1 R4.2. Specifically, WECC_URE1's process for verifying that only ports and services required for operations at all access points are enabled included only evaluating a ten percent random sample of firewall rule sets. This is the only review WECC_URE1 performed for this purpose. WECC_URE1 also did not have a baseline of all required ports and services for all access points, so it would have been unable to determine which ports and services were required, even if a full review of all rule sets was performed. The devices in scope included the 16 physical access points to the Electronic Security Perimeter (ESP). The root cause of this violation is a lack of compliance understanding. WECC_URE1 did not have a documented baseline of firewall ports and services as required under CIP-005-1 R4.2. Consequently, the annual verification required under CIP-005-1 R4 was an overly cumbersome process. | CIP-005-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to perform a CVA to verify that only ports and services required for operations at all ESP access points were enabled. Such failure to perform a CVA of the electronic access points to the ESPs poses significant risk to the entity's Cyber Assets. This increased risk may allow for unauthorized internal and/or external access, which could allow for successful cyber-attacks against CCAs essential to the operation of the Bulk Electric System (BES). However, WECC_URE1 implemented several physical and logical layers of defense that would likely have prevented and detected anomalous network activity inside, and passing through the access points. First, WECC_URE1 implemented restricted ports and services and did not allow all traffic to pass through the access points. Second, internal routers in the ESP were set to drop unknown network destinations thereby limiting the traffic that could pass through and out of the ESP. Finally, intrusion detection system sensors were placed in-line for most access points to the ESP which would have likely detected any abnormal network traffic or conditions passing into or out of the ESP. | the date the Standard became enforceable on WECC_URE1 | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) developed firewall rule management system (application and database) to store firewall rules and the business justification metadata for each firewall rule; 2) created annual firewall rule verification review process and procedures using the new firewall rule management system; 3) created annual router rule verification review procedure for performing manual review of the rules and their business justification; 4) trained staff on new processes and procedures; 5) put firewall rule management system into production; 6) completed full annual firewall rule verification; and 7) completed full annual router rule verification. | 2015-10-28 | 2016-05-18 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013893 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R1. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford the CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R1, WECC_URE1 failed to perform security testing for these devices. Specifically, the entity was not performing security testing for these devices on the DMZ network (where the devices in scope were located). These devices on the demilitarized zone (DMZ) were also not monitoring security events, enforcing local account restrictions, implementing a patch program, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R1; R1.1; R1.2; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to provide CIP-007-3a R1 protections to 30 CCAs located within its control centers. Failure to provide CIP-007-3a R1 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | when WECC_URE1 moved or replaced all CCAs into the ESP and completed its security testing | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) moved (or replaced) all non-compliant CCAs from the ESP; 2) performed the security testing required by CIP-007-3a R1; 3) reviewed and updated the procurement process to improve its efficiency; and 4) began initiative to standardize and simplify information systems and network architecture. | 2014-12-11 | 2016-08-05 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013894 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R2. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its primary and backup control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R2, WECC_URE1 failed to enable only those ports and services necessary for normal and emergency operations for three of the 30 CCAs. Specifically, the entity was not ensuring only those ports and services necessary were enabled for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, implementing a patch program, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R2; R2.1; R2.2; R2.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-007-3a R2 protections to three CCAs located within its control centers. Specifically, WECC_URE1 was not ensuring only those ports and services necessary were enabled for these devices on the network. Failure to provide CIP-007-3a R2 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | when WECC_URE1 retired non-compliant systems and replaced them with new, compliant systems inside the ESP and moved the data dependencies to new or existing compliant systems in the ESP and included the devices that had not been included in the script, which activates allowable ports and services | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) retired non-compliant systems and replaced them with new, compliant systems inside an ESP and moved the data dependencies to new or existing compliant systems in an ESP; 2) included the devices that had not been included in the script, which activates allowable ports and services; 3) reviewed and updated the procurement process to improve its efficiency; and 4) applied intrusion detection agents to all control center servers and workstations within the ESP. | 2014-11-20 | 2016-08-08 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013895 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R3. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R3, WECC_URE1 failed to implement a security patch management program to 30 CCAs. Specifically, the entity did not implement a security patch management program for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, using only ports necessary, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-007-3a R3 protections to 30 CCAs located within its control centers. WECC_URE1 did not implement a security patch management program for these CCAs. Failure to provide CIP-007-3a R3 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated procedures to reflect changes to the automated and manual processes by which the patch management is done; and 2) reviewed and updated the procurement process to improve its efficiency. | 2015-08-26 | 2016-08-04 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013896 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R4. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its primary and backup control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R4, WECC_URE1 failed to use anti-virus and other malicious software prevention tools for three of the 30 CCAs. Specifically, the entity was not using antivirus or other anti-malware tools for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, implementing a patch program, using a patch management program, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R4; R4.1; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-007-3a R4 protections to three of 30 CCAs located within its control centers. Specifically, WECC_URE1 was not using anti-virus or other anti-malware tools on these devices on its network. Failure to provide all CIP-007-3a R4 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) installed software to protect from malicious software; and 2) reviewed and updated the procurement process to improve its efficiency. | 2015-08-20 | 2016-07-08 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013898 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its primary and backup control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R5, WECC_URE1 failed toimplement the technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimizes the risk of unauthorized system access for 30 CCAs located within its primary and backup control centers. Specifically, the entity was not implementing technical and procedural controls that enforced user authentication for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, performing security testing, implementing a patch program, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R5; R5.1; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-007-3a R5 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 did not implement technical and procedural controls that enforced user authentication for these devices on its network. Failure to provide CIP-007-3a R5 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) created and maintained procedures for relevant systems; 2) created and maintained audit trails for relevant systems; 3) performed an annual review of access on all systems; 4) managed admin, default, and shared accounts; and 5) reviewed and updated the procurement process to improve its efficiency. | 2015-08-25 | 2016-08-08 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013899 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its primary and backup control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R6, WECC_URE1 failed to ensure that all cyber assets within the ESP implemented automated tools or organizational process controls to monitor system events that are related to cyber security for 22 CCAs located within its control centers. Specifically, the entity was not logging and monitoring security events for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, implementing a patch program, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R6; R6.1; R6.2; R6.3; R6.4; R6.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide the CIP-007-3a R6 protections to 22 CCAs located within its control centers. Specifically, WECC_URE1 failed to log and monitor security events for these devices on its network. Failure to provide CIP-007-3a R6 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented tools or controls to monitor and alert on system events; 2) maintained event log files and retain for 90 days; 3) reviewed logs of system events and maintain records of review; and 4) reviewed and updated the procurement process to improve its efficiency. | 2015-07-28 | 2016-08-05 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013900 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R8. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its primary and backup control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R8, WECC_URE1 failed to perform CVAs at least annually for 22 CCAs within the ESP. Specifically, the entity was not performing vulnerability assessments for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, implementing a patch program, or using antivirus. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R8; R8.1; R8.2; R8.3; R8.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide the CIP-007-3a R8 protections to 22 CCAs located within its control centers. Failure to provide all CIP-007-3a R8 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) performed Cyber Vulnerability Assessments on all CCAs; 2) reviewed ports and services in use; 3) reviewed default accounts; 4) reviewed and updated the procurement process to improve its efficiency; and 5) automated the intrusion detection process, which runs continually and is reviewed weekly. | 2015-11-08 | 2016-08-04 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013901 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R9. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its primary and backup control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-007-3a R9, WECC_URE1 failed to review and update the documentation specified in CIP-007-3a at least annually for 30 CCAs located within its control centers. Specifically, the entity was not ensuring all CIP-007 documentation was being updated and reviewed at least annually for these devices on the demilitarized zone (DMZ) network (where the devices in scope were located). These devices on the DMZ were also not monitoring security events, enforcing local account restrictions, implementing a patch program, using antivirus, and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the cyber asset level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-007-3a | R9 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide all CIP-007-3a R9 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 was not ensuring all CIP-007 documentation was being updated and reviewed at least annually for these devices on the network. Failure to provide all CIP-007-3a R9 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center electronic security perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) created, maintained, and updated CIP-007 documentation as required by the standard; and 2) reviewed and updated the procurement process to improve its efficiency. | 2016-07-27 | 2016-08-04 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013903 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R2. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-005-3a R2, WECC_URE1 failed to implement and document the organizational processes and technical procedural mechanisms for control of electronic access at all access points to the ESP for 30 CCAs located within its control centers. Specifically, the entity was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the demilitarized zone (DMZ) network (where the devices in scope were located). The DMZ network was also not monitored for electronic access 24 hours a day, 7 days a week as required by CIP-005 R3 and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-005-3a | R2; R2.1; R2.2; R2.3; R2.4; R2.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-005-3a R2 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the network. Failure to provide ports and services protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) documented and implemented the process or mechanisms for control of all Electronic Access Points in the ESP; 2) ensured the access control model denies by default and requires the specification of explicit access permissions; 3) ensured that ESP access points enable only those ports and services required for operations; 4) ensured procedures are in place for securing dial-up access; 5) ensured that strong procedural or technical controls (such as two-factor authentication) are in place; 6) ensured that documentation is in place to describe access authorization, authentication and authorization review; 7) ensured that documentation is in place to describe authorization review; and 8) reviewed and updated the procurement process to improve its efficiency. | 2016-05-01 | 2016-08-10 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013904 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-005-3a R1, WECC_URE1 failed to ensure that every CCA resides within an ESP for 30 CCAs located within its control centers. Specifically, the entity was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the demilitarized zone (DMZ) network (where the devices in scope were located). The DMZ network was also not monitored for electronic access 24 hours a day, 7 days a week as required by CIP-005 R3 and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-005-3a | R1; R1.1; R1.2; R1.3; R1.4; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-005-3a R1 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the network. Failure to provide all CIP-005-3a R1 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) modified existing architecture to ensure all CCAs reside within an ESP; 2) documented the ESPs and access points; and 3) reviewed and updated the procurement process to improve its efficiency. | 2015-08-21 | 2016-08-10 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013905 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R3. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-005-3a R3, WECC_URE1 failed to implement and document an electronic or manual process for monitoring and logging access at access points to the ESP 24 hours a day, seven days a week for 30 CCAs located within its control centers. Specifically, the entity was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the demilitarized zone (DMZ) network (where the devices in scope were located). The DMZ network was also not monitored for electronic access 24 hours a day, 7 days a week as required by CIP-005 R3 and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-005-3a | R3; R3.1; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-005-3a R3 protections to 30 CCAs located within its control centers. The network was not monitored for electronic access 24 hours a day, seven days a week. Failure to provide all CIP-005-3a protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented and maintained logging and monitoring access for each access point; 2) maintained logs for 90 days; and 3) reviewed and updated the procurement process to improve its efficiency. | 2015-08-25 | 2016-08-10 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013906 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R4. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-005-3a R4, WECC_URE1 failed to perform a cyber vulnerability assessment of the electronic access points to the ESP at least annually for 30 CCAs located within its control centers. Specifically, the entity was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the demilitarized zone (DMZ) network (where the devices in scope were located). The DMZ network was also not monitored for electronic access 24 hours a day, 7 days a week as required by CIP-005 R3 and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-005-3a | R4; R4.1; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide CIP-005-3a R4 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. Failure to provide the CIP-005-3a R4 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) performed and documented an annual CVA process; 2) implemented a process for reviewing ports and services; 3) documented all access points to the ESP; 4) completed a review of account, password, and network management; and 5) reviewed and updated the procurement process to improve its efficiency. | 2016-06-15 | 2016-08-10 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP). WECC considered WECC_URE1's compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be applicable to this violation.
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013907 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R5. WECC_URE1 listed 30 newly identified Critical Cyber Assets (CCAs) located within its control centers on its CCA list and was required to afford these CCAs all of the CIP-003 through CIP-009 protections within 12 months of listing the CCAs per the NERC implementation plan. WECC_URE1 contacted WECC to inform them that WECC_URE1 would not meet the required implementation timeline and to determine the next steps. WECC recommended WECC_URE1 file Self-Reports for each protection not implemented by the required date. Subsequently, WECC_URE1 filed Self-Reports for CIP-005-3a R1-R5 and CIP-007-3a R1-R9, excluding R7 because it failed to provide these specific protections to the 30 CCAs located within its control centers by the required date. The CCAs in scope functioned as part of seven systems used for network flow curtailments for managing System Operating Limits (SOL) excursions, curtailment order through OATI, calculating topology informed network flowgate curtailment, domain controllers, and network switches. Specific to CIP-005-3a R5, WECC_URE1 failed to review, update, and maintain all documentation to support compliance with the requirements of CIP-005-3a. Specifically, the entity was not protecting these devices behind an access point and therefore did not have only those ports and services necessary allowed into and out of the demilitarized zone (DMZ) network (where the devices in scope were located). The DMZ network was also not monitored for electronic access 24 hours a day, 7 days a week as required by CIP-005 R3 and did not have vulnerability assessments performed to verify if all necessary minimum protections were being applied at the network level. The root cause of the violation was a major delay in receiving hardware. It took 160 calendar days from the start of the procurement until the hardware was received by WECC_URE1, when it should have taken less than 90 days. The delay led WECC_URE1 to move the new servers into production without following the prescribed process. | CIP-005-3a | R5; R5.1; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to provide the CIP-005-3a R5 protections to 30 CCAs located within its control centers. Specifically, WECC_URE1 did not review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. Failure to provide CIP-005-3a R5 protections to CCAs could increase the number of attack vectors to other CCAs within WECC_URE1's control center network. However, WECC_URE1 implemented strong controls to prevent and detect an attack to WECC_URE1's control centers. Specifically, WECC_URE1 implemented firewall access rules at the control center Electronic Security Perimeter (ESP) which allowed only traffic necessary and required along with an intrusion detection system at the ESP level in the control center. Also, access controls are monitored 24 hours a day, seven days a week at the control center and anomalous activity, such as an attacker scanning and attempting to connect to devices within the network and control center ESP using telnet, would have likely been prevented and detected at the network layer and also at the device level restrictions. WECC_URE1 also implemented account restrictions on the devices within the network and ESP, anti-malware tools, and also continuously monitored security configurations and ports. These controls would have also likely detected and prevented any compromise of the CCAs and supervisory control and data acquisition (SCADA) system controlling WECC_URE1's load by alerting on suspicious activity and forcing the attacker to have the correct usernames and passwords to manipulate the SCADA system. | the date that WECC_URE1 was required to implement the protections on the devices | Mitigation Plan completion | No Penalty (for WECC2013012260, WECC2013013088, WECC2014013893, WECC2014013894, WECC2014013895, WECC2014013896, WECC2014013898, WECC2014013899, WECC2014013900, WECC2014013901, WECC2014013903, WECC2014013904, WECC2014013905, WECC2014013906, and WECC2014013907) | Self-Report | To mitigate this violation, WECC_URE1: 1) reviewed, updated and maintained CIP-005-3a documentation for electronic security perimeters; and 2) reviewed and updated the procurement process to improve its efficiency. | 2016-07-28 | 2016-08-10 | Admits | WECC reviewed WECC_URE1's Internal Compliance Program (ICP).
2017-02-28 | FERC | NP17-16-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015015191 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. While performing its Cyber Vulnerability Assessment (CVA), WECC_URE2 discovered one device located within the Electronic Security Perimeter (ESP) with an account that had not been removed or disabled as required by CIP-007-3a R5.2.1. The device provides historical information about WECC_URE's electric system utilization. The local account on the server was a vendor-created account with a unique password that should have been disabled before the device was commissioned into the ESP. The root cause of the violation was poor procedural documentation at the time the server was commissioned. WECC_URE2 failed to disable the account in question due to poor procedural documentation for resolving inconsistencies with user accounts on a newly commissioned asset. Specifically, WECC_URE2 technicians applied the vendor instructions, not to change the password the vendor created, to all, instead of only specific, accounts, which left a temporary account active when the asset was commissioned. | CIP-007-3a | R5; R5.2; R5.2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2 failed to remove or disable an account on one device located within the ESP. Failing to secure default user accounts could lead to a malicious individual gaining access to the Critical Cyber Assets within the Energy Management System, harming its functionality, and affecting the reliability of the BPS. WECC_URE2 implemented preventive controls by password protecting the account, which was also actively logged by WECC_URE2's central account management tools. WECC_URE2 personnel utilize security monitoring analysis and response systems to continuously monitor and alert for malicious activity. Additionally, access to the device was limited to a small group of individuals who completed CIP cyber security training and had current personnel risk assessments on file. Further, the device on which the account was created is electronically protected by a network firewall and is located inside an ESP with Physical Security Perimeters. The system is located on an isolated network where there is no direct access to the corporate network or the internet, and all traffic to the network passes through secured access points. Finally, the server at issue only records historical data and has no control functionality for the BPS. | when WECC_URE2 commissioned the device | when WECC_URE2 disabled the account on the device | 34000 | Self-Report | To mitigate this violation, WECC_URE2: 1) disabled the account on the server; 2) validated procedures to accurately describe the processes to configure assets, gather evidence, and assess compliance in support of CIP-007-6 R5; 3) updated account management tracking logs to support changes to procedures; 4) updated appropriate spreadsheets to document CIP-007-6 R5 compliance assessment for each asset associated with a Medium or High Impact Bulk Electric System (BES) Cyber System; and 5) implemented a process to audit user accounts on a quarterly basis. | 2015-11-18 | 2016-02-22 | Agrees/Stipulates | WECC reviewed and considered WECC_URE2's internal compliance program (ICP) a mitigating factor in the penalty determination. WECC_URE2 self-reported this violation approximately 250 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount.
2017-01-30 | FERC | NP17-14-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015404 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. WECC_URE1 failed to adequately implement security controls testing on two Physical Access Control Systems (PACS) servers as required for CIP-007-3 R1 pursuant to CIP-006-3c R2.2. The PACS system was upgraded to allow continued functioning in a fully supported NERC-compliant environment. As a consequence of the change, system event logs from the two PACS servers were not being transmitted to WECC_URE1's daily security report for periodic review. As part of routine maintenance activity on the hardware supporting the PACS software, WECC_URE1's IT department detected that daily security event reports did not include electronic access event information from two local PACS servers. Logs were being created and maintained by the PACS servers; however, the electronic access event information was not transmitted to WECC_URE1's daily security event reporting and therefore not being reviewed timely. This reporting failure was not noticed during the routine log reviews because the daily PACS security report typically contains only information from the PACS client workstations. Electronic access events on the client workstations occurred many times each day, whereas the electronic access events on PACS servers occurred approximately once a month. WECC_URE1 began an initial review of the server logs and found no security events issues or malware issues on the logs. Subsequent to the log review, WECC_URE1 performed a root cause analysis and determined that system testing and documentation for the upgrade on the two PACS servers per CIP-007-R1.1 were incomplete. Specifically, WECC_URE1's test plan called for “system integration testing” (SIT) and “user acceptance testing” (UAT) but the plan did not indicate what steps the tests were to include, nor did available documentation provide information as to the content of the tests. The SIT and UAT focused on functional testing and did not include testing of security controls related to the security event report. The configuration of electronic access events on the two PACS servers to the daily security event report did not occur. Prior to the upgrade, the two PACS servers had been reporting system logs, to include electronic access events, to WECC_URE1's security event report that were reviewed as required. The root cause of this violation was the failure of WECC_URE1 to adequately implement security controls testing as required by CIP-007-3 R1. | CIP-006-3c | R2; R2.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to perform adequate testing during an upgrade of the PACS servers which resulted in the system event logs of the two PACS servers not being reviewed for 258 days. Failure to perform adequate testing on Cyber Assets could lead to future changes being conducted without a clear understanding of the current configuration, leading to potential device failures as new changes are applied. PACS server logs were generated and maintained by the servers. WECC_URE1 reviewed the PACS server logs for system events related to electronic access attempts once the logs were configured correctly to appear on the security event report, and confirmed that no security events related to electronic access attempts occurred during the violation period. Additionally, the risk was further minimized by the fact that electronic and unescorted physical access to the devices was restricted to a small number of trained and authorized personnel. Each server was installed in a lock-box, controlled by card key and pin-pad access. Electronic access was controlled by Active Directory and restricted by both firewalls and network configuration. The only data that was not reported on the daily security event report was access attempts to the two PACS servers. WECC_URE1 had performed both operational and functional testing during the upgrade, and all physical access controls at WECC_URE1 continued to perform as required and expected during the upgrade. No harm is known to have occurred. | when WECC_URE1 failed to adequately implement security controls testing on two PACS servers | when WECC_URE1's PACS IT team developed and implemented an interim change management test script that specifically identified security testing | 17000 | Self-Report | To mitigate this violation, WECC_URE1: 1) developed and implemented an interim change management test script that specifically identified security testing; 2) comprehensively revised its test procedure for changes that deviate from the existing baseline configuration as part of the overall transition of cyber security practices from CIP Version 3 to CIP Version 5; and 3) trained all applicable personnel on the new procedures and controls. | 2016-06-16 | 2016-10-12 | Agrees/Stipulates | WECC_URE1 discovered this violation and self-reported nearly four months after discovery. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted nearly four months after the noncompliance was discovered. WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although WECC_URE1 has a documented ICP that has been provided to WECC, had the ICP been implemented properly, with appropriate internal controls in place, WECC_URE1 would have been able to identify, assess, and correct this violation in a timely manner. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2017-01-30 | FERC | NP17-14-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014872 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1.8. Specifically, WECC_URE2 stated that as part of its management effort to develop detailed roles and responsibilities within its IT department, WECC_URE2 discovered that security patches for its Physical Access Control System (PACS) had not been assessed in over a year. WECC_URE2 conducted a full extent of condition review to identify any other areas of possible noncompliance as per CIP-006-1 R1.8. As a result of the review, WECC_URE2 identified noncompliance with CIP-003-3 R5 (R5.1.2, R5.2, and R5.3), CIP-004-3a R4.1, CIP-007-1 R1 (R1.1 and R1.2), R2, and R5.2.3, CIP-007-3a R3, R5 (R5.1.3, R5.2.3, R5.3, and R5) and R9, CIP-008-3 R1.5, and CIP-009-3 R1 and R5, as it relates to PACS. WECC_URE2 failed to ensure 29 PACS devices were provided the protections as required by CIP-006-1 R1.8. The devices in scope were PACS Node Controllers, a PACS server, a PACS database server, a virtual host, and virtual workstations, affecting Critical Assets. The root causes of this issue were failure of WECC_URE2 to communicate and coordinate between lines of business and to provide sufficient controls to ensure periodic compliance activities were completed when individuals left WECC_URE2. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 failed to ensure PACS devices were provided the protections as required by CIP-006-1 R1.8. Failing to provide multiple security controls for PACS could result in two areas of unexpected vulnerabilities and disruptions: 1) disruption of the intended function and operation of the PACS technologies, which includes changes, modifications or disabling existing PACS at Critical Assets; and 2) introducing vulnerabilities, such as unauthorized system accounts, malware or removal of monitoring controls on the PACS themselves. The result of these can be unauthorized personnel accessing Critical Assets and Critical Cyber Assets, resulting in damage to equipment, power cycling, or shutting down critical systems, thus potentially affecting the BPS. WECC_URE2 implemented good internal controls to eliminate potential unauthorized physical access. This included administrative, technical, and physical controls such as: 1) electronic badge card reader systems to control physical access to the PSPs; 2) 24x7 security monitoring of the PSPs; 3) personnel risk assessments for both role separation and function and 4) authentication systems to control access to Critical Assets. In addition, WECC_URE2 implemented a visitor control program and a contractor screening process, thereby reducing the risk of actions that could negatively affect the BPS. | when the Standard became mandatory and enforceable on WECC_URE2 | when WECC_URE2 provided the protections of CIP-006-3a R2.2 to the last remaining PACS device in scope | 55000 | Self-Certification | To mitigate this violation, WECC_URE2: 1) brought the devices in scope into compliance. Specifically, WECC_URE2: a. CIP-003-3 R5.1.2: completed the annual review of designated personnel responsible for authorizing access to protected information. b. CIP-003-3 R5.2: completed the annual review of access to protected information. c. CIP-003-3 R5.3: completed the annual review of the CIP-003 R5 procedure. d. CIP-004-3a R4.1: completed the quarterly reviews of the lists of personnel who have cyber access to the PACS. e. CIP-007-3a R3: completed security patch assessments and applied, where applicable. f. CIP-007-3a R5.1.3: completed the annual review of user accounts with access to the PACS. g. CIP-007-1 R5.2.3: began using a tool to manage its administrator and admin accounts. h. CIP-007-3a R5.3: began using a tool to manage the passwords for the administrator and admin accounts. i. CIP-007-3a R9: completed the annual review of the procedures required by CIP-007-3a R1 through R8. j. CIP-008-3 R1.5: completed the annual review of the Cyber Security Incident Response Plan. k. CIP-009-3 R1: completed the annual review of the recovery plan. l. CIP-009-3 R5: completed all backup media testing. m. CIP-007-1 R1.1 and R1.2: updated procedures to include language on how WECC_URE2 tests. n. CIP-007-1 R2: documented a process related to ports and services. o. CIP-007-3a R5: documented controls to enforce access authentications. 2) added events to a centralized group calendar to remind WECC_URE2 IT OpsNet staff of the required reviews; 3) engaged WECC_URE2's Enterprise Risk team to assist IT with the quarterly and annual review events and dates by performing spot checks and monitoring WECC_URE2's adherence to the review cycles; and 4) deployed a new PACS and configured all shared accounts used in the PACS environment to be managed through a password management tool. | 7/1/2015 | 6/28/2016 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although WECC_URE2 has a documented ICP that has been provided to WECC, had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC applied an aggravating factor and escalated the disposition treatment with a penalty because of the duration of the violation. WECC considered WECC_URE2's CIP-006-1 R1.8 compliance history to be an aggravating factor in the penalty determination.
2016-12-29 | FERC | NP17-12-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015210 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. SERC_URE1 failed to afford the electronic access control and monitoring (EACM) Cyber Assets the protective measures specified in CIP-007-3a R8, by failing to conduct a cyber vulnerability assessment (CVA) on the EACM Cyber Assets for one year. As part of mitigation for a prior violation, SERC_URE1 conducted a CVA. However, the CVA that SERC_URE1 conducted was limited to the ESP access points, Critical Cyber Assets (CCAs), and non-critical Cyber Assets within the ESP. As a result, SERC_URE1 failed to conduct a CVA on the EACM devices that year. In total, SERC_URE1 failed to perform CVAs for all of its EACM devices. Prior to this issue, SERC_URE1 last conducted a CVA that included the EACM devices the year before. SERC_URE1 discovered this issue while preparing for the next year's CVA. In all prior years, SERC_URE1 performed the CVA for all Cyber Assets in scope at the same time. During the year at issue, SERC_URE1 assumed that the CVA addressed all Cyber Assets requiring a CVA (as it had done in all previous years) and failed to make the distinction that not all involved Cyber Assets in scope of the CVA were included. Due to this mistake, SERC_URE1 did not conduct the required CVA for EACM devices. The root cause of this violation was a misunderstanding of the CVA scope and the Cyber Assets that were to be included in the year's CVA effort. The duration of the violation was approximately eight months. | CIP-005-3a | R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1's failure to conduct a CVA on the EACMs could have allowed security vulnerabilities to go unidentified, remaining available for exploitation for an extended period. However, SERC_URE1 annually reviewed and changed the passwords for all EACM devices and accounts in service that are part of this instant issue. SERC_URE1 reviewed the existing ports and services several times the year of the violation. Modifying the EACM network switch ports and services requires a serial connection, meaning that a person must be physically located at the Cyber Asset to make modifications. SERC_URE1's logs show that its EACM network switches were accessed only three times, all by personnel who were authorized for such access. SERC_URE1 also secures all the affected EACM Cyber Assets within a firewall secured subnet with no remote access permitted, restricting potential attack vectors. If an unauthorized individual gained physical access to the EACM devices, the individual would still need a password to access the servers, workstations, and the application software. SERC_URE1 completely isolates the EACM subnet from the network containing CCAs, limiting any potential crossover impacts that could affect or degrade the energy management system. | One day after SERC_URE1 failed to conduct a CVA covering EACM devices for the year at issue. | When SERC_URE1 conducted the next year's CVA, which included the EACM devices. | $50,000 (for SERC2015015209, SERC2015015210, SERC2016015560, and SERC2016015561) | Self-Report | To mitigate this violation, SERC_URE1: 1) completed the required CVA on the EACM Cyber Assets; and 2) established an internal control to monitor the completion of the annual CVA. | 2015-08-31 | 2016-11-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2016-12-29 | FERC | NP17-12-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015209 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. SERC_URE1 failed to afford the physical access control system (PACS) Cyber Assets the protective measures specified in CIP-007-3a R8, by failing to conduct a cyber vulnerability assessment (CVA) on the PACS Cyber Assets for one year. As part of mitigation for a prior violation, SERC_URE1 conducted a CVA. However, the CVA that SERC_URE1 conducted was limited to the ESP access points, Critical Cyber Assets (CCAs), and non-critical Cyber Assets within the ESP. As a result, SERC_URE1 failed to conduct a CVA on the PACS devices for the year at issue. In total, SERC_URE1 failed to perform CVAs for all of its PACS devices. Prior to this violation, SERC_URE1 last conducted a CVA that included the PACS devices the year before. SERC_URE1 discovered this violation while preparing for the next year's CVA. In all prior years, SERC_URE1 performed the CVA for all Cyber Assets in scope at the same time. During the year at issue, SERC_URE1 assumed that the CVA addressed all Cyber Assets requiring a CVA to be conducted (as it had done in all previous years) and failed to make the distinction that not all involved Cyber Assets in scope of the CVA were included. Due to this, SERC_URE1 did not conduct the required CVA for PACS devices. The root cause of this violation was a misunderstanding of the CVA scope and the Cyber Assets that were to be included in the year's CVA effort. The duration of the violation was approximately eight months. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1's failure to conduct a CVA on the PACS devices could have allowed security vulnerabilities to go unidentified, remaining available for exploitation for an extended period. However, SERC_URE1 annually reviewed and changed the passwords for all PACS devices and accounts that were part of this violation. Additionally, SERC_URE1 reviewed the existing ports and services several times that year. The PACS door controllers are firmware-based appliances and, as such, require firmware changes to update any ports and services in use and on the baseline. No firmware updates were made for the door controllers during the violation. SERC_URE1 also secures all the affected PACS Cyber Assets within a firewall secured subnet with no remote access permitted, restricting potential attack vectors. SERC_URE1 completely isolates the PACS subnet from the network containing CCAs, thereby limiting any potential crossover impacts that could affect or degrade the energy management system. | One day after SERC_URE1 failed to conduct a CVA covering PACS devices for the year at issue. | When SERC_URE1 conducted the next year's CVA, which included the PACS devices. | $50,000 (for SERC2015015209, SERC2015015210, SERC2016015560, and SERC2016015561) | Self-Report | To mitigate this violation, SERC_URE1: 1) completed the required CVA on the PACS Cyber Assets; and 2) established and calendared an internal control task to monitor future completion of CVAs for the Cyber Assets at issue in this violation. | 2015-08-31 | 2016-11-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2016-12-29 | FERC | NP17-12-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015560 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-005-3a R1.5. SERC_URE1 failed to properly identify several servers as Electronic Access Control and Monitoring Systems (EACMS) and thus could not provide evidence that it afforded the servers the protective measures specified in CIP-005-3a R1.5. SERC_URE1 used servers on the corporate network to maintain logs of access to the ESP firewalls and to generate alerts and reports as part of monitoring access at ESP access points, as required by CIP-005-3a R3. SERC_URE1 interpreted the required logging function and the required monitoring function in CIP-005-3a R3 to be two separate and distinct functions, with only the latter falling under CIP-005-3a R1.5. However, in addition to using these server reports to demonstrate compliance, SERC_URE1 also manually reviewed these reports each day and issued alerts based on issues identified in that review. Since SERC_URE1 manually reviewed these reports and generated alerts based on that review, SERC_URE1 should have identified these servers as EACMS. SERC_URE1 normally used servers to perform this function, one in the primary control center and one in the back-up control center. However, during the Compliance Audit, SERC_URE1 was in the process of replacing the original servers with newer ones, and had them all in service and operational for approximately two to three months. The root cause of this violation was a misinterpretation by SERC_URE1 of the Standard and Requirement. The duration of the violation was approximately two and a half years. | CIP-005-3a | R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1's failure to identify and protect the EACMS servers could have led to compromised servers, the inability to generate alerts for unauthorized access to CIP assets, and the inability to detect successful unauthorized access attempts. However, SERC_URE1's firewalls performed both ‘access to’ and ‘access through’ monitoring and alerting. The firewalls operated independently from the servers so that they would have remained operational if the servers had failed. | When the audit period began. | Mitigation Plan completion. | $50,000 (for SERC2015015209, SERC2015015210, SERC2016015560, and SERC2016015561) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) designated the involved servers as EACMs under Version 5 of the CIP Standards; and 2) sent an email to responsible staff to make them aware that the servers are properly considered EACMs. | 2016-07-01 | 2016-11-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC determined SERC_URE1's compliance history should not serve as a basis for aggravating the penalty.
2016-12-29 | FERC | NP17-12-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2016015561 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-006-3c R1.6.1. SERC_URE1 failed to maintain visitor logs that documented the date and time of visitors' entry and exit, including the date and time, to and from two Physical Security Perimeters (PSPs). The SERC audit team reviewed visitor access logs for the SERC_URE1 control center PSPs and found multiple logging issues with the manual log-books, including incomplete lines within the logs and missing sign-in times or sign-out times dating back approximately one year. Specifically, SERC_URE1 failed to log entry and exit times on multiple occasions, including for large groups of student visitors on tours, for which SERC_URE1 only documented the entry and exit dates. The root cause of this violation was multiple human performance failures, in which SERC_URE1 employees failed to follow documented procedures for appropriate logging visitors to the PSP. The duration of the violation was approximately a year and a half. | CIP-006-3c | R1.6.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, if a problem or issue arose, SERC_URE1's failure to maintain complete visitor logs would make any forensic review difficult, because there would be an incomplete log of who was within the secured area at the time. However, SERC_URE1 had several security measures in place to protect the PSP. For example, SERC_URE1 had live video surveillance cameras covering some areas of the PSPs and could view this footage in real time. Further, SERC_URE1 staffed its control centers twenty-four hours a day, seven days a week. To gain access to the PSP in question, an individual would first have to pass through a carded gate arm. | The first documented log in which SERC_URE1 failed to properly log visitors to the PSP. | When SERC_URE1 revised its logging form and provided training on visitor logging to employees. | $50,000 (for SERC2015015209, SERC2015015210, SERC2016015560, and SERC2016015561) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) modified the form used to log visitor access to provide separate columns for the date and time of ingress and egress for visitors; 2) placed an increased emphasis on visitor logging in the annual cyber training that is required of all employees with access to PSPs; 3) provided additional awareness of logging requirements, through periodic reminders on SERC_URE1 digital signage; and 4) constructed a new facility that houses the primary energy control center and support staff. The new facility significantly reduced the number of PSP doorways. | 2016-09-08 | 2016-11-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history and determined that there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015024 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. Specifically, for the first instance; WECC_URE1 reported that, two third-party vendor Security Officers (Officer A and Officer B) with authorized NERC unescorted physical access rights, assumed the responsibility as "escorts" for visiting contract personnel to the control center. Officer A escorted four contractors through the Physical Security Perimeter (PSP) via a card reader (CR) into an enclosed hatch room located behind the control room. Six minutes after Officer A escorted four contractors, Officer B escorted three different contractors into the control center PSP via a CR. Once all three contractors were in the PSP, Officer B exited the PSP via a CR, leaving the three contractors inside the PSP without an escort. The three contractors remained in camera view until Officer A appeared on-screen approximately four minutes later to continue his escorting duties. Officer A appeared on-screen without his original four assigned visitors that he had previously escorted into the hatch room. This same type of activity occurred multiple times throughout the day during an approximately three hour period. WECC determined that per CIP-006-3a R1.6, WECC_URE1 failed to continuously escort the visitors, as required by WECC_URE1's visitor control program, for approximately three hours. For the second instance, WECC_URE1 reported that, a third-party vendor Security Officer (Officer X) arrived at the control center to perform NERC monitoring duties. Officer X arrived without his company-issued ID Badge. Officer X had completed his required NERC CIP training, but his access order to provision authorized unescorted physical access to PSPs was not yet approved. Therefore, Officer X was considered a visitor and was to be continuously escorted by personnel with authorized unescorted physical access to PSPs. Two other Security Officers (Officer Y and Officer Z) assumed escorting responsibilities over Officer X. Approximately three minutes after Officer X arrived, Officer Y and Officer Z escorted Officer X, along with two contractors into the control center PSP via a CR. Approximately six minutes later, Officer Y exited the PSP alone. Officer Z and Officer X were in the PSP together with the contractors, and Officer Z assumed sole escorting responsibility over Officer X and the contractors. Approximately six minutes later, Officer Z escorted the two contractors out of the PSP, leaving Officer X without an escort while in the PSP for approximately two more hours. WECC determined that per CIP-006-3a R1.6, WECC_URE1 failed to continuously escort the visitor, as required by WECC_URE1's visitor control program, for approximately two and a half hours. The root cause of both issues was failure of WECC_URE1's third-party vendor to adhere to their contractual agreement. | CIP-006-3c | R1; R1.6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to ensure continuous escorting of unauthorized visitors within a PSP, which could allow said access to go unnoticed and unchecked. Such access may then be used to cause harm to Critical Cyber Assets (CCAs) essential to the operation of the BPS, thereby potentially negatively affecting the BPS. In both instances, WECC_URE1 had video monitoring of the visitors in scope and verified no malicious activity occurred. In the second instance, the security officer’s authorized access was pending approval, he had an approved personnel risk assessment (PRA), and he had the required NERC CIP training. Additionally, related to the first instance, WECC_URE1's control center is continuously manned and the CCAs were continuously monitored, thereby reducing the risk of actions that could negatively affect the BPS. | The first instance began when the contractors were left inside the PSP unescorted The second instance began when the Security Officer was left inside a PSP unescorted | The first instance ended approximately three hours later when WECC_URE1 resumed escorting of the contractors within the PSP The second instance ended approximately two and a half hours later when WECC_URE1 resumed escorting of the security officer within the PSP | $60,000 (for WECC2015015024 and WECC2016015456) | Self-Report | To mitigate this violation, WECC_URE1: 1) resumed the escorting of the contractors within the PSP; 2) resumed the escorting of the security officer within the PSP; and 3) held meetings with its contract service provider's leadership team reminding them of their contractual obligations as outlined in WECC_URE1's Master Service Agreement to abide by NERC CIP Standards and WECC_URE1's visitor control program, which includes specific guidelines for accessing NERC-Restricted areas. | 8/21/2015 | 7/1/2016 | Agrees/Stipulates | Credit was not given for WECC_URE1's internal compliance program (ICP). Although WECC_URE1 has a documented ICP that has been provided to WECC, it is Enforcement’s belief that had the ICP been implemented properly, WECC_URE1 would have been able to identify, assess, and correct this violation in a timely manner. WECC_URE1 discovered the first instance of this violation and self-reported 161 days after discovery. Therefore, Enforcement did not apply self-reporting credit to the penalty amount for this issue. WECC considered WECC_URE1's compliance history in determining the penalty. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015456 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. Specifically, for the first instance, WECC_URE1 reported that an employee (Employee A) with authorized unescorted physical access rights to a PSP, assumed the responsibility of an escort for an Information Technology (IT) employee (Employee B) that did not have unescorted physical access rights to the PSP. Employee A escorted Employee B into the PSP and signed him into the NERC CIP Visitor Log. Employee B was inside the PSP to replace Employee A's computer and copy files from the old to the new computer. Employee A left Employee B in his office, unescorted, from for approximately fifteen minutes and a second time for approximately thirty minutes. It was not until Employee A escorted Employee B out of the PSP that Employee A realized the oversight and immediately contacted the NERC CIP Compliance team to report the incident. WECC determined that per CIP-006-3a R1.6, WECC_URE1 failed to continuously escort Employee B, as required by WECC_URE1's visitor control program, for approximately 45 minutes. For the second instance, WECC_URE1 reported that, a third-party vendor Security Officer (Officer A) with authorized unescorted physical access rights to a PSP assumed the responsibility of an escort for another third-party vendor Security Officer (Officer B), who did not have unescorted physical access rights to the PSP. Officer B was supposed to be stationed at the exterior of the PSP cage to perform manual monitoring for a planned outage to the badge system. Officer A incorrectly stationed Officer B, inside the PSP cage. Approximately five minutes later, the operations center received a call from a power system operator to report that Officer B had been left unescorted inside the PSP cage. The operations center operator immediately contacted the PSP Security and requested they escort Officer B out of the PSP cage, which was completed at approximately ten minutes. Due to the NERC in-person training completed by the power system operator, he quickly recognized the unescorted Security Officer's presence in the PSP was a problem and reported the situation to the operations center. WECC determined that per CIP-006-3a R1.6, WECC_URE1 failed to continuously escort Officer B, as required by WECC_URE1's visitor control program, for approximately 20 minutes. The root cause of the first issue was a lapse in judgement by one employee for not remembering proper escorting procedures previously trained on as part of the mitigation for WECC2015015024. The root cause of the second issue was lack of a third-party vendor adhering to the contractual agreement. | CIP-006-3c | R1; R1.6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to ensure continuous escorting of unauthorized visitors within a PSP which could allow said access to go unnoticed and unchecked. Such access could be used to cause harm to CCAs essential to the operation of the BPS, thereby negatively affecting the BPS. In both instances, the unescorted employee and the Security Officer did not have electronic access to Critical Cyber Assets (CCAs). Additionally, the unescorted employee and the Security Officer were not left entirely alone in the PSP, as it was occupied by other employees who were authorized to be there. | The first instance began when an employee was left unescorted within a PSP The second instance began when a Security Officer was left inside a PSP unescorted | The first instance ended on approximately 45 minutes later when WECC_URE1 resumed escorting of the employee within the PSP The second instance ended when approximately 15 minutes later WECC_URE1 removed the Security Officer from the PSP | $60,000 (for WECC2015015024 and WECC2016015456) | Self-Report | To mitigate this violation, WECC_URE1: 1) resumed the escorting of the employee within the PSP; 2) had the individual involved in the first incident recall and re-review the visitor escort pamphlet, thus retraining themselves on the proper visitor escort protocol for a NERC CIP PSP; 3) completed the “PSP footprint reduction” project, which reduced the number of people whose regular work location was within a PSP; 4) removed the Security Officer from the PSP; 5) held meetings with its contract service provider's leadership team reminding them of their contractual obligations as outlined in WECC_URE1's Master Service Agreement to abide by NERC CIP Standards and WECC_URE1's visitor control program, which includes specific guidelines for accessing NERC-Restricted areas; and 6) worked with its security vendor to implement an internal control of a recording on its toll-free start-of-shift telephone line. The recording states that officers assigned to provide physical security during a scheduled outage of the badge system are never permitted to enter a PSP, unless they are currently cleared by WECC_URE1 and possess their NERC ID badge, or they are escorted continuously by an individual who is authorized with unescorted physical access to the PSP. | 12/22/2015 | 10/13/2016 | Agrees/Stipulates | Credit was not given for WECC_URE1's internal compliance program (ICP). Although WECC_URE1 has a documented ICP that has been provided to WECC, it is Enforcement’s belief that had the ICP been implemented properly, WECC_URE1 would have been able to identify, assess, and correct this violation in a timely manner. WECC considered WECC_URE1's compliance history in determining the penalty. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC200901795 | Settlement Agreement | During a Spot Check, WECC determined that WECC_URE2 was in violation of CIP-004-1 R4. WECC determined that WECC_URE2 failed to maintain lists of personnel containing specific electronic access rights to Critical Cyber Assets (CCAs). WECC reviewed the WECC_URE2 documentation for evidence of compliance with the Standard and determined there was insufficient documentation of cyber access rights. Specifically, the documentation described only general access rights to systems within the Electronic Security Perimeter (ESP) and did not include the specific electronic access rights to CCAs as required by the Standard. Furthermore, WECC_URE2 produced two documents listing system users; however, the lists failed to identify the specific systems for which these individuals had access. A subsequent data request for more detailed documentation of specific electronic access rights failed to demonstrate compliance with the Standard. WECC also reviewed documentation demonstrating quarterly reviews of personnel with access to CCAs. WECC reviewed WECC_URE2's perimeter access review documents for each quarter during a period of a year. WECC found that the document did not provide details on all personnel that were included in the previous and following quarterly reviews. Specifically, personnel were missing from the quarterly review. WECC_URE2 produced no additional evidence to demonstrate a change in personnel access rights between the quarters. While reviewing the same lists, WECC also identified one WECC_URE2 employee that had a change in physical access rights, however no documentation was provided to confirm an update to the access lists was made within seven days of the change in access rights. WECC issued a data request to WECC_URE2 to determine if the lists had been updated within seven days as required by the Standard. Based on the response provided by WECC_URE2, WECC determined that its lists had not been updated within seven days of the change in access rights. Based on documentation, interviews and observation, WECC determined that WECC_URE2 had a violation of CIP-004-1 R4 because it failed to maintain lists containing detailed specific electronic access rights for personnel with authorized cyber access to CCAs. WECC also confirmed that WECC_URE2 failed to review access lists on a quarterly basis because its review did not include all individuals with physical access rights during the previous and following reviews. Additionally, WECC_URE2 failed to update access lists within 7 days of a change of access rights for one individual as required by the Standard. WECC completed a Reliability Standard Audit Worksheet (RSAW) detailing the findings and evidence reviewed, and forwarded the documentation to the WECC Compliance Enforcement Department (Enforcement) for its review and consideration. WECC Enforcement reviewed the RSAW and concluded that WECC_URE2 had a violation of the CIP-004-1 R4 Standard because it failed to maintain, review and update access list(s) containing detailed specific access rights of personnel with authorized cyber or authorized unescorted physical access to CCAs as required by the Standard. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to maintain, update, and review access lists containing specific electronic and physical access rights for all personnel with access to CCAs as required by the Standard. The error could lead to personnel without authorized access rights, achieving or retaining access privileges to CCAs. WECC_URE2 had partially mitigated the risk by implementing a new access control system during the same quarter it failed to perform the quarterly review. Furthermore, WECC_URE2's non-specific electronic access controls reduce the likelihood of non-authorized system usage. | WECC_URE2's Mitigation Plan completion date for an earlier violation of the same standard | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Spot Check | To mitigate this violation, WECC_URE2: 1) reviewed the CCA Access Control List and ensure removal of access is occurring as specified in CIP-004-1 R4; 2) performed and properly documented quarterly reviews of the CCA Access Control List; and 3) ensured specific logical access for each CCA is documented in the quarterly reviews. | 2010-03-19 | 2010-09-01 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE2's compliance history in determining the disposition track.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC200901796 | Settlement Agreement | During a Spot Check, WECC determined that WECC_URE2 was in violation of CIP-007-1 R1. WECC determined that WECC_URE2 failed to implement cyber security test procedures and document testing results pursuant to CIP-007-1 R1. During the CIP Spot Check, WECC reviewed documents provided by WECC_URE2 to demonstrate compliance with CIP-007-1 R1. WECC_URE2 provided over 30 documents to demonstrate compliance with this Standard, including its current change and configuration management plan used to enforce testing procedures and change management. WECC_URE2 also provided its former process documents used for this Standard during an earlier part of the compliance review period. Based on the documentation provided, WECC determined that WECC_URE2 failed to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls. Specifically, WECC determined that WECC_URE2 failed to implement cyber security test procedures and document testing results as required by CIP-007-1 R1.1. Prior to approximately six months before the audit, WECC_URE2 did not have a procedure for testing the affect of new Cyber Assets or significant changes to existing Cyber Assets within the ESP on existing security controls. WECC based this finding on WECC_URE2's cyber security test procedures document, which did not have cyber security test procedures for significant changes to Critical Cyber Assets (CCAs) within the ESP. WECC_URE2 later introduced revised cyber security test procedures that had a procedure for testing existing security controls; however, no evidence was provided to demonstrate that this procedure was followed as documented. WECC also discovered that WECC_URE2 failed to provide documentation that its test environment reflected the production environment, as required by CIP-007-1 R1.2. Although WECC_URE2's test environment was within its ESP, it provided no base configuration documentation to establish similarities and deltas between production and test environments. Furthermore, WECC found no evidence that WECC_URE2 was documenting security control tests when significant changes were made to critical cyber assets CCAs, as required in R1.3. As a result, no documented test results were available to validate that users or system accounts retained the proper permissions after system changes were implemented. Based on documentation, interviews and observation, WECC determined that WECC_URE2 had a violation of CIP-007-1 R1 because WECC_URE2 failed to implement cyber security test procedures and document testing results as required by CIP-007-1 R1.1. WECC_URE2 also failed to document that testing is performed in a manner that reflects the production environment as required by CIP-007-1 R1.2. Finally, WECC_URE2 did not document its test results as required by the Standard as required by CIP-007-1 R1.3. WECC concluded that WECC_URE2 had a violation of the CIP-007-1 R1 because it failed to have adequate test procedures or follow established test procedures to ensure that new Cyber Assets and significant changes to existing Cyber Assets, within the ESP, did not adversely affect WECC_URE2's existing cyber security controls. In addition, WECC_URE2 failed to provide documentation that its test environment reflected the production environment and failed to implement cyber security test procedures and document testing results, as required by R1.2 and R1.3, respectively. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this situation, WECC_URE2 failed to have procedures to determine what affect significant changes to Cyber Assets would have on existing cyber security controls. Despite the absence of a formal process, it is noted that WECC_URE2 did check for vulnerabilities in another manner. In the event of a planned change, WECC_URE2 performed scans and completed a worksheet with change management steps. Although this process is not sufficient to demonstrate compliance, it does reduce the potential impact of changes to existing security controls. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Spot Check | To mitigate this violation, WECC_URE2: 1) examined the change control process documentation and ensured that the process for testing cyber security controls is adequate; 2) updated the base configuration documentation to establish similarities and deltas between production and test environments; 3) modified test and change control procedures to better capture evidence showing the risks and effects of the deltas between production and test environments; 4) modified documentation on how test environments are maintained and controlled; and 5) developed procedures to ensure a direct mapping between execution evidence and the cyber controls tests, which will also include the collection of cyber security test results. | 2010-03-30 | 2010-09-01 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102961 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. During an on-site audit, WECC discussed with WECC_URE2 its Self-Report. According to WECC, WECC_URE2 stated that it failed to assess patches for 20 Critical Cyber Assets (CCAs) within 30 days of availability of the patches. Specifically, WECC_URE2 stated that it failed to assess patches for ten converters and ten routers. WECC determined that WECC_URE2 was in violation of CIP-007-1 R3 for failing to assess security patches on 20 of its CCAs within 30 days of the patches being available. The cause of the violation was that WECC_URE2's personnel responsible for assessing patches were not on the vendor mailing list for the devices in scope, so were not getting the notifications for when patches are available. | CIP-007-1 | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to assess security patches may result in vulnerabilities remaining unaddressed for extended periods of time. In this case, WECC_URE2 failed to assess, within 30 days, security patches for 20 of its CCAs used for access control and monitoring of ten Electronic Security Perimeters. As a compensating measure, WECC_URE2 has strong technical and procedural controls that may limit exposure of the CCAs involved in this violation to improper or malicious use. In addition, each of the CCAs involved in the violation are located in Physical Security Perimeters, which also serves to reduce the changes that the CCAs are subject to improper or malicious use. | when the Standard became mandatory and enforceable on WECC_URE2 | when WECC_URE2 performed the required security patch assessments | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Self-Report | To mitigate this violation, WECC_URE2: 1) implemented a program to check periodically for upgrades and patches; 2) completed assessment of previous releases; 3) tested and installed all applicable patches and upgrades on all affected devices; and 4) assigned the lead communications engineer and maintenance reliability compliance coordinator to check the vendor websites on a 30-day basis and upon discovery of a new patch release the patch will be assessed for applicability. | 2011-08-24 | 2012-05-10 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102962 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R5. During an on-site audit, WECC discussed with WECC_URE2's its Self-Report. According to WECC, WECC_URE2 stated that it failed to rename default accounts on two Critical Cyber Assets (CCAs) as required by CIP-007-1 R5.2.1. In this regard, WECC_URE2 did change the password of the default administration account as required by CIP-007 R5.2.1, but it did not rename the account on two CCAs. WECC_URE2 also failed to provide an audit trail of account use for its shared accounts as required by CIP-007-1 R5.2.3. Finally, WECC_URE2 failed to change passwords on 16 of its CCAs as least annually, as required by CIP-007-1 R5.3.3. According to WECC, WECC_URE2 misinterpreted the requirement to apply only to “user” and “administrative” accounts instead of all accounts including maintenance, shared, administrator, and system accounts. Passwords for user and administrative accounts were rotated but some maintenance accounts on specific machines were not rotated as per the requirement. The Supervisory Control and Data Acquisition (SCADA) manager determined that the Windows system administrator misunderstood which accounts required a modification of passwords annually and when personnel changes occurred. WECC determined that WECC_URE2 is in violation of CIP-007-1 R5.2.1 for failing to rename default accounts on two CCAs, CIP-007-1 R5.2.3 for failing failed to provide an audit trail of account use for its shared accounts, and CIP-007-1 R5.3.3 for failing to change passwords on sixteen of its CCAs at least annually. The cause was a misunderstanding of the requirement. | CIP-007-1 | R5; R5.2.1; R5.2.3; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to establish technical and procedural controls to ensure that account and user access is implemented in compliance with CIP-007-1 R5 may allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. As compensating measures, WECC_URE2 has established strong technical and procedural controls that limit the risk of exposure to the CCAs identified. The physical and logical controls for these devices are limited to its personnel that have been provisioned access via its change control and management, personnel risk assessment, and CIP training programs. WECC_URE2 has also established strong technical and procedural controls that limit the risk of exposure to the CCAs identified. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Self-Report | To mitigate this violation, WECC_URE2: 1) reviewed all system accounts and passwords to determine when the last time passwords were changed; 2) modified passwords and account names, where appropriate; 3) created a process for the SCADA manager to create a new user workbook report for quarterly account review; and 4) used a new version of the energy management system (EMS) system that does not require passwords and account name s to be embedded in the EMS code. | 2012-03-23 | 2012-06-28 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102963 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R6. During an on-site audit, WECC discussed with WECC_URE2 its Self-Report. According to WECC, WECC_URE2's process for managing cyber security events monitoring is documented. However, WECC_URE2 could not produce evidence that it monitored for security events on 21 Critical Cyber Assets (CCAs). WECC_URE2, while implementing and documenting the organizational processes and technical and procedural mechanisms for monitoring for security events, did not do so for “all” Cyber Assets within the Electronic Security Perimeter (ESP). Because WECC_URE2 could not provide evidence that it monitored for security events on the above CCAs, WECC concluded that WECC_URE2 was in violation of CIP-007-1 R6. WECC determined that WECC_URE2 was in violation of CIP-007-1 R6 because it could not provide evidence that it monitored security events on the above CCAs, as required by CIP-007-1 R6.1. The cause was that the cyber assets were configured to send logs to the incorrect IP address. Therefore, the centralized logging server was not receiving the logs. The IP was also configured with the old IP address of the syslog server due to a miscommunication between the IT and maintenance groups. | CIP-007-1 | R6; R6.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to implement security controls to monitor cyber security system events, may allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. In addition, such access may then be used to cause harm to CCAs essential to the operation of the Bulk Electric System, thereby potentially negatively affecting the BPS. As compensating measures, WECC_URE2 had established strong technical and procedural controls that limit the risk of exposure to the CCAs identified. The physical and logical controls for these devices are limited to its personnel that have been provisioned access via its change control and management, personnel risk assessment, and CIP training programs. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Self-Report | To mitigate this violation, WECC_URE2 went to the affected locations and made configuration changes such that all devices listed in the Self-Report were logging to the security event server. | 2011-10-03 | 2012-05-10 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012054 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1. Specifically, WECC_URE2 reported that it failed to identify 15 devices as Critical Assets used in the access control and monitoring of its Physical Security Perimeters (PSPs). WECC_URE2 reported that because the devices were not properly identified as Physical Access Control and Monitoring (PACM) devices, the devices did not receive the protections required by CIP-006-1 R1, specifically R1.8. A WECC Subject Matter Expert (SME) reviewed WECC_URE2's Self-Certification. As part of the review, the SME requested additional information from WECC_URE2 concerning the violation. Based on a review of all information received, the SME determined that WECC_URE2 was in violation of CIP-006-1 R1, specifically R1.8. The SME determined that WECC_URE2 had 15 devices that had not been classified as Critical Assets used in the access control and monitoring of its PSP. As a consequence of WECC_URE2's failure to properly identify the assets as PACM devices, the SME determined that WECC_URE2 failed to afford the 15 devices the protections required by CIP-006-1 R1.8, specifically the protections of CIP-005 R2, and R3; CIP-007 R1-R9; and CIP-009 R1-R5. The SME determined that the violation included 15 out of WECC_URE2's 22 PACM devices. WECC reviewed the Self-Certification and SME findings. Based on this review, WECC determined that WECC_URE2 is in violation of CIP-006-1 R1. Specifically, WECC determined that WECC_URE2 failed to afford the protections outlined in CIP-006-1 R 1.8, specifically the protections of CIP-005 R2 and R3; CIP-007 R1-R9; and CIP-009 R1-R5, to 15 PACM devices. WECC determined that the violation was a result of WECC_URE2's failure to properly identify the devices as Critical Assets used in the access control or monitoring of its PSPs. WECC determined that the PACM were not behind a firewall or other electronic perimeter. This was confirmed by checking individual asset, application, router and firewall configurations. The causes of the violation were that CIP roles and responsibilities were not understood by system operators, when the system was implemented it was not identified as being in scope, and the methodology to identify assets was not consistent between the groups managing components of PACM. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation occurred over a period of approximately four years and included approximately 68% of WECC_URE2's PACM devices. WECC determined that, based on the duration and magnitude of WECC_URE2's failure, there was an increased opportunity for malicious cyber attacks to occur. Furthermore, WECC determined that WECC_URE2's failure created a situation where WECC_URE2 may have been unable to properly detect and prevent potential cyber attacks. Although WECC_URE2 failed to afford various protections required by CIP-006-1 R1 to 15 PACM devices, each of the devices is located on WECC_URE2's corporate network and is monitored 24 hours a day 7 days a week. Additionally, each of the devices has strong passwords that comply with additional CIP criteria. Finally, all of the devices reside within secure facilities where access is limited to employees who have undergone personnel risk assessments and have Critical Asset training. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Self-Certification | To mitigate this violation, WECC_URE2: 1) clarified CIP roles and responsibilities and provided training to management stakeholders on CIP-006 and refresher SME training for CIP compliance specific to CIP-006; 2) applied CIP controls to PACM and addressed system not being captured by making changes to the CIP review process and Cyber Vulnerability Assessment process to find unknown systems which may be in scope; 3) improved organizational continuity for demonstrating compliance by producing a set of procedures that show how to gather, maintain, store, and submit execution evidence for compliance activities; 4) developed a single methodology for identifying all Cyber Asset classes between all functional groups; 5) corrected network documentation and improved the documentation update process; and 6) provided focused awareness of interrelationships between CIP-005, CIP-006, and CIP-007 by providing refresher SME training for CIP compliance specific to CIP-006. | 2013-08-01 | 2015-09-23 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014018 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R6. Specifically, WECC_URE2 reported that it failed to review logs of system events related to cyber security and maintain records documenting review of logs, as required by CIP-007 R6. While WECC_URE2 reported that log reviews were being conducted, evidence of the review was insufficient. Additionally, WECC_URE2 reported that there were insufficient procedures and internal controls to assure the log reviews were occurring and being documented in a way that demonstrates compliance with the Requirement. WECC reviewed the Self-Report at WECC_URE2's mock audit results. WECC reviewed the details of the Self-Report and issued data requests for additional information. Based on the review, WECC determined that WECC_URE2 failed to establish a method to document the review and handling of events related to cyber security. While the evidence reviewed confirmed that WECC_URE2 was logging security events related to cyber security and generating alerts to response personnel, WECC_URE2 had no process or evidence to demonstrate that the alerts were being reviewed. WECC determined that WECC_URE2 was in violation of CIP-007-1 R6 for failing to review logs of system events related to cyber security and maintain records documenting review of logs. The root cause was insufficient procedures and internal controls to assure the log reviews were occurring and being documented in a way which demonstrates compliance. The cause was an insufficient procedures and internal controls to assure the log reviews were occurring and being documented in a way which demonstrates compliance with the Requirement. | CIP-007-1 | R6; R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2's devices were generating alerts and the alerts were being reviewed; however, WECC_URE2 was not capturing any evidence of these reviews. Without the documentation, there is no assurance that these reviews were consistently occurring. Failing to review system events related to cyber security could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Nevertheless, WECC_URE2 implemented good preventive controls. Specifically, WECC_URE2 enabled logging and alerting on all devices where technically capable. WECC_URE2's alerts were configured in a manner to notify responsible personnel of any potential cyber security events on its system. Although WECC_URE2 was not documenting its review and handling of the events, it does appear its response personnel were receiving the alerts and training on properly responding to them, reducing the risk of an event going unnoticed and unchecked. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | No penalty (for WECC200901795, WECC200901796, WECC201102961, WECC201102962, WECC201102963, WECC2013012054, and WECC2014014018) | Self-Report | To mitigate this violation, WECC_URE2 implemented a policy of log review and attestation of the review. | 2014-07-31 | 2015-11-19 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE2's compliance history in determining the disposition track. WECC considered WECC_URE2's compliance history to be an aggravating factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901552 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-1 R1. WECC_URE3 stated in its Self-Report that it failed to document cyber security testing as required by the Standard. WECC_URE3 is required to document testing in a manner that reflects the production environment under CIP-007-1 R1.2. WECC_URE3 is also required to document the results of its cyber security testing under CIP-007-1 R1.3. During an interview with WECC_URE3 personnel regarding this violation, a WECC subject matter expert (SME) confirmed that WECC_URE3 did not document any cyber security testing. Based on information from the Self-Report and the subsequent interview with WECC_URE3, WECC determined that WECC_URE3 had a violation of CIP-007-1 R1 because it failed to document its cyber security testing and results. WECC reviewed the Self-Report and the SME’s findings and concluded that WECC_URE3 had a violation of CIP-007-1 R1 because WECC_URE3 failed to have test procedures covering new Cyber Assets as required by R1; failed to document that testing is being performed as required by R1.2; and failed to document test results as required by R1.3. Because the violation period of R1.1 found during the Spot Check coincides with the Self-Reported violations of R1.2 and R1.3, WECC processed this violation in conjunction with WECC200901713. | CIP-007-1 | R1; R1.2; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to create or implement procedures for a range of equipment and significant changes to Cyber Assets as required by the Standard. However, WECC_URE3 described during a WECC interview that it was using subject expert experience and a security utility program to measure the effect of changes and test functionality on changes to its Supervisory Control and Data Acquisition (SCADA)/Automatic Generation Control (AGC) systems. Additionally, all testing was performed on a development system prior to installation on the production system in a manner that ensured the reliability of the online system remained intact | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Report | To mitigate this violation, WECC_URE3: 1) developed and implemented a SCADA Change Authorization Form; and 2) installed a software tool for detecting and reporting system changes. | 2009-07-30 | 2009-08-26 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901626 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-1 R4. Supplemental information was provided during an interview with WECC_URE3 personnel. WECC_URE3 stated in its Self-Report that its anti-virus and malware prevention tools were not being applied to various Cyber Assets within its Electronic Security Perimeter (ESP). Because CIP-007-1 R4 requires that WECC_URE3 shall use anti-virus software and other malicious software prevention tools on all Cyber Assets, within the ESP, WECC_URE3 reported a violation of the Standard. WECC_URE3 did not have a properly working process for updating the anti-virus and malware prevention signatures on the platforms where they are installed and was in violation of CIP-007-1 R4.2. WECC reviewed the violation Self-Report and additional information and determined that WECC_URE3 failed to have an implemented process for using anti-virus software and other malware prevention on Cyber Assets within WECC_URE3’s ESP. Specifically, WECC_URE3 identified it has an active platform where it demonstrated there was a technically feasible malware scanning solution. However, anti-virus software and other malware prevention tools had not been deployed on these platforms as required. Based on WECC_URE3’s failure to deploy anti-virus software and other malware prevention tools, WECC determined that WECC_URE3 had a violation of CIP-007-1 R4. WECC reviewed the Self-Report and concluded that WECC_URE3 had a violation of the CIP-007-1 R4 because WECC_URE3 failed to use anti-virus software and other malicious software prevention tools on all Cyber Assets within the ESP as required by the Standard. | CIP-007-1 | R4; R4.2 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to deploy anti-virus software on Cyber Assets within the ESP means an increased risk of exposure to malware. Although WECC_URE3 has mitigating controls to reduce the risk of external attacks, cyber incidents can originate from internal sources. Although insiders are not likely to have malicious intent, they may unintentionally plant malicious software by connecting infected systems or devices to an internal network resulting in a compromise of the integrity/confidentiality of the system or by affecting system performance, availability, and/or storage capacity. WECC_URE3 has highly-restrictive firewall rules in place that reduced the risk. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Report | To mitigate this violation, WECC_URE3 implemented anti-virus signature updating and system scanning to prevent viruses and malware on systems within the Supervisory Control and Data Acquisition (SCADA) ESP. | 2009-11-19 | 2009-12-09 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901645 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. WECC_URE3 stated in its Self-Report that it failed to document security patches and security upgrades to Cyber Assets within the Electronic Security Perimeter (ESP). WECC_URE3 reported a violation because it failed to document assessments within 30 calendar days as required by R3.1 and implementations as required by R3.2. During an internal review, WECC_URE3 discovered that it had not been following its configuration management process for security patches to Cyber Assets. Specifically, WECC_URE3 reported that it failed to document the process implementation, compensating measures to mitigate risks, or the acceptance of risk. The WECC_URE3 process states that security patch assessments must be documented within 30 calendar days, as required by CIP-007-1 R3.1. WECC_URE3 also reported that it failed to document the implementation of security patches as required by R3.2. Although WECC_URE3 had established and documented a security patch management program as required by CIP-007-1, the program had not been fully implemented. Based on information from the Self-Report and the subsequent interview with WECC_URE3, a WECC subject matter expert (SME) determined that WECC_URE3 had a violation because it failed to document security patches as required by CIP-007-1 R3.1, and failed to document the implementation of security patches to Cyber Assets within the ESP as required by R3.2. The WECC_URE3 process states that security patch assessments must be documented within 30 calendar days, as required. WECC_URE3 also reported that it failed to document the implementation of security patches as required by R3.2. WECC concluded that WECC_URE3 had a violation of CIP-007-1 R3 because WECC_URE3 failed to document the assessment of security patches as required by R3.1, or the implementation of security patches as required by R3.2. The cause was WECC_URE3 not following its procedure. | CIP-007-1 | R3; R3.1; R3.2 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to document security changes to Critical Assets may result in an increased risk of a cyber attack on the assets. Although WECC_URE3 has mitigating controls to reduce the risk of external attacks, cyber incidents can originate from internal sources. Although insiders are not likely to have malicious intent, they may unintentionally plant malicious software by connecting infected systems or devices to an internal network resulting in a compromise of the integrity/confidentiality of the system or by affecting system performance, availability, and/or storage capacity. Although not fully implemented, WECC_URE3 had established and documented a security patch management program as required by CIP-007-1, which helped reduce the risk. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Report | To mitigate this violation, WECC_URE3 assessed patches, installed the patches where appropriate, and completed the documentation associated with the patches, for all Supervisory Control and Data Acquisition (SCADA) systems. | 2009-10-27 | 2009-10-28 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. Although WECC_URE3 self-reported this violation, because it self-reported during the 60-day CIP Spot Check notification window, no Self-Report credit was applied. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901710 | Settlement Agreement | During a Spot Check WECC determined that WECC_URE3 was in violation of CIP-003-1 R1. WECC determined that the WECC_URE3 Cyber Security Policy failed to address three requirements in CIP-002 through CIP-009 as required by CIP-003-1 R1.1. WECC also determined that the WECC_URE3 Cyber Security Policy was not approved by the senior manager as required by CIP-003-1 R1.3. WECC notified WECC_URE3 at the time of the review that there was a violation of the Standard. During the Spot Check, WECC_URE3 presented a Program Cyber Security Plan (PCSP) as evidence of its compliance with CIP-003-1 R1. WECC reviewed the PCSP and determined it did not address CIP-002-1 R1, CIP-002-1 R2, and CIP-002-1 R4 as required by CIP-003-1 R1.1. Because CIP-003-1 R1.1 requires that an entity’s Cyber Security Policy address each of the requirements in CIP-002 through CIP-009, WECC determined this was a violation of the Standard. WECC also determined that WECC_URE3’s assigned senior manager had not approved the PCSP as required by CIP-003-1 R1.3. The WECC_URE3 PCSP’s annual review and approval had actually been performed by the chief information officer, not the assigned senior manager. WECC_URE3 offered no evidence that the authority to conduct the annual review had been delegated. Because CIP-003-1 R1.3 requires that annual review and approval of the Cyber Security Policy be performed by the senior manager, WECC determined this was a violation of the Standard. WECC concluded that WECC_URE3 had a violation of CIP-003-1 R.1 because it failed to address all CIP standards in its Cyber Security Policy as required by R1.1, and also failed to have the assigned senior manager approved the plan as required R1.3. | CIP-003-1 | R1; R1.1; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE3 failed to address three CIP-002 requirements in its Cyber Security Policy, it was found to be compliant with the individual standards. Furthermore, although a WECC_URE3 senior manager did not approve the PCSP, it was approved and reviewed at a high level within the organization. This approval is a good indication of WECC_URE3 management’s commitment to the PCSP. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Spot Check | To mitigate this violation, WECC_URE3: 1) updated its Cyber Security Policy to be compliant with CIP-002 through CIP-009; and 2) submitted evidence that the Cyber Security Policy was approved by the designated senior manager. | 2009-09-01 | 2010-07-30 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901711 | Settlement Agreement | During a Spot Check WECC determined that WECC_URE3 was in violation of CIP-004-1 R2. During the Spot Check, WECC_URE3 identified a Program Cyber Security Plan (PCSP) as its cyber security training, to demonstrate compliance with CIP-004-1 R.2. The entity provided two annual versions of the document. WECC determined that the PCSP had not been annually reviewed as required by CIP-004-1 R2, as it was last updated in more than a year prior. WECC_URE3 offered no evidence that the PCSP had been reviewed or updated since its introduction. Because the Standard requires that an annual review be conducted on the cyber security training program, WECC determined this was a violation of CIP-004-1 R2 because WECC_URE3 did not review and update its cyber security training materials annually. WECC concluded that WECC_URE3 had a violation of CIP-004-1 R2 because WECC_URE3 failed to review and update its cyber security training materials as required by CIP-004-1 R2. | CIP-004-1 | R2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this violation, WECC_URE3 failed to annually review the plan as required. Although WECC_URE3 failed to have a documented cyber security training program, it had provided training to all individuals with access to Critical Cyber Assets on the prior version of the PCSP. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Spot Check | To mitigate this violation, WECC_URE3 updated its Cyber Security Policy. The new document was reviewed and approved by WECC_URE3's then interim designated senior manager. | 2009-09-01 | 2010-09-03 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901712 | Settlement Agreement | During a Spot Check WECC determined that WECC_URE3 was in violation of CIP-004-1 R4. WECC determined that WECC_URE3 failed to maintain lists of individuals with administrative access to Critical Cyber Assets as required by CIP-004-1 R4. WECC_URE3 also failed to perform quarterly reviews of its access lists as required by CIP-004-1 R4.1. WECC notified WECC_URE3 at the time of the Spot Check review that there was a possible violation of CIP-004-1 R4. During the Spot Check, WECC_URE3 provided WECC with several lists detailing individuals with access to WECC_URE3’s Critical Cyber Assets (CCAs). After reviewing the documents, WECC determined that WECC_URE3 had failed to maintain a list of individuals with administrative access to CCAs. WECC_URE3 confirmed that there were two individuals with administrative access that did not appear on the presented lists. WECC_URE3’s response to a WECC Spot Check data request provided no additional evidence of the missing access lists or proof that the network personnel access file had been reviewed as required. Because CIP-004-1 requires that WECC_URE3 maintain lists of all personnel with access to CCAs, WECC determined this was a violation of the CIP-004-1 R4. Additionally, WECC established that WECC_URE3 had not performed quarterly reviews of all access lists. Specifically, WECC_URE3 had not reviewed its document that details the individuals with access to network equipment with the WECC_URE3 Electronic Security Perimeter (ESP). As evidence of compliance, the entity provided a document which discusses and documents its quarterly reviews of access lists. The document showed a reviewer name for two quarters, however it did not have a specific date of review. Because the review dates could not be confirmed, WECC determined this was a violation of the Standard. WECC concluded that WECC_URE3 had a violation of the CIP-004-1 R4 because WECC_URE3 failed to maintain a list of all individuals with access to Critical Cyber Assets as required by R4 and also failed to perform quarterly reviews of those lists as required CIP-004-1 R4.1. | CIP-004-1 | R4; R4.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to maintain lists of those with access to CCAs could result in individuals having unnecessary access to systems. Such access could potentially be misused to perform unauthorized actions on CCAs, possibly affecting the Bulk Electric System. In this situation, WECC_URE3 has strong physical access controls to control access to its CCAs. Furthermore, WECC_URE3 does not allow remote access to its CCAs from outside the Physical Security Perimeter. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Spot Check | To mitigate this violation, WECC_URE3: 1) reviewed the Supervisory Control and Data Acquisition (SCADA) access list and has continued to do quarterly reviews; 2) performed analysis to identify issues in the access list control; 3) identified possible solutions to eliminate gaps in the processes; and 4) implemented a document management system which includes alerts for document review. | 2009-06-30 | 2010-08-25 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC200901713 | Settlement Agreement | During a Spot Check WECC determined that WECC_URE3 was in violation of CIP-007-1 R1. WECC determined that WECC_URE3 failed to create cyber security test procedures as required by R1.1. WECC_URE3 provided its supervisory control data acquisition form and a security change control process documents as evidence of WECC_URE3 test procedures. WECC found that WECC_URE3's test procedures did not cover new Cyber Assets; it only covered patches to WECC_URE3’s Critical Cyber Assets (CCAs) within its Electronic Security Perimeter (ESP). WECC also found that WECC_URE3 did not have procedures in place that address significant changes in all Cyber Assets within the ESP, only its CCAs. Based on the procedures presented by WECC_URE3, WECC concluded that WECC_URE3 had a violation of R1.1. WECC concluded that WECC_URE3 had a violation of CIP-007-1 R1 because WECC_URE3 failed to create cyber security test procedures for significant changes to all Cyber Assets as required by R1.1. Because the violation period of R1.1 found during the Spot Check coincides with the Self-Reported violations of R1.2 and R1.3, WECC processed this violation in conjunction with WECC200901552. | CIP-007-1 | R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to create or implement procedures for a range of equipment and significant changes to cyber assets as required by the Standard. However, WECC_URE3 described during a WECC interview that it was using subject expert experience and a security utility program to measure the effect of changes and test functionality on changes to its SCADA/Automatic Generation Control (AGC) systems. Additionally, all testing was performed on a development system prior to installation on the production system in a manner that ensured the reliability of the online system remained intact. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Spot Check | To mitigate this violation, WECC_URE3: 1) performed gap analysis of documentation and evidence; 2) confirmed base configuration documentation to establish similarities between production and development environments utilizing existing tool; and 3) confirmed procedures are developed to ensure a direct mapping between execution evidence and the cyber controls tests. | 2010-06-17 | 2010-09-01 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201002235 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-004-1 R4. A WECC subject matter expert (SME) reviewed the Self-Report and conducted a telephone interview with WECC_URE3 personnel. The SME determined an individual with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) retired. The individual was an employee of a company that WECC_URE3 had a Joint Use Agreement with. The other company did not inform WECC_URE3 of the retirement in a timely manner. The SME determined WECC_URE3 should have revoked access rights for this individual within seven calendar days of the employee’s retirement. Based on the interview and the Self-Report, the SME determined WECC_URE3 did not revoke this individual’s access in a timely manner and thus determined WECC_URE3 had a violation of CIP-004-1 R4.2. The SME further determined WECC_URE3 did not quarterly review its lists of its personnel who have access to CCAs, and update the lists within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights of such personnel. Therefore, the SME determined WECC_URE3 had a violation of CIP-004-1 R4.1. WECC determined that WECC_URE3 did not conduct quarterly review of its lists of personnel with authorized cyber or authorized unescorted physical access to CCAs or update its lists within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights of such personnel. WECC further determined WECC_URE3 failed to revoke access to CCAs within seven calendar days for personnel who no longer require such access to CCAs. Therefore, WECC determined WECC_URE3 has a violation of CIP-004-1 R4, specifically R4.1 and R4.2. | CIP-004-1 | R4; R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 did not review the lists of its personnel who have access to CCAs quarterly and update the lists within seven calendar days of any change of personnel with such access to CCAs, nor did it revoke such access within seven days. Such a failure could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the Bulk Electric System (BES), thereby potentially negatively impacting the BES. However, in this case, the violation relates to WECC_URE3’s failure to revoke access within seven days of an employee retiring. During the individual’s time as a WECC_URE3 employee, the individual appropriately had authorized access to CCAs. Further, as a compensating measure, WECC_URE3 maintains manual logging of physical access of personnel entering and exiting its facilities. | seven calendar days after the personnel no longer required such access | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Report | To mitigate this violation, WECC_URE3 removed all Joint User Agreement company employees' access in the access control system, until it could be confirmed the company employees understood the requirements and retook the cyber security training. | 2010-08-23 | 2011-06-02 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3’s CIP-004 R4 compliance history to be an aggravating factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201002237 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R2. A WECC subject matter expert (SME) reviewed the Self-Certification and conducted a telephone interview with WECC_URE3 personnel. The SME determined two PCs at WECC_URE3’s substation did not have a record of ports and services being evaluated and disabled, and therefore WECC_URE3 did not establish and document a process to ensure that only ports and services required for normal and emergency operations are enabled. The SME determined the two PCs are connected to WECC_URE3’s Electronic Security Perimeter (ESP). WECC_URE3 classified these PCs as Critical Cyber Assets (CCAs). Thus, the SME determined WECC_URE3 had a violation of CIP-007-1 R2. WECC determined that WECC_URE3’s failure to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled on the two PCs is a violation of CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 did not ensure that only those ports and services required for normal and emergency operations are enabled for two PCs. A failure to ensure that only those ports and services required for normal and emergency operations are enabled poses significant risk to the entity's Cyber Assets by potentially allowing for unauthorized internal or external access, which could allow for successful cyber attacks against CCAs essential to operation of the Bulk Electric System. However, as compensating measures, WECC_URE3 stated that it implemented controls to log and monitor access to CCAs within the ESP within which the two PCs reside. In addition, the access point to this ESP only allows access to the ports and services necessary for normal operations. Further, the violation is limited to two legacy PCs within WECC_URE3’s system. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Certification | To mitigate this violation, WECC_URE3: 1) removed the devices from the network and had the network administrator verify disconnection; and 2) ensured future Cyber Assets, if connected to the network, will utilize a current operating system and not a legacy operating system. | 2010-02-02 | 2010-10-20 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201002238 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R3. A WECC subject matter expert (SME) determined two PCs at WECC_URE3’s substation did not have a record of an assessment for implementation of security patches. The SME determined the two PCs are connected to WECC_URE3’s Electronic Security Perimeter (ESP). WECC_URE3 classified these PCs as Critical Cyber Assets (CCAs). The SME determined WECC_URE3 did not document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades and failed to document the implementation of security patches for the PCs. Thus, the SME determined WECC_URE3 had a violation of CIP-007-1 R3. WECC determined that WECC_URE3’s failure to document its assessment of security patches and security upgrades for applicability to the two PCs within 30 calendar days of the patches or upgrades being made available is a violation of CIP-007-1 R3. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to assess security patches and upgrades for two PCs. A failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against CCAs essential to the operation of the Bulk Electric System. As a compensating measure, WECC_URE3 personnel stated that all other devices on the applicable network are current on patches pursuant to WECC_URE3’s security patch management plan. In addition, WECC_URE3 implemented controls to log and monitor access to CCAs within the ESP in scope. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Certification | To mitigate this violation, WECC_URE3: 1) removed the devices from the network and had the network administrator verify disconnection; and 2) ensured future Cyber Assets, if connected to the network, will utilize a current operating system and not a legacy operating system. | 2010-02-02 | 2010-10-20 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3’s CIP-007 R3 compliance history to be an aggravating factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201002239 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R4. A WECC subject matter expert (SME) determined WECC_URE3 did not use anti-virus software and other malicious software malware prevention tools on two PCs at WECC_URE3’s substation. The SME determined the two PCs are connected to WECC_URE3’s Electronic Security Perimeter (ESP). WECC_URE3 classified these PCs as Critical Cyber Assets (CCAs). The SME determined WECC_URE3 did not use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within its ESP. Thus, the SME determined WECC_URE3 had a violation of CIP-007-1 R4. WECC determined that WECC_URE3’s failure to use anti-virus software and other malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on the two PCs within its ESP is a violation of CIP-007-1 R4. | CIP-007-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 did not use anti-virus software and other malicious software (malware) prevention tools for its Cyber Assets, on two PCs. Failure to do so could allow existing or new malicious software, originating from, e.g., a security patch, service pack, vendor release, application or database update, to be introduced to the Cyber Assets, thereby exposing cyber security vulnerabilities into the CCAs. If exposed, such vulnerabilities could negatively affect the normal operation of the Bulk Electric System. As a compensating measure, WECC_URE3 installed anti-virus and other malicious software prevention tools on all other capable devices on the network in scope. In addition, WECC_URE3 personnel stated that WECC_URE3 implemented controls to log and monitor access to CCAs within the ESP in scope. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Certification | To mitigate this violation, WECC_URE3: 1) removed the devices from the network and had the network administrator verify disconnection; and 2) ensured future Cyber Assets, if connected to the network, will utilize a current operating system and not a legacy operating system. | 2010-02-02 | 2010-10-20 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009538 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R4. A WECC subject matter expert (SME) contacted WECC_URE3 to discuss its self-certification. According to the WECC SME, WECC_URE3 stated that it failed to rename default administrator accounts on ten devices prior to putting them into production. All ten devices are Critical Cyber Assets (CCAs). Nine of the devices are used to collect data such as power voltage status, circuit breaker status and alarms, from protective relays and transmit that data to Remote Terminal Units (RTU). One of the devices involved in this violation is an RTU that controls physical equipment in substations. The WECC SME concluded that WECC_URE3 was in violation of CIP-007-1 R5.2.1. WECC reviewed WECC_URE3’s Self-Certification and determined that WECC_URE3 is in violation of CIP-007-1 R5.2.1 for failing to rename default administrator accounts on ten CCAs prior to putting them into production. WECC_URE3 did not include the removal, disabling, or renaming of such accounts where possible, for accounts that must remain enabled, passwords were changed prior to putting any system into service. The cause of this finding was due to the misinterpretation of CIP-007-R5. Prior to this finding during the WECC_URE3 Self-Certification for 2011, it was the general understanding that WECC_URE3 met compliance for CIP-007-R5.2.1 on the device by controlling access authentication through technical and procedural controls. | CIP-007-1 | R5.2.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to rename default administrator accounts prior to putting them into service could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the Bulk Electric System (BES), thereby potentially negatively affecting the BES. These devices are located at various substations inside Electronic Security Perimeters and Physical Security Perimeters. As compensating measures, WECC_URE3 stated that the default administrator accounts passwords were changed annually, met the CIP-007 R5.3 complexity requirements, were changed when there were personnel changes, and access to the devices required multi-factor authentication. In addition, all personnel with access to the accounts had current CIP training and personnel risk assessments and the devices were monitored continuously for physical and cyber access and account access was reviewed quarterly. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Certification | To mitigate this violation, WECC_URE3: 1) contacted engineering labs to confirm administrator accounts could be changed and requested information about how to proceed; 2) tested the process for changing administer accounts; 3) renamed the default administrator accounts; and 4) communicated the details of the violation at the Annual Maintenance and Engineering Meeting to develop a common understanding of the NERC requirement and the need to rename administrator accounts on CCAs prior to putting them into service. | 2012-03-14 | 2012-08-30 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010260 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-002-2 R3. A WECC subject matter expert (SME) contacted WECC_URE3 to discuss its Self-Report. According to the WECC SME, WECC_URE3 stated that it failed to identify one of its Critical Cyber Assets (CCAs). The CCA WECC_URE3 failed to identify is a laptop used to periodically conduct Cyber Vulnerability Assessments (CVA) on WECC_URE3’s Electronic Security Perimeters (ESPs). The laptop involved met WECC_URE3’s CCA criteria and should have been added to its CCA list when it was put into service. The WECC SME concluded that WECC_URE3 was in violation of CIP-002-2 R3. WECC determined that WECC_URE3 is in violation of CIP-002-2 R3 for failing to identify one of its devices as a CCA. The root cause was that the laptop was connected to the Supervisory Control and Data Acquisition (SCADA) ESP in order to conduct CVA scans and was not considered a potential CCA due to its temporary connection to the ESP. At the time the laptop was put into service, there was not a documented methodology for CCA determination. The only determination criteria in the past was if the Cyber Asset was in an ESP then it was considered a CCA and temporary devices were not considered in the process and the laptop was excluded. | CIP-002-2 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify CCAs could result in leaving CCAs unprotected and vulnerable to a cyber threat, and could pose a risk to the associated Critical Asset. This can negatively impact the operation of the Bulk Electric System. In this instance, WECC_URE3 failed to identify one CCA that met its criteria for a CCA and was not added to its CCA list. The device in scope was a laptop used to conduct CVAs. The device was routinely added and removed from all of the entity’s ESPs to conduct these periodic CVAs. As this was a laptop used on different ESPs in different physical locations, WECC_URE3 cannot ensure this device was inside an identified Physical Security Perimeter (PSP) at all times. As compensating measures, WECC_URE3 stated that only one individual had access to the device, it was only added to an ESP when it was conducting a CVA, and it was only used on designated ESPs and, thus when in service, was always in a protected network behind restrictive firewalls, and implemented AV/Malware prevention tools. WECC_URE3 also stated that although the device was mobile, while it was connected to an ESP it was in an identified and protected PSP. Finally, WECC_URE3 stated that the device in scope would no longer be considered a CCA using WECC_URE3’s current CCA identification methodology. | when the device involved was put into service | Mitigation Plan completion | No penalty (for WECC200901552, WECC200901626, WECC200901645, WECC200901710, WECC200901711, WECC200901712, WECC200901713, WECC201002235, WECC201002237, WECC201002238, WECC201002239, WECC2012009538, WECC2012010260) | Self-Report | To mitigate this violation, WECC_URE3: 1) implemented a methodology for determining CCAs; and 2) provided on the job training on the use of this new methodology and specifically temporary devices. | 2012-04-11 | 2012-10-25 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a factor in the disposition determination. WECC considered WECC_URE3’s CIP-002 R3 compliance history to be an aggravating factor in the disposition determination.
2016-12-29 | FERC | NP17-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2015014880 | Settlement Agreement | WECC_URE4 submitted a Self-Report and approximately a month later WECC_URE4 submitted a Self-Certification stating that it was in violation of CIP-006-1 R3. WECC_URE4 identified the noncompliance during a mock audit. WECC_URE4 reported that it failed to implement appropriate technical and procedural controls per CIP-006-1 R3 guidelines. WECC reviewed the Self-Certification information and determined that WECC_URE4 failed to implement appropriate technical and procedural controls for monitoring physical access at two emergency/service doors to a Physical Security Perimeter (PSP) for twenty-four hours a day, seven days a week. The two PSP access points did not incorporate card readers and are identified as the emergency/service exit doors. Both are secured using mechanical hardware with magnetic door contacts monitored twenty-four hours a day, seven days a week remotely by the contracted security guards via intrusion monitoring software. However, when the first authorized personnel enters the PSP, he or she disables the alarm system, which disables the control room motion detection devices and the magnetic door contacts on the service doors. This allows additional authorized personnel to unlock the dead bolt with a key and enter the PSP through the service doors without any logging and/or triggering an alarm if the door is left open, since the motion detectors are disabled when the control room is occupied. WECC determined that WECC_URE4 is in violation of CIP-006-1 R3 for failing to implement appropriate technical and procedural controls for monitoring physical access to a PSP. The root cause of the violation was a lack of compliance understanding. The system was set up prior to the existence of the CIP standards and WECC_URE4 did not believe it was an issue when the CIP standards became enforceable. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to implement appropriate technical and procedural controls for monitoring physical access at two emergency/service doors to a PSP twenty-four hours a day, seven days a week. Failing to implement technical and procedural controls for monitoring physical access at two emergency/service doors could allow unauthorized personnel access to the PSP. If the Physical Access Control System (PACS) would have been disarmed and the mechanical key lock defeated, unauthorized personnel would have access to several 230 kV transmission lines and the bus tie breaker between WECC_URE4 and a neighboring entity. WECC_URE4 implemented a dead bolt lock that restricted physical access to the PSP and a seven foot fence with barbed wire to prevent unauthorized physical access to the substation, as preventive controls. As an additional preventive control, the keys used to open the dead bolt locks are assigned to numerous individuals. Keys are accounted for using a key log and no one can access the two service doors without a key. WECC_URE4 also implemented good detective controls. Specifically, WECC_URE4 has employees who are working inside the PSP during normal business hours, and a guard monitors the two service doors via closed-circuit television cameras during non-business hours. Together, these employees would detect if someone attempted to physically damage the devices. Additionally, as revealed by an engineering study, loss of the transmission lines and tie-breaker from the substation in scope would not cause an overload or excessive voltage deviation. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, WECC_URE4: 1) removed the doors from the PACS, so the alarms will now alert when doors are open and will be monitored by a guard twenty-four hours a day, seven days a week; 2) installed an audible alarm on the exterior of the control room that must be silenced and reset over the alarm monitoring software from the twenty-four hours a day, seven days a week, guard office; and 3) updated its procedures and added signage to require personnel to call security before using either service door. | 2014-11-12 | 2015-08-14 | Agrees/Stipulates | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the disposition determination. WECC_URE4 did not receive mitigating credit for self-reporting because the Self-Report was submitted during the self-certification period.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014993 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-005-3a R1. During a review by NPCC_URE1 of software updates available from the vendor, a mismatch was discovered between the software updates reported by NPCC_URE1's automated patch notification system and the vendor. A project to develop a patches system was intended to include development of automated feeds for 20 systems in question but was never completed. The Cyber Security team did not implement a manual process to address the gap. After discovering this issue, NPCC_URE1 instituted a manual process for reviewing patch availability on a weekly basis and noted whether updates were available. | CIP-005-3a | R1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 20 Cyber Assets support three functions, 1) central logging and reporting/analysis of logs, 2) network intrusion detection, and 3) monitoring for changes to systems and applications. The Cyber Assets in question are a secondary means of monitoring the Electronic Security Perimeter (ESP) for suspicious activity. Additionally, although they are Intrusion Prevention Systems, they were only being used to detect suspicious activity not prevent it. Finally, these Cyber Assets do not operate or monitor Bulk Electric System (BES) elements. | when the Standard became mandatory and enforceable | when NPCC_URE1 completed 2 months of manual process execution | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) drafted manual procedures to look up software updates; and 2) implemented manual procedures to record assessments of these software updates. | 2015-08-05 | 2016-07-22 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014994 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-005-3a R2. Regular scans of ports and services by NPCC_URE1 discovered an unknown IP address and service combination on a monitoring system deployed at the control center. Further investigation revealed that the IP address and service were enabled during a troubleshooting engagement. The IP address and service provided access to an on-board diagnostic service processor in the underlying server for this monitoring system. This was an undocumented port and service that was not needed for normal or emergency operations. Based on the results from the scan, an incident ticket was filed with the Network Support team. Finally, after investigating the matter, the interface and server configuration were updated to remove the IP address and service via an outage. The root cause was the NPCC_URE1 employee failing to follow change management procedures. The employee had been principally engaged with troubleshooting the monitoring system and had set up a specific interface and forgot to remove it after completing an effort with that system. | CIP-005-3a | R2. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Cyber Asset is used to monitor network activity, which is a passive control that cannot itself prevent or stop a cyber attack and is not used to operate or monitor Bulk Electric System (BES) elements. Additionally, the service that was exposed was only accessible by someone with a specific username and password. | when the IP address was enabled | when a service outage addressed the service and the IP address | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) filed change request and executed to remove interface configuration that removed the errant IP address from the mainboard configuration and left the configuration expected for the Security Information and Event Management (SIEM); 2) removed the Lead Cyber Security Analyst from his position. | 2014-12-17 | 2016-07-08 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014995 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-005-3a R1. NPCC_URE1 did not document the assessment or implementation of security patches for software that is utilized on eight Cyber Assets (CAs). The violation started 31 days after the vendor released the next patch. The eight CAs support external interactive access. NPCC_URE1 automates a script that checks the vendor website for security updates. However, the website was changed and the script that checked the website for patch notifications failed to provide updates. The script did not include error checking to notify the team when it failed. | CIP-005-3a | R1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The eight CAs that utilize the software are not used to control or monitor Bulk Electric System (BES) elements. They provide access for support staff for maintenance of Critical Cyber Assets (CCA). CCAs supporting the Energy Management System and Electronic Dispatch services have local firewalls in place to prevent direct network access from the affected CAs. Additionally, the servers are in separate DMZ networks that are isolated from access from the affected CAs. The patches were installed during their annual patch run. | 31 days after the vendor released the patch that was not assessed | when the first assessment activity after mitigating the violation occurred | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) fixed the collection script; and 2) included error checking to notify the support team if the collection script fails to download any reported vulnerabilities. | 2014-12-01 | 2016-05-18 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014996 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-005-3a R1. NPCC_URE1 could not provide evidence with respect to the deployment and maintenance of two Cyber Assets (CAs), which support external interactive access to the Electronic Security Perimeter (ESP). The root cause was a miscommunication between two support teams within NPCC_URE1. Each of the two support teams believed the other was responsible for CIP compliance for the two cyber systems. | CIP-005-3a | R1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The two CAs in question are not used to control or monitor Bulk Electric System (BES) elements. They provide load balancing support for servers in the Energy Management System (EMS) network. The access points are located on an internal NPCC_URE1 network which limits the access to personnel on the corporate network. The devices were working properly. NPCC_URE1 reviewed its CIP assets and found no other assets that were in violation. | when the Standard became mandatory and enforceable | when the two CAs were retired | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) retired both CAs; 2) established replacement interactive remote access to ESP terminal servers; and 3) added groups to CA listing to prevent confusion over ownership. | 2015-08-24 | 2016-07-08 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014997 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-007-3a R3. Three Cyber Assets (CAs) were not patched with the security patches identified in an annual patch run. The CAs run a service that pings remote IP addresses on the electronic dispatch network to determine whether there is a loss of connectivity with the routers deployed at the generators in the field. In preparation for the annual patch run, these systems were identified as requiring a platform refresh. The team was unable to complete this refresh project. The requirement to patch the existing systems was never reevaluated and missed their annual patching cycle. | CIP-007-3a | R3. | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The patches that were not applied were all identified as non-critical in nature. All critical patches during this timeframe were applied to all the systems in a timely manner. These servers are within the Electronic Security Perimeter (ESP) and are used to monitor electronic dispatch network availability. | when the CAs missed their annual patch cycle | when patches were applied to affected systems | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) updated all patches for the Linux systems; and 2) installed software management service to address detailed monitoring and reporting on the Linux server package state. | 2015-12-30 | 2016-06-14 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014998 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-007-3a R8. NPCC_URE1 performed and documented the cyber vulnerability assessments (CVAs), but did not document the action plan and execution status to remediate or mitigate vulnerabilities identified in the several CVAs. The root cause was due to a misunderstanding by NPCC_URE1 to create a document outlining the CVA's action plan. | CIP-007-3a | R8. | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. NPCC_URE1 remediated the vulnerabilities found in their CVA but did not document the actions within an action plan. | the first day that the CVA did not contain an action plan | when completed the CVA and drafted an action plan | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) completed an outage plan to organize activity for the CVA; 2) executed the CVA including drafting of action plan for review by affected parties; and 2) updated the business process describing control actions for execution of CVA. | 2015-08-26 | 2016-07-08 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014999 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-007-3a R6. Certain operating systems were not sending user login success or failure events to central syslog servers. The result was that reviews of such security events were not possible from the time these systems were deployed. This was discovered while collecting evidence for control room workstations. The investigation broadened in scope to include all operating systems. An emergency outage was declared to address the issue once a fix was developed and tested to address all the in-scope systems affected by this problem. The root cause was a faulty configuration file that was intended to function on old systems but did not function correctly on newer versions. | CIP-007-3a | R6. | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was found for control room workstations and servers. If a cyber security incident involving one or more of the assets in question were to occur, user audit trail would not have been easily accessible. This could impede or prevent investigation from succeeding in identifying the root cause of the cyber incident if one were to occur. Actual event logs are retained locally on the systems in question but not for the full 90-day period. Supervisors note the people using the workstations every shift. Additionally, changes to the operating system is noted by monitoring software and reviewed daily. | when configuration changes to server and desktops were deployed | when NPCC_URE1 completed an outage to address the noncompliance | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) changed steps in the operating system build instructions for administrators building operating systems in CIP areas to include settings needed to send all security events to Security Information and Event Management (SIEM); and 2) configured a report in SIEM to collect list of cyber assets logging from CIP covered areas and compare against list of Cyber Assets. | 2015-12-30 | 2016-04-20 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC_URE1 did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming compliance audit. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's CIP-007 R6 compliance history to be an aggravating factor in the penalty determination.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015000 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 had an issue of CIP-007-3a R5. NPCC_URE1 submitted an approved Technical Feasibility Exception (TFE) with mitigation measures that required NPCC_URE1 to change root passwords every 90 days. There was one instance where NPCC_URE1 failed to change their password within 90 days. A password was changed and not changed again until 131 days later. The root cause was due to the supervisor failing to schedule the root password change in time for the 90-day interval. An administrator was leaving the team who knew the old root password. The supervisor did not want to change the password twice, once prior to an administrator leaving the team, and then once after the member had left the team. | CIP-007-3a | R5. | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 had set its compensating measures to change its passwords every 90 days. The Standard requires the passwords to be changed annually. | when the password aged beyond 90 days from the last password change | when the password was changed | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) developed a management review process for the age of administrative credentials in the relevant systems; and 2) requested a material change to the TFE in NPCC's compliance portal. | 2015-09-25 | 2016-06-10 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's CIP-007 R5 compliance history in determining the penalty and there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015001 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 had an issue of CIP-005-3a R5. Two Cyber Assets (CAs), which support external interactive access, were not configured to send logs to the log retention server. The access logs were not retained for 90 days. The root cause was a miscommunication between two support teams within NPCC_URE1. Each of the two support teams believed the other was responsible for CIP compliance for the two cyber systems. | CIP-005-3a | R5. | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The two CAs in question do not control or monitor Bulk Electric System (BES) elements. The two CAs provide load balancing support for the servers in the Energy Management System (EMS) network that are protected under CIP version 3. Additionally, terminal servers directly related to the path for interactive remote access provide logs to the central server. The two CAs were performing their intended functions. | when the Standard became mandatory and enforceable | when the two CAs were retired | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) retired both CAs; 2) established replacement interactive remote access to Electronic Security Perimeter (ESP) terminal servers; and 3) added groups to CA listing to prevent confusion over ownership. | 2015-08-24 | 2016-07-08 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015002 | Settlement Agreement | During a Compliance Audit NPCC determined that NPCC_URE1 was in violation of CIP-005-3a R4. The audit team determined that NPCC_URE1 performed and documented the cyber vulnerability assessments (CVA), but did not document the action plan and execution status to remediate or mitigate vulnerabilities identified in the three years of CVAs. The root cause was due to a misunderstanding by NPCC_URE1 to create a document outlining the CVA's action plan. | CIP-005-3a | R4. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. NPCC_URE1 remediated the vulnerabilities found in its CVA but did not document the actions within an action plan. | when the CVA did not contain an action plan | when NPCC_URE1 completed the CVA which included drafting an action plan | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Compliance Audit | To mitigate this violation, NPCC_URE1: 1) completed an outage plan to organize activity for the CVA; 2) executed the CVA including drafting of action plan for review by affected parties; and 3) updated the business process describing control actions for execution of CVA. | 2015-08-26 | 2016-07-08 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015520 | Settlement Agreement | NPCC_URE1 submitted a self-report stating that it was in violation of CIP-006-3c R2. NPCC_URE1 discovered that they had not configured their access rights software at control center guard shacks correctly. The access rights software is used to restrict access to Cyber Assets only to those NPCC_URE1 employees and contractors that had undergone seven-year background checks. The access rights software was not configured correctly and failed to confirm background checks were completed prior to granting access to the control center guard shacks. NPCC_URE1 identified one NPCC_URE1 employee and one NPCC_URE1 contractor that had access rights to the guard shacks that had not otherwise undergone a seven-year background check. The employee underwent a background check many years earlier and the contractor had a background check done in roughly the same time period. All other NPCC_URE1 employees and contractors with access to guard shacks have up-to-date background checks. The guard shacks contain workstations with a running instance of the software program in use to relay alerts from door sensors for badges as well as provide control for disabling locks on doors to areas containing Critical Cyber Assets (CCAs). This issue applied to only the guard shack entries in access rights in the control centers. The Cyber security team checked other Physical Security Perimeters (PSPs) and confirmed that the access rights setting indicating a requirement for seven-year background check and training for CIP protections was in place as expected. Investigation into the audit trail for settings in access rights for the guard shacks did not indicate the setting was altered. The setting was never enabled for the guard shacks in access rights, because when the access rights software was first employed by NPCC_URE1, the guard shacks did not contain Cyber Assets and were not labeled as PSPs. | CIP-006-3c | R2. | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The area in question is the NPCC_URE1 guard shacks and there are no Cyber Assets located in the guard shack that have a direct impact on the operability of the Bulk Electric System (BES). The guard shacks have computer assets that can allow for physical access to the NPCC_URE1 campus. The shack is only accessible to individuals with NPCC_URE1 approved access rights, who must badge into the controlled access point. The infrastructure in the guard shack was at all times behind that controlled access point. Only approved NPCC_URE1 staff or contractors would be able to gain access. As a level of security past that, only NPCC_URE1 staff and contractors that had applied for and been given access rights specifically for the guard shack would be able to badge in. Further, the small area is staffed on a continuous basis by an armed police officer. In order for a person to have exploited this oversight, they would have had to have a) been an NPCC_URE1 employee who passed a full background check to gain access rights, b) been in NPCC_URE1 employment for over seven years, and c) been able to explain their actions to the armed police officer staffing the shack. The contractor had no indicated access to the guard shacks during the duration of the noncompliance. The employee entered the main control center guard shack once during the duration of the noncompliance. | when the Standard became mandatory and enforceable | when access was removed from the employee and contractor | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Self-Report | To mitigate this violation, NPCC_URE1: 1) reviewed its CIP-002 inventory of Cyber Assets in order to; (a) confirm that the access rights software restricts access only to those NPCC_URE1 employees or contractors that have background checks; and (b) contains controls so that the access rights software will be updated in the event there are future changes to Electronic Security Perimeter (ESPs) and PSPs as a result of changes to the Cyber Asset inventory; and 2) checked all current PSPs in the access rights system to confirm that future access requests would require background checks within the last seven years before allowing normal authorization to proceed. | 2015-09-23 | 2016-06-13 | Admits | NPCC reviewed NPCC_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC_URE1 received mitigating credit for self-reporting this noncompliance. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1 compliance history and determined there were no relevant instances of noncompliance.
2016-10-31 | FERC | NP17-4-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015812 | Settlement Agreement | NPCC_URE1 submitted a self-report stating that it was in violation of CIP-007-3a R6. NPCC_URE1 implements part of its security event monitoring by collecting log entries from systems using a set of relay systems running log handling software to a central syslog collector which then forwards all log information to the security information and event management system. NPCC_URE1 investigated an issue with its log handling software and discovered that it failed to perform its primary logging from backup control center systems. A subset of systems at the control center which are configured to log directly to syslog, but do not have local copies of the lost logs for approximately one month. Additional systems (operating system servers) are configured to log to the relay and to local disk. The logs these systems sent to the relay during the timeframe mentioned above were lost. The same logs, however, were logged to local disk on these systems, and are retained in nightly backups. The root cause was a bug in the rsyslog software used to collect logs and forward them to the Security Information and Event Management (SIEM). | CIP-007-3a | R6. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. None of the systems affected directly implement reliability functions. However, it affected nine systems associated with a high impact Bulk Electric System cyber system, as well as 4 network switches, 1 firewall device, and 4 virtualization hosts. | when the Cyber Assets stopped sending logs for monitoring purposes | when the logging issue was resolved | $75,000 for NPCC2015015001, NPCC2015014996, NPCC2015015002, NPCC2015014995, NPCC2015014993, NPCC2015014994, NPCC2015014999, NPCC2015015000, NPCC2015014997, NPCC2015014998, NPCC2016015520, and NPCC2016015812. | Self-Report | To mitigate this violation, NPCC_URE1: 1) took an emergency outage to restart the non-working process on the intermediary logging relay systems; 2) implemented software to check and alert if logs have not been produced in six hours; and 3) developed and deployed a status report to track last received logs per cyber asset and support detection of systems not logging for long durations. Additionally, developed a process for security operations center analysts to use report and follow up on systems indicated as not logging. To mitigate this violation, NPCC_URE1 will: 1) begin combined process development using the status report dashboard and Security Operations Center analyst effort and software checks along with System Administration response; and 2) finish development and show evidence of activity of process using both agent results and Security Operations Center analyst and System Administrator efforts. | 11/23/2016 (approved completion date) | TBD | Admits | NPCC reviewed NPCC_URE1 internal compliance program and considered it to be a neutral factor in the penalty determination. NPCC_URE1 received mitigating credit for self-reporting this noncompliance. NPCC did consider NPCC_URE1's admitting to the violation as a mitigating factor in the penalty determination. NPCC considered NPCC_URE1's CIP-007 R6 compliance history in determining the Penalty. NPCC considered NPCC_URE1's CIP-007 R6 compliance history to be an aggravating factor in the penalty determination.
2016-08-31 | FERC | NP16-25-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012566 | Notice of Confirmed Violation | MRO determined that MRO_URE1 was in violation of CIP-002-1 R1. Specifically, MRO_URE1 failed to document a risk-based assessment methodology (RBAM) for its control center and back up control center (R1.2.1); its systems and facilities critical to system restoration (R1.2.4); and its Special Protection Systems (SPS) that support the reliable operation of the Bulk Electric System (BES) (R1.2.6). The cause of this violation was the entity's failure to understand the level of detail that must be in an RBAM to meet the requirements of the Standard. | CIP-002-1 | R1 | Medium | Lower | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 substantially complied with the requirement and could have complied through wording adjustments to each of the asset categories. The control room Cyber Assets were identified as Critical Cyber Assets (CCAs), as well as its Supervisory Control and Data Acquisition (SCADA) system and the SPS. MRO_URE1 did not declare any restoration facilities as critical, but those types of assets are Low Impact in CIP V5’s Impact Rating Criteria. Furthermore, CIP-002-5.1 (CIPv5) no longer requires methodology statements, and instead only requires a process document for BES asset consideration. No additional CCAs were identified when the issue was mitigated. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 updated its RBAM | No penalty (for MRO2013012566, MRO2013012568, MRO2013012572, MRO2013012574, and MRO2013012575) | Compliance Audit | To mitigate the issue, MRO_URE1 updated its RBAM documentation to include more information regarding its methodology and risk assessments. | 2014-01-23 | 2014-01-23 | Accepts | MRO_URE1 has no relevant history of noncompliance with CIP-002-1 R1.
2016-08-31 | FERC | NP16-25-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012568 | Notice of Confirmed Violation | MRO determined that MRO_URE1was in violation of CIP-005-1 R4. Specifically, MRO_URE1 did not completely document the vulnerability assessment process that was used on the access points to the Electronic Security Perimeter (ESP). MRO_URE1's documentation did not include a description of the key steps and activities that MRO_URE1 performed during its cyber vulnerability assessment (CVA). Documentation did not include discovery of all access points to the ESP nor any reviews performed of controls for default accounts, passwords, and network management community strings. MRO_URE1 provided evidence of work being done; however, there was no clear connection between what MRO_URE1's documented CVA process stated and what work was actually performed for the CVA. The cause of this violation was the entity's failure to understand and document the level of detail required by the Standard in its CVA process document. | CIP-005-1 | R4 | Medium | Lower | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential risk was minimal, as the finding was related to the failure to properly document required CVA procedures and it was not related to the failure to properly perform the required CVA activities. During a subsequent Compliance Audit, MRO determined that MRO_URE1 was performing the required procedures to complete all activities in the Standard, but had failed to properly document these procedures. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 provided the updated document that contained documented procedures for its CVA | No penalty (for MRO2013012566, MRO2013012568, MRO2013012572, MRO2013012574, and MRO2013012575) | Compliance Audit | To mitigate the issue, MRO_URE1 updated its ESP and SCADA CVA process. | 2014-01-23 | 2014-01-23 | Accepts | MRO_URE1 has no relevant history of noncompliance with CIP-005-1 R4.
2016-08-31 | FERC | NP16-25-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012572 | Notice of Confirmed Violation | MRO determined that MRO_URE1was in violation of CIP-006-1 R3. Specifically, MRO_URE1 failed to provide technical controls for monitoring a Physical Security Perimeter (PSP) access point. The Operations Office had an access point issue with its PSP because it had an exterior door that was locked with a conventional lockset, but was not equipped with any type of alarm sensors to alert system operations personnel of an open door. The cause of this violation, was MRO_URE1's failure to recognize that this unique exterior door was an access point that required an alarm when it implemented its PSP after the Standard became mandatory upon MRO_URE1. | CIP-006-1 | R3 | Medium | Severe | The issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because the door was secured with a dead bolt lock and the outside of the door did not have a handle or a keyhole that an adversary could use to open the door. The risk was not minimal due to the long duration of the violation and because the entry point provided access to the telecommunication and computer rooms, which could have potentially caused disruption to the system if they had been exploited by an adversary. | when the Standard became mandatory and enforceable on MRO_URE1 | when door position sensors were installed and connected to MRO_URE1's Security Management System | No penalty (for MRO2013012566, MRO2013012568, MRO2013012572, MRO2013012574, and MRO2013012575) | Compliance Audit | To mitigate the issue, MRO_URE1 installed door position sensors and connected them to MRO_URE1's Security Management System | 2013-06-06 | 2014-01-23 | Accepts | MRO_URE1 has no relevant history of noncompliance with CIP-006-1 R3.
2016-08-31 | FERC | NP16-25-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012574 | Notice of Confirmed Violation | MRO determined that MRO_URE1 was in violation of CIP-007-3-a R7. Specifically, MRO_URE1 redeployed a server without having its data storage media erased. The cause of this violation is that MRO_URE1 failed to adhere to its procedure that required the deletion of data storage media prior to redeployment and MRO_URE1 did not have any controls to review that its procedures were followed. | CIP-007-3a | R7 | Lower | Severe | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 did not fully erase the data storage media, but it deleted significant amounts of the data storage media prior to, or on the day of redeployment. Specifically, prior to redeployment, MRO_URE1 removed the original IP address and network configuration. On the day the device was redeployed, the old user profiles were deleted and the Admin and Guest accounts were renamed. These actions deleted all the Supervisory Control and Data Acquisition (SCADA) domain sensitive information from the device. Additional factors further reduced the risk. The device was not accessible, as no non-administrative users were given logical access to the device, and no users had remote login privileges. Finally, physical access to the device was controlled because the server remained within a Physical Security Perimeter at all times. | when MRO_URE1 redeployed the device without erasing the data storage media first | when MRO_URE1 erased the media on the device | No penalty (for MRO2013012566, MRO2013012568, MRO2013012572, MRO2013012574, and MRO2013012575) | Compliance Audit | To mitigate the issue, MRO_URE1: 1) completely erased the media on the device; and 2) implemented a media erasure tool that completely erases media. | 2014-08-22 | 2016-01-29 | Accepts | MRO_URE1 has no relevant history of noncompliance with CIP-007-3a R7.
2016-08-31 | FERC | NP16-25-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012575 | Notice of Confirmed Violation | MRO determined that MRO_URE1 was in violation of CIP-007-1 R8. Specifically, MRO_URE1 did not completely document the vulnerability assessment process that was used on Cyber Assets within the Electronic Security Perimeter (ESP). MRO_URE1's documentation did not include a description of the key steps and activities that MRO_URE1 performed during its cyber vulnerability assessment (CVA), including any reviews performed on controls for default accounts. MRO_URE1 was able to document that it performed all the required steps but was unable to connect its CVA process document to the activities actually performed in conducting the CVA. The cause of this violation was the entity's failure to understand and document the level of detail required by the Standard in its CVA process document. | CIP-007-1 | R8 | Lower | Severe | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential risk was minimal, as the finding was related to the failure to properly document required CVA procedures and it was not related to the failure to properly perform the required activities. During a subsequent Compliance Audit, MRO determined that MRO_URE1 was performing the required procedures to complete all activities that are required by the Standard, but had failed to properly document these procedures. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 updated its ESP and Supervisory Control and Data Acquisition (SCADA) CVA Process | No penalty (for MRO2013012566, MRO2013012568, MRO2013012572, MRO2013012574, and MRO2013012575) | Compliance Audit | To mitigate the issue, MRO_URE1 updated its ESP and SCADA CVA Process. | 2014-01-23 | 2014-01-23 | Accepts | MRO_URE1 has no relevant history of noncompliance with CIP-007-1 R8.
2016-08-31 | FERC | NP16-25-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013472 | Settlement Agreement | WECC performed a Compliance Audit of an affiliate of WECC_URE1. During the Compliance Audit, WECC determined the affiliate of WECC_URE1 had three issues with CIP-006-1. WECC and the affiliate of WECC_URE1 executed a Settlement Agreement to settle the prior violations. WECC_URE1 submitted a Self-Certification stating that it had three issues with CIP-006-1. These three issues are identical to the issues identified by WECC during an affiliate of WECC_URE1's Compliance Audit of CIP-006-1. Regarding the first issue, WECC_URE1 failed to identify seven Physical Access Control System (PACS) workstations that provision physical access to WECC_URE1's Physical Security Perimeters (PSPs). WECC_URE1 also did not provide these workstations with the protective measures specified in CIP-006-1 R1.8. Seven WECC_URE1 employees had access to the workstations. Regarding WECC_URE1's second issue with CIP-006-1 R1.8, WECC_URE1 failed to implement strong technical controls for external access into the PACS network as required by CIP-005-1 R2. Regarding the third issue, WECC_URE1 failed to file Technical Feasibility Exceptions (TFEs) for six door controllers that do not support monitoring for system events related to cyber security as required by CIP-007-1 R6. WECC_URE1 later reported that it was in violation of CIP-006-3 R1.7. During the first half of the year, WECC_URE1 tested a new PSP. WECC_URE1 installed CCAs into the PSP making the PSP operational. The PSP contains nine CCAs. Seven of the CCAs are workstations that maintain the Energy Management System (EMS). The remaining two CCAs are switches between the workstations and the EMS. WECC_URE1 did not update the physical security plan within ninety calendar days of a physical security system redesign or reconfiguration after the PSP became operational. WECC_URE1 updated the physical security plan approximately six months later. The root cause was related to a lack of communication between WECC_URE1 and its supporting organizations regarding the violations that WECC identified in its audit of the affiliate of WECC_URE1. The root cause for the second issue was related to lack of procedural document for updating the PSP plan. | CIP-006-1 | R1; R1.7; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to provide all the CIP protections to seven PACS workstations as required by CIP-006-1 R1.8 and failed to implement strong technical controls for external interactive access into the PACS networks. Additionally, WECC_URE1 did not update its physical security plan within ninety calendar days after operational CCAs were put into a PSP as required by CIP-006-3 R1.7. Because of these failures, a malicious individual could have potentially gained logical or physical access to the PACS workstations and PACS server that provision access to all of WECC_URE1's PSPs. Although WECC_URE1 failed to provide all the CIP-006 R1 protections, WECC_URE1 implemented restricted physical access to the PACS workstations through the use of individual and device authentication, antivirus, and application white listing. WECC_URE1 also logically protected the workstations by implementing multiple network perimeter control and monitoring devices including firewalls, intrusion detection systems, and remote access using two-factor authentication. WECC_URE1's PACS is monitored twenty-four hours a day, seven days a week by WECC_URE1's security personnel. WECC_URE1 reviews access rights quarterly. WECC_URE1 uses an automated tool to monitor the PACS system events on the server. Field controller access is also controlled through the PACS application by the PACS server. | when WECC_URE1 was required to comply with this Standard | Mitigation Plan completion | 0 | Self-Certification | To mitigate this violation, WECC_URE1: 1) retired its existing PACS; 2) replaced the retired PACS with a new PACS; 3) located the new PACS in a separate network that will not provide for external, interactive access; 4) submitted the required TFEs; 5) generated a NERC floor plan showing the location of the new PSP; 6) documented the physical security plan and other corporate documentation with the new PACS workstations; 7) completed a PSP implementation checklist and a procedure detailing the necessary steps and actions that should be taken prior to the deployment and certification of a new NERC PSP; and 8) distributed the PSP implementation checklist and procedure, via email, to all WECC_URE1 department compliance managers and supporting organizations to ensure a broad understanding of the documented requirements. | 2015-11-20 | 2016-06-29 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2016-08-31 | FERC | NP16-25-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC200901720 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-1 R2. In its Self-Certification, WECC_URE2 reported that it was “Substantially Compliant” with this Standard. WECC_URE2 failed to assign and document a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. A WECC subject matter expert (SME) interviewed WECC_URE2 to investigate the reported violation. During the SME interview, WECC_URE2 confirmed it was not compliant with CIP-003-1 R2. WECC determined that WECC_URE2 had a violation of the Standard because it failed to assign and document a senior manager with overall responsibility for leading and managing WECC_URE2's implementation of, and adherence to, Standards CIP-002 through CIP-009, as required by CIP-003-1 R2. WECC determined that WECC_URE2 had a violation of this Standard because it failed to assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. The root cause for the violation was because WECC_URE2's senior management designation was due to organizational chain of command structure differences between WECC_URE2 and its parent company. WECC_URE2 and its parent company have host/tenant ownership of the structure of all Cyber Information Technology assets and the parent company's chief information officer is the designated authority on all cyber assets. However, the parent company has no direct authority and control of cyber assets. | CIP-003-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2 violated this Standard by failing to assign or document a senior manager with overall CIP responsibility by the effective date of the Standard. The Implementation Plan requires that an entity assign a senior manager in advance of its required compliance with Standards CIP-002 through CIP-009, in order to ensure the timely preparation and implementation of CIP Standards. Without a designated senior manager, it is less likely that an entity will be prepared for compliance with CIP Standards, therefore presenting an increased risk to the reliability of the BPS. WECC_URE2's delay in identifying a senior manager could mean that it has less than half the time to prepare itself, under the direction of a senior manager, for compliance with Standards CIP-002 through CIP-009. To mitigate the risk, WECC_URE2's cyber assets, used for power generation within the region, are protected by strict standards currently in place. Further, according to the Self-Certification worksheet submitted by WECC_URE2, it stated it was “Substantially Compliant” with the Standard. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, WECC_URE2: 1) designated a senior manager with overall responsibility for leading and managing WECC_URE2's implementation of, and adherence to, Standard CIP-002 through CIP-009; and 2) created a system-wide approach to evaluate and combine cyber information technology requirements with Cyber CIP standards. | 2009-07-22 | 2009-10-29 | Agrees/Stipulates | WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014643 | Settlement Agreement | SERC determined that SERC_URE1 was in violation of CIP-007-3a R3. SERC_URE1 failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). As part of the Mitigation Plan for a prior CIP-007 R3 violation, SERC_URE1 committed to create a comprehensive list of all third-party software applications running on the Cyber Assets within the ESP. During an internal review of its compliance program, SERC_URE1 discovered that it failed to assess security patches for a third-party software application that were released during an approximately one year period. The security patches at issue were applicable to energy management system (EMS) workstations and affected Cyber Assets, including Critical Cyber Assets (CCAs). The root cause of the first issue was that SERC_URE1 failed to document that it had installed this third-party software application on the affected Cyber Assets. While investigating the first issue, SERC_URE1 identified a second issue in which it found it failed to assess security patches for a second third-party software application. Although SERC_URE1 added this third-party software application to its inventory of software applications running on Cyber Assets within the ESP as part of its Mitigation Plan for the prior CIP-007 R3 violation, it failed to effectively document the SERC_URE1 personnel responsible for tracking and conducting security patch reviews. This procedural deficiency and a complete personnel turnover within the information and technology security team caused SERC_URE1 to not assess any of the available software security patches for servers or workstations during a 27 month period. SERC_URE1 subsequently found that four patches were applicable. This issue affected CCAs, Cyber Assets, Electronic Access Control or Monitoring Systems (EACM) servers, and Physical Access Control System (PACS) workstations. The root cause of the second issue was that SERC_URE1 did not clearly document the roles and responsibilities of personnel responsible for assessing security patches. SERC_URE1 identified a third issue several months later. After SERC_URE1 completed its Mitigation Plan for a previous violation regarding the classification of the intrusion prevention system (IPS), it established a source of security patches for all software. SERC_URE1 shifted security patch review responsibilities from one employee to another. The new employee responsible discovered that the patch source identified previously was for the IPS only, and did not include the security patches for the IPS sensors or network active bypass (NAB) units. SERC_URE1 assessed the IPS sensors and NAB security patches and determined that it missed firmware security updates. SERC_URE1 determined that security updates were applicable to IPS sensors and security updates were applicable to NAB units. The root cause of the third issue was that the designated software source website utilized by SERC_URE1 to check for firmware and security patches only published firmware updates for the IPS and did not include firmware and security patches for the IPS sensors or NAB units. SERC determined that SERC_URE1 was in violation of CIP-007-3a R3 because it failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESPs. | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to assess security patches within 30 days of availability could allow malicious individuals to exploit known vulnerabilities for an extended period. However, the affected Cyber Assets were within established ESPs and Physical Security Perimeters (PSPs). Monitoring of Cyber Assets within the ESP and PSP would have alerted SERC_URE1 personnel to any unauthorized activity. SERC_URE1 did not receive any alerts from the affected Cyber Assets as a result of this violation. Further, SERC_URE1 had layers of perimeter security, such as network segmentation and isolation of security zones, multiple levels of firewalls, intrusion detection systems, logging and alerting, and multi-level authentication mechanisms to protect these Cyber Assets. | when SERC_URE1 completed its list of third-party software applications but omitted one such third-party software application from its inventory list for assessment of available security patches | when SERC_URE1 assessed the missed security updates for the NABs and IPS sensors for applicability | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: For the first issue: 1) assessed the patches for the third-party software application involved in the first issue; 2) updated and patched to current levels the software on EMS workstations; 3) removed one EMS workstation from the CCA list and retired it prior to the scheduled software upgrade; 4) updated the EMS workstation build procedure document and all other EMS server build procedure documents to include a step to confirm that the build sheet utilized matches SERC_URE1's third-party software list; and 5) circulated an email to affected personnel describing the updated build procedure document. This email circulation was intended to educate affected personnel about the updated step within the procedure to confirm that the build sheets utilized match SERC_URE1's third party software list. For the second issue: 1) assessed the patches for the third-party software client involved in the second issue; 2) formally documented the assignment of ownership for the software patch assessment to the IT security department; 3) upgraded the software in the entire CIP environment and applied all current patch updates; 4) created a procedure for the software assessment and update process; and 5) developed and provided training on the newly created software assessment and update process. For the third issue: 1) assessed the security patches for the IPS sensors and the firmware updates for the NABs involved in the third issue; 2) drafted thorough work instructions for the IPS patch assessment process; 3) subscribed to email alerts regarding security patches from the designated software source; 4) installed all available security patches for the IPS sensors; 5) confirmed with the vendor that there is a known issue that impacts logging on the NABs, and it will not be fixed in the current release version. As a result the NABs will remain on the current code version; and 5) had its employee with primary responsibility train the necessary personnel. For all three issues: 1) configured and updated all CIP documentation organizer (CDO) placeholders and reminders for CIP-007 R3 software assessment. The CDO is an automated tool which is used, among other things, to remind designated personnel monthly of the CIP-007 R3 assessment due dates. | 2015-09-21 | 2015-12-10 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's CIP-007 R3 compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014761 | Settlement Agreement | SERC determined that SERC_URE1 was in violation of CIP-004-3 R4. SERC_URE1 submitted an expansion of scope after finding two additional issues. SERC_URE1 failed to maintain lists of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. It also failed to update the access lists within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights of such personnel. In order to actually gain remote or logical access to SERC_URE1 CCAs or electronic access control and monitoring (EACM) devices, an individual needed both: (1) proper authentication server credentials and (2) proper firewall access permissions. SERC_URE1 self-identified all of the issues described in this violation during quarterly access reviews or other internal meetings. On four separate instances, SERC_URE1 effectively revoked three individual’s respective electronic access rights to CCAs and/or EACMs that no longer needed such access by removing the individuals’ access rights to either the authentication server or removing the necessary firewall access permissions, both of which were necessary to actually gain electronic access to the CCAs or EACMs. Thus, the removal of either (1) the access rights to the authentication server or (2) the necessary firewall access permissions prevented the individuals from electronically accessing the CCAs and EACMs at issue. SERC_URE1 removed the remaining access rights from the individuals in the following months. Pursuant to CAN-0007, while SERC_URE1 did not remove all aspects of electronic access within the seven day timeframe required by its internal procedures, its actions resulted in the inability of the affected individuals to access the CCAs and EACMs at issue. Therefore, SERC determined that these four instances did not constitute a violation of CIP-004 R4. SERC_URE1 updated the list of personnel with authorized access to CCAs and EACMs to include a new user who had been approved for electronic access to an EACM. SERC_URE1 properly established access permission on the authentication server, but failed to properly configure access to the firewall, thereby preventing the individual from electronically accessing the EACM. During a quarterly access list review, SERC_URE1 discovered that the electronic access rights on the access list did not match the actual access rights of the individual and corrected this discrepancy on the same day. SERC_URE1 determined that its delay in discovering this issue was because the access list correctly indicated the access SERC_URE1 should have granted the individual despite SERC_URE1 failure to actually grant the individual such access. SERC_URE1 left an individual on the authorized access list after retiring the Cyber Asset that the individual had been authorized to access. SERC_URE1 replaced the Cyber Asset with a different type of device, and the individual had no need for access to the newly deployed Cyber Asset. During a planning session between two workgroups, SERC_URE1 discovered this issue and resolved it by removing the individual from the access list. SERC_URE1 determined that its delay in discovering this issue was because the personnel conducting the list review failed to recognize that the individual no longer supported the retired Cyber Asset. SERC_URE1 generated a work order to remove access for an individual, but the technician erroneously closed the ticket and SERC_URE1 updated the access list, but did not complete the work in the two systems to remove access. SERC_URE1 did not remove the user from the firewall configuration nor from the authentication server. The authentication fob held by the individual expired, effectively revoking the individual’s access pursuant to CAN-0007 on that day. SERC_URE1 discovered this issue during a quarterly access list review. Several days later, SERC_URE1 removed the individual’s access rights from the firewall configuration, completing the access revocation pursuant to SERC_URE1's procedures. SERC_URE1 generated a work order to remove access for an individual, but the technician erroneously closed the ticket and SERC_URE1 updated the list without completing the work to remove the user from the firewall configuration and the authentication server. During a quarterly access list review, SERC_URE1 discovered that the individual that had authorized external interactive access to a firewall but was not on the authorized access list. SERC_URE1 resolved this issue by properly revoking the individual’s access. An energy management system (EMS) staff member elevated an individual’s permissions from read-only to full control so the individual could update ‘on-call’ displays within the EMS, which required full control permissions, not read-only permissions. However, SERC_URE1 failed to add the individual to the authorized access list. The individual at issue had received training and had an approved Personnel Risk Assessment conducted, but the individual’s original role did not require full control permission. During a quarterly access list review, SERC_URE1 discovered this issue and resolved it by changing the individual’s permission back to read-only. There were two primary causes to the violations. First, SERC_URE1 had inadequate procedures for provisioning and removing access rights that lacked sufficient detail and resulted in SERC_URE1 personnel failing to update access lists and failing to revoke access within required timeframes. Second, SERC_URE1 personnel did not follow established procedures for granting access rights, resulting in an individual obtaining elevated access permissions that were not required for their job. SERC determined that SERC_URE1 was in violation of CIP-004-3 R4 because it failed to maintain its list of personnel with authorized cyber or authorized unescorted physical access to CCAs and EACMs. | CIP-004-3 | R4 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1's failure to maintain updated lists of individuals with authorized cyber access to CCAs and EACM devices could and did allow individuals who were no longer approved for access to maintain access to CCAs and EACM devices. It also allowed an individual to obtain elevated access rights without proper approvals or documentation of the access rights. Such failures could allow malicious individuals to modify or corrupt CCAs, EACM devices, or other Cyber Assets and disrupt SERC_URE1's control of its portion of the BPS. However, all SERC_URE1 personnel involved in the violation were in good standing at the time of and after the violation. The personnel who retained or were granted elevated access rights in error did not use those access rights during the violation. SERC_URE1 only failed to update 0.95% of individuals on the access lists. | eight days after SERC_URE1 retired a Cyber Asset without updating the access list | when SERC_URE1 resolved the last issue by changing the individual’s access permissions back to read-only | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: 1) modified the logical expression in the dynamic access policy to remedy the access discrepancy between the list of personnel with authorized external interactive access into a secure network segment containing an EACM system and actual provisioned external interactive access into the secure network segment on the access point firewall; 2) remedied the access discrepancy between the list of personnel with authorized provisioned external interactive access on access point firewalls into secure network segments containing an EACM system and the source system access. Specifically, SERC_URE1 removed the access for two individuals involved from the source system; 3) remedied the access discrepancy between the list of personnel with authorized provisioned external interactive access on access point firewalls into secure network segments containing EACM systems and the source system access. Specifically, SERC_URE1 removed the access for one individual from the source system; 4) remedied the access discrepancy between the list of personnel with authorized external interactive access on access point firewalls into secure network segments containing an EACM system used for logging and monitoring and the sources system access. Specifically, SERC_URE1 removed the access for the one individual from the source system; 5) remedied the access discrepancy between the list of personnel with authorized access on an EACM system and the source system access. Specifically, SERC_URE1 removed the access for one individual from the source system; 6) remedied the access discrepancy between the list of personnel with authorized access to an EMS server and the source system access. Specifically, SERC_URE1 removed the individual from the EMS server access list; 7) revised the CIP asset configuration checklist, which contains the checklists to be used in the retirement of a CIP Asset and the addition of a new CIP Asset, to provide specific instructions on updating the CIP-004 R4 access lists when there is a retirement or addition of a CIP Asset; 8) circulated an email to affected personnel reminding them that the CIP asset configuration checklist requires that a request form be completed to remove and/or add accounts during the retirement of a CIP Asset or the addition of a new CIP Asset. This email circulation was intended to educate affected personnel about the importance of reviewing locally configured users for unique access accounts and, if appropriate, submit a form requesting removal of access for any uniquely configured local account; 9) circulated an email to affected personnel reminding them that the CIP-004 R4 quarterly access review is intended to confirm that the access lists reviewed match the source system access. This email circulation was intended to educate affected personnel about the importance of ensuring that all individuals that are authorized to have CIP Access and are listed on the access list must have that associated access within the source system; 10) circulated an email to affected personnel reminding them of the proper CIP-004 R4 access requirements procedures. This email circulation was intended to educate affected personnel about, among other things, the proper operational procedures for provisioning and/or removing access as well as the importance of completing the work at the time of closing the request, thus ensuring that the work is completed and the access list is updated concurrently; 11) changed an involved individual’s user permission from control to view only; 12) held meetings with the EMS staff member that did not follow SERC_URE1's established CIP-004 R4 access procedures. The incident was discuss, the procedures were reviewed, and the importance of making sure that all changes made to the EMS have the proper approvals was stressed; 13) held a meeting with all EMS staff where the incident was discussed and the importance of making sure that all changes made to the EMS have the proper approval was stressed; 14) completed a system update that one of the systems involved no longer requires “control” user permissions to update the transmission ops engineering on-call display; 15) discussed the system change during the weekly EMS meeting with all EMS staff. The topic was intended to educate the affected personnel on the change in the system where “control” user permissions are no longer required to update the transmission ops engineering on-call display; and 16) modified the logical expression in the dynamic access policy to remedy the access discrepancy between (a) the list of personnel with authorized external interactive access into an Electronic Security Perimeter (ESP) network segment containing management interfaces for an EACM intrusion detection and/or prevention system sensor and bypass unit and (b) actual provisioned external interactive access into the ESP network segment on the access point firewall. | 2015-09-30 | 2016-03-11 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015099 | Settlement Agreement | SERC determined SERC_URE1 was in violation of CIP-005-3a R1.5. SERC_URE1 failed to provide all electronic access control and monitoring (EACM) Cyber Assets the protective measures specified in CIP-007-3a R3 by failing to assess security patches within 30 days of their availability. After SERC_URE1 submitted the Self-Report, SERC sent SERC_URE1 an audit detail letter notifying it of a Compliance Audit. SERC_URE1 submitted an expansion of scope stating that it failed to provide EACM firewalls the protective measures specified in CIP-007-3a R5.3.3 by failing to change the shared account password on those devices. A SERC_URE1 employee with responsibility for security patch assessment passed away unexpectedly. SERC_URE1 reassigned the employee’s tasks to other individuals but failed to follow its established process for assessing patches. SERC_URE1 discovered available patches that it failed to assess within 30 calendar days of availability. On the same day, SERC_URE1 assessed all the patches and only found a single patch to be applicable to two access control servers. SERC_URE1 discovered this failure to assess security patches while implementing an internal control as part of the mitigation of a patching failure involving Critical Cyber Assets (CCAs) (SERC2015014643). The root cause of this violation was SERC_URE1 failed to promptly reassign responsibility for security patch assessment. While reviewing evidence regarding the security patching issue above, SERC_URE1 discovered that it failed to change the shared account password for firewalls. SERC_URE1 conducted an extent-of-condition review and found no other similar issues existed. The root cause of this violation was SERC_URE1 failed to provide procedures to the team with responsibility over the firewalls regarding the changing of passwords. SERC determined that SERC_URE1 was in violation of CIP-005-3a R1.5 because SERC_URE1 failed to properly assess available EACM security patches for applicability within 30 calendar days as required by CIP-007-3a R3.1 and it failed to change a shared account password for EACM firewalls as required by CIP-007-3a R5.3.3. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to assess security patches for multiple EACM Cyber Assets could allow vulnerabilities on EACM systems to remain available for exploitation by an adversary using known weaknesses. SERC_URE1's failure to change passwords on default accounts for over one year enhanced the threat from patching issues by providing a potential access point into the energy management system (EMS) and the unpatched EACM systems. However, SERC_URE1 only failed to assess security patches for four months. Although SERC_URE1 found one patch that applied to two EACM servers, it found that the remaining unassessed patches released for the EACM firewalls, routers, and switches (the access points) did not apply to the SERC_URE1 environment, limiting the impact of the failure to assess patches. SERC_URE1 utilized layered defense-in-depth, including in part, perimeter security, such as network segmentation and isolation of security zones, and multiple levels of screening firewalls. SERC_URE1 also deployed intrusion detection and prevention systems with logging and alerting and had strong remote access and multi-level authentication mechanisms in place to protect all Cyber Assets beyond the controls specified under CIP-007. Further, SERC_URE1 monitored for any security events on its networks 24 hours a day, seven days a week. SERC_URE1 implemented data leakage protection and alerting technology to protect against the exfiltration of sensitive information from any of its networks. All involved Cyber Assets resided within a secured Physical Security Perimeter. | one day after the last day SERC_URE1 could have changed the shared account password annually | when SERC_URE1 changed the shared account password on the EACM firewalls | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: 1) assessed the security patches for the third-party software applications, CIP firewalls, and routers and switches; 2) as part of the continuous improvement process, updated the network team’s patch assessment work instructions; 3) upgraded to new appliances running the newest software; 4) verified and re-assessed the security patches missed; 5) restructured the IT network infrastructure team and created sub-teams within the team for each system. Each system has two primary owners and both primary owners are responsible for, among other things, ensuring the assessment of security patches is completed monthly and agreeing on the applicably of each patch. The owners are also responsible for changing the shared/non-shared account passwords annually or more frequently based on risk. Additionally, the network infrastructure CIP coordinator will ensure the accuracy and integrity of the evidence uploaded to the CIP documentation organizer; 6) held a meeting with the new patch assessment team members. The individuals are senior members of the network infrastructure staff and will round out the technical knowledge of the current patch assessment team members. The team discussed the following items: (a) regular monthly meetings have been scheduled with the patch assessment team members to review patches that have been released for the month and assess applicability; (b) understanding the monthly meeting requirements; (c) understanding the patch application requirements; (d) reviewed the draft patch assessment process; and (e) reviewed current month patches; 7) changed the shared account password for all CIP firewalls; 8) created a draft for the password change work instructions for each asset class. This process includes instructions on the gathering, reviewing, confirmation and uploading of accurate evidence; 9) distributed a document to the network team that provided a list of the team’s CIP systems and their respective system owners. This document also contains a list of the CIP responsibilities of the team which includes password changes and ensuring patch assessments are accurate; and 10) added the network infrastructure CIP coordinator to the late evidence CIP documentation organizer (CDO) notifications and wrote rules into Outlook to copy network infrastructure management on these notifications to ensure task completion and oversight of job responsibilities. The CDO is an automated tool which is used, among other things, to remind designated personnel of CIP evidence deadlines. | 1/19/2016 | 2016-04-06 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015254 | Settlement Agreement | SERC determined SERC_URE1 was in violation of CIP-007-3a R1. SERC_URE1 failed to test significant changes for adverse cyber security impacts prior to implementing new software and software upgrades into the production environment. An energy management system (EMS) vendor started a major EMS upgrade effort for SERC_URE1. The EMS vendor completed testing the planned upgrade and all software, and approved the EMS upgrade as being ready for deployment. In preparation for deployment to production, the vendor initiated onsite functional testing in the SERC_URE1 test environment. The EMS upgrade included an updated database software client. The vendor encountered a persistent functional issue that it resolved in the test environment by replacing the tested and approved version of the database client with the most recent version. The vendor did not disclose this change from the approved version to SERC_URE1 and the vendor pushed out the untested version of the software client to EMS workstations classified as Critical Cyber Assets (CCAs). SERC_URE1 initiated a work order ticket to install additional software clients and discovered this violation while completing a testing checklist required by an SERC_URE1 internal control to reaffirm testing quality and results. At this time, SERC_URE1 also tested and confirmed that the upgraded version of the database client did not degrade or compromise any existing cyber security controls. As a result, SERC_URE1 had an untested significant change on these CCAs for six days. To determine the cause of the persistent functional issue described above, the vendor also installed a software update in the SERC_URE1 test environment that the vendor thought could help reconcile the problem or identify the cause. The vendor did not make SERC_URE1 personnel aware of this untested change from the approved tested version of the EMS upgrade. This software did not resolve the persistent functional issue and was not necessary for SERC_URE1 to operate the upgraded EMS. However, upon completion of the EMS testing in the non-production test environment, the vendor failed to remove this untested software upgrade. The vendor applied the software upgrade to a segment of the test environment specific to the image used for any new workstation that would be deployed in the future. However, the software upgrade did not affect existing EMS workstation images because the vendor did not push the software upgrade into the production environment. However, SERC_URE1 built new EMS workstations and deployed them into production with the untested software upgrade. SERC_URE1 personnel discovered this issue while conducting a quality review of its testing checklist results. SERC_URE1 found that the software version on the five newly deployed workstations differed from the documented software on the testing checklist. SERC_URE1 immediately engaged the EMS vendor on the cause of this issue and any potential impacts that the removal of the updated software may have on the production environment. After the vendor reviewed and confirmed that no adverse impacts would occur from removing the software, SERC_URE1 removed the updated software. SERC_URE1 failed to test this software update on the EMS workstations classified as CCAs for a total of 164 days. The root cause of this violation was the EMS vendor failing to inform SERC_URE1 personnel that it upgraded existing software and installed additional software. SERC determined that SERC_URE1 was in violation of CIP-007-3a R1 because SERC_URE1 failed to test significant changes to its EMS for adverse cyber security impacts prior to implementing new software and software upgrades into the production environment. | CIP-007-3a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1's failure to test significant changes to CCAs could permit existing cyber security controls to be eliminated or compromised, potentially degrading the EMS and creating impacts to the BPS. However, for the first instance involving the workstations, SERC_URE1 tested the changes within six days and confirmed that they had no adverse impact on the existing cyber security controls. While the second instance went untested for 164 days, the violation affected only a handful of workstations and the untested change was removed after ensuring that removal would not adversely impact existing cyber security controls. SERC_URE1 utilized layered defense-in-depth, including, in part, perimeter security, such as network segmentation and isolation of security zones, and multiple levels of firewalls for screening. SERC_URE1 had intrusion detection and prevention systems with logging and alerting, and strong remote access and multi-level authentication mechanisms in place to protect all Cyber Assets beyond the controls specified under CIP-007. SERC_URE1 monitored for any security events on its networks 24 hours a day, seven days a week. SERC_URE1 implemented data-leakage protection and alerting technology to protect against the exfiltration of sensitive information from any of its networks. SERC_URE1 had fully patched the new EMS system and all Cyber Assets involved resided within an established Physical Security Perimeter. | when the SERC_URE1 vendor upgraded EMS workstations with untested database software | when SERC_URE1 removed the untested software from the EMS workstations | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: 1) completed CIP-007 R1 testing on the software client at issue. The testing identified no security control variations from the baseline, showing that no changes to production had been made as a result of the new client install; 2) after confirmation from the vendor, removed the untested software update from the workstations; 3) built a new workstation in the test environment for the sole purpose of maintaining a more controlled “golden image” to be used for deploying production workstations. Use of this workstation is restricted to personnel that maintain the workstation configuration; 4) revised the CIP asset configuration minor change checklist guidance to include software installations and upgrades; 5) updated the EMS testing work instructions to include a statement that CIP-007 R1 testing should be done after all functional testing is complete; 6) circulated an email to affected personnel describing the updated EMS testing work instructions. This email circulation was intended to educate affected personnel about the updated statement within the procedures to ensure that CIP-007 R1 testing be completed after all functional testing is complete; and 7) held a meeting with all EMS staff where the updated EMS testing work instructions were discussed. | 2015-09-25 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC determined that SERC_URE1's CIP-007 R1 compliance history should not serve as a basis for aggravating the penalty.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015400 | Settlement Agreement | SERC determined SERC_URE1 was in violation of CIP-007-3a R5.3.3. SERC_URE1 failed to change passwords on Critical Cyber Assets (CCAs), both shared and non-shared accounts. Specifically, SERC_URE1 did not change the passwords of routers and switches. SERC_URE1 performed an extent-of-condition assessment and determined that it properly changed passwords annually on all other Cyber Assets. SERC_URE1 utilized a single password management procedure for all CIP password requirements. This procedure applied to the CCAs involved in this violation, however the procedure lacked specific detailed steps on how to properly complete and validate password changes for these specific CCAs. In the past, SERC_URE1 assigned one individual the responsibility to implement and document the required password changes. However, this time, SERC_URE1 did not assign an individual with this responsibility. Additionally, SERC_URE1 had not documented detailed steps on how to complete and validate the password changes on the devices. SERC_URE1 discovered this violation while conducting an evidence review involving a previous Self-Report. The root cause of this violation was a lack of detailed work instructions in the account management procedure. SERC determined that SERC_URE1 was in violation of CIP-007-3a R5.3.3 because SERC_URE1 failed to change shared and non-shared account passwords on CCAs. | CIP-007-3a | R5; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to properly change the passwords on CCAs annually could allow the affected CCAs to become vulnerable to a cyber attack. However, to prevent potential cyber attacks on its CCAs, SERC_URE1 had the following internal controls: perimeter security, such as network segmentation and isolation of security zones, and multiple levels of screening firewalls; intrusion detection and prevention systems with logging and alerting; and strong remote access and multi-level authentication mechanisms in place to protect all Cyber Assets beyond the controls specified under CIP-007. Further, SERC_URE1 monitored for any security events on its networks 24 hours a day, seven days a week. Additionally, SERC_URE1 implemented data leakage protection and alerting technology to protect against the exfiltration of sensitive information from any of its networks. All involved CCAs resided within a secured Electronic Security Perimeter and a Physical Security Perimeter with monitoring enabled. | when SERC_URE1 failed to change its passwords | when SERC_URE1 changed the passwords | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: 1) restructured the IT network infrastructure team and created sub-teams within the team for each system. Each system has two primary owners and both primary owners are responsible for, among other things, changing the shared/non-shared account passwords annually or more frequently based on risk; 2) changed the “enable” shared account password for the energy management system (EMS) routers; 3) removed the local (non-shared) account in question from the EMS routers; 4) removed the local (non-shared) account in question from an involved switch; 5) changed the “enable” shared account password for the EMS switches; 6) distributed a document to the network team that provided a list of the team’s CIP systems and their respective network team system owners. This document also contained a list of the CIP responsibilities of the team which includes password changes. 7) added the IT network infrastructure CIP coordinator to the late evidence CIP documentation organizer (CDO) notifications and wrote rules into Outlook to copy network infrastructure management on these notifications to ensure task completion and oversight of job responsibilities. The CDO is an automated tool which is used, among other things, to remind designated personnel of CIP evidence deadlines; 8) network team finalized the password change work instructions for each asset class; and 9) network team conducted training on the updated password change work instructions. | 2016-01-19 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's CIP-007-1 R5 compliance history to be an aggravating factor in the penalty determination. SERC determined that SERC_URE1's CIP-005 R1.5 and CIP-006-1 R1.8 compliance history should not serve as a basis for aggravating the penalty.
2016-06-29 | FERC | NP16-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015015405 | Settlement Agreement | SERC determined SERC_URE1 was in violation of CIP-005-3a R2. Specifically, SERC_URE1 failed to implement organizational processes and technical and procedural mechanisms for control of electronic access at one access point to the Electronic Security Perimeter (ESP). SERC_URE1 implemented a CIP-005 R2 procedure. In the procedure, SERC_URE1 specified how to establish, maintain, manage, and validate the ESP security controls. The procedure also specified the necessity of the deny all access rules for all access points and required review and approval of a change ticket for any changes to any approved and existing access rules. SERC_URE1 had a vendor onsite to resolve some final issues with implementing a configuration management system for its CIP Cyber Assets under CIP Version 5. During on-site maintenance, a SERC_URE1 vendor could not resolve communications issues with the intrusion prevention system (IPS) at certain locations. SERC_URE1 initiated and approved a change order to open the required ports and services on two firewalls necessary to permit the new configuration management system to communicate with EMS workstations, which were Cyber Assets within the ESP. The primary SERC_URE1 technician that typically handled these types of requests was unavailable, but due to the urgency of the request, a less-experienced team member completed the work order. While processing the change, the individual did not verify proper configuration and placement of a required deny-all rule. SERC_URE1 implemented the change and omitted the deny rule, which permitted any subnet traffic through and provided a login prompt to that traffic. SERC_URE1 discovered this violation when it received an alert from an automated scan for vulnerabilities of the network IPS sensors. SERC_URE1 implemented the proper deny-all rule, and the duration of the noncompliance lasted approximately 32 hours. The root cause of this violation was SERC_URE1's over-dependence on a single individual to conduct firewall rule changes and a lack of support in the event the primary individual was unavailable. SERC determined that SERC_URE1 was in violation of CIP-005-3a R2 because SERC_URE1 failed to implement organizational processes and technical and procedural mechanisms for control of electronic access at one access point to the ESP. | CIP-005-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to properly implement a firewall rule with deny-all criteria could allow unauthorized corporate network traffic to access the opened port and gain access to Cyber Assets within the ESP. However, access would have been limited to only Intrusion Detection System/IPS sensors and would require possession of valid credentials and knowledge of how to gain access to those devices. SERC_URE1 discovered the violation through detective internal controls and corrected the violation within 32 hours. Additionally, SERC_URE1 utilized layered defense-in-depth, including in part, perimeter security, including network segmentation and isolation of security zones, and multiple levels of screening firewalls. SERC_URE1 deployed intrusion detection and prevention systems with logging and alerting and had strong remote access and multi-level authentication mechanisms in place to protect all Cyber Assets beyond the controls specified under CIP-007. Further, SERC_URE1 monitored for any security events on its networks 24 hours a day, seven days a week and implemented data leakage protection and alerting technology to protect against the exfiltration of sensitive information from any of its networks. All involved Cyber Assets resided within a secured ESP and a Physical Security Perimeter with monitoring enabled. | when SERC_URE1 modified access into the ESP and failed to properly implement the appropriate restrictive firewall access rule | when SERC_URE1 corrected the firewall rules to include the required restrictions | $65,000 (for SERC2015014643, SERC2015014761, SERC2015015099, SERC2015015254, SERC2015015400, and SERC2015015405) | Self-Report | To mitigate this violation, SERC_URE1: 1) configured the backend rule and added the "do not authenticate" rule in the access control, authentication, and accounting rule 2) restructured the IT network infrastructure team and created sub-teams within the team for each system. Each system has two subject matter experts or primary owners thus ensuring multiple primary owners are available to complete requests of this nature; 3) distributed a document to the network team that provided a list of the team’s CIP systems and their respective network team system owners. This document also contained a list of the CIP responsibilities of the team; and 4) held a technical session to review access control, authentication, and accounting rules and dynamic access policy configurations with the IT network infrastructure team. | 2016-01-19 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's CIP-005 R2 compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-20-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015369 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. Security patches were inadvertently installed on Physical Access Controls Systems (PACS) devices, consisting of servers and workstations, without following the CIP-007-3 R3 patching procedures, as required in CIP-006-3 R2.2. A FRCC_URE1 Senior Systems Programmer was implementing a change order to install patches on the non-CIP test server. The patching tool required the programmer to select the devices that would receive the patches. However, the programmer inadvertently included the CIP PACS devices along with the selection of the non-CIP test server. The patches themselves did not create issues, the issue was that they were not procedurally applied per CIP-007-3 R3. The programmer immediately realized the mistake, but was unable to stop the patches from being deployed since the patching tool had no cancelation feature. The programmer attempted to log in directly to the PACS devices to cancel the patches, but they had already been applied. The programmer tested the functionality to ensure that the patches had not caused to function improperly. Two weeks after the inadvertent patch installation, the programmer opened a scheduled change order to re-apply the same patches to the PACS devices, to ensure that all of patches were properly applied (procedurally) and that necessary CIP-007-3 R3 pre- and post-scans were performed. The patches were successfully reapplied. The patching procedure verified that all applicable patches had been applied to the devices and completed the remaining steps of the patching process. FRCC_URE1 performed a root cause analysis and determined that the primary root cause was the programmer's screen had a visibility issue that made it difficult to see the devices being selected in the patch management tool. Additionally, the procedure should have included a validation step requiring verification that the patches were matched with the correct device, prior to applying and the patching tool should not be able to patch both test and production environments simultaneously. The patch groups should have been separated within the patching tool. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS).The inadvertent patching process mistake could have potentially compromised the functionality of the PACS system or the PACS server could have become unresponsive. However, if the PACS system or server were to have been rendered unresponsive, the controls at the doors (allowing/disallowing access) would still function, and logs would still be produced. Once the devices became responsive again, the logs and alerts would be sent to the central PACS server. During the time the devices are unresponsive, the guards would not receive alarms concerning the door status for a Propped Door or Forced Door event. However, the guards would know that the application was not responsive, and would activate the established compensating procedures for such a situation. Additionally, the patches in question had been applied to other devices on the corporate network without issue before they were applied on the PACS devices. No harm is known to have occurred. | when the programmer inadvertently installed patches | when the programmer ensured that all of the applicable patches had been applied to the devices and completed the remaining steps of the patching process | $35,000 (for FRCC2015015366, FRCC2015015368, and FRCC2015015369) | Self-Report | To mitigate this issue, FRCC_URE1: 1) ensured that all of the applicable patches had been applied to the devices and completed the remaining steps of the patching process on; 2) the CIP Senior Manager sent out communications (to vice president of information technology & chief information officer) on situational awareness related to NERC compliance; 3) changed the patching tool to separate the specific production and test PACS environments into individual scan results. This will prevent inadvertent device selection for the PACS environment in the future; 4) changed the patching tool to separate all other NERC production and test environments into individual scan results. This will prevent inadvertent device selection for all other NERC environments; 5) separated NERC and non-NERC virtual patching consoles. This will prevent corporate (non-NERC) patching from inadvertently being applied to NERC devices; 6) changed resolution settings/replace monitor as necessary for all patching programmers; 7) revised the Security Patch Management Program and associated desk level procedures (DLPs) to include greater awareness of the impacts of the processes to NERC compliance, add a validation step for applying the patches, and delineate the necessary steps to follow in the event of a process failure, including a strict timeline for resolution of the issue; and 8) performed refresher training to applicable SMEs, patching implementers, and asset owners on the revised patching process and associated DLPs. | 2015-12-18 | 2016-02-08 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-20-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015368 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.4. FRCC_URE1 failed to afford protections as required by CIP-005-3a R1.4 for non-CCA devices: Integrated Lights Out (iLOs), and Modular Smart Arrays (MSAs) that were connected to an Electronic Security Perimeter (ESP). A network analyst submitted a request to identify and add the servers and the storage arrays (which were to be added to an ESP) to the asset management database. However, the analyst neglected to include the iLO devices associated with the servers to the database. The network analyst submitted an additional request (a change order) to configure a network switch to enable ports to allow communications to the devices in the ESP network. However, again the iLO devices were not included in the request as required in CIP-003-3 R6. The non-CCA devices where connected to the network upon approval of the request. It wasn't until several months later that the correct requests were opened to properly add the iLO devices to the asset management database, and to complete the remaining onboarding tasks that did not take place under the original request to configure the network switch. FRCC_URE1 performed a root cause analysis for this noncompliance and determined that the root causes were inadequate preventative controls that allowed the network analyst to overlook the iLO devices when submitting the necessary change orders and a lack of training and clear procedures. The network analyst did not understand that by connecting the devices to the ESP, CIP protections were required regardless of the fact the operating system had not been installed on the associated servers that the devices support. | CIP-005-3a | R1; R1.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The servers that the iLOs are attached to are still powered off and have no operating system installed on them, and the MSAs have not been utilized for data storage. The devices were not reachable (when communications were established to the iLO devices during the approved change process) due to firewall rules in place, which meant the devices were unable to communicate during the period of noncompliance. No harm is known to have occurred | when the iLO devices were connected to the network without having the required protection | when the iLO devices were added to the asset management database | $35,000 (for FRCC2015015366, FRCC2015015368, and FRCC2015015369) | Self-Report | To mitigate this issue, FRCC_URE1: 1) properly on-boarded (procedurally processed) the devices as NERC devices. The Manager of Network Technology reviewed the two-step onboarding/change management process with network analyst; 2) communication was sent from the CIP Senior Manager, (vice president of information technology & chief information officer) on situational awareness related to NERC compliance; 3) specifically address iLOs in the New NERC Asset form; and 4) facilitated a combined NERC change management session between IT techs, IT Security, and Asset Management to clarify the procedures in the NERC Change Management Process relative to the timing of onboarding NERC devices and the associated change type to use and communicated any clarifications to applicable team members. | 2015-12-23 | 2016-02-08 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's CIP-003-3 R6 and CIP-006-3c R2 compliance history involving similar conduct to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-20-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015366 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a R2, 2.2. FRCC_URE1 inadvertently configured Electronic Security Perimeter (ESP) firewall rules that enabled ports and associated services on devices within a demilitarized zone (DMZ) network that were not required for normal or emergency operations or monitoring to communicate through a NERC ESP access point. The incorrect firewall rules were in-place for a period of seven days. A security analyst implemented a change to configure firewall rules to allow network access to a new DMZ testing environment in preparation for an upgrade of the Energy Management System (EMS). To allow internal access to the new DMZ, a new firewall rule was defined that allowed eight new servers in a DMZ to access the corporate network. During the implementation of the rules in the change, the security analyst discovered that he had omitted a rule allowing traffic out of the new DMZ environment. The analyst corrected the omission by adding a new rule to allow outbound communication from the new DMZ to the corporate network. However, the rule configuration also inadvertently allowed communication into the existing ESP for EMS, which shares the same perimeter firewall with the new DMZ. According to the firewall logs, the first traffic to cross the firewall from the new DMZ network into the ESP occurred when the senior network and systems analyst activated the interface. The traffic was blocked when the emergency change was implemented. A security analyst discovered the problem as they were implementing security measures on the eight new servers in the new DMZ. Upon confirmation of the rule configuration, the analyst then initiated an emergency change to stop all traffic to the ESP from the servers in the new DMZ. The traffic was blocked when the emergency change was implemented. FRCC_URE1 performed a root cause analysis for this noncompliance and determined that the root causes were a lack of preventive tools or controls in place to prevent this type of error and the analyst involved relied too much upon institutional knowledge, rather than existing procedures. | CIP-005-3a | R2 R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC_URE1 inadvertently allowed communication into the existing ESP for EMS, which shared the same perimeter firewall with the new DMZ, and therefore could have exposed its network system to malicious cyber attacks and affected FRCC_URE1's operations. The potential risk to the BPS was minimized because the point of attack would have to been to access one of the servers, and to gain access, credentials would be required. There were only four applicable individuals with credentials, all are long-term trusted employees that have current NERC physical and interactive remote access. The servers were in the various initial stages of being onboard and not all of the devices were connected for the entire duration. The only software installed on the servers was the operating system, and applicable patches were applied prior to onboarding the devices. The only type of communications allowed into the ESP environment by the rule were from the new access restricted (future NERC EMS test environment) DMZ. No interactive access from the new network was made in to the ESP environment and there were no corporate assets, people, and/or any other Energy Control Center DMZs that could access the ESP while these rules were in place. Additionally, the new DMZ network and the EMS ESP share a Physical Security Perimeter (PSP). There were no workstations with access, but there were new servers in the DMZ allowed access by the rule. The four individuals had credentials with access to servers in the new DMZ environment. However, those credentials did not allow access into the systems within the ESP. Neither upgrades to devices nor updates to an individual’s credentials would have allowed access. No harm is known to have occurred. | when the analyst configured firewall rules to allow network access to a new DMZ testing environment | when traffic was blocked and the emergency change was implemented | $35,000 (for FRCC2015015366, FRCC2015015368, and FRCC2015015369) | Self-Report | To mitigate this issue, FRCC_URE1: 1) corrected the inadvertent firewall rule; 2) sent communications from the CIP Senior Manager, (to vice president of information technology & chief information officer) on situational awareness related to NERC compliance; 3) created a new desk level procedure (DLP), which includes peer review, for firewall rule changes; and 4) trained applicable team members on the new DLP. | 2016-01-13 | 2016-02-08 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's CIP-005-3a R2 compliance history to be an aggravating factor in the penalty determination.
2016-06-29 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013763 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-003-3 R5. RFC_URE1's documented program for managing access to protected Critical Cyber Asset (CCA) information does not clearly define a process for maintaining a list of designated personnel responsible for authorizing access to protected CCA information and validating that list on an annual basis. Specifically, RFC_URE1 failed to properly and timely document the addition and removal of authorizers to protected CCA information. RFC_URE1 was keeping two lists for documenting its authorized access approvers to protected CCA information. The first list was maintained manually in an Excel spreadsheet and is known as the Information Protection Owner List. The second list, known as the Number 1 and 2 Report, was an automated system-based list that is generated from RFC_URE1's Active Directory. The Number 1 and 2 Report was used to annually review the processes for controlling access privileges to protected information. When compared, ten differences in documented authorizers were identified between the two lists. RFC_URE1 also lacked adequate evidence to establish that it fully performed an annual review of the list of authorized approvers. The root cause of this violation relates to the management practice of verification, RFC_URE1 did not have a procedure to ensure accuracy between the lists after modifications. The differences in documented authorizers between the two lists arose from uncorrected human performance errors in manually updating the lists. The errors, such as former approvers being removed from one list and remaining on the other list, were not caught or corrected because RFC_URE1 did not have a process step built into its procedure to compare both lists to ensure accuracy after a change was made to one or both lists. This lack of built-in verification allowed the errors in each list to go uncorrected. | CIP-003-3 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 uses formal self-assessment processes to assess compliance to the Standard, which are separate from maintaining the list of authorizers and verifying the list of authorizers during the annual review. For restricted information, all repositories are housed on RFC_URE1 internal networks and to access any repository, an individual must be on the RFC_URE1 system and have RFC_URE1 assigned credentials. Most restricted information is housed on shared drives and similar repositories that have department and or team level access restrictions, which require specific approvals by a manager or higher. RFC_URE1's access request system routes any access requests to the current owner of a protected information repository. The repository owner typically has the best direct knowledge of the need for that access and is in the best position to assess whether that access should be granted. This setup mitigates the risk posed by this violation because the current authorized approvers are still in control of approving and rejecting access to protected information repositories. | when RFC_URE1 was required to comply with the Standard | when RFC_URE1 created a single, accurate list of authorized access approvers to protected CCA information | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) resolved identified discrepancies between existing authorized approver lists to create a single accurate list of authorized approvers; 2) assessed existing procedures and the current plan for integration with the legacy program and developed a plan to either revise these procedures or accelerate integration; 3) developed a detailed plan and schedule for the implementation of revised procedures and integration; 4) developed and delivered training to all impacted personnel responsible for maintaining and annually verifying the authorized approver list; 5) implemented the improved and integrated program for the maintenance and annual verification of the authorized approver list; and 6) performed a quality assurance assessment to verify that the improved and integrated program is operating as intended and will remediate any discrepancies. RFC_URE1 also assessed opportunities for further process improvements and developed a report on conclusions from the assessment. After this assessment, RFC_URE1 determined that two enhancements and communications can be made to further the annual review process. 1) Revise the RFC_URE1 CCA Information Protection Procedure. 2) Revise the Access and Account Monitoring Procedure. RFC_URE1 confirmed in its evidence that it completed these two revisions. | 2015-01-30 | 2015-09-11 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-06-29 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014186 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-004-3a R4. RFC_URE1 identified that lists of personnel with authorized cyber or authorized unescorted physical access have not been maintained in accordance with CIP-004 R4. All relevant access control information was retained across various systems, but RFC_URE1 determined that the collective set of information was not maintained and consolidated in a manner to facilitate prompt and accurate reviews. RFC_URE1 also identified instances where lists were not updated and accesses were not revoked within the seven-day timeframe required under CIP-004 R4.1 and CIP-004 R4.2. RFC_URE1 conducted a review of all quarterly certifications of logical and physical access conducted during prior years. Through this review, RFC_URE1 identified and confirmed a total of 66 accounts where access was not revoked within the seven day timeframe under CIP-004 R4. These instances were the result of gaps in RFC_URE1's access revocation procedures. RFC_URE1 discovered that the identification of new access control lists for CIP resources that are in-scope is not a documented process and relies primarily on manual investigation. Similarly, the consolidation of the in-scope access control lists into one authoritative list of all personnel with CIP information, electronic, and physical access is not a documented process. Monitoring of active access revocation requests and of accounts with pending training expiration is not sufficiently documented and relies primarily on manual investigation. Escalation of access revocation requests nearing completion deadlines and identification of all access rights held by a CIP access holder that are to be revoked are both insufficiently documented and rely primarily on manual investigation. Certain technical limitations at RFC_URE1 resulted in an over-reliance on manual investigations and processes in lieu of automated processes. The root cause of this violation related to the management practice of verification. RFC_URE1 relied on manual processes for creating, managing, and reviewing its lists of personnel with CIP access and for responding to access revocation requests. RFC_URE1's master list of individuals with CIP access required the manual consolidation of multiple discrete reports into a single view of current access. These high-volume manual processes resulted in human performance errors because of RFC_URE1's over-reliance on manual verification. | CIP-004-3a | R4 | Lower | Higher | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Physical access badges, laptops, and network IDs are all revoked and disabled immediately upon an individual’s termination or departure, which minimizes the risk of unauthorized access once an employee or contractor has left the company because the individual can no longer access any Physical Security Perimeters or Electronic Security Perimeters. Additionally, none of these individuals were terminated for cause. Each of the 66 individuals that did not have their access revoked within the seven-day timeframe was a trusted employee or contractor with a valid Personnel Risk Assessment and CIP training. Lastly, for all of the identified instances where access lists were not updated or access was not revoked in a timely fashion, there were no occurrences where such accesses were exploited or misused. | when RFC_URE1 failed to revoke user access | when RFC_URE1 revised its access revocation procedure to ensure timely processing of CIP access removals and revocations | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) verified that the current authoritative list of in-scope CIP resources is comprehensive; 2) developed a process for determining, managing, and reviewing that all in-scope access control lists are documented and accounted for; 3) developed a method to clearly view and prioritize all open CIP access revocation tickets based on the required due date to revoke access; 4) revised the Access Revocation Procedure to ensure timely processing of CIP access removals and revocations; 5) developed a checklist/job aid to accompany the revised Access Revocation Procedure; 6) reviewed and revised the Access and Account Monitoring Procedure; 7) provided training on the revised Access Revocation Procedure to responsible personnel; 8) developed a process and associated documentation for creating a single consolidated list of personnel with CIP information, electronic, and physical access; 9) performed a quality assurance assessment to verify that the improved and revised process is operating as intended; 10) provided training and communications on the above access control lists maintenance process and procedure changes to responsible personnel; and 11) performed an overall quality assurance assessment to verify that all process enhancements for both CIP access removals and CIP access list maintenance are being executed in accordance with revised procedures. A part of the entity's CIP Version 5 implementation program includes an access controls and automation project, which includes an identity and access management solution called the Access Controls and Automation System (ACAS). The ACAS will centralize access management and governance processes and procedures and support CIP Version 5 compliance. The improved automation in ACAS will provide benefits to RFC_URE1 and assist in preventing similar access issues from reoccurring in the future, particularly related to the granting and revocation of CIP access. | 2015-06-15 | 2015-10-26 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2016-05-31 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013840 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-005-1 R1. RFC_URE1 stated that during an internal review of its Cyber Vulnerability Assessment (CVA) findings, RFC_URE1 identified that it did not have adequate evidence of the assessment of the following two types of Electronic Access Control and Monitoring Assets (EACMs) pursuant to CIP-005 R1.5: Security Event Monitoring System and Intrusion Detection System. While RFC_URE1 collected and analyzed data for 10 Security Event Monitoring and Intrusion Detection assets as part of the CVA assessment, the CVA report did not clearly state that the assets did not have any identified vulnerabilities. RFC_URE1 had a lack of clear evidence linking the various phases, from raw data to the analysis, the assessment, and the final report of the CVA process. As part of an extent of condition review, RFC_URE1 identified that eight assets were not configured to forward their internal asset logs to a log repository, which comprises this violation of CIP-005-1 R1. The root cause of this violation related to the management practice of asset and configuration management. RFC_URE1 maintained weak procedural controls for the generation and documentation of the CVA analysis and report, particularly in managing contractor performance in support of compliance activities. As a result of these weak procedural controls, the assets were not adequately inventoried and monitored in the CVA assessment and report. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the assets in question were external to the RFC_URE1-defined NERC CIP Electronic Security Perimeters (ESPs) and had very limited communication ability with specific assets within the ESPs. The assets that did not log had a minimal impact to the Bulk Electric System because they had no direct control function or telemetry monitoring of critical assets. RFC_URE1 also employs a layered security model. These assets have been deployed within their own regulated private network, which is separate from both the business and control networks, and the hosts themselves have been hardened – all mitigating the risk posed by the violation. Lastly, at the time of the assessment, the assets were meeting all of RFC_URE1's security controls. | when RFC_URE1 was required to comply with the Standard | when the assets were fully incorporated into RFC_URE1's CVA | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) reviewed the existing processes for maintaining CVA evidence, particularly with regard to EACMS; 2) communicated requirements for documenting and retaining CVA evidence to all responsible and impacted personnel; 3) conducted the incomplete CVA, including all EACMs devices; and 4) performed a quality assurance assessment to confirm that evidence of performing the CVA for EACMS was appropriately documented and maintained in accordance with established processes. | 2015-01-30 | 2015-08-17 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-005 R1 compliance history to be an aggravating factor in the penalty determination.
2016-05-31 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014535 | Settlement Agreement | RF determined that RFC_URE1 was in violation of CIP-005-1 R1 as a result of a Compliance Audit. RFC_URE1 had not identified all access points to the electronic security perimeters (ESPs). RFC_URE1's vendor identified and recommended that ten assets, which are Critical Cyber Assets (CCAs), that had not previously been declared as ESP access points should be declared as ESP access points. RFC_URE1 updated its documentation to correctly identify these ten assets as ESP access points. RFC_URE1 was also able to show that all ten of the newly identified assets were being provided all security controls as required by CIP-002 through CIP-009. The root cause of this violation related to the management practice of workforce management. RFC_URE1 employees did not fully understand the CIP-005-1 R1 requirements, as RFC_URE1's subject matter experts focused only on routable traffic crossing the ESP in defining electronic access points. RFC_URE1 did not understand that non-routable data traffic crossing an ESP boundary needed to have a defined electronic access point. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the assets in question were external to the RFC_URE1 defined NERC CIP Electronic Security Perimeters and had very limited communication ability with specific assets within the ESPs. The assets that did not log had a minimal impact to the Bulk Electric System (BES) because they had no direct control function or telemetry monitoring of critical assets. RFC_URE1 also employs a layered security model and these assets have been deployed within their own regulated private network which is separate from both the business and control networks and the hosts themselves have been hardened – all mitigating the risk posed by the violation. Lastly, at the time of the assessment, the assets were meeting all of RFC_URE1's security controls. | when RFC_URE1 was required to comply with the Standard | when RFC_URE1 updated its documentation - ESP Diagram - to correctly identify the CCAs in question as ESP access points | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Compliance Audit | To mitigate this violation, RFC_URE1: 1) reviewed the existing processes for maintaining CVA evidence, particularly with regard to EACMS; 2) communicated requirements for documenting and retaining CVA evidence to all responsible and impacted personnel; 3) conducted the CVA, including all EACMS devices; and 4) performed a quality assurance assessment to confirm that evidence of performing the CVA for EACMS was appropriately documented and maintained in accordance with established processes. | 2015-01-30 | 2015-08-17 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-005 R1 compliance history to be an aggravating factor in the penalty determination.
2016-05-31 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013760 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-005-3a R3. RFC_URE1 identified a set of Critical Cyber Assets (CCAs) that were not properly configured to log at the time of installation. RFC_URE1 implemented the Security Event Monitoring system. This system is used to meet the technical requirements for logging, monitoring, and alerting under CIP-005 R3, CIP-007 R5.2.3 and CIP-007 R6.5. The security event monitoring system has been used to collect asset logs, alert on specific event criteria, and provide reports for event monitoring since its installation. RFC_URE1 identified that when the system was installed, eight hardened assets were not configured to forward their internal asset logs to the log repository. In addition, an intrusion detection system was also installed the same year. This system is used to meet the requirements for detecting actual unauthorized access under CIP-005 R3.2. The intrusion detection system has been used to investigate anomalous network traffic since installation. RFC_URE1 identified that the method the intrusion detection system uses to alert does not meet the CIP-005 R3.2 requirement. It identifies suspicious or anomalous network traffic and alerts these events to its internal dashboard. It is not capable of alerting externally, meaning it only presents the alert on the internal console dashboard. Upon realization that CIP-005 R3 requires external automated alerting, RFC_URE1 should have requested a Technical Feasibility Exception (TFE) because the intrusion detection system only provides manual alerting. RFC_URE1 failed to submit a TFE request. The root cause of this violation related to the management practice of workforce management. Specifically, the root cause was a misunderstanding of the requirements of CIP-005 R3. RFC_URE1 incorrectly believed that manual monitoring, without an approved TFE, was acceptable under CIP-005 R3. RFC_URE1's misunderstanding meant it did not request TFEs or implement an automated system that would have achieved compliance. | CIP-005-3a | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The security event monitoring assets that did not log had no direct control function or telemetry monitoring of critical assets. Although a compromise of the assets would place the logging of the specific CIP assets at risk, the monitoring and alerting of the other CIP assets would generally identify anomalous behavior. This monitoring and alerting minimize the risk that an actual impact to a CIP asset could occur without being detected. Unauthorized access to the assets would not allow any access to any other NERC Cyber Asset, CCA, Electronic Access Control and Monitoring Assets (EACMs), or Protected Cyber Assets (PCAs). For the intrusion detection system violation, system events and signature alerts are reviewed on a regular basis, thereby minimizing any risk as a result of the system's inability to alert in accordance with the requirements of CIP-005 R3. During those reviews, no unauthorized access events or any malicious events were detected. All of the actions required to meet the standard commitments were put in place when the intrusion detection system was installed. This is a primarily documentation violation as it arose from not completing a TFE. | when RFC_URE1 installed the security event monitoring system | when RFC_URE1 properly configured all of its security event monitoring assets to forward their internal asset logs to the log repository and filed a TFE | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented measures to ensure the identified security event monitoring assets are forwarding their logs; 2) conducted an assessment of existing processes and defined interim improvements to ensure that new EACMS devices are properly configured to log at the time of installation; 3) developed and delivered training to impacted personnel responsible for implementing process improvements and controls; 4) prepared and filed a TFE for the intrusion detection system alerting instances where the CIP-005 R3 requirement cannot be met; 5) developed a plan to transition to a significant change testing program; 6) conducted training on the change testing program; 7) communicated the implementation start date of change testing procedure to all impacted personnel; and 8) performed a quality assurance assessment on a sample set of newly installed devices to verify that the significant change testing procedure is being implemented as intended. | 2015-06-29 | 2015-10-26 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013839 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-005-3a R5. During review of evidence as part of an extent-of-condition analysis, RFC_URE1 identified instances where it did not have sufficient evidence to establish the timely completion of annual reviews and approvals of documentation specified in CIP-005-3 R5 that is subject to annual review obligations. Specifically, RFC_URE1 identified 26 procedures that are subject to the CIP-005 R5 annual review requirement. RFC_URE1's program defines annually as once per calendar year and no more than 16 months between events or activities. For two of those 26 procedures, CIP Security Alert and System Monitoring Procedure and CIP Access Authorization Procedure, RFC_URE1 did not have clear evidence in the revision history of each document showing that an annual review and approval meeting the RFC_URE1 annual criteria was performed. The root cause of this violation related to the management practices of verification and asset and configuration management. There was no built-in check to verify that all procedures and documents that were to be updated had clear evidence in their revision history to indicate that an annual review and approval had been performed. Additionally, the procedures and associated documents did not have a clear owner, an individual responsible to make sure that the update was properly completed. This lack of a clear owner meant the procedures were not effectively inventoried or monitored. | CIP-005-3a | R5 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The missed annual reviews pose minimal risk because all lists and diagrams that relate to CIP operational concerns were reviewed and approved annually so there were no potential security or protection impacts related to missed annual reviews. RFC_URE1 assesses compliance through formal self-assessment processes and not by the installation of updates. Updates are completed to meet the specific CIP obligation that requires the update and to identify areas of improvement. Additionally, all updates were completed, though not always on time or with complete documentation. | when RFC_URE1 failed to show it performed an annual review | when RFC_URE1 obtained evidence showing that the two procedures had a completed annual review and approval that met RFC_URE1's internal criteria | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) developed an inventory of all CIP-005 documentation that is subject to the annual review requirement in preparation for the previous year's annual reviews; 2) reviewed the inventory to assess annual review completion dates and to determine which documents, if any, were not reviewed within the 2013 annual review timeframe; and 3) conducted and completed annual reviews of all RFC_URE1 CIP-005 documents in inventory as part of the company-wide annual review process, ensuring that any documents identified as part of the inventory review are reviewed and approved within the annual review timeframe. | 2014-12-31 | 2015-04-08 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014167 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-006-3c R1. A RFC_URE1 intern working as an escorted visitor, and the intern’s escort breached the applicable RFC_URE1 CIP visitor access program within a Physical Security Perimeter (PSP). While the RFC_URE1 intern’s Personnel Risk Assessment (PRA) and CIP training were complete, his unescorted access approval was not yet approved. Therefore, the RFC_URE1 intern was still being treated as a visitor. During the visit, the RFC_URE1 intern was left alone within the PSP for approximately 22 minutes, while the escort met with other personnel down the hall. During this time, the intern attempted to badge out of the PSP to use the restroom. Due to the established access controls, his exit was denied and a door alarm notification was transmitted to the Security Operations Center (SOC). Immediately upon receipt of the door alarm notification, the SOC reported the incident to the security guard on duty, who responded, spoke with the intern and his escort, and verified the source of the alarm. RFC_URE1 failed to maintain continuous escorted access of a visitor within the PSP. The root cause of this violation related to the management practice of workforce management through a lack of effective training. The RFC_URE1 employee escorting the intern within the PSP did not follow RFC_URE1 procedures and protocols for escorting a visitor within a PSP by leaving the intern unattended in a PSP. | CIP-006-3c | R1; R1.6 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 has live video surveillance cameras positioned to view both the interior and exterior sides of the EOB PCS Room PSP access point. The Security Operations Center (SOC) has the ability to view live and recorded video for these cameras. This video can also be viewed from the guard station at the electric operations building at RFC_URE1. In addition to the video surveillance, on site security staff performs a minimum of two walk-through security checks of the PSP per 8-hour shift. The PSP included a limited number of Critical Cyber Assets (CCA) in the PSP associated with RFC_URE1's Energy Control System (ECS). There were no other assets requiring CIP protection such as EACMS, EAP, or PACS in the PSP. These CCA require a user ID and password to be entered to log onto the computer, and a separate user ID and password to be entered in order to access the ECS application. In addition to the CCAs, there are desktop computers in the PSP connected to the corporate data network, but any attempt to access assets subject to CIP protection require a separate user ID and password for remote access via a jump server, as well as two-factor authentication, none of which was available to the intern. All wall and desk cabinets within the PCS Room that contain any CIP information are locked. The RFC_URE1 intern involved had already completed his PRA and CIP training and was being escorted as a visitor while the approval of his physical unescorted access request to the PSP was being completed, and was left unescorted for a short period of time. Additionally, on attempting to exit, the security alarms were triggered to notify the SOC, who reported the incident to the security guard on duty, who responded and verified the source of the alarm. RFC_URE1 promptly identified, responded to, and corrected the Alleged Violation. All security controls worked as designed when the RFC_URE1 intern attempted to exit the PSP without proper authorization or an escort. | when the intern was left unescorted within the PSP | when RFC_URE1 conducted a mandatory stand-down meeting with all relevant personnel to reinforce visitor access processes | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1 conducted a mandatory stand-down meeting, with all relevant personnel. During this meeting, the PSP visitor access processes were reviewed and reinforced to ensure that all personnel adequately understood the importance of following all aspects of RFC_URE1 visitor access processes and procedures at all times. The discussion included a particular emphasis on personnel responsibilities when escorting individuals in protected areas, and the importance of physical security and compliance with the NERC CIP Standards. To prevent recurrence, RFC_URE1 also: 1) developed a checklist to support PSP visitor access program which details the requirements and responsibilities of personnel escorting a visitor into a PSP; 2) updated applicable RFC_URE1 visitor access procedures to include the new checklist and required that the checklist be distributed to and reviewed with escorting personnel at the time a visitor is being processed and before the escort begins; 3) trained security performing personnel on the new checklist requirement; and 4) communicated the new checklist requirement to all personnel with authorized unescorted PSP access. | 2014-12-19 | 2015-01-27 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-006 R1 compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013759 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-006-1 R2. RFC_URE1 determined that certain Physical Access Control Systems (PACS) devices associated with the building control system (BCS) were not afforded all of the protective measures and controls required under CIP-006 R2.2. Two sets of BCS assets were affected. The first set of assets, BCS servers and workstations, had been appropriately classified as PACS, however, RFC_URE1 had insufficient evidence to demonstrate that the PACS had been afforded all of the protective measures and controls required under CIP-006 R2.2. In this first set of assets, a total of two BCS servers and six BCS workstations were affected. The second set of assets involved BCS net controllers that had not been appropriately classified as PACS. As a result, the BCS net controllers were not afforded any of the protective measures and controls required under CIP-006 R2.2. A total of three BCS net controllers were impacted. RFC_URE1 is currently in the process of retiring the BCS System and transitioning its PACS to a different system. The root cause of this violation related to the management practices of workforce management through a lack of effective training and ineffective asset and configuration management. RFC_URE1 did not adequately train the new BCS application support team, as the team did not properly identify the appropriate BCS assets as PACS and did not complete all documentation requirements. The BCS assets were also not properly inventoried or monitored, as some BCS net controllers were not classified as PACS. | CIP-006-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The identified PACS cyber assets do not support critical functions and operations for the Bulk Electric System. Additionally, all assets affected currently reside within a defined Physical Security Perimeter (PSP). In order to physically access those devices, an individual would need authorized unescorted physical access to the PSP in which they reside. RFC_URE1 also did not identify any instances of deliberate attempts to circumvent existing physical access controls. The assets in question are afforded a baseline level of protection based on RFC_URE1's general corporate policies and procedures and a defense-in-depth security strategy. | when RFC_URE1 was required to comply with the Standard | when RFC_URE1 installed CIP controls for the new system and effectively retired the BCS System | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) developed a comprehensive plan to retire the BCS System and transfer to the new system. This transfer included technical and procedural controls and the identification of any Technical Feasibility Exceptions (TFEs) as necessary; 2) performed the cutover to the new system and applied CIP controls; 3) trained impacted personnel who will be responsible for performing compliance activities on all requisite CIP controls being applied to the new servers, workstations, and net controllers; and 4) performed a quality assurance assessment to verify that the implemented controls are operating as intended and assessed opportunities for improvement. | 2015-07-31 | 2015-10-26 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013758 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-007-3a R1. RFC_URE1 discovered it had insufficient evidence of cyber security controls testing associated with certain cyber assets as required under CIP-007 R1. Specifically, RFC_URE1 identified an instance where security control testing was not fully documented for one redundant Electronic Access Control and Monitoring Asset (EACMS) syslog server. After this initial identification, RFC_URE1 further identified eight EACMS logging devices where cyber security controls testing evidence and results were not fully retained and documented as required by RFC_URE1 procedures. Additionally, RFC_URE1 found similar documentation issues with 11 Physical Access Control Systems constituting BCS Servers, workstations, and net controllers. RFC_URE1 failed to document and retain cyber security controls testing evidence. The root cause of this violation related to the management practice of workforce management through ineffective training. Personnel responsible for installing or performing significant changes for cyber assets were confused about their responsibilities, particularly whose responsibility it was to document pre-change conditions. This confusion occurred due to the insufficient training given to the responsible personnel on the cyber security controls testing process and documentation requirements. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's infrastructure design provides layers of security that minimize the risk of an impact. The devices in question were in a demilitarized zone and or/behind secure firewalls. RFC_URE1's standard change control policies and procedures require verification of multiple security controls to provide a baseline level of security that further minimizes the risk. For the redundant syslog server in particular, cyber security controls testing was being performed, but the documentation was not adequately completed. The logs for the redundant syslog server were sent to a primary device as well as the redundant device. The primary device was logging normally and would have collected the required logs to monitor the Bulk Electric System. | when RFC_URE1 first failed to complete cyber security controls testing on the devices at issue | Mitigation Plan completion | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) developed training materials on cyber security controls testing, including requirements around the performance of such tests and documentation of evidence; 2) identified impacted personnel, including personnel responsible for installing new cyber assets and performing significant changes to existing cyber assets for which cyber security controls testing would be required pursuant to CIP-007 R1; 3) delivered training to impacted personnel; and 4) performed a quality assurance assessment on a sample set of significant changes to verify that cyber security controls tests are being performed and documented in accordance with company processes and procedures. | 2014-12-31 | 2015-04-07 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-007 R1 compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014094 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-007-1 R3. RFC_URE1 failed to properly monitor four firewalls and failed to properly inventory and document 13 patches for ten switches. RFC_URE1 recently began to implement patch management tools to provide a greater degree of automation. These enhanced compliance tools allow RFC_URE1 to generate reports for all issued patches for a certain period of time in order to effectively and timely assess each patch for possible implementation. After these improvements were implemented, an initial report was run to verify patching assessments. This report revealed that some CIP-007 R3 patching controls were not applied in accordance with RFC_URE1 processes for a set of CIP-classified assets and intrusion detection system (IDS) assets. For four firewalls, RFC_URE1 identified one patch that was assessed but not implemented, two patches that were mistakenly assessed as not applicable, and three assessed patches were not required to be assessed by RFC_URE1. For ten switches, 13 patches were not identified. RFC_URE1 completed additional research that revealed nine patches for three IDS assets that were issued, but not identified, and therefore not timely assessed for applicability or implemented. The root cause of this violation related to the management practices of workforce management through ineffective training and poor asset and configuration management. RFC_URE1 personnel responsible for evaluating and applying patches did not fully understand their responsibilities and were confused about the data and format required to use the patch management tool because they were ineffectively trained. Additionally, the four firewalls were not properly monitored, and 13 patches for 10 switches were not properly inventoried and documented, which shows poor asset management. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the assets affected sit behind several layers of protection. RFC_URE1 utilizes a secure network architecture and employs a layered security model to protect these assets. Each of these assets has been deployed with their own demilitarized zone, which is separate from both the business and control networks. The assets themselves have been hardened against attack, are not Internet-facing assets, and reside behind several layers of protection and firewalls. To reach these assets, a would-be attacker would have to first infiltrate 2 to 3 layers of firewalls before even being able to attempt an attack on the devices. These security controls mitigate the risk posed to the Bulk Electric System. | when the first patch was not applied | Mitigation Plan completion | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) verified which in-scope cyber assets are included in the automated patch identification process; 2) verified what software installed on in-scope cyber assets is configured appropriately in the patching tool; 3) conducted an extent of condition analysis to verify the scope of the issue; 4) performed all outstanding security patch assessments and scheduled applicable patches for implementation; 5) decided to enhance the existing RFC_URE1 security patch management program or adopt the patch management program to prevent recurrence; 6) delivered training on the revised or adopted security patch management procedures to all impacted RFC_URE1 personnel; and 7) performed a quality assurance assessment of RFC_URE1 patches to ensure that patches were appropriately identified, assessed, and scheduled. | 2015-06-05 | 2015-08-17 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-007 R3 compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014172 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-007-3a R5. As a result of an internal assessment, RFC_URE1 identified instances in which passwords for certain accounts were not changed at least annually. In total, RFC_URE1 identified 51 accounts where passwords were not updated within 365 days as required by CIP-007-3a R5. In particular, RFC_URE1 identified instances where personnel designated as backups or emergency users had not logged into their accounts within the last 365 days. RFC_URE1 does not have the technical capability to automatically disable these accounts upon password expiration. Therefore, once a password expires, the account user is prompted to change the password when he or she logs in for the first time after the previous password has expired. In the identified cases, because the users had not logged into their accounts within the last 365 days, the user had also not been prompted to change their account password within the last 365 days as the Standard requires. As a result, the passwords associated with these accounts expired without being changed within the annual time frame. Of the 51 accounts where passwords were not updated within 365 days, 20 involved accounts on the Energy Control System, 25 involved user accounts on the regulated private network domain, and six involved accounts on the security event monitoring application. If users had attempted to access any of the accounts more than 365 days after their last access attempt, the user would have been prompted to make a password change when the user logged in, thus ensuring that a password change would have occurred the next time the account was used. The root cause of this violation related to the management practice of reliability quality management through ineffective and incomplete controls for monitoring the age of an account’s password. The process RFC_URE1 relied upon to ensure passwords were updated, counting on users to periodically access their accounts and then update their passwords, was defective and incomplete because many backup users did not access their accounts annually. RFC_URE1 did not have in place additional controls, independent of a user accessing his or her account, which would ensure that passwords were changed at least once every 365 days. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Many of the passwords for these accounts have redundant controls, password complexity and length requirements, in place. The users with access to these accounts were up-to-date with their annual training and personnel risk assessments. Additionally, monitoring controls are in place to alert the appropriate CIP asset owners when multiple failed login attempts are made. For an outside intruder to exploit these accounts, the intruder would need to infiltrate several layers of firewalls or obtain physical access to a protected Physical Security Perimeter before the intruder could gain access to these accounts. RFC_URE1 has also determined that the accounts in question have not been used to gain access, interactive or otherwise, to any CIP assets since the passwords expired. | when RFC_URE1 was required to comply with the Standard | the date RFC_URE1 finished updating or deleting all overdue and expired passwords | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) identified all user accounts for which passwords were not changed within the annual timeframe; 2) determined which accounts are necessary and need to remain active and which accounts need to be deleted; 3) required password changes on user accounts that need to remain active; 4) deleted user accounts that do not need to remain active; 5) developed a procedure for monitoring user account password ages. This procedure was documented and contained steps for monitoring account password ages approaching 365 days, to ensure that passwords are changed within the required timeframe, and for disabling accounts if necessary; 6) developed and scheduled a plan for implementation; 7) delivered training to all personnel responsible for performing tasks under the new procedure; and 8) communicated implementation of the new procedure to all impacted personnel. | 2015-01-27 | 2015-08-07 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013761 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-007-3a R6. RFC_URE1 identified a set of Electronic Access Control and Monitoring Assets (EACMS) that were not properly configured to log at the time of installation. RFC_URE1 implemented a security event monitoring system. This system is used to meet the technical requirements for logging, monitoring, and alerting under CIP-005 R3, CIP-007 R5.2.3, and CIP-007 R6.5. RFC_URE1 has used this system to collect asset logs, alert on specific event criteria, and provide reports for event monitoring since its installation. RFC_URE1 identified that when the system was installed, eight hardened appliances were not capturing their own logs and not forwarding their internal asset logs to a log repository. The root cause of this violation related to the management practice of reliability quality management. RFC_URE1's weak procedural controls for the installation of new assets, which did not provide sufficient detailed steps to ensure that a device was capturing its own logs prior to the completion of the installation, caused RFC_URE1 to not identify that eight devices were not capturing their own logs. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The assets that do not log have a minimal impact to the Bulk Electric System because they have no direct control function or telemetry monitoring of critical assets. The assets in question were in a demilitarized zone and/or behind secure firewalls. The assets have a very limited number of accounts with access, and interactive access to these assets occurs infrequently. Unauthorized access to the assets would not allow any access to any other NERC Cyber asset, Critical Cyber Asset, EACMS, or Protected Cyber Asset. Although a compromise of the assets would place the logging of specific CIP assets at risk, RFC_URE1 has monitoring and alerting of other CIP assets in place that is designed to identify anomalous behavior. Lastly, RFC_URE1's infrastructure design provides layers of security that minimize the risk of an impact. | when RFC_URE1 first implemented the security event monitoring system | the date RFC_URE1 confirmed that all assets were forwarding all of their logs appropriately | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented measures to ensure the identified security event monitoring assets are forwarding their logs; 2) defined process improvements such as enhancements to existing processes and controls and the development of new processes and controls to ensure that new EACMS devices are properly configured to log at the time of installation; 3) developed and delivered training to impacted personnel on process improvements; 4) developed a plan to transition to a significant change testing program; 5) developed and delivered training to impacted personnel on the change testing program; 6) communicated implementation of change testing program; and 7) performed a quality assurance assessment on a sample set of newly installed devices to verify that the change testing program is being implemented as intended. | 2015-06-29 | 2015-10-26 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013757 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-007-3a R9. RFC_URE1 identified instances where it did not have sufficient evidence to establish the timely completion of annual reviews and approvals of documentation specified in CIP-007-3a R9 as subject to annual review obligations. RFC_URE1 identified 31 procedures that are subject to the CIP-007 R9 annual review requirement. RFC_URE1's program defines annually as once per calendar year and no more than 16 months between events or activities. Seven of the 31 identified procedures did not indicate clear evidence of having an annual review with approval that met the RFC_URE1 annual criteria. The seven procedures are as follows: (1) CIP Security Alert and System Monitoring Procedures; (2) Corporate Security Account Management Procedure; (3) Corporate Security CIP Change Control Procedure; (4) CIP Access Authorization Procedure; (5) Energy Control System (ECS) Testing Environment; (6) Security Incident Response Process; and (7) Shared Accounts Procedure. The root cause of this violation related to the management practices of verification and asset and configuration management. There was no built-in check to verify that a review was completed and approval obtained for each procedure that was scheduled to be updated. Additionally, the procedures and associated documents did not have a clear owner, an individual responsible to make sure that the update was properly completed. This lack of a clear owner meant the procedures were not effectively inventoried or monitored. | CIP-007-3a | R9 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The missed annual reviews posed minimal risk because all lists and diagrams that relate to CIP operational concerns were separately reviewed and approved annually. Additionally, processes in the original document were not materially modified from the processes that existed during the timeframe of the missed annual reviews. RFC_URE1 also independently assesses compliance through formal self-assessment processes and not by the installation of updates. Updates are completed to meet the specific CIP obligation that requires the update and to identify areas of improvement. Lastly, all updates were completed, though not always on time or with complete documentation. | when RFC_URE1 could not provide evidence that the seven procedures had an annual review | the date RFC_URE1 completed, and documented, annual reviews with approval for the seven procedures | $25,000 (for RFC2014013763, RFC2014014186, RFC2014013840, RFC2014014535, RFC2014013760, RFC2014013839, RFC2014014167, RFC2014013759, RFC2014013758, RFC2014014094, RFC2014014172, RFC2014013761, and RFC2014013757) | Self-Report | To mitigate this violation, RFC_URE1: 1) developed an inventory of RFC_URE1 CIP-007 documentation; 2) reviewed the inventory to assess annual review completion dates and determined which documents, if any, were not reviewed within the annual review timeframe; and 3) conducted the following annual review and ensured that all inventory documents were reviewed and approved within the annual review timeframe. | 2014-12-31 | 2015-04-07 | Neither Admits nor Denies | RFC_URE1 has been highly cooperative throughout the entire enforcement process as it voluntarily provided RF with an abundance of information regarding the Violations in a manner that was detailed, well-organized, and timely. RFC_URE1's level of cooperation has been exemplary and RF awards a significant amount of mitigating credit for this cooperation to encourage this sort of response by other Registered Entities in the future. RF considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014708 | Settlement Agreement | SERC_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-3a R3.1. SERC_URE1 failed to assess security patches for applicability within 30 days of availability for Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 went operational with a new energy management system (EMS). SERC_URE1 used an automated tool that assimilated available security bulletins, which SERC_URE1 used to assess security patches for applicability, but SERC_URE1 omitted service packs from inclusion in the tool. As a result, SERC_URE1 did not review, assess or install two service packs and did not include subsequent security patches affiliated with the two service packs in the automated tool. Thus, SERC_URE1 did not assess 22 security patches within 30 days of availability. The release dates of these security patches ranged during a two and a half year period. After discovering the issue, SERC_URE1 determined that seven patches were not applicable and 15 patches were required. This issue affected 28.3% of the total Cyber Assets within the SERC_URE1 CIP program. SERC_URE1 discovered this issue when an employee saw a patch in the corporate patch queue that did not show up in the EMS patch queue. The employee was assisting in a corporate patching issue when he learned of the issue. While conducting an extent-of-condition review, SERC_URE1 subject matter experts found a second application with security patches that SERC_URE1 had not assessed within 30 days of availability. While installing the new EMS, SERC_URE1 installed the application on a single non-critical Cyber Asset within the ESP. SERC_URE1 had not used the application since installation and failed to assess the applicability of three patches that were available. In total, SERC_URE1 failed to assess 25 security patches for applicability within 30 days of their availability. The root cause of the first issue was that the SERC_URE1 security patch assessment process lacked specificity on how to manage potential security patches specific to service packs. The root cause of the second issue was that the individuals responsible for reviewing patches did not know that the second application was present in the CIP-protected environment because SERC_URE1 personnel had not used the application since installing it. Specifically, the patching process used by the individuals lacked specificity regarding how to handle/what to do with service packs, as well as applicable patches associated with uninstalled service packs. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to assess security patches for applicability within 30 days of being available could have allowed malicious individuals to exploit known vulnerabilities for an extended period. However, SERC_URE1 requires the use of a screening firewall, a jump host solution, two-factor authentication, and a proxy server, to gain remote access to Cyber Assets within the ESP, limiting the ability of an external individual to exploit any vulnerabilities on the Cyber Assets at issue. SERC_URE1 centrally monitored logs from the implicated Cyber Assets and any anomalous events would generate an alert to the appropriate response personnel. SERC_URE1 has not had any incidents during the violation period in which the cause is known to be malicious, suspected to be malicious, or unknown. The Cyber Assets at issue were within secured ESPs and Physical Security Perimeters with controlled access. All personnel with access to the Cyber Assets at issue had received cyber security training and had a valid personnel risk assessment. | when SERC_URE1 installed a new EMS without ensuring that all applicable security patches had been assessed | Mitigation Plan completion | $5,000 | Self-Certification | To mitigate this violation, SERC_URE1: 1) retroactively identified the missing security patches; 2) documented, evaluated for applicability, tested, and implemented if applicable, each missing patch; 3) modified the procedure on reviewing, logging, and tracking security patches to include greater details about how, where, and what to look for when reviewing security patches; 4) conducted a self-review of the modified patch process material as well as instruction from third-party support with subject matter experts to ensure that the patch processes are fully understood; and 5) modified its change management process and associated change management form to include a step for identifying all applications on devices associated with the change. | 2015-03-20 | 2015-12-10 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014764 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-005-3a R2.2. SERC_URE2 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) at all access points to the ESP. SERC_URE2 removed a failed Cyber Asset from within the ESP. During the decommissioning of the Cyber Asset, SERC_URE2 did not eliminate the firewall rules for traffic to the Cyber Asset from the three ESP firewalls associated with that specific Cyber Asset. This mistake permitted ports on each of the three firewalls to remain open and available. SERC_URE2 performed an extent-of-condition and discovered two additional port issues. In the first additional issue, SERC_URE2 removed an application but left open a port in error. In the second additional issue, SERC_URE2 discovered another Cyber Asset that had a firewall rule in place for a port that was not required. SERC_URE2 originally thought that the port was required for a time sync with the global positioning clocks, but upon further review, SERC_URE2 determined that the Cyber Asset at issue was only used for frequency and not time. SERC_URE2 closed all of the ports upon discovery. The root cause of this violation was a failure by SERC_URE2 personnel to follow the existing change control and configuration management procedures. | CIP-005-3a | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2's failure to disable open ports and services that were not required for normal or emergency operations could allow a malicious individual to gain access to and control of Critical Cyber Assets (CCAs), potentially leading to a loss of control or visibility over SERC_URE2's portion of the BPS. However, the firewall rules for the initial issue that were not required were associated with a previous access control appliance that was on a subnet by itself. Once SERC_URE2 removed the previous access control appliance, there was no Cyber Asset on the subnet that could have used the ports or seen authentication requests from the firewall. The ports for the application in the first additional issue were all outbound ports, limiting the potential attack vectors, reducing access opportunities, and restricting vulnerabilities. The port open to the devices in the second additional issue was open only to a trusted de-militarized zone and other restricted subnets. Any outsider attempting to connect to a device involved in the second additional issue using the port would not get a response because the device was not actually providing that service. | when SERC_URE2 enabled the firewall rules that permitted the open port that was not required | Mitigation Plan completion | $20,000 (for SERC2015014604, SERC2015014635, SERC2015014762, and SERC2015014764) | Compliance Audit | To mitigate this violation, SERC_URE2: 1) removed the access list and rules in the firewall that open ports to/from and allow authentication via the former IP address of the Cyber Asset; 2) provided training to appropriate personnel to emphasize the need to consider other devices, especially firewalls, when removing an asset from service; and 3) removed the firewall rules formerly used by the application and the rules opening the port to the devices. | 2015-05-19 | 2015-11-16 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to its mitigating activities, SERC_URE2 has completed or agreed to complete the following additional actions: a. SERC_URE2 adopted a cyber and physical security objective as part of SERC_URE2's strategic plan. SERC_URE2 staff briefed the Board regarding the initial progress in meeting the objective and will provide subsequent written reports to the Board on a monthly basis and in-person verbal updates to the Board on a quarterly basis. b. SERC_URE2 has budgeted funds to replace existing Remote Terminal Units (RTUs) without password protection capability with RTUs that have password protection to restrict configuration changes and firmware updates. SERC_URE2 expects to replace the RTUs over a two year period. c. In addition to performing the required cyber vulnerability assessment (CVA), SERC_URE2 will perform a cyber vulnerability review on non-CIP assets. The review will include the above active CVA as well as intrusion risk assessments on IT and operations technology networks.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014604 | Settlement Agreement | SERC sent SERC_URE2 an audit detail letter notifying it of an upcoming Compliance Audit. SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. SERC_URE2 failed to ensure that the Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP) were afforded the protective measures specified in CIP-003 R6 and CIP-007 R2, R4, R5, R6, and R8. SERC later determined that this violation extended back to Version 1 of the Standard. Prior to the Compliance Audit, SERC_URE2 retained a third-party consultant to conduct audit preparations. The consultant determined that SERC_URE2 failed to afford its physical access control system (PACS) door controllers with the protections referenced in CIP-006-1 R1.8 since the date of mandatory compliance. Specifically, SERC_URE2 had not: (a) established what ports and services were necessary for normal and emergency operations and disabled a single port that was not required for normal and emergency operations as required by CIP-007 R2; (b) requested a Technical Feasibility Exception (TFE) for the inability for account passwords to meet the complexity requirements specified in CIP-007 R5.3; and (c) requested a TFE due to the inability to run anti-virus and malware prevention software as required by CIP-007 R4. In addition to the issues noted in the Self-Report, SERC determined that SERC_URE2 had not: (a) established a configuration management benchmark documentation for the PACS door controllers and did not include them in the change control form for CIP-003 R6; (b) requested a TFE for the PACS door controllers that were not capable of monitoring for cyber security events as required by CIP-007 R6. SERC_URE2 believed that the door status monitoring performed by the PACS door controllers that would be communicated to the PACS server constituted status monitoring and eliminated the need for a TFE for the PACS door controllers; and (c) included the PACS controllers in its cyber vulnerability assessment (CVA) as required by CIP-007 R8. The door controllers at issue had no accounts, but did have ports and services. The vendor who conducted the annual SERC_URE2 CVAs did not include the PACS controllers. A different vendor conducted a CVA and identified the issue. However, SERC_URE2 failed to follow-up and reconcile the noted issue at that time. During the CVA, SERC_URE2 rediscovered the CVA issue. During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-006-3c R2.2. SERC_URE2 failed to afford the protective measures specified in CIP-007 R2 to a PACS server. SERC determined that the Compliance Audit finding was related to the Self-Report and consolidated the violations. SERC found that an SERC_URE2 PACS server deployed had a port that was required to be open in order for a back-up tool to function properly on the PACS server. However, SERC_URE2 did not properly document the port on its internal benchmarking documentation to indicate that the port was required for normal operations. The root cause of this violation was a failure by SERC_URE2 to recognize that the PACS devices were subject to all the specified requirements noted in CIP-006-1 R1.8, resulting in several failures to document necessary ports and services and configuration management benchmarks or submit requests for TFEs, and a failure to correct deficiencies identified during a CVA. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2's failure to afford the PACS devices all of the applicable protective measures specified in CIP-006-1 R1.8 could have allowed unauthorized individuals to gain physical or electronic access to Critical Cyber Assets or non-critical Cyber Assets and potentially damage or manipulate those devices. However, for the first issue, the PACS door controllers are firmware-based appliances and the unauthorized reconfiguration or modification of these devices would be difficult. For the second issue, SERC_URE2 needed the open port and simply omitted it from the baseline documentation. SERC_URE2 had placed the involved PACS server on a separate Electronic Security Perimeter (ESP) subnet and the firewall blocked the open port from any inbound access. Finally, all the PACS devices were protected within ESPs and PSPs. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $20,000 (for SERC2015014604, SERC2015014635, SERC2015014762, and SERC2015014764) | Self-Report | To mitigate this violation, SERC_URE2: 1) established a baseline to document required ports and services for door controllers per CIP-003 R6; 2) scanned all controllers to ensure only those required ports are open; 3) filed TFEs for controllers for CIP-007 R4 and R5.3; 4) provided reminder training to affirm the need to document all cyber devices in CIP scope, including those performing limited specific tasks; 5) filed TFE for controllers for CIP-007 R6; 6) completed a CVA of the controllers to mitigate failure to include them in prior years; 7) modified the CVA process form to include instructions to ensure that all CIP relevant Cyber Assets are covered by the test plan before it is approved; 8) revised the ports baseline in the configuration management database (CMD) to justify a port being open for the PACS server; 9) conducted an annual CVA to ensure all ports are properly documented in the CMD and prevent recurrence of undocumented ports; and 10) document the PACS server log messages and implement automated alerting when those logs occur. | 12/31/2015 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE2's compliance history to be an aggravating factor in the penalty determination. In addition to its mitigating activities, SERC_URE2 has completed or agreed to complete the following additional actions: a. SERC_URE2 adopted a cyber and physical security objective as part of SERC_URE2's strategic plan. SERC_URE2 staff briefed the Board regarding the initial progress in meeting the objective and will provide subsequent written reports to the Board on a monthly basis and in-person verbal updates to the Board on a quarterly basis. b. SERC_URE2 has budgeted funds to replace existing Remote Terminal Units (RTUs) without password protection capability with RTUs that have password protection to restrict configuration changes and firmware updates. SERC_URE2 expects to replace the RTUs over a two year period. c. In addition to performing the required cyber vulnerability assessment (CVA), SERC_URE2 will perform a cyber vulnerability review on non-CIP assets. The review will include the above active CVA as well as intrusion risk assessments on IT and operations technology networks.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014635 | Settlement Agreement | SERC sent SERC_URE2 an initial notice of a Compliance Audit. SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R5. SERC_URE2 failed to implement technical and procedural control for monitoring physical access at all access points to the Physical Security Perimeters (PSPs) 24 hours a day, 7 days a week. An SERC_URE2 operator went on shift during the night without his or her access badge, which the operator had forgotten at home. The previous shift operator who was being relieved permitted the operator access to the PSP where the operators worked. However, after being left alone for the shift, the operator left the PSP for approximately four minutes and blocked the door open to permit a return. When the door was blocked open, the security console at SERC_URE2 received a “door held open” alarm but the security personnel failed to respond or react to the alarm because the security personnel believed the alarm resulted from cleaning staff with authorized unescorted access. Instead, the security personnel acknowledged the alarm to silence it. SERC_URE2 had documented procedures for how to manage access for personnel with lost or forgotten access badges, as well as procedures for how security personnel must handle entry alarms once received. Annual training also covered this aspect as well as the necessity to maintain the integrity of the PSP. The procedures and training further specified that any anomalies encountered not addressed within existing training or procedures should be brought to the attention of a CIP representative immediately for proper resolution. The procedure for lost or stolen access cards contained the precautionary language about undocumented situations. The instant issue in which a night-shift operator worked alone within a PSP was not documented in the procedure. The operator’s supervisor was made aware that the operator had forgotten their badge at the start of the shift pursuant to the SERC_URE2 procedure. The supervisor attempted to contact the employee to discuss having the employee return home to retrieve the badge or have a family member deliver it to the worksite, but found the operator had already left the control center without the badge. The root cause of this violation was a failure to follow established SERC_URE2 procedures. | CIP-006-3c | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE2's failure to immediately investigate a “door held open” alarm caused by an SERC_URE2 operator propping the door open resulted in an approximately four-minute period during which the PSP was unoccupied and no security personnel investigated or guarded the PSP. Further, the operator’s workstation was unlocked during this period. This violation could have allowed an unauthorized individual to gain physical access to Critical Cyber Assets (CCAs) without being challenged, enabling that individual to damage, destroy, or misuse the CCAs. However, the workstation within the PSP could only directly operate elements of the BPS if an individual with the appropriate credentials logged on and took action. The operators in this location lacked such credentials. In addition, the PSP in question is within the SERC_URE2 headquarters building, which has locked doors that are operated by approved security badge card readers. SERC_URE2 reviewed video footage and confirmed that no one entered the PSP during this incident. | when the security console received the alarm for “door held open” but failed to respond immediately | when the operator returned to the PSP and secured the PSP door | $20,000 (for SERC2015014604, SERC2015014635, SERC2015014762, and SERC2015014764) | Self-Report | To mitigate this violation, SERC_URE2: 1) distributed a reminder email to personnel with unescorted access to PSPs reminding personnel of the importance of contacting their supervisor or CIP Standard owner for any situations where an appropriate response is unknown or unclear; 2) disciplined the employee that initiated the incident and dismissed the security staff that failed to investigate the alarm; 3) minimized nuisance and false alarms related to PSP monitoring by placing a longer delay between opening and initiating of the door held open alarm and retraining the cleaning crews to be more mindful of the door alarms to avoid these types of alarms; 4) installed a dedicated recording/monitoring system for cameras monitoring PSP access points; 5) reviewed, and if applicable updated, physical security policies to address additional scenarios encountered which contributed to violations; 6) reviewed, and if applicable, updated training programs to ensure personnel with unescorted access to PSPs understand what steps to take when procedures are unclear or situations are not addressed by a specific procedure; and 7) had staff complete refresher training on the procedures related to alarm response for personnel charged with responding to alarms. | 2015-06-05 | 2015-09-08 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In addition to its mitigating activities, SERC_URE2 has completed or agreed to complete the following additional actions: a. SERC_URE2 adopted a cyber and physical security objective as part of SERC_URE2's strategic plan. SERC_URE2 staff briefed the Board regarding the initial progress in meeting the objective and will provide subsequent written reports to the Board on a monthly basis and in-person verbal updates to the Board on a quarterly basis. b. SERC_URE2 has budgeted funds to replace existing Remote Terminal Units (RTUs) without password protection capability with RTUs that have password protection to restrict configuration changes and firmware updates. SERC_URE2 expects to replace the RTUs over a two year period. c. In addition to performing the required cyber vulnerability assessment (CVA), SERC_URE2 will perform a cyber vulnerability review on non-CIP assets. The review will include the above active CVA as well as intrusion risk assessments on IT and operations technology networks.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014762 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-3a R3.1. SERC_URE2 subsequently identified additional instances of violations with CIP-007 R3. SERC_URE2 failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of the availability of the patches or upgrades for several Cyber Assets within the Electronic Security Perimeter (ESP). A firmware update became available. SERC_URE2 received and was aware of the update within 30 days of its release. However, SERC_URE2 did not realize that the firmware update was for security issues. SERC_URE2 personnel thought the update was solely related to operational functionality bug fixes because “security update” was not prominent in the bulletin. As a result, SERC_URE2 took no action on the release and did not assess its applicability to Cyber Assets within the ESP. SERC_URE2 had three affected Cyber Assets in service. SERC_URE2 discovered a second issue and notified SERC. SERC_URE2 was investigating a software program within its energy management system (EMS) for broader use within its CIP program when it discovered that SERC_URE2 had not assessed a security patch that had been issued for the software program within 30 days of the security patch being released. SERC_URE2 included the software program, which is used for monitoring, in the EMS deployment and deployed the software program in a basic functioning state on one of two domain controllers in the primary control center and one of two domain controllers in the back-up control center. SERC_URE2 never configured the software program for use or activated any functionality within the EMS application. After discovery of the second issue, SERC_URE2 did a full extent-of-condition for all installed software applications and patch review issues. SERC_URE2 submitted an expansion of scope to SERC after it discovered a set of firmware-based switches that it did not assess for possible security updates after SERC_URE2 deployed them with the new EMS. SERC_URE2 deployed these two switches in order to isolate the EMS system from any external networks in the event an intrusion was detected. SERC_URE2 could operate the switches manually, but they also had an automated component, which enabled SERC_URE2 to operate them from within the EMS application. SERC_URE2 had previously attempted to find sources for any security updates to these switches, but found none and did not continue to conduct monthly checks on the manufacturer website for software updates. SERC_URE2 is not aware of any security updates for these firmware-based switches being issued but has resumed checking the manufacturer website monthly in order to confirm if any security updates are released. The root cause of the first issue was a failure of SERC_URE2 personnel to fully read the update bulletin and recognize the firmware update was for a security issue, not just functional fixes. The root cause of the second issue was human error. SERC_URE2 failed to document that the application was deployed with the new EMS. The root cause of the third issue was that, after initially searching for security updates and finding none, SERC_URE2 did not continue to conduct monthly checks for security updates. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 's failure to assess security patches within 30 days of availability could have left vulnerabilities on Cyber Assets available for exploit by malicious individuals for an extended period. However, for the first and third issues, the Cyber Assets at issue were firmware-based appliances, making the ability to modify or affect the operating parameters of the Cyber Assets difficult. For the second issue, the application involved was active but unutilized. The affected Cyber Assets did not communicate outside the ESP because the firewall would block any external connections, and the Cyber Assets resided within a secured ESP and Physical Security Perimeter with monitoring and logging enabled. | when SERC_URE2 installed the new EMS with the monitoring application included | Mitigation Plan completion | $20,000 (for SERC2015014604, SERC2015014635, SERC2015014762, and SERC2015014764) | Compliance Audit | To mitigate this violation, SERC_URE2: 1) applied the firmware release with the security update to the device; 2) conducted security patch evaluation training; 3) applied the latest patch for the software program; 4) create a support account for IT personnel to access patches; and 5) reviewed all software and firmware in the configuration management database to ensure patches are being reviewed and document the patch source. | 2015-08-14 | 2015-09-11 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to its mitigating activities , SERC_URE2 has completed or agreed to complete the following additional actions: a. SERC_URE2 adopted a cyber and physical security objective as part of SERC_URE2's strategic plan. SERC_URE2 staff briefed the Board regarding the initial progress in meeting the objective and will provide subsequent written reports to the Board on a monthly basis and in-person verbal updates to the Board on a quarterly basis. b. SERC_URE2 has budgeted funds to replace existing Remote Terminal Units (RTUs) without password protection capability with RTUs that have password protection to restrict configuration changes and firmware updates. SERC_URE2 expects to replace the RTUs over a two year period. c. In addition to performing the required cyber vulnerability assessment (CVA), SERC_URE2 will perform a cyber vulnerability review on non-CIP assets. The review will include the above active CVA as well as intrusion risk assessments on IT and operations technology networks.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015015164 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE4 was in violation of CIP-009-3 R1. SERC_URE4's recovery plan did not address the minimum requirements called for by CIP-009 R1. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE4's recovery plan for Critical Cyber Assets (CCAs) did not meet the requirements of CIP-009-3 R1 because it did not specify the required actions in response to events or conditions of varying severity or duration that would activate the recovery plan and did not define the roles and responsibilities of responders. Instead, SERC_URE4 utilized a broader business recovery or business continuity type plan for CIP-009-3 R1 with a focus on the redundancy of the Cyber Assets at both the primary control center as well as the back-up control center, noting the ability to move between the two sites in the event of a site failure. In the event of a total failure of both sites, SERC_URE4 cited manual operations and a reliance on neighboring entities. In addition, the recovery plan does not contain references to the recovery of Cyber Assets, other than guidance on where replacement Cyber Assets could be purchased and how to find the proper data restoration media. The root cause of this violation was a misunderstanding by SERC_URE4 on what was required to be in the CIP-009 R1 recovery plan for CCAs. Specifically, SERC_URE4 compliance staff failed to understand that recovery plans must include all criteria laid out by the standard/requirement and not just what would be included in the business continuity plan. SERC_URE4 misinterpreted the standard believing the term "recovery" was indicating recovering operations at the backup site, rather than recovering Cyber Assets. | CIP-009-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE4's failure to specify the required actions in response to events or conditions of varying duration and severity and to define the roles and responsibilities of responders in its recovery plan for CCAs could have delayed the recovery of CCAs after an event that compromised the operation of those CCAs. However, SERC_URE4 had a high-level business continuity plan that identified the ability to continue operations through back-up sites and use manual operations and rely on neighboring entities in the event of a total failure of the primary and backup sites. SERC_URE4 did not need to use the recovery plan during the duration of the violation. | when the Standard became mandatory and enforceable on SERC_URE4 | Mitigation Plan completion | $20,000 (for SERC2015015164, SERC2015015165, SERC2015015166, and SERC2015015167) | Compliance Audit | To mitigate this violation, SERC_URE4: 1) updated its procedures to reflect how it will address the recovery of individual CCAs following failover; and 2) trained appropriate personnel regarding all procedural changes, including formal reinforcement training with energy management system backup and recovery procedures. | 2015-08-10 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015015166 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE4 was in violation of CIP-005-3a R1.5. SERC_URE4 did not afford four electronic access control and monitoring (EACM) Cyber Assets the protective measures specified in CIP-007-3a R5.3.2 because the EACM Cyber Assets could not technically enforce password strength (a combination of alpha, numeric, and “special” characters) and SERC_URE4 did not submit a request for a Technical Feasibility Exception (TFE). During the on-site audit, SERC_URE4 discovered that its network intrusion detection system (NIDS), consisting of four servers classified as EACM Cyber Assets, did not technically enforce password complexity. The password module that SERC_URE4 used had technical limitations that prevented it from properly managing the complexity of the root account password. Upon discovery, SERC_URE4 disclosed this issue to the SERC audit team on site and initiated immediate efforts to remediate. The four EACM Cyber Assets at issue were put into service when SERC_URE4 implemented a new energy management system (EMS). The root cause of this violation was a misunderstanding by SERC_URE4 of the technical abilities and limitations of modules used to enforce password complexity requirements. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4's failure to enforce password complexity on the EACM devices could allow a malicious individual to guess or crack the passwords and gain control of the EACM devices, giving them unauthorized access to Critical Cyber Assets (CCAs) However, the EACM devices did not have direct control of any CCAs and are not used to meet CIP logging requirements. SERC_URE4 had procedural controls in place to ensure use of passwords with the required complexity. SERC_URE4 installed the EACM devices to enhance its security posture and came into audit scope due to the classification of the system as an EACM. This violation lasted less than five months. | when SERC_URE4 implemented the EACM devices and used a password module that did not technically enforce the complexity requirements on root account passwords | Mitigation Plan completion | $20,000 (for SERC2015015164, SERC2015015165, SERC2015015166, and SERC2015015167) | Compliance Audit | To mitigate this violation, SERC_URE4: 1) found another application that would apply the complexity requirement to the root account; and 2) installed and tested the application. | 2015-08-07 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015015165 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE4 was in violation of CIP-006-3c R2. SERC_URE4 failed to afford physical access control system (PACS) devices the protective measures specified in CIP-007-3a R5.2.3 by documenting shared account usage in all cases. SERC_URE4 had a policy that required individuals who used shared accounts to manually document the shared account use on a log sheet. SERC discovered that an employee used a shared administrator account and failed to log the usage of the shared account for the PACS. The actual log-on and usage of the shared account was captured in the events logging for the PACS but did not document the individual that used the account. On the date of the discovery, SERC_URE4 initiated an extent of condition review comparing the actual events logs from the PACS servers to the manual spreadsheet over the previous 90 days and included all shared accounts in service across the CIP environment. SERC_URE4 did not find any additional failures to log usage of shared accounts on the PACS servers. Approximately three months after the failed log, SERC_URE4 implemented an automated solution to log shared account usage on all shared accounts The root cause of this violation was a human performance failure. The individual using the shared account in question failed to complete the required manual log of account usage. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE4's failure to accurately log usage of a shared account could hinder an investigation of who made certain changes to a system or whether such access was unauthorized. However, The PACS Cyber Assets were secured within a Physical Security Perimeter (PSP), with restricted and logged access. This issue was the only noted occurrence over the previous 90-day period. SERC_URE4 did not identify any unauthorized modifications or changes to the PACS. | when a SERC_URE4 employee using the shared account failed to log the usage on the manual log entry form | Mitigation Plan completion | $20,000 (for SERC2015015164, SERC2015015165, SERC2015015166, and SERC2015015167) | Compliance Audit | To mitigate this violation, SERC_URE4: 1) updated its process to use an automated log system created in-house that runs a log on script at user log on that detects if the account is in the “Shared Account” group; and 2) trained appropriate personnel regarding all procedural changes, including formal reinforcement training on automated procedures. | 2015-08-07 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2015015167 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE4 was in violation of CIP-007-3a R1.3. SERC_URE4's testing procedure did not sufficiently address documentation of test results, which caused SERC_URE4 to not consistently document and retain test results. During the Compliance Audit, SERC reviewed several significant changes in which SERC_URE4 lacked evidence showing that it conducted testing. SERC_URE4's documented testing procedures lacked the details needed to obtain consistent evidence that testing occurred. SERC_URE4 did not provide evidence that testing had consistently occurred. The root cause of this violation was a failure by SERC_URE4 to have detailed enough testing procedures to ensure that SERC_URE4 staff would consistently test and maintain evidence of testing. | CIP-007-3a | R1; R1.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE4's failure to demonstrate testing of all significant changes for adverse impacts to existing cyber security controls could have resulted in implemented changes disabling or removing existing security controls, increasing the risk of unauthorized access to Critical Cyber Assets or the introduction of security vulnerabilities. However, SERC_URE4 had a port scanning tool set to run every 10 hours to detect and alert on any ports changes that were made. SERC_URE4 secured all Cyber Assets within an established Electronic Security Perimeter and a Physical Security Perimeter. | the day after SERC_URE4 completed its Mitigation Plan for the prior violation | Mitigation Plan completion | $20,000 (for SERC2015015164, SERC2015015165, SERC2015015166, and SERC2015015167) | Compliance Audit | To mitigate this violation, SERC_URE4: 1) developed a new test procedure for security controls; and 2) trained appropriate personnel regarding all procedural changes, including formal reinforcement training with security controls testing procedure. | 2015-08-10 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE4's compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015014963 | Settlement Agreement | SERC determined that SERC_URE3 was in violation of CIP-006-3c R2.2. SERC_URE3 failed to identify physical access control systems (PACS) door controllers as PACS devices and therefore failed to afford these Cyber Assets the protective measures specified in R2.2. SERC later determined that the violation extended back to Version 1 of the Standard and Requirement, when the Requirement was found at CIP-006-1 R1.8. SERC_URE3 failed to consider two components serving the back-up control center as part of the PACS. As a result, SERC_URE3 had no evidence that it afforded the components the protective measures required by CIP-006-3c R2.2. The components were Cyber Assets that fulfilled the function of an intelligent door controller, but were also a part of the physical lock mechanism. The access control components were firmware-based and stored badge information, verified that the badge was authorized, communicated to the lock mechanism to unlock the door, and stored logs of each badge presentation. Individuals could access the controller ports of these intelligent door controllers from outside the Physical Security Perimeter (PSP) because the controller ports were located on the exterior of the door. SERC_URE3 conducted any programming of these devices from the exterior of the PSP. SERC_URE3 believed that because the Cyber Assets were a part of the actual physical lock, they fell under the exclusionary statement within CIP-006-3c R2 that provides: “Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall … be afforded the protective measures specified in … [the list of Requirements found in CIP-006-3c R2]” However, because the intelligent door controllers fulfilled the PACS obligation of authorizing and logging access, they were a primary part of the PACS system and SERC_URE3 was required to provide them with the protective measures listed in CIP-006-3c R2.2. Therefore, while SERC_URE3 properly applied the exclusion to the physical badge reader and lock components, SERC_URE3 should not have extended the exclusion to the Cyber Assets that stored badge information, verified badge authorization, and communicated to the lock mechanism to unlock the door. The root cause of this violation was SERC_URE3's misapplication of the CIP-006-3c R2 exemption language, which caused it to not consider the Cyber Assets within the locks to be PACS devices. As a result, SERC_URE3 could not provide evidence that it provided the intelligent door controllers the protections required by CIP-006-3c R2.2. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because SERC_URE3 failed to consider the intelligent door controllers to be PACS devices and failed to afford these Cyber Assets the required protective measures. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3's failure to properly protect the Cyber Assets that authorized access to its PSP for more than six years could have permitted access by unauthorized personnel who could modify or add to existing access permissions, giving them physical access to Critical Cyber Assets. However, the PACS devices in question were within a secured building that had video monitoring sent to the energy control center guard and the central monitoring station. The device involved was firmware-based and had no firmware upgrades issued during the violation, limiting potential security concerns. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2015014963, SERC2015014966, SERC2015014968, and SERC2015014970) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) installed, tested, and implemented a PACS which includes the standby control center, at this facility; and 2) conducted communication and training of the PACS at the standby control center. | 2016-04-01 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's CIP-006-1 R1.8 compliance history to be an aggravating factor in the penalty determination.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015014966 | Settlement Agreement | SERC determined that SERC_URE3 was in violation of CIP-006-3c R1.1. SERC_URE3 failed to ensure all Cyber Assets within an Electronic Security Perimeter (ESP) resided within a completely enclosed (six-wall) Physical Security Perimeter (PSP). SERC later determined that this violation extended back to Version 1 of the Standard. A SERC_URE3 Critical Asset substation had dial-up remote access to its Critical Cyber Assets (CCAs), but no external routable remote access. However, the substation also had CCAs within it that used routable protocols internal to the substation ESP to communicate. SERC_URE3 interpreted CIP-006-3, Section D.1.5.2, “For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall not be required to comply with Standard CIP-006-3 for that single access point at the dial-up device” to apply not only to the single access point but to all CCAs at the substation. As a result, SERC_URE3 concluded that the substation did not require a PSP because the CCAs within it were only accessible via dial-up remote access. While the exception found in Section D.1.5.2 is applicable to the “single access point at the dial-up device,” SERC_URE3 had CCAs within the substation that used routable protocols. Thus, SERC_URE3 should have established a PSP to protect the CCAs at the substation that used routable protocols. SERC_URE3 took actions, including removing the dial-up access to some CCAs, that resulted in reclassifying the substation as a Critical Asset that had no CCAs. The root cause of this violation was SERC_URE3's misinterpretation of the CIP-006 Standard, specifically Section D.1.5.2. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.1 because SERC_URE3 failed to ensure all Cyber Assets within an ESP resided within a completely enclosed (six-wall) PSP. | CIP-006-1 | R1; R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3's failure to secure all Cyber Assets within an ESP within an established six-wall PSP could allow unauthorized individuals to gain physical access to CCAs without being detected and allow those individuals to alter or compromise the Cyber Assets or their data. SERC_URE3 failed to provide the required protection to the CCAs for almost five years. However, SERC_URE3 had physical access controls in place for the substation, which included a locked perimeter fence, on-site security personnel making regular periodic security checks, a restricted access control house that used a badge reader which contained all involved Cyber Assets, a request and approval process for obtaining card access to the control house, and access logging through the badge reader. No known security breaches of this site occurred during the violation. | when the Standard became mandatory and enforceable on SERC_URE3 | when SERC_URE3 took actions that resulted in the reclassification of the site as a Critical Asset with no CCAs | $45,000 (for SERC2015014963, SERC2015014966, SERC2015014968, and SERC2015014970) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) removed dial-up remote access to the facility involved; 2) in preparation for CIP V5, identified the facility where dial-up remote access previously existed as a facility housing Bulk Electric System Cyber Systems with a Medium Impact rating; 3) installed, tested, and implemented a physical access control systems (PACS) at this facility; and 4) conducted communication and training on the PACS at this facility. | 2016-04-01 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC determined that SERC_URE3's CIP-006 R1 compliance history should not serve as a basis for aggravating the penalty.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015014968 | Settlement Agreement | SERC determined that SERC_URE3 was in violation of CIP-005-3a R3. SERC_URE3 failed to document its security monitoring processes to detect and alert for attempts at or actual unauthorized accesses when conducting manual reviews. SERC later determined that the violation extended back to Version 1 of the Standard. SERC_URE3 utilized an automated tool and rule-based aggregation to monitor and log access to the Electronic Security Perimeter (ESP) firewalls as well as to alert for attempts at or actual unauthorized accesses. However, SERC_URE3 depended on manual log reviews to detect and alert for attempts at or actual unauthorized access into the ESP through the firewall. Although SERC_URE3 had an isolated network and limited access avenues into the ESP, SERC_URE3's assessment of access was limited to a manual periodic review of access logs and SERC_URE3 did not have a documented process for how to conduct these manual log reviews or what to look for in the reviews. As a result, SERC_URE3 relied on experienced personnel to conduct this manual review by using professional judgment, looking for anything that appeared out of the ordinary, and any unauthorized or unusual traffic through the firewall would have been readily evident to them. If personnel saw any unusual traffic during this review, they would conduct a more in-depth review of a sample of logs. However, without a documented process for conducting these manual reviews, SERC_URE3 could not ensure consistent implementation of the manual review process or consistent documentation of the results of those reviews. The root cause of this issue was SERC_URE3's misunderstanding of the Standard and Requirement, specifically the requirement to document its process. SERC determined that SERC_URE3 was in violation of CIP-005-1 R3 because SERC_URE3 failed to implement and document, where technically feasible, security monitoring processes to detect and alert for attempts at or actual unauthorized accesses to the ESP. | CIP-005-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3's failure to have documented processes for the manual review of all attempts at or actual unauthorized access to the ESP could result in inconsistent manual reviews of logs, potentially allowing an intrusion attempt or actual intrusion to go undetected for an extended period. However, SERC_URE3's overall network topology used layered firewalls outside of the ESP, restricting traffic to the firewall. SERC_URE3 had policies in place that prohibited interactive sessions through the ESP access points, limiting potential attack vectors. SERC_URE3 limited external connectivity and did not permit direct Internet accessible communication, which provided SERC_URE3 with known traffic patterns that would allow any unexpected or anomalous traffic to be readily apparent to an experienced log reviewer. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2015014963, SERC2015014966, SERC2015014968, and SERC2015014970) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) researched and purchased a new ESP firewall; 2) developed criteria for logging and alerting; 3) tested filtering of firewall logs and alerting capabilities of the new firewall; 4) implemented security information and event management email alerts for loss of logging by the firewall; 5) developed a backup manual process to review firewall logs. To aid in the transition to CIP V5, the review will be conducted as prescribed in NERC CIP-007-5, Part 4.4; and 6) completed training on the manual review process. | 2016-04-01 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2015014970 | Settlement Agreement | SERC determined that SERC_URE3 was in violation of CIP-009-3 R1. SERC_URE3 failed to create a sufficient recovery plan for Critical Cyber Assets (CCAs). SERC_URE3 revised its recovery plan document, making the document to be more of a broad business recovery or business continuity-type plan. The document focused on the redundancy of the involved systems at both the primary control center as well as the back-up control center (both Critical Assets) and the ability to move between the two sites in the event of a site failure at either. The document did not specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plans and did not define the roles and responsibilities of responders. The root cause of this violation was SERC_URE3's lack of understanding of what CIP-009-3 R1 required. SERC determined that SERC_URE3 was in violation of CIP-009-3 R1 because SERC_URE3 failed to create a sufficient recovery plan for CCAs. | CIP-009-3 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3's failure to specify the required actions in response to events or conditions of varying duration and severity and to define the roles and responsibilities of responders in its recovery plan for CCAs could have delayed the recovery of CCAs after an event that compromised the operation of those CCAs. However, SERC_URE3 had high-level business continuity plans to permit continuation of operations through a back-up site. SERC_URE3 did not need to use the recovery plan during the violation. | when SERC_URE3 revised its recovery plan | Mitigation Plan completion | $45,000 (for SERC2015014963, SERC2015014966, SERC2015014968, and SERC2015014970) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) developed updated recovery plans to meet the requirements of CIP Version 5. These plans include a higher level of detail related to the recovery of specific assets, the events or conditions and severity that would activate the plan, and roles and responsibilities; and 2) completed communication and training of the updated recovery plans. | 2016-04-01 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3 compliance history and determined there were no relevant instances of noncompliance.
2016-04-28 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014706 | Settlement Agreement | SERC_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-3 R2. SERC_URE1 failed to document changes to the senior manager and the senior manager’s delegates within 30 calendar days of the effective date. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE1 identified this issue while preparing for a Compliance Audit. However, SERC_URE1 did not report the issue until approximately eight months later. SERC_URE1 stated that it did not report the issue immediately upon discovery because it wanted to ensure that it had not overlooked a newer version of the signed form. Ineffective document management practices were the primary cause of the issue. SERC_URE1 designated a delegate for the senior manager responsible for CIP compliance by name, title, and date of designation. The date of designation of the delegate was approximately one month earlier. Approximately three months later, the individual left the position and was no longer a delegate for the senior manager. However, SERC_URE1 did not update the change to the delegation document until approximately one and a half years later. In addition, the delegate designation document was signed by an individual working for the SERC_URE1 parent company who indicated they were signing the document as a delegate for the senior manager. However, there is no documentation of any delegation of authority to that individual and it is therefore an invalid designation of authority to the other named delegates. The delegate designation document is the earliest documented evidence that SERC_URE1 has regarding its compliance with CIP-003 R2, more than three years after it was required to be compliant. After the delegate designation document was signed, SERC_URE1 failed in multiple instances to document changes to the senior manager and delegates within 30 calendar days of the effective dates of those changes. | CIP-003-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 personnel annually approved its risk-based assessment methodology (RBAM) and Critical Asset list. In addition, SERC_URE1 has no Critical Assets or Critical Cyber Assets (CCAs), and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 revised the designation and delegation document | $0 (for SERC2015014706 and SERC2015014898) | Self-Certification | To mitigate this violation, SERC_URE1: 1) revised the senior manager designation and delegation document to accurately reflect the current senior manager and delegates; 2) updated the compliance calendar to include a recurring 25-day reminder to check the employment status of each individual on the senior manager assignment document; and 3) worked with the corporate human resources team to implement an automated notification process of employees with changes to their employment status that will be sent directly to the corporate compliance team on a weekly basis. | 2015-12-18 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE1 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE1 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE1 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE1 shall provide SERC with written updates on SERC_URE1's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE1 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE1 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE1 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE1 shall provide evidence at the next scheduled update showing SERC_URE1 documented the change within 30 days (in addition to providing its current list).
2016-04-28 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014898 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-3 R3. SERC_URE1 failed to develop a list of Critical Cyber Assets (CCAs) using its list of Critical Assets. SERC identified this issue while reviewing SERC_URE1 documentation for an associated issue and requested that SERC_URE1 submit a Self-Report. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE1 applied its risk-based assessment methodology (RBAM) and determined that it had no Critical Assets. SERC_URE1 erroneously interpreted the Standard and Requirement to require a CCA list only when the RBAM resulted in Critical Assets. Therefore, SERC_URE1 did not create a null list of CCAs using its null list of Critical Assets. SERC_URE1's misinterpretation of the Standard and Requirement is the primary cause of the issue. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 has no Critical Assets or CCAs, and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2015014706 and SERC2015014898) | Self-Report | To mitigate this violation, SERC_URE1: 1) applied its RBAM to determine the list of Critical Assets and list of CCAs; 2) had the RBAM, list of Critical Assets, and list of CCAs approved by the designated CIP senior manager's delegate; 3) set up a process in which the corporate compliance team uses third-party software to auto-generate work orders and custom reporting for CIP-002 compliance obligations; and 4) created an event reminder in the corporate compliance calendar for annual review of the RBAM, list of Critical Assets, and list of CCAs. | 2016-01-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after SERC identified the violation while reviewing SERC_URE1 documentation for an associated issue. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE1 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE1 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE1 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE1 shall provide SERC with written updates on SERC_URE1's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE1 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE1 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE1 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE1 shall provide evidence at the next scheduled update showing SERC_URE1 documented the change within 30 days (in addition to providing its current list).
2016-04-28 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014707 | Settlement Agreement | SERC_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-3 R2. SERC_URE2 failed to document changes to the senior manager and the senior manager’s delegates within 30 calendar days of the effective date. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE2 identified this issue while preparing for a Compliance Audit. However, SERC_URE2 did not report this issue until approximately eight months later. SERC_URE2 stated that it did not report the issue immediately upon discovery because it wanted to ensure that it had not overlooked a newer version of the signed form. The primary cause of this issue was ineffective document management practices. SERC_URE2 designated a delegate for the senior manager responsible for CIP compliance by name, title, and date of designation. The date of designation of the delegate was approximately one month earlier. Approximately three months later, the individual left the position and was no longer a delegate for the senior manager. However, SERC_URE2 did not update the change to the delegation document until approximately one-and-a-half years later. In addition, the delegate designation document was signed by an individual working for the SERC_URE2 parent company who indicated they were signing the document as a delegate for the senior manager. However, there is no documentation of any delegation of authority to that individual and it is therefore an invalid designation of authority to the other named delegates. The delegate designation document is the earliest documented evidence that SERC_URE2 has regarding its compliance with CIP-003 R2, more than three years after it was required to be compliant. After the delegate designation document was signed, SERC_URE2 failed in multiple instances to document changes to the senior manager and delegates within 30 calendar days of the effective dates of those changes. | CIP-003-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 personnel annually approved its risk-based assessment methodology (RBAM) and Critical Asset list. In addition, SERC_URE2 has no Critical Assets or Critical Cyber Assets (CCAs), and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE2 | when SERC_URE2 revised the designation and delegation document | $0 (for SERC2015014707, SERC2015014896, and SERC2015014897) | Self-Certification | To mitigate this violation, SERC_URE2: 1) revised the senior manager designation and delegation document to accurately reflect the current senior manager and delegates; 2) updated the compliance calendar to include a recurring 25-day reminder to check the employment status of each individual on the senior manager assignment document; and 3) worked with the corporate human resources team to implement an automated notification process of employees with changes to their employment status that will be sent directly to the corporate compliance team on a weekly basis. | 2015-12-18 | TBD | Admits | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE2 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE2 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE2 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE2 shall provide SERC with written updates on SERC_URE2's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE2 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE2 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE2 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE2 shall provide evidence at the next scheduled update showing SERC_URE2 documented the change within 30 days (in addition to providing its current list).
2016-04-28 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014896 | Settlement Agreement | SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-002-3 R3. SERC_URE2 failed to develop a list of Critical Cyber Assets (CCAs) using its list of Critical Assets. SERC identified this issue while reviewing SERC_URE2's documentation for an associated issue and requested that SERC_URE2 submit a Self-Report. SERC later determined this issue dated back to Version 1 of the Standard. SERC_URE2 applied its risk-based assessment methodology (RBAM) and determined that it had no Critical Assets. SERC_URE2 erroneously interpreted the Standard and Requirement to require a CCA list only when the RBAM resulted in Critical Assets. Therefore, SERC_URE2 did not create a null list of CCAs using its null list of Critical Assets. SERC_URE2's misinterpretation of the Standard and Requirement is the primary cause of the issue. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 has no Critical Assets or CCAs, and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2015014707, SERC2015014896, and SERC2015014897) | Self-Report | To mitigate this violation, SERC_URE2: 1) applied its RBAM to determine the list of Critical Assets and list of CCAs; 2) had the RBAM, list of Critical Assets, and list of CCAs approved by the designated CIP senior manager's delegate; 3) set up a process in which the corporate compliance team uses third-party software to auto-generate work orders and custom reporting for CIP-002 compliance obligations; and 4) created an event reminder in the corporate compliance calendar for annual review of the RBAM, list of Critical Assets, and list of CCAs. | 2016-01-28 | TBD | Admits | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after SERC identified the violation while reviewing SERC_URE2 documentation for an associated issue. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE2 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE2 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE2 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE2 shall provide SERC with written updates on SERC_URE2's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE2 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE2 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE2 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE2 shall provide evidence at the next scheduled update showing SERC_URE2 documented the change within 30 days (in addition to providing its current list).
2016-04-28 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014897 | Settlement Agreement | SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-002-3 R4. A SERC_URE2 employee, other than the senior manager or delegate(s) designated per CIP-003-3 R2, performed the annual review and approval of the risk-based assessment methodology (RBAM) and the list of Critical Assets for two years. SERC identified this issue while reviewing SERC_URE2's documentation for an associated issue and requested that SERC_URE2 submit a Self-Report. While SERC_URE2 annually approved the RBAM and Critical Asset null list, annual approvals were conducted by an employee who was not properly designated pursuant to the requirements of CIP-003-3 R2. In SERC_URE2's documentation, SERC_URE2 identified the plant manager as the senior manager or delegate responsible for annual approvals. Internally, the plant manager designated the employee who performed the approvals for the two years to be the plant manager’s designee during the plant manager’s absence. The primary cause of this issue was that SERC_URE2 failed to understand that in order for a SERC_URE2 employee to properly approve the RBAM and Critical Asset list, SERC_URE2 had to identify the individual in the CIP-003-3 R2 designation and delegation document. SERC determined that SERC_URE2 was in violation of CIP-002-3 R4 because SERC_URE2's senior manager or delegates identified per CIP-003-3 R2 did not perform the two annual approvals of the RBAM and the list of Critical Assets. | CIP-002-3 | R4 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 has no Critical Assets or Critical Cyber Assets (CCAs), and is a minimal size entity. | the day after SERC_URE2 failed to annually approve the RBAM and list of Critical Assets | Mitigation Plan completion | $0 (for SERC2015014707, SERC2015014896, and SERC2015014897) | Self-Report | To mitigate this violation, SERC_URE2: 1) had the designated CIP senior manager's delegate approve the current RBAM, list of Critical Assets, and list of CCAs; 2) educated the individuals listed on the CIP senior manager designation and delegation document of the delegate responsibilities and limitations; and 3) added compliance calendar event reminders. | 2016-01-28 | TBD | Admits | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after SERC identified the violation while reviewing SERC_URE2 documentation for an associated issue. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE2 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE2 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE2 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE2 shall provide SERC with written updates on SERC_URE2's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE2 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE2 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE2 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE2 shall provide evidence at the next scheduled update showing SERC_URE2 documented the change within 30 days (in addition to providing its current list).
2016-02-29 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014706 | Settlement Agreement | SERC_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-3 R2. SERC_URE1 failed to document changes to the senior manager and the senior manager’s delegates within 30 calendar days of the effective date. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE1 identified this issue while preparing for a Compliance Audit. However, SERC_URE1 did not report the issue until approximately eight months later. SERC_URE1 stated that it did not report the issue immediately upon discovery because it wanted to ensure that it had not overlooked a newer version of the signed form. Ineffective document management practices were the primary cause of the issue. SERC_URE1 designated a delegate for the senior manager responsible for CIP compliance by name, title, and date of designation. The date of designation of the delegate was approximately one month earlier. Approximately three months later, the individual left the position and was no longer a delegate for the senior manager. However, SERC_URE1 did not update the change to the delegation document until approximately one and a half years later. In addition, the delegate designation document was signed by an individual working for the SERC_URE1 parent company who indicated they were signing the document as a delegate for the senior manager. However, there is no documentation of any delegation of authority to that individual and it is therefore an invalid designation of authority to the other named delegates. The delegate designation document is the earliest documented evidence that SERC_URE1 has regarding its compliance with CIP-003 R2, more than three years after it was required to be compliant. After the delegate designation document was signed, SERC_URE1 failed in multiple instances to document changes to the senior manager and delegates within 30 calendar days of the effective dates of those changes. | CIP-003-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 personnel annually approved its risk-based assessment methodology (RBAM) and Critical Asset list. In addition, SERC_URE1 has no Critical Assets or Critical Cyber Assets (CCAs), and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 revised the designation and delegation document | $0 (for SERC2015014706 and SERC2015014898) | Self-Certification | To mitigate this violation, SERC_URE1: 1) revised the senior manager designation and delegation document to accurately reflect the current senior manager and delegates; 2) updated the compliance calendar to include a recurring 25-day reminder to check the employment status of each individual on the senior manager assignment document; and 3) worked with the corporate human resources team to implement an automated notification process of employees with changes to their employment status that will be sent directly to the corporate compliance team on a weekly basis. | 2015-12-18 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE1 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE1 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE1 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE1 shall provide SERC with written updates on SERC_URE1's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE1 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE1 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE1 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE1 shall provide evidence at the next scheduled update showing SERC_URE1 documented the change within 30 days (in addition to providing its current list).
2016-02-29 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2015014898 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-3 R3. SERC_URE1 failed to develop a list of Critical Cyber Assets (CCAs) using its list of Critical Assets. SERC identified this issue while reviewing SERC_URE1 documentation for an associated issue and requested that SERC_URE1 submit a Self-Report. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE1 applied its risk-based assessment methodology (RBAM) and determined that it had no Critical Assets. SERC_URE1 erroneously interpreted the Standard and Requirement to require a CCA list only when the RBAM resulted in Critical Assets. Therefore, SERC_URE1 did not create a null list of CCAs using its null list of Critical Assets. SERC_URE1's misinterpretation of the Standard and Requirement is the primary cause of the issue. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 has no Critical Assets or CCAs, and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2015014706 and SERC2015014898) | Self-Report | To mitigate this violation, SERC_URE1: 1) applied its RBAM to determine the list of Critical Assets and list of CCAs; 2) had the RBAM, list of Critical Assets, and list of CCAs approved by the designated CIP senior manager's delegate; 3) set up a process in which the corporate compliance team uses third-party software to auto-generate work orders and custom reporting for CIP-002 compliance obligations; and 4) created an event reminder in the corporate compliance calendar for annual review of the RBAM, list of Critical Assets, and list of CCAs. | 2016-01-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after SERC identified the violation while reviewing SERC_URE1 documentation for an associated issue. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE1 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE1 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE1 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE1 shall provide SERC with written updates on SERC_URE1's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE1 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE1 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE1 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE1 shall provide evidence at the next scheduled update showing SERC_URE1 documented the change within 30 days (in addition to providing its current list).
2016-02-29 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014707 | Settlement Agreement | SERC_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-3 R2. SERC_URE2 failed to document changes to the senior manager and the senior manager’s delegates within 30 calendar days of the effective date. SERC later determined that this issue dated back to Version 1 of the Standard. SERC_URE2 identified this issue while preparing for a Compliance Audit. However, SERC_URE2 did not report this issue until approximately eight months later. SERC_URE2 stated that it did not report the issue immediately upon discovery because it wanted to ensure that it had not overlooked a newer version of the signed form. The primary cause of this issue was ineffective document management practices. SERC_URE2 designated a delegate for the senior manager responsible for CIP compliance by name, title, and date of designation. The date of designation of the delegate was approximately one month earlier. Approximately three months later, the individual left the position and was no longer a delegate for the senior manager. However, SERC_URE2 did not update the change to the delegation document until approximately one-and-a-half years later. In addition, the delegate designation document was signed by an individual working for the SERC_URE2 parent company who indicated they were signing the document as a delegate for the senior manager. However, there is no documentation of any delegation of authority to that individual and it is therefore an invalid designation of authority to the other named delegates. The delegate designation document is the earliest documented evidence that SERC_URE2 has regarding its compliance with CIP-003 R2, more than three years after it was required to be compliant. After the delegate designation document was signed, SERC_URE2 failed in multiple instances to document changes to the senior manager and delegates within 30 calendar days of the effective dates of those changes. | CIP-003-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 personnel annually approved its risk-based assessment methodology (RBAM) and Critical Asset list. In addition, SERC_URE2 has no Critical Assets or Critical Cyber Assets (CCAs), and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE2 | when SERC_URE2 revised the designation and delegation document | $0 (for SERC2015014707, SERC2015014896, and SERC2015014897) | Self-Certification | To mitigate this violation, SERC_URE2: 1) revised the senior manager designation and delegation document to accurately reflect the current senior manager and delegates; 2) updated the compliance calendar to include a recurring 25-day reminder to check the employment status of each individual on the senior manager assignment document; and 3) worked with the corporate human resources team to implement an automated notification process of employees with changes to their employment status that will be sent directly to the corporate compliance team on a weekly basis. | 2015-12-18 | TBD | Admits | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE2 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE2 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE2 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE2 shall provide SERC with written updates on SERC_URE2's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE2 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE2 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE2 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE2 shall provide evidence at the next scheduled update showing SERC_URE2 documented the change within 30 days (in addition to providing its current list).
2016-02-29 | FERC | NP16-13-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2015014896 | Settlement Agreement | SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-002-3 R3. SERC_URE2 failed to develop a list of Critical Cyber Assets (CCAs) using its list of Critical Assets. SERC identified this issue while reviewing SERC_URE2's documentation for an associated issue and requested that SERC_URE2 submit a Self-Report. SERC later determined this issue dated back to Version 1 of the Standard. SERC_URE2 applied its risk-based assessment methodology (RBAM) and determined that it had no Critical Assets. SERC_URE2 erroneously interpreted the Standard and Requirement to require a CCA list only when the RBAM resulted in Critical Assets. Therefore, SERC_URE2 did not create a null list of CCAs using its null list of Critical Assets. SERC_URE2's misinterpretation of the Standard and Requirement is the primary cause of the issue. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 has no Critical Assets or CCAs, and is a minimal size entity. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2015014707, SERC2015014896, and SERC2015014897) | Self-Report | To mitigate this violation, SERC_URE2: 1) applied its RBAM to determine the list of Critical Assets and list of CCAs; 2) had the RBAM, list of Critical Assets, and list of CCAs approved by the designated CIP senior manager's delegate; 3) set up a process in which the corporate compliance team uses third-party software to auto-generate work orders and custom reporting for CIP-002 compliance obligations; and 4) created an event reminder in the corporate compliance calendar for annual review of the RBAM, list of Critical Assets, and list of CCAs. | 2016-01-28 | TBD | Admits | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. SERC_URE2 did not receive mitigating credit for self-reporting because the Self-Report was submitted after SERC identified the violation while reviewing SERC_URE2 documentation for an associated issue. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. In addition, SERC_URE2 has completed or agreed to complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination: a. SERC_URE2 shall provide SERC with its results after applying the Impact Rating Criteria required by CIP-002-5.1 R1 (using Attachment 1 to CIP-002-5.1). SERC_URE2 shall also provide evidence that the CIP Senior Manager or delegate reviewed and approved the CIP-002-5.1 R1 identifications, as required by CIP-002-5.1 R2. b. SERC_URE2 shall provide SERC with written updates on SERC_URE2's identification of, and any changes to, the CIP Senior Manager or delegate(s) identified pursuant to CIP-003-5 R3. SERC_URE2 shall provide updated CIP-003-5 R3 documentation to SERC on a scheduled basis. c. If no changes occur between updates, SERC_URE2 shall provide SERC the current documents identifying the CIP Senior Manager and any delegates and a statement that no changes have occurred since the last update. If the SERC_URE2 CIP Senior Manager or delegate(s) changes at any point before one of the scheduled updates, SERC_URE2 shall provide evidence at the next scheduled update showing SERC_URE2 documented the change within 30 days (in addition to providing its current list).
2016-02-29 | FERC | NP16-13-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012867 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-003-3 R2. Specifically, WECC_URE1 reported that it failed to assign a senior manager with overall responsibility for leading and managing the entity's implementation of, and adherence to, Standards CIP-002 through CIP-009, as required by CIP 003-3 R2. WECC later determined that this issue dated back to Version 1 of the Standard. WECC reviewed WECC_URE1's Self-Report and contacted WECC_URE1 to request additional information. Based on the information disclosed by WECC_URE1, WECC determined that WECC_URE1 also be in violation of CIP 003 R2 for not having a formally documented CIP Senior Manager. WECC_URE1 stated that it had three different CIP senior managers that were assumed responsible, but not formally documented, as required by CIP 003 R2.1. WECC determined that WECC_URE1 failed to assign and document a senior manager with overall responsibility for leading and managing the entity's implementation of, and adherence to, Standards CIP-002 through CIP-009, as required by CIP 003-1 R2. The root cause of the violation was a misunderstanding of the requirements of the standard, as WECC_URE1 previously assumed that CIP-003 R2 did not apply as WECC_URE1 does not have Critical Assets or Critical Cyber Assets (CCAs). | CIP-003-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to designate a CIP senior manager with overall responsibility for leading and managing the entity's implementation of, and adherence to, Standards CIP-002 through CIP-009. Failure to assign a senior manager for leading and managing the entity's implementation of CIP Standards increases the risk that due to a lack of executive supervision, the protective measures required by the CIP standards may not be adequately implemented. WECC_URE1 currently does not have any Critical Assets, or CCAs identified; however, without delegated management there is some risk that when new assets are added, they may not be identified or protected due to lack of management oversight. WECC_URE1 currently has seven miles of 115 kV lines and two step-down transmission substations. WECC_URE1 has strong preventive controls, to prevent devices from being unprotected. Specifically, at all times, there was one individual with overall responsibility for managing the CIP program. WECC_URE1 has emails and other media to demonstrate an individual was acting as CIP senior manager, but the individuals were never formally documented. Additionally, WECC_URE1 had good compensating controls. Specifically WECC_URE1 has limited access to the BPS containing only 7 miles of 115 kV lines and 2 step-down substations. WECC_URE1 also has one Under Frequency Load Shedding system, but it is not capable of shedding 300 MW or more. | when the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | No penalty | Self-Report | To mitigate this violation, WECC_URE1 created a document assigning a single senior manager with overall responsibility and authority for leading and managing WECC_URE1's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | 2013-09-05 | 2013-10-02 | Agrees/Stipulates | WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2016-02-29 | FERC | NP16-13-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014651 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it was in violation of CIP-002-3 R4. Specifically, WECC_URE1 reported that it failed to keep a signed and dated record of the senior manager or delegate(s)'s approval of the Risk-Based Assessment Methodology (RBAM), the list of Critical Assets, and the list of Critical Cyber Assets (CCAs). WECC reviewed WECC_URE1's Self Report and contacted WECC_URE1 to request additional information. WECC_URE1 stated that it reviewed the RBAM, the list of Critical Assets, and the list of CCAs; however, WECC_URE1 did not record or document the review process. Therefore, WECC_URE1 failed to keep a signed and dated record of the senior manager or delegate’s approval, as required by CIP-002-3 R4. WECC determined that WECC_URE1 failed to keep a signed and dated record of the senior manager or delegate's approval of the RBAM, the list of Critical Assets, and the list of CCAs. The root cause of the violation was an inadequate process. WECC_URE1's original RBAM document and process were not approved by WECC and WECC_URE1 created a (WECC approved) revised RBAM document and process; however, the current Doc Reminder pointed to the original RBAM document and process. In other words, the Doc Reminder referenced the original (RBAM) document and process and not the revised one. | CIP-002-3 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to keep a signed and dated record of the senior manager or delegate's approval of the RBAM, the list of Critical Assets and the list of CCAs. Failing to annually approve the RBAM may result in an ineffective RBAM being used to determine Critical Assets and CCAs. If Cyber Assets and CCAs are not discovered through an effective RBAM, the entity may not provide the appropriate CIP protections. WECC_URE1 implemented strong compensating measures to mitigate the risk of this issue. WECC_URE1 currently does not have any Critical Assets or CCAs. WECC_URE1 has 3 115 kV (radio) transmission lines that connect to 1 other entity and has 16 substations. | the beginning of the year in which WECC_URE1 failed to keep a record that it approved its RBAM, Critical Assets and CCAs lists | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, WECC_URE1: 1) reviewed and approved the RBAM, Critical Asset list, and CCA list; 2) updated the doc reminder to point to the new document; and 3) implemented use of filenet to keep track of documents. | 2015-02-17 | 2015-08-14 | Agrees/Stipulates | WECC considered WECC_URE1's compliance history to be an aggravating factor in the disposition of this violation.
2016-02-29 | FERC | NP16-11-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015059 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R2. Upon further review, this violation was later changed to CIP-007-3a R9, in which FRCC_URE1 failed to document changes resulting from modifications to the system within thirty days of the change being completed. Specifically, while conducting a Cyber Vulnerability Assessment, FRCC_URE1 discovered nine ports (all undocumented and enabled) for two Critical Cyber Assets (CCAs) and four non-CCAs. • Two ports were activated from the installation of firmware for two CCA storage arrays at the control center. The devices were added to an existing Technical Feasibility Exception (TFE). • Three ports were discovered for two non-CCAs at a station. Both of the assets were later decommissioned. • Three ports were discovered for one non-CCA at a station. The three assets were added to an existing TFE. • One port was discovered for one CCA at the control center. The device was replaced. The root cause of each of these violations is a lack of understanding of NERC's CIP-007 documentation requirements. | CIP-007-3a | R9 | Lower | High | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1 failing to properly document changes from its previous baseline of its ports and services scan, within 30 days, could have exposed its network system to malicious cyber attacks and could have impacted FRCC_URE1's operations. The risks were reduced because all devices referenced in this violation were located in an Electronic Security Perimeter (ESP) which restricts access to only approved known specific ports and services. This minimizes the risk of any malicious activity from outside the ESP, as the new ports and services activated on a Cyber Asset within the ESP would require modifications to the Access Point in order for traffic from outside to take advantage of the additions. Furthermore all the Cyber Assets were also located within a Physical Security Perimeter (PSP). A subsequent review of all Cyber Assets ultimately revealed that only ports and services required for normal and emergency operations were actually enabled. Also, none of the ports in question were observed by the network security controls and monitoring to have been exploited in any harmful manner. | when the first undocumented port was discovered | Mitigation Plan completion | $21,000 (for: FRCC2015015059, FRCC2015015112, and FRCC2015014923) | Self-Report | To mitigate this violation, FRCC_URE1: 1) decommissioned (due to pre-existing plans) assets which had 3 ports, at the station; 2) added 3 devices (5 ports) to existing TFEs. Internal documents to add these devices to the existing TFEs were signed by the CIP Senior Manager; 3) replaced the device (located at the control center) associated with the 9th port. The device was replaced with new hardware, as well as upgraded with a new operating system; and 4) reviewed with applicable team members the interim procedure for establishing the ports and services baselines for consistency. | 5/29/2015 | 2015-12-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's CIP-007-3a R9 compliance history to be an aggravating factor in the penalty determination. These violations evaluated individually were minimal or moderate risk. However, there was a trend identified through repeat violations that increased the risk to reliability that resulted in additional focus through Spreadsheet Notice of Penalty (SNOP) and Settlement.
2016-02-29 | FERC | NP16-11-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015015112 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. FRCC_URE1 failed to afford the protective measures specified in CIP-003-3 R6 as it relates to protecting Physical Access Control Systems (PACS). Specifically, this violation concerns two instances where PACS-related devices were not afforded the protective measures specified in Standard CIP-003-3 R6 (Change Control and Configuration Management). FRCC_URE1 did not properly document the adding, modifying, or replacing of PACS application devices. Case #1 - a FRCC_URE1 employee requested that a workstation be re-defined (re-configured) to the PACS application without it being procedurally being processed (tested and documented), as per the protections of CIP-006-3 R2.2. Upon discovering the error of adding the workstation to the PACS application, a formal removal request was completed, and properly documented, to remove the asset from the PACS application approximately two months later. Case #2 - a PACS server was procedurally processed (tested and documented) to the PACS application. However, the associated Integrated Lights Out (iLO) for managing the server was not identified as a Cyber Asset and not procedurally processed at the same time as the server because it was not on the cyber asset list. A cyber security analyst discovered during a periodic logging review that the device was not on the cyber asset list. A formal request was submitted to have the asset processed and added to the PACS application and the device was processed as a cyber asset five days later. The root cause for both noncompliances was poor understanding/training of the onboarding (procedurally processing: verifying, testing, and documenting) process. | CIP-006-3c | R2 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The devices were secured in a Physical Security Perimeter (PSP), and could only be accessed by authorized personnel. In the first instance, the workstation (Device #1) was being managed by the corporate enterprise tools, and the devices received frequent Anti-Virus signatures and security patches. In the second instance, the absence of procedurally processing the iLO did not significantly increase the risk to the BPS. This iLO device is only capable of supporting a limited number of NERC-required security controls. If, in a worst case scenario event, the iLO was misused, the PACS server could be made unresponsive. However, the controls at the doors (allowing/disallowing access) would still function and logs would still be produced. Once the devices became responsive again, the logs and alerts would be sent to the central PACS server. During the time the devices are unresponsive, the guards would not receive alarms concerning the door status for propped door or forced door. However, the guards would recognize that the application was not responsive and would respond by activating established compensating procedures. | when the first workstation was re-defined to the PACS application | Mitigation Plan completion | $21,000 (for: FRCC2015015059, FRCC2015015112, and FRCC2015014923) | Self-Report | To mitigate this issue, FRCC_URE1: 1) removed Device #1 workstation from the PACS application; 2) trained responsible facility services personnel on the change control and configuration management process; 3) added facility services as an implementer to the change control and configuration management process; 4) communicated to applicable employees on the addition of facility services as an implementer for the change management of PACS assets; 5) onboarded Device #2 iLO as a PACS asset with associated protections; 6) reviewed change management process and procedures with staff. | 2015-07-28 | 2015-12-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's CIP-003-3 R6 compliance history to be an aggravating factor in the penalty determination. These violations evaluated individually were minimal or moderate risk. However, there was a trend identified through repeat violations that increased the risk to reliability that resulted in additional focus through Spreadsheet Notice of Penalty (SNOP) and Settlement.
2016-02-29 | FERC | NP16-11-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014923 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. FRCC_URE1 had failed to perform a personnel risk assessment (PRA) on an individual employee before granting electronic access to Physical Access Control System (PACS) servers as required by the protective measure of CIP-004-3 R3. A special order request was submitted to FRCC_URE1 Human Resources (HR) to grant an employee NERC access to the PACS servers who will be working on access administration activities for its operations. Because the employee PRA data is not yet tracked in the FRCC_URE1 HR system, the access administration analyst was unable to verify if the employee had a current PRA. Internal controls discovered the error when the access showed up on the PRA exception report, but because the report was not being reviewed daily, it was not discovered until approximately ten days later. Access was subsequently removed. A manager coordinated with HR to have the background check performed. The PRA was completed by HR three days later with no disqualifying issues. All other protective measures of CIP-006-3c R2.2 were maintained. The root cause was poor understanding/training related to the importance of reviewing the exception report on a daily basis amongst FRCC_URE1 HR employees. If this report would have been checked, they would have found that the employee did not have the PRA approval. | CIP-006-3c | R2; R2.2 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). An unauthorized employee that had not undergone a PRA was mistakenly given access to PACS workstations and associated servers. Access to PACS workstations and physical access control servers could have been used to manipulate physical access to Physical Security Perimeters (PSPs), which would have left workstations vulnerable to physical attacks, and could have potentially provided an attacker with physical access to restricted areas. However, in this particular case, the risk was greatly reduced because the employee had not yet been given a PACS operator account, and therefore could not have logged into the PACS system to provide or alter card key access. Therefore, even if PACS devices could have been made unresponsive, the controls at the doors (allowing/disallowing access) would have still functioned and logs would have still been produced. Once the devices were made responsive again, the logs and alerts would be sent to the central PACS server. The risk was also reduced because the employee was a long-term trusted employee for fourteen years, and had received required NERC training before being granted access. The PRA was promptly conducted without any disqualifying issues. | when the unauthorized access was provided | when the unauthorized access was removed | $21,000 (for: FRCC2015015059, FRCC2015015112, and FRCC2015014923) | Self-Report | To mitigate this issue, FRCC_URE1: 1) removed access for the employee in question; 2) conducted a PRA for the employee; 3) updated the procedure for reviewing the exception report, and relevant staff was coached on reviewing the exception report on a daily basis; and 4) developed a process for verifying active PRAs for its employees before granting NERC access. | 4/17/2015 | 2015-12-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's CIP-006-3c R2.2 compliance history to be an aggravating factor in the penalty determination. These violations evaluated individually were minimal or moderate risk. However, there was a trend identified through repeat violations that increased the risk to reliability that resulted in additional focus through Spreadsheet Notice of Penalty (SNOP) and Settlement.
2016-02-29 | FERC | NP16-6-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013014 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-003-1 R6. Specifically, MRO_URE1 did not establish and document a change management process that addressed all possible entity- or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs). MRO observed that the MRO_URE1 change management process allowed for non-significant changes to occur without being documented. During the audit, MRO found one change to a database where MRO_URE1 could not identify how or why the change occurred, and it was not documented. It was discovered that this database change was approved and appropriate, however, it was not documented as required by CIP-003-1 R6. MRO determined that the MRO_URE1 change management process did not require in every instance documenting changes to hardware, rebooting a system, or changing the power sources, as MRO_URE1 considered these to be non-significant changes. The cause of this violation was a misunderstanding of the Requirement to document all entity- or vendor-related changes to hardware and software components of CCAs. MRO_URE1 had implemented a process to consider all changes, but did not require that the changes determined to be non-significant be documented according to its change management process. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although, MRO_URE1 had implemented a documented change management process, that process only tracked significant changes instead of all changes as required by the Standard. The failure to document changes could result in MRO_URE1 spending additional time investigating system issues because it did not have the documentation related to all system changes, which may prolong any event or issue. MRO also considered that MRO_URE1 performed a system scan of the affected system, but it did not document any analysis or review the results of the system scan, which could have revealed a system issue. MRO considered the following factors that reduced the risk of the violation: 1) MRO_URE1 annually tests its recovery plan for CCAs; 2) MRO_URE1 has processes and procedures in place to restore its CCAs; 3) MRO_URE1 utilizes anti-virus software and other measures; 4) MRO_URE1 provides its CCAs some measure of protection from physical attacks by keeping its CCAs within an effective Electronic Security Perimeter (ESP); 5) MRO_URE1 has maintained, documented, and implemented a physical security plan that offers a level of protection to its CCAs; 6) MRO_URE1 performs annual vulnerability assessments; and 7) MRO_URE1 utilizes technically feasible automated tools or controls that monitor system events that are related to cyber security. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 modified its change management process to document all entity- or vendor-related changes to CCAs | $75,000 (for MRO2013013014, MRO2013013017, MRO2013013018, MRO2013013021, and MRO2013013022) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) reviewed the current change control process and determined it needed to revise the decision tree within its change control process document so that it includes all the changes and not just the ones identified as significant; 2) evaluated all of the existing internal change control options and multiple external control tools; 3) reviewed the number of nonsignificant changes that have made been made since MRO_URE1 updated its decision tree and procedure; MRO_URE1 estimated there were approximately 240 changes that would have been classified as non-significant changes; 4) compared external and internal change control options and control tool capabilities for sufficient change control tracking and evidence collection; and 5) signed a contract with a set implementation schedule to implement a product that will meet the CIP V3 and V5 requirements. To mitigate this violation, MRO_URE1 will upgrade its change management system. | 2/26/2016 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. MRO_URE1 cooperated fully with MRO's investigation and MRO considered MRO_URE1's cooperation to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance. A possible violation of CIP-003-1 R6 against an affiliate entity was consolidated into this violation. MRO has determined that MRO_URE1 and the affiliate entity are equally responsible for the monetary penalty.
2016-02-29 | FERC | NP16-6-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013017 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-005-1 R1. Specifically, MRO_URE1 violated CIP-005-1 R1.5 by violating the requirements of CIP-003-1 R6 (change control and configuration management) and CIP-007-1 R1 (test procedures). MRO_URE1 violated CIP-003-1 R6 by failing to establish and document a change management process that addressed all possible entity- or vendor-related changes to hardware and software components, as addressed above in MRO2013013014. MRO_URE1 violated CIP-007-1 R1 by utilizing incomplete test procedures to perform cyber security testing, as addressed in MRO2013013021. This violation resulted from the requirement in CIP-005-1 R1.5 to afford the protective measures specified in Standard CIP-003-1 R6 and CIP-007-1 R1 to Cyber Assets used in the access control and monitoring of the Electronic Security Perimeters (ESPs). The cause of the CIP-003-1 R6 violation was a misunderstanding of the Requirement to document all entity- or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs) and the CIP-007-1 R1 violation is the result of a weak procedure. The MRO_URE1 procedure was incomplete and did not list the test steps to be performed, which led to the failure to produce sufficient evidence to demonstrate the testing that was performed, the test steps, or the test procedures. | CIP-005-1 | R1: R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, MRO_URE1 could introduce undocumented changes and MRO_URE1 would have to spend additional time investigating system issues because it did not have the documentation related to all system changes, which may prolong any event or issue. Although MRO_URE1 had implemented a change management procedure, it only tracked significant changes instead of all changes as required by CIP-003-1 R6. Additionally, MRO_URE1 performed a system scan of the affected system, but it did not document any analysis or review the results of the system scan. Further, MRO_URE1 may have adversely impacted the security of its CCAs by applying changes without utilizing the required cyber security control in CIP-007-1 R1. MRO considered the risk of this violation was reduced by the following factors: 1) MRO_URE1 annually tests its recovery plan for CCAs; 2) MRO_URE1 has processes and procedures in place to restore its CCAs; 3) MRO_URE1 utilizes anti-virus software and other measures; 4) MRO_URE1 provides its CCAs some measure of protection from physical attacks by keeping its CCAs within an effective ESP; 5) MRO_URE1 has maintained, documented, and implemented a physical security plan that offers a level of protection to its CCAs; 6) MRO_URE1 performs annual vulnerability assessments; and 7) MRO_URE1 utilizes technically feasible automated tools or controls that monitor system events that are related to cyber security. | when the Standard became mandatory and enforceable | present | $75,000 (for MRO2013013014, MRO2013013017, MRO2013013018, MRO2013013021, and MRO2013013022) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the testing procedures to cover procedures to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; 2) reviewed the current change control process and determined it needed to revise the decision tree within its change control process document so that it includes all the changes and not just the ones identified as significant; 3) reviewed the security testing procedures and confirmed it has the ability to verify all security testing controls but determined there was a need to modify its processes or tool sets in order to collect sufficient evidence; 4) compared external and internal change control options and control tool capabilities for sufficient change control tracking and evidence collection; 5) modified the security testing process to include all required security controls; 6) evaluated external security testing tools and practices and decided to implement an enterprise service management software in conjunction with internal tools to achieve NERC CIP security testing requirements; 7) reviewed the number of nonsignificant changes that have been made since MRO_URE1 updated its decision tree and procedure; MRO_URE1 estimated there were approximately 240 changes that would have been classified as non-significant changes; and 8) signed a contract with a set implementation schedule to implement a product that will meet the CIP V3 and V5 requirements. To mitigate this violation, MRO_URE1 will: 1) document test results to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; and 2) implement a new change control and security testing processes in development and testing environments and then into production. | 2/26/2016 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. MRO_URE1 cooperated fully with MRO's investigation and MRO considered MRO_URE1's cooperation to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance. A possible violation of CIP-005-1 R1 against an affiliate entity was consolidated into this violation. MRO has determined that MRO_URE1 and the affiliate entity are equally responsible for the monetary penalty.
2016-01-28 | FERC | NP16-6-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013018 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-006-1 R1. Specifically, MRO_URE1 violated CIP-006-1 R1 by violating the requirements of CIP-007-1 R1. MRO_URE1 violated CIP-007-1 R1 by utilizing incomplete test procedures to perform cyber security testing, as addressed in MRO2013013021. This violation resulted from the requirement in CIP-006-1 R1.8 to afford the protective measures specified in Standard CIP-007-1 R1 to Cyber Assets used in the access control and monitoring of the Physical Security Perimeters (PSPs). The CIP-007-1 R1 violation is the result of a weak procedure. The MRO_URE1 procedure was incomplete and did not list the test steps to be performed, which led to the failure to produce sufficient evidence to demonstrate the testing that was performed, the test steps, or the test procedures. | CIP-006-1 | R1: R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, MRO_URE1 may have adversely impacted cyber security by not documenting or implementing testing procedures prior to initiating a change. Although MRO_URE1 had a change management procedure and was tracking significant changes, the evidence of testing of adverse impacts on security controls was incomplete. Additionally, MRO_URE1 performed a system scan of the affected system, but it did not document any analysis or review the results of the system scan, which could have revealed a system issue. MRO considered the following factors that reduced the risk of the violation: 1) MRO_URE1 annually tests its recovery plan for Critical Cyber Assets (CCAs); 2) MRO_URE1 has processes and procedures in place to restore its CCAs; 3) MRO_URE1 utilizes anti-virus measures; 4) MRO_URE1 provides its CCAs some measure of protection from physical attacks by keeping its CCAs within an effective ESP (Electronic Security Perimeter); 5) MRO_URE1 has maintained, documented, and implemented a physical security plan that offers a level of protection to its CCAs; 6) MRO_URE1 performs annual vulnerability assessments; and 7) MRO_URE1 utilizes technically feasible automated tools or controls that monitor system events that are related to cyber security. | when the Standard became mandatory and enforceable | present | $75,000 (for MRO2013013014, MRO2013013017, MRO2013013018, MRO2013013021, and MRO2013013022) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the testing procedures to cover procedures to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; 2) reviewed the current change control process and determined it needed to revise the decision tree within its change control process document so that it includes all the changes and not just the ones identified as significant; 3) reviewed the security testing procedures and confirmed it has the ability to verify all security testing controls but determined there was a need to modify its processes or tool sets in order to collect sufficient evidence; 4) compared external and internal change control options and control tool capabilities for sufficient change control tracking and evidence collection; 5) modified the security testing process to include all required security controls; 6) evaluated external security testing tools and practices and decided to implement an enterprise service management software in conjunction with internal tools to achieve NERC CIP security testing requirements; 7) reviewed the number of nonsignificant changes that have made been made since MRO_URE1 updated its decision tree and procedure; MRO_URE1 estimated there were approximately 240 changes that would have been classified as non-significant changes; and 8) signed a contract with a set implementation schedule to implement a product that will meet the CIP V3 and V5 requirements. To mitigate this violation, MRO_URE1 will: 1) document test results to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; and 2) implement a new change control and security testing processes in development and testing environments and then into production. | 2/26/2016 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. MRO_URE1 cooperated fully with MRO's investigation and MRO considered MRO_URE1's cooperation to be a mitigating factor in the penalty determination. MRO considered the compliance history of MRO_URE1 and its affiliate entity in determining the penalty. MRO determined that MRO_URE1's compliance history should not serve as a basis for aggravating the penalty. A possible violation of CIP-006-1 R1 against an affiliate entity was consolidated into this violation. MRO has determined that MRO_URE1 and the affiliate entity are equally responsible for the monetary penalty.
2016-01-28 | FERC | NP16-6-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013021 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1, was in violation of CIP-007-1 R1. Specifically, MRO_URE1 had incomplete test procedures to perform required cyber security testing. The procedures did not include the required testing steps, nor did they include specific requirements to retain testing evidence to support compliance. During the Compliance Audit, MRO staff performed sampling and discovered three changes to Critical Cyber Assets (CCAs) that did not have sufficient documentation regarding the testing procedure. Further, the documentation of testing evidence that did exist failed to address multiple controls including user/system accounts and passwords, logging, and ports and services. The cause of the violation is a weak procedure. The MRO_URE1 procedure was incomplete and did not list the test steps to be performed, which led to the failure to produce sufficient evidence to demonstrate the testing that was performed, the test steps, or the test procedures. | CIP-007-1 | R1; R1.1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, MRO_URE1 may have adversely impacted the security of its CCAs by applying changes without utilizing the required cyber security controls. Although MRO_URE1 had a change management procedure and was tracking significant changes, the evidence of testing of adverse impacts on security controls was incomplete. Additionally, MRO_URE1 performed a system scan of the affected system, but it did not document any analysis or review the results of the system scan, which could have revealed a system issue. MRO considered the following factors that reduced the risk of the violation: 1) MRO_URE1 annually tests its recovery plan for CCAs; 2) MRO_URE1 has processes and procedures in place to restore its CCAs; 3) MRO_URE1 utilizes anti-virus measures; 4) MRO_URE1 provides its CCAs some measure of protection from physical attacks by keeping its CCAs within an effective ESP (Electronic Security Perimeter); 5) MRO_URE1 has maintained, documented, and implemented a physical security plan that offers a level of protection to its CCAs; 6) MRO_URE1 performs annual vulnerability assessments; and 7) MRO_URE1 utilizes technically feasible automated tools or controls that monitor system events that are related to cyber security. | when the Standard became mandatory and enforceable | present | $75,000 (for MRO2013013014, MRO2013013017, MRO2013013018, MRO2013013021, and MRO2013013022) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the testing procedures to cover procedures to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; 2) reviewed the current change control process and determined it needed to revise the decision tree within its change control process document so that it includes all the changes and not just the ones identified as significant; 3) reviewed the security testing procedures and confirmed it has the ability to verify all security testing controls but determined there was a need to modify its processes or tool sets in order to collect sufficient evidence; 4) compared external and internal change control options and control tool capabilities for sufficient change control tracking and evidence collection; 5) modified the security testing process to include all required security controls; 6) evaluated external security testing tools and practices and decided to implement an enterprise service management software in conjunction with internal tools to achieve NERC CIP security testing requirements; 7) reviewed the number of nonsignificant changes that have made been made since MRO_URE1 updated its decision tree and procedure; MRO_URE1 estimated there were approximately 240 changes that would have been classified as non-significant changes; and 8) signed a contract with a set implementation schedule to implement a product that will meet the CIP V3 and V5 requirements. To mitigate this violation, MRO_URE1 will: 1) document test results to minimize adverse effects on the following existing cyber security controls (a) user/system accounts & passwords, (b) logging, and (c) ports and services; and 2) implement a new change control and security testing processes in development and testing environment and then into production. | 1/29/2016 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. MRO_URE1 cooperated fully with MRO's investigation and MRO considered MRO_URE1's cooperation to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance. A possible violation of CIP-007-1 R1 against an affiliate entity was consolidated into this violation. MRO has determined that MRO_URE1 and the affiliate entity are equally responsible for the monetary penalty.
2016-01-28 | FERC | NP16-6-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013022 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-007-3a R2. Specifically, MRO_URE1 did not ensure that all ports and services required were documented and approved in its baseline documentation. MRO_URE1 did not completely identify the ports and services required for normal and emergency operations in its baseline for two of the six devices sampled during the audit. These two sampled devices contained open ports that were not accurately documented in MRO_URE1's baseline documentation of ports and services. One of the two sampled devices with an undocumented open port was used for backing up data for the Energy Management System (EMS) and other NERC CIP devices in the Electronic Security Perimeter (ESP). It was a network storage device in the ESP. If this system were compromised, and data unavailable, it could impact recovery of Critical Cyber Assets (CCAs). The other sampled device with an undocumented open port was on a virtual machine. If this virtual machine were compromised, there is a possibility that other virtual machines on the same host could have become compromised. The other virtual machines on the same host supported the Inter-Control Center Communications Protocol (ICCP), Data Acquisition, Historian, and supervisory control and data acquisition (SCADA) virtual machines for MRO_URE1. There was a risk that these machines could have been affected by compromising the Front End Processor (FEP device). The cause of this violation was the reliance on inaccurate system scan results. MRO_URE1 used an external program for its initial baseline documentation of ports and services. Those results were not accurate. Utilizing an internal system command resulted in the identification of more ports than the external program scan. | CIP-007-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The ports and services were eventually listed as ‘required’ by MRO_URE1, but the ports and services were not on the formal baseline as required by the Reliability Standard. Ports and services that are left open unnecessarily can potentially introduce a larger attack surface that adversaries may be able to exploit. However, MRO considered the risk of this violation was reduced by the following factors: 1) MRO_URE1 utilizes anti-virus software and other measures; 2) MRO_URE1 provides its CCAs some measure of protection from physical attacks by keeping its CCAs within an effective ESP; 3) MRO_URE1 has maintained, documented, and implemented a physical security plan that offers a level of protection to its CCAs; and 4) MRO_URE1 utilizes technically feasible automated tools or controls that monitor system events that are related to cyber security | when the earliest sampled device with an undocumented open port was deployed | when MRO_URE1 added the ports to the baseline | $75,000 (for MRO2013013014, MRO2013013017, MRO2013013018, MRO2013013021, and MRO2013013022) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) immediately added the identified ports and services to the baseline documentation as they were all deemed as necessary; 2) performed a comprehensive review of all CCAs to ensure the ports and services are correctly listed in the baseline documentation. To mitigate this violation, MRO_URE1 will review all CCAs, Physical Access Control System devices, and access points to ascertain if there are any more CIP devices that do not have their baselines properly documented. If MRO_URE1 determines that any baseline edits are needed, MRO_URE1 will update the baselines so that the final baseline will be accurate. Any discrepancies will be reported to MRO per this milestone. This will include a report for the most recent baselines. | 2/29/2016 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. MRO_URE1 cooperated fully with MRO's investigation and MRO considered MRO_URE1's cooperation to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance. A possible violation of CIP-007-3 R2 against an affiliate entity was consolidated into this violation. MRO has determined that MRO_URE1 and the affiliate entity equally responsible for the monetary penalty.
2015-12-30 | FERC | NP16-6-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013394 | Settlement Agreement | SERC_URE1 submitted a Self-Certification to SERC stating that it was in violation of CIP-005-3a R2. SERC_URE1 reported that it failed to document, individually or by specified grouping, the configuration of the ports and services at all access points to the Electronic Security Perimeter (ESP) required for operations and for monitoring Cyber Assets within the ESP. During a third-party vendor mock CIP audit, SERC_URE1 discovered that neither the prior year cyber vulnerability assessment (CVA) report nor the ports and services baseline document contained the required business justification for all enabled ports and services. SERC_URE1 failed to document the justification for open ports and services on four electronic access points protecting two ESPs. SERC_URE1 had 88 Critical Cyber Assets (CCAs) within the affected ESPs. SERC reviewed SERC_URE1's final CVA report with the supporting evidence and learned that there were 51 instances where ports and services were enabled through the firewall but the enabled ports and services were not justified or required to be enabled on the Cyber Assets contained within. The root cause of this violation was a failure by SERC_URE1 to properly train its personnel on the procedure for documenting ports and services under CIP-005 after transitioning from its old energy management system (EMS) to its new EMS. | CIP-005-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1's failure to document the required business justification for all enabled ports and services and disable unnecessary ports and services at access points to the ESPs could increase the attack surface into the ESP and allow an unauthorized person to gain access to CCAs within an ESP and disrupt the normal operations of those CCAs. However, SERC_URE1's ESP firewalls were protected behind multiple firewalls within the corporate network, and electronic security monitoring was deployed. The firewalls were located within a Physical Security Perimeter and thus afforded physical access controls. SERC_URE1 also required two-factor authentication to access the CCAs. SERC_URE1 subsequently determined that all but two of the enabled ports and services were required for operations or monitoring of Cyber Assets within the ESP. In addition, a SERC audit team subsequently conducted an on-site review and found no further concerns regarding CIP-005 R2. | when SERC_URE1 transitioned to a new EMS without justifying open ports and services | Mitigation Plan completion | $35,000 (for SERC2014013394 and SERC2014014449) | Self-Certification | To mitigate this violation, SERC_URE1: 1) conducted training for personnel dealing with CIP-005 standards; 2) closed two open ports on two sets of firewalls; and 3) conducted an analysis of firewall rules to verify all open ports were justified. | 2014-08-11 | 2015-09-10 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014449 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-005-3a R1. SERC_URE1 did not afford its electronic access control and/or monitoring (EACM) devices the protective measures specified in CIP-007-3 R3.2. Specifically, SERC_URE1 failed to implement security patches that had been assessed for EACM devices and it did not document compensating measures applied to mitigate risk exposure for patches that were not installed on the EACM devices. SERC_URE1 assessed 11 cyber security patches as applicable to Electronic Security Perimeter (ESP) access points (firewalls) within 30 days. However, SERC_URE1 did not deploy or schedule these 11 security patches for deployment or document any compensating measures to mitigate risk exposure for the patches that were not installed. During the Compliance Audit, SERC_URE1 subject matter experts stated that SERC_URE1 had prior operational difficulties and issues while attempting to deploy security patch updates to the firewalls, so SERC_URE1 was reluctant to pursue deployment for these. The vendor had issued workarounds for most of the vulnerabilities that the patches were to remediate. However, there is no evidence to demonstrate that SERC_URE1 ever considered or reviewed the workarounds for possible mitigation of the vulnerabilities. According to SERC_URE1 subject matter experts, prior to the start of the Compliance Audit, SERC_URE1 documented the compensating measures in place for the 11 security patches, and scheduled implementation of the patches to occur. The root cause of this issue was a lack of adherence to internal SERC_URE1 procedures because SERC_URE1 had prior operational difficulties while attempting to deploy security patch updates to the firewalls. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1's failure to deploy security patches or document compensating measures for security patches that were not deployed for more than two years left known vulnerabilities available on access points to the ESP without documented compensating measures, potentially providing an attack vector for malicious individuals. Any external user must first use a virtual private network to gain access to the SERC_URE1 corporate network before SERC_URE1 would grant access to any CIP-protected network. SERC_URE1 restricts the use of email within all ESPs through technology-based solutions, reducing the possible attack vectors for an exploit of the unpatched security vulnerabilities. Intrusion detection systems, in combination with access and security alerts, were in place to monitor systems and detect and alert on any unauthorized access events. The firewalls in question are located between the control centers and field devices and do not connect directly to the corporate network nor provide connectivity to the internet. | 31 days after the initial patch was released and subsequently assessed for applicability with no implementation plan created and no compensating measure documented | when SERC_URE1 implemented the 11 security patches | $35,000 (for SERC2014013394 and SERC2014014449) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) installed the patches in question; 2) updated its patch management process to require the evaluation, documentation, and approval of compensating/mitigating measures for each applicable patch that is assessed regardless of planned installation date; and 3) conducted security patch/upgrade process document training. | 2014-12-10 | 2015-07-26 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. . SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013850 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. WECC_URE1 failed to ensure visitors and employees logged initial and all entry and exits to and from Physical Security Perimeters (PSPs). Specifically, WECC_URE1 reported that for two days, it worked on a fire suppression project at its headquarters, involving two contractors with several employees. WECC_URE1 assigned two employees to the project. The project was located in two controlled CIP spaces, a communications room, and an adjoining control center which contains a combined total of 15 assets (six Critical Cyber Assets (CCAs) capable of controlling WECC_URE1's energy management system (EMS), three Physical Access Control (PAC) devices, one firewall, one Access Control Monitoring (ACM) device, and four access points. A WECC_URE1 employee was on site and served as an escort for the contractors. However, the WECC_URE1 employees allowed the contractors to enter and exit the controlled CIP spaces without being logged into WECC_URE1's controlled area visitor log (visitor log), as required by WECC_URE1's Physical Security Plan. A WECC_URE1 employee did log an initial entry and final exit to the visitor log; however, the WECC_URE1 employees did not log every entry and exit of each contractor, as is required by WECC_URE1's Physical Security Plan. In addition, one WECC_URE1 employee did not log himself into the controlled area. WECC_URE1 submitted a second Self-Report stating that it was in violation of CIP-006-3c R1. WECC_URE1 failed to manually log all access into and out of a PSP and failed to appropriately use physical access controls. WECC_URE1 reported that several people entered a PSP without swiping their badge to log access. WECC reviewed WECC_URE1's Self-Reports and determined that, in the first instance, WECC_URE1 failed to ensure employees logged initial and all entry and exits to and from PSPs. Specifically, during work on the fire suppression system, an employee tailgated behind another employee and thus did not use the employee's badge to log the entrance. Both of the employees were authorized for access to the PSP. Additionally, WECC determined that WECC_URE1 failed to ensure visitors logged each entry to and exit from PSPs. While working on the fire suppression system, the six workers were required to enter and exit the PSP multiple times, but only logged the initial entrance and final exit through the PSP. The root cause for this instance was that personnel failed to follow proper procedures for logging access to PSPs. WECC also determined that, in the second instance, WECC_URE1 failed to ensure that employees logged each entry and exit from all PSPs. Specifically, four authorized employees allowed three separate unauthorized employees to enter and exit two PSPs (tailgating) because the three employees did not have authorized physical access to the PSP. As a result of their examination, WECC determined that WECC_URE1 was in violation of CIP-006-3c R1. WECC determined that WECC_URE1 was in violation of CIP-006-3c R1 for its failure to log all access in and out of a PSP (R1.6) and for its failure to ensure the appropriate use of physical access controls (R1.4). The root cause for this instance was that employees failed to implement their training regarding access procedures per its policies and procedures. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to log all access into and out of a PSP and failed to ensure the appropriate use of physical access controls. WECC_URE1's failure to appropriately log access to its control center could have resulted in these visitors’ unauthorized access to the CCAs within the control center to go unnoticed and unchecked. WECC_URE1 did implement strong preventative controls to prevent access and harm to the CCAs. Specifically, WECC_URE1 ensured all visitors were escorted at all times by authorized personnel reducing the likelihood of a visitor obtaining unauthorized access to CCAs. The escorts were personnel with access to the PSPs who were trained on the proper use of CCAs and vetted with a seven-year background check. Additionally, WECC_URE1's security personnel monitored the physical access points in scope by CCTV cameras that track and uniquely identify each visitor’s entrance and exit, reducing the likelihood that a visitor could gain unauthorized access to PSPs without being noticed or checked by security personnel. WECC_URE1 also implemented strong detective controls to detect any access and harm to the CCAs. Specifically, WECC_URE1 implemented physical security monitoring controls that would alert operators of any access into the control center, and WECC_URE1 operators are trained to call the control center to verify who was inside. If the operators could not identify who was inside the PSP, procedures required the operators to contact security to further investigate. In addition, WECC_URE1's control center was able to detect any unauthorized or suspicious configuration changes to the EMS settings. The control center was operated 24 hours a day, seven days a week, so the operators could mitigate any detected suspicious activity occurring within the control center. | the earliest date that a possible visitor logging issue was identified | Mitigation Plan completion | $0 (for WECC2014013850, WECC2015014620, WECC2014014503, and WECC2014014498) | Self-Report | To mitigate this violation,WECC_URE1: 1) gave the involved WECC_URE1 employees verbal coaching, counseling, and remedial training regarding proper logging, escorting, and PSP job planning procedures under WECC_URE1's Physical Security Plan; 2) gave the involved WECC_URE1 employees notes in their personnel files as a means of discipline. Both employees recognized the seriousness of the incident; 3) provided guidance via e-mail to all employees with unescorted access to CIP controlled areas. This guidance focused on escort responsibilities, including logging procedures and WECC_URE1's PSP job planning procedure; 4) Security personnel and Reliability Compliance personnel met with Engineering and Project Management personnel to discuss the seriousness of the incident, review escort responsibilities and logging procedures, and to discuss WECC_URE1's PSP job planning procedure; 5) held various meetings to discuss compliance risk and access as part of WECC_URE1's Internal Compliance Program (ICP). WECC_URE1 determined that the number of individuals with unescorted access to CIP spaces should be decreased. This will increase the contact that WECC_URE1 employees have with WECC_URE1's Security Department. The reduction of the number of employees with unescorted access was completed; 6) had its Security Department develop two new online training modules which focus on proper access, logging, and escorting responsibilities in WECC_URE1's CIP spaces. One is a quiz module. WECC_URE1 assigned both of these modules as mandatory training to individuals who frequently access CIP spaces and who escort contractors. All WECC_URE1 employees that were assigned this training completed it; 7) developed a “CIP-at-a-Glance” resource intranet webpage that contains key, easily accessible information relating to CIP-006 and other procedures. The “CIP-at-a-Glance” webpage is accessible via link from WECC_URE1's intranet. The “CIP-at-a-Glance” webpage became active, and a notification and link for the webpage were provided in WECC_URE1's newsletter; 8) developed a periodic PSP reporting process requiring certain project management supervisors to report to WECC_URE1's Security Department personnel regarding work or projects scheduled to occur within CIP spaces. This process will help to ensure job plans are developed and CIP awareness is increased; 9) gave a “Lessons Learned” presentation at a WECC_URE1 meeting in an effort to increase CIP Awareness, maintain transparency and openness, and further WECC_URE1's strong Culture of Compliance; 10) had its Security Program Administrator speak with an employee involved in that incident. He discussed the issue that was occurring with the employee and reiterated the proper procedure for logging authorized unescorted physical access. He further asked the employee to discuss this matter and information with the rest of the wiremen on site that day. Both conversations were intended to prevent further occurrences and to educate and remind WECC_URE1 employees of proper procedures under its Physical Security Plan and relevant requirements; 11) implemented an internal compliance investigation, which is part of its Reliability Compliance Program. These investigations are detective controls that lead to other preventative controls, such as training, coaching and counseling and process improvements; 12) provided all WECC_URE1 employees involved in the incident remedial training utilizing the CIP Cyber Security Training PowerPoint. They were additionally provided verbal coaching by a supervisor. Retraining regarding appropriate access procedures occurred for all WECC_URE1 wiremen working at all locations involved in the incidents also occurred during this timeframe; 13) held two meetings with the director and supervisors to discuss the importance of three cultures: security, reliability and compliance; 14) emailed all employees with authorized unescorted access to CIP spaces concerning appropriate procedures and held meetings with working groups to discuss physical access. Also WECC_URE1 added additional signage to System Operations to remind employees about tailgating and logging; 15) installed a second visitor log in the System Operations area to make it simpler for exit logging of visitors from within that space and disabled a second entry badge reader pending relocation of the badge reader at main entrance; 16) held a collaborative session with a cross-section of employees to discuss solutions to tailgating and logging issues; 17) painted the outside/entrance door at a Switchyard yellow to identify it as a CIP location; 18) reduced the number of employees who had CIP access rights; 19) relocated the badge reader at a CIP location to allow for easier access for badge swiping; 20) added additional supervisors to WECC_URE1's weekly PSP reporting process and the director personally met with the three control system engineers involved in the incident to discuss root cause and physical access procedures; 21) held a meeting with the supervisors of all individuals who are authorized for unescorted access to discuss the seriousness of these issues, proper procedures and expectations; 22) disabled access to CIP spaces through certain doors and posted Security Guards at the entrances to WECC_URE1's four CIP spaces on an interim basis. WECC_URE1 also implemented an interim visitor access procedure that prevents any visitors in CIP spaces without prior approval from WECC_URE1's CIP Senior Manager (or designee); and 23) had a WECC_URE1 Senior Manager (or designee) approve the Physical Security Plan modifying the headquarters control center consolidating two Physical Security Perimeters. The Physical Security Plan includes procedures for the use of video as compensating logging control. | 1/20/2015 | 9/30/2015 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to the above-listed Mitigation Activities for the violations contained in this Settlement Agreement, WECC_URE1 chose to continue its efforts to eliminate tailgating and logging issues by purchasing preventative turnstiles and laser tailgating detection technology, which is being installed at each of its locations containing CCAs. This project is a direct result of the violations contained in this Settlement Agreement and is evidence of WECC_URE1's commitment to reliability and compliance; and provides another layer of security for WECC_URE1's most important Critical Cyber Assets. The turnstiles purchased by WECC_URE1 are a revolving door mechanism that will only turn in one direction and are designed to accommodate only one person in the turnstile space per rotation. The turnstile will be in a locked position. When an authorized person presents the proper credentials to the card reader located outside of each entrance point, the turnstile will rotate once to allow one person passage from the unsecured side of the turnstile to the secured side of the turnstile. The threshold of the turnstile is equipped with laser technology that detects when one person has crossed into the turnstile. If for some reason, more than one person attempted to squeeze into the turnstile space, an audible alarm would sound both inside the secured space and at WECC_URE1's Security Operations Center, which is manned 24x7 by a CIP monitor. The turnstile will effectively eliminate tailgating, by only allowing one person access at a time. The turnstile will also effectively eliminate visitor logging issues, as an authorized individual/escort will not be able to hold open a door or allow a visitor to walk into a secured space without being logged. An authorized escort will have to follow a process and execute a specific action in order to allow a visitor into one of the secured spaces. WECC_URE1 is incorporating logging as part of that process, such that an unauthorized individual will not be able to enter a CIP secured space unless he/she is logged into the space by an authorized WECC_URE1 employee. WECC considered this project to be above and beyond what is required for compliance and a significant factor in assessment of a $0 penalty. WECC considered WECC_URE1's CIP-006 R1 compliance history to be an aggravating factor in the resolution of this violation.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014620 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. WECC_URE1 failed to change the password on an annual basis per the CIP-007-3 R5.3.3 guidelines as required by CIP-006-3c R2.2. Specifically, WECC_URE1 reported that a WECC_URE1 Control System Engineer was performing the annual password change for his individual accounts. During the process, he discovered that a password for an individual user account on the Physical Access Control System (PACS) had not been changed in the prior year. WECC_URE1 had a group policy requiring the password to be changed every 340 days. However, the user had not logged into the account in question for more than six months prior to the discovery, so the requirement to change the password had not been initiated. The user’s account was disabled that day. The account in scope would have allowed the user to access the following two (2) PACS workstations with operator privileges. The account in scope would only allow the user to acknowledge alarms, clear alarms, and attach operator notes to alarms. The account in scope would not allow access to servers or access control panels, and it is not allowed to remotely control physical access points. WECC reviewed WECC_URE1's Self-Report. WECC determined that WECC_URE1 failed to ensure the protective measures specified per CIP-006-3c R2.2 guidelines. Specifically, WECC_URE1 failed to change the password on annual basis per CIP-007-3 R5.3.3 guidelines. The root cause of this violation is an inadequate policy. The entity had an Active Directory (AD) group policy set that required the password to be changed every 340 days. However, the user did not log into the account for more than six months prior to the discovery. The individual was responsible to change the password at the time of the incident and not the administrator. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to follow its password policy by not changing the password to an individual account on an annual basis. This individual account had alarm privileges that allowed the user to acknowledge alarms, clear alarms, and attach notes associated to the alarms; however, the account could not turn off the alarms. Failing to change passwords at least annually could allow individuals no longer authorized or other unauthorized individuals to have access to the nine PACS devices in scope. This access could allow the unauthorized person to alter the volume of the alarms so the on-site security guards could not hear the alarms while other malicious individuals entered Physical Security Perimeters (PSPs) However, WECC_URE1 implemented good preventive controls to prevent unauthorized access. Specifically,WECC_URE1 implemented an Active Directory group policy that restricts log-in access to only two PACS devices at the same time. In other words, a malicious individual would not be able to access more than two of the nine PACS devices through any one account at a certain time. WECC_URE1 also implemented good detective controls to detect any unauthorized access. Specifically, the entity implemented alerts to track and detect log-in failures and password attempts. The on-call personnel can review account logs and discover that an unauthorized user attempted to log-in with this particular account. Additionally, WECC_URE1 implemented strong compensating controls in case unauthorized access did occur. Even though the password had not been changed in this instance within the appropriate period, the password was expired, and the system would have required that the password be changed upon the next login attempt. WECC_URE1 had security guards on-site to visually monitor the CCTV cameras that digitally record all employees who enter PSPs and address any audio alarms 24 hours a day, seven days a week. The security guards would likely have been aware of any suspicious activities. | the beginning of the year in which the password was not changed | Mitigation Plan completion | $0 (for WECC2014013850, WECC2015014620, WECC2014014503, and WECC2014014498) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its group policy to create an obligation for user interactive access account passwords to be changed every 180 days; and 2) implemented a tool to track inactivity and automatically change the password on user interactive access accounts that have been inactive for more than 90 days to ensure that all passwords are changed at least once per calendar year, even if the account is not being regularly used. | 2015-02-06 | 10/6/2015 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to the above-listed Mitigation Activities for the violations contained in this Settlement Agreement, WECC_URE1 chose to continue its efforts to eliminate tailgating and logging issues by purchasing preventative turnstiles and laser tailgating detection technology, which is being installed at each of its locations containing Critical Cyber Assets (CCAs). This project is a direct result of the violations contained in this Settlement Agreement; is evidence of WECC_URE1's commitment to reliability and compliance; and provides another layer of security for WECC_URE1's most important CCAs. The turnstiles purchased by WECC_URE1 are a revolving door mechanism that will only turn in one direction and are designed to accommodate only one person in the turnstile space per rotation. The turnstile will be in a locked position. When an authorized person presents the proper credentials to the card reader located outside of each entrance point, the turnstile will rotate once to allow one person passage from the unsecured side of the turnstile to the secured side of the turnstile. The threshold of the turnstile is equipped with laser technology that detects when one person has crossed into the turnstile. If for some reason, more than one person attempted to squeeze into the turnstile space, an audible alarm would sound both inside the secured space and at WECC_URE1's Security Operations Center, which is manned 24x7 by a CIP monitor. The turnstile will effectively eliminate tailgating, by only allowing one person access at a time. The turnstile will also effectively eliminate visitor logging issues, as an authorized individual/escort will not be able to hold open a door or allow a visitor to walk into a secured space without being logged. An authorized escort will have to follow a process and execute a specific action in order to allow a visitor into one of the secured spaces. WECC_URE1 is incorporating logging as part of that process, such that an unauthorized individual will not be able to enter a CIP secured space unless he/she is logged into the space by an authorized WECC_URE1 employee. WECC considered this project to be above and beyond what is required for compliance and a significant factor in assessment of a $0 penalty. WECC considered WECC_URE1's CIP-006 R2 compliance history to be an aggravating factor in the resolution of this violation.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014503 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R6. WECC_URE1 failed to manually log all access into and out of a Physical Security Perimeter (PSP) and failed to appropriately use physical access controls. WECC_URE1 reported that a Forced Entry alarm notified a CIP Guard. The CIP Guard responded to the alarm and observed several people entering a PSP without logging their access by swiping their badge. The CIP Guard notified WECC_URE1's Security Program Administrator. WECC_URE1's Security Program Administrator then reviewed video of the incident and verified that a WECC_URE1 employee opened a CIP door using the request-to-exit button, allowing two other WECC_URE1 employees, both of whom were authorized for unescorted access, to enter the PSP without logging their access. The Security Program Administrator then conducted an extensive review of additional video footage and Transaction Logs and found several additional instances of a failure to log access. There were additional instances. In one instance, a WECC_URE1 system operator, who is authorized for unescorted access to CIP spaces, presented his badge and entered into the CIP space. A second employee, who was also authorized for unescorted access, immediately followed the first employee without presenting his badge. In a second instance, the halon system discharged at the facility. Two WECC_URE1 wireman, both of whom are authorized for unescorted access into the facility, were dispatched to the facility to determine the cause of the halon discharge and address any issues found. Because of the halon that had discharged, it was necessary to prop open doors to the facility in order to ventilate the space. The doors were propped open for approximately one hour. During that time, the WECC_URE1 authorized employees did not present their badge each and every time they reentered the facility while they were conducting their remediation work. In a third instance, three control system engineers took a CIP consultant to WECC_URE1's communication room and control center for a walk-through. When a person enters into one of these spaces, they can then enter into the other space without exiting the original door. When the control system engineers traversed the communications room, they briefly entered the control center and instances of tailgating and/or inaccurate logging occurred. A subsequent interview revealed that the control system engineers were unaware that the two spaces are separate PSPs. WECC reviewed WECC_URE1's Self-Report. WECC determined that WECC_URE1 failed to ensure that employees logged each entry and exit from all PSPs. Specifically, there were several incidents of employees allowing other employees to enter and exit PSPs by tailgating. As a result of their examination, WECC determined that WECC_URE1 was in violation of CIP-006-3c R6. The root cause of this violation is that the employees did not fully understand the WECC_URE1's CIP-006-3 R6 guidelines. | CIP-006-3c | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure that employees logged each entry and exit from all PSPs. Failure to ensure each entry and exit from all PSPs are logged could have potentially resulted in the unauthorized employees obtaining unauthorized physical and/or logical access to the Critical Cyber Assets (CCAs). However, WECC_URE1 implemented strong preventative controls to prevent harm from unauthorized access. Specifically, WECC_URE1 ensured all employees were escorted at all times by authorized personnel, reducing the likelihood of an employee obtaining unauthorized (logical) access and/or physically damaging the CCAs within the Electronic Security Perimeter (ESP) and PSP. WECC_URE1 also implemented strong detective controls to detect unauthorized access. Specifically, WECC_URE1 monitored all physical access points in scope by CCTV cameras that tracked and digitally recorded employees who did not use their badge to log their access when entering the PSP. Additionally, WECC_URE1 implemented strong compensating controls in case unauthorized access did occur. WECC_URE1 security guards visually monitored the CCTV cameras and addressed any audio alarms 24 hours a day, seven days a week. | when the initial failure to log access occurred | Mitigation Plan completion | $0 (for WECC2014013850, WECC2015014620, WECC2014014503, and WECC2014014498) | Self-Report | To mitigate this violation, WECC_URE1: 1) had the Security Program Administrator contact the facility on the day of the incident and spoke with Employee 1. He discussed the issue that was occurring with Employee 1 and reiterated the proper procedure for logging authorized unescorted physical access. He further asked Employee 1 to discuss this matter and information with the rest of the wiremen on site that day. Both conversations were intended to prevent further occurrences and to educate and remind WECC_URE1 employees of proper procedures under its Physical Security Plan and relevant requirements; 2) implemented an internal compliance investigation, which is part of its Reliability Compliance Program. These investigations are detective controls that lead to other preventative controls, such as training, coaching and counseling and process improvements; 3) provided remedial training to all WECC_URE1 employees involved in the facility incident utilizing the CIP Cyber Security training PowerPoint. They were additionally provided verbal coaching by a supervisor. Retraining regarding appropriate access procedures occurred for all WECC_URE1 wiremen working at all locations involved in the incidents also occurred during this timeframe; 4) held two meetings with supervisors to discuss the importance of three cultures: security, reliability and compliance; 5) emailed all employees with authorized unescorted access to CIP spaces concerning appropriate procedures and the director held meetings with working groups to discuss physical access. WECC_URE1 added additional signage to System Operations to remind employees about tailgating and logging; 6) installed a second visitor log in the System Operations area to make it simpler for exit logging of visitors from within that space and disabled a second entry badge reader pending relocation of the badge reader at main entrance; 7) held a collaborative session with a cross-section of employees to discuss solutions to tailgating and logging issues; 8) painted the outside/entrance door at the Switchyard yellow to identify it as a CIP location; 9) reduced the number of employees who had CIP access rights; 10) relocated the badge reader at the Switchyard to allow for easier access for badge swiping; 11) added additional supervisors to WECC_URE1's weekly PSP reporting process and the director personally met with the three control system engineers involved in the incident to discuss root cause and physical access procedures; 12) held a meeting with the supervisors of all individuals who are authorized for unescorted access to discuss the seriousness of these issues, proper procedures and expectations; 13) disabled access to CIP spaces through certain doors and posted Security Guards at the entrances to WECC_URE1's CIP spaces on an interim basis. WECC_URE1 also implemented an interim visitor access procedure that prevents any visitors in CIP spaces without prior approval from WECC_URE1's CIP Senior Manager (or designee); and 14) had a WECC_URE1 Senior Manager (or designee) approved the Physical Security Plan modifying the headquarters control center consolidating two Physical Security Perimeters. The Physical Security Plan includes procedures for the use of video as compensating logging control. | 1/20/2015 | 3/27/2015 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to the above listed Mitigating Activities for the violations contained in this Settlement Agreement, WECC_URE1 chose to continue its efforts to eliminate tailgating and logging issues by purchasing preventative turnstiles and laser tailgating detection technology, which is being installed at each of its locations containing CCAs. This project is a direct result of the violations contained in this Settlement Agreement and is evidence of WECC_URE1's commitment to reliability and compliance; and provides another layer of security for WECC_URE1's most important CCAs. The turnstiles purchased by WECC_URE1 are a revolving door mechanism that will only turn in one direction and are designed to accommodate only one person in the turnstile space per rotation. The turnstile will be in a locked position. When an authorized person presents the proper credentials to the card reader located outside of each entrance point, the turnstile will rotate once to allow one person passage from the unsecured side of the turnstile to the secured side of the turnstile. The threshold of the turnstile is equipped with laser technology that detects when one person has crossed into the turnstile. If for some reason, more than one person attempted to squeeze into the turnstile space, an audible alarm would sound both inside the secured space and at WECC_URE1's Security Operations Center, which is manned 24x7 by a CIP monitor. The turnstile will effectively eliminate tailgating, by only allowing one person access at a time. The turnstile will also effectively eliminate visitor logging issues, as an authorized individual/escort will not be able to hold open a door or allow a visitor to walk into a secured space without being logged. An authorized escort will have to follow a process and execute a specific action in order to allow a visitor into one of the secured spaces. WECC_URE1 is incorporating logging as part of that process, such that, an unauthorized individual will not be able to enter a CIP secured space unless he/she is logged into the space by an authorized WECC_URE1 employee. WECC considered this project to be above and beyond what is required for compliance and a significant factor in assessment of a $0 penalty. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014498 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R2. WECC_URE1 failed to update its database and establish a baseline of authorized ports and services prior to adding two Critical Cyber Assets (CCAs) in the electronic security perimeter (ESP). WECC_URE1 reported that, while completing the annual Cyber Vulnerability Assessment (CVA) it discovered that there were no ports and services listed in the approved ports and services table of WECC_URE1's CIP database for two devices. Both devices are time clocks used for precision timing in the energy management system (EMS) and are classified as CCAs. Both devices were classified when they were installed replacing similar devices. Prior to installing the devices, tests were performed on a representative device, as required by WECC_URE1's procedure. Cyber security control applications were also reviewed in accordance with the procedure, and the system security control evaluation was completed. Documentation of the result of the test was recorded in WECC_URE1's CIP database. The documentation of the results of the ports and services review indicates that one of the new time clocks was scanned with a network vulnerability scanner and a manual cross check was made against the list of approved ports and services. However, the record of authorization and business justification for the port and/or service was not documented in the CIP database, as is required in WECC_URE1's CIP-007-3 R2 ports and services procedure. After performing the CVA and discovering the missing documentation, the required documentation was added to the CIP database. WECC determined that WECC_URE1 was in violation of CIP-007-3a R2 for failing to update its database and establish a baseline of authorized ports and services prior to adding two CCAs in the ESP. The root cause of this violation is failure to follow WECC_URE1's Cyber Security controls testing procedure. | CIP-007-3a | R2 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to establish a ports and services baseline for two time clocks, so it could not ensure that it enabled only those ports and services required for normal and emergency operations on these devices. The time clocks allow network time protocol syncing to the EMS within the ESP that maintains control of the supervisory control and data acquisition (SCADA) system. Falsely assuming that these devices in scope have no unauthorized ports open could lead WECC_URE1 to a false assurance concerning the security of these devices and result in the failure to add additional compensating measures that would strengthen the overall security of the ESP. However, WECC_URE1 implemented preventative controls to prevent harm from unauthorized access. Specifically, WECC_URE1 implemented a peer review process for new devices that are added to the ESP. This peer review process verifies that the assigned personnel followed all the steps within the job plan. The peer review process is done 30 days prior to any new hardware additions. WECC_URE1 also has an internal review process (upon request) to check the integrity of the database for differences. WECC_URE1 also implemented strong detective controls to detect the unauthorized access. Specifically, WECC_URE1 has two operators within the PSPs 24 hours a day, seven days a week that could prevent a disgruntled employee or personnel from directly connecting to these clocks and running a port scanner with a laptop or running a remote port scan via the ESP network. Further, WECC_URE1 found that all undocumented ports were required for the normal operation of the cyber assets in scope. Although the ports and services were undocumented, WECC_URE1 had reviewed all available ports and services prior to deployment of cyber assets in scope. | when WECC_URE1 failed to update its database and establish a baseline of authorized ports and services prior to adding two CCAs in the ESP | when the required documentation was added to the CIP database | $0 (for WECC2014013850, WECC2015014620, WECC2014014503, and WECC2014014498) | Self-Report | To mitigate this violation, WECC_URE1: 1) revised its CIP-007-3 R1 Cyber Security controls testing procedure to utilize local configuration review of time clock devices instead of scans to determine accessible ports; 2) revised its CIP-007-3 R8 Cyber Vulnerability Assessment job plan and has developed the CIP-007-3 R1 Cyber Security controls testing job plan to include specific instructions on testing, evaluating, and documenting ports and services for each type of device in service at WECC_URE1; and 3) documented the authorized ports and services in the CIP database after they were found to be required for normal or emergency operation per its CIP-007-3 R8 Cyber Vulnerability Assessment procedure. | 2015-02-20 | 2015-04-06 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to the above listed Mitigating Activities for the violations contained in this Settlement Agreement, WECC_URE1 chose to continue its efforts to eliminate tailgating and logging issues by purchasing preventative turnstiles and laser tailgating detection technology, which is being installed at each of its locations containing CCAs. This project is a direct result of the violations contained in this Settlement Agreement and is evidence of WECC_URE1's commitment to reliability and compliance; and provides another layer of security for WECC_URE1's most important CCAs. The turnstiles purchased by WECC_URE1 are a revolving door mechanism that will only turn in one direction and are designed to accommodate only one person in the turnstile space per rotation. The turnstile will be in a locked position. When an authorized person presents the proper credentials to the card reader located outside of each entrance point, the turnstile will rotate once to allow one person passage from the unsecured side of the turnstile to the secured side of the turnstile. The threshold of the turnstile is equipped with laser technology that detects when one person has crossed into the turnstile. If for some reason, more than one person attempted to squeeze into the turnstile space, an audible alarm would sound both inside the secured space and at WECC_URE1's Security Operations Center, which is manned 24x7 by a CIP monitor. The turnstile will effectively eliminate tailgating, by only allowing one person access at a time. The turnstile will also effectively eliminate visitor logging issues, as an authorized individual/escort will not be able to hold open a door or allow a visitor to walk into a secured space without being logged. An authorized escort will have to follow a process and execute a specific action in order to allow a visitor into one of the secured spaces. WECC_URE1 is incorporating logging as part of that process, such that, an unauthorized individual will not be able to enter a CIP secured space unless he/she is logged into the space by an authorized WECC_URE1 employee. WECC considered this project to be above and beyond what is required for compliance and a significant factor in assessment of a $0 penalty.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013013158 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-004-3a R4. WECC_URE2 failed to maintain an accurate list of personnel with authorized unescorted physical access to Critical Cyber Assets (CCAs). In this Self-Report, WECC_URE2 stated that an employee retired from WECC_URE2, this employee’s physical access to the CCAs was not revoked until ten calendar days after the change in personnel. By not revoking the employee’s physical access and updating its access list within seven calendar days after the change in personnel WECC_URE2 did not comply with CIP 004-3a R4. WECC_URE2 notified a WECC Subject Matter Expert (SME) of a scope increase to the Self-Report. WECC_URE2 stated that an employee left WECC_URE2 for a new position. The employee’s physical access was not revoked until 19 calendar days after the effective date of the change in personnel. By not revoking the employee’s physical access and updating its access list within seven calendar days WECC_URE2 did not comply with CIP 004-3a R4. WECC_URE2 launched an investigation of its identity and access management system to identify discrepancies with its physical access lists. In doing so, WECC_URE2 discovered other individuals who had improper access to CCAs: an additional 27 had access to CCAs but were not on the approved access list; 23 individuals were on the access list but no longer needed access; and one individual who was given physical access rights approved for someone else. WECC determined that WECC_URE2 failed to have an accurate access list for 51 individuals, as detailed previously. WECC determined that the scope increase was due to a change in WECC_URE2's new access list software (identity and access management system). Specifically, WECC_URE2 implemented the identity and access management system for access management. The new system experienced technical errors in access requests and deletions. | CIP 004-3a | R4; R4.1; R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 implemented controls to reduce the risk of this violation. Specifically, all of the individuals had a current Personnel Risk Assessment (PRA) and had completed NERC CIP Cyber Security Training, and left the company on good terms, making them less likely to cause harm to company devices. WECC_URE2 also has logical access control procedures, which it affords to its Cyber Assets through Active Directory and Terminal Access Controller Access Control System authentication controls. These access controls would have prevented the individuals from gaining unauthorized electronic access to the devices. Further, the individuals’ physical access was limited to primarily workstations and a few backup servers. WECC_URE2 also implemented controls to detect if unauthorized users gained electronic access to CCAs and PSPs. Specifically, WECC_URE2 implemented continuous physical and logical logging and monitoring of CCAs within the PSPs and Electronic Security Perimeters (ESPs). These controls would initiate alerts to network administrators if an unauthorized individual had multiple failed log-on attempts. WECC_URE2 also stated that if it suffered a loss of functionality or critical data it would follow the process it has laid out in its CIP-009 Recovery Plan. WECC_URE2 further stated that it maintains disaster recovery/failover instances of critical hardware and applications which could be used in case of physical damage to the systems. | when WECC_URE2 implemented its identity and access management system | Mitigation plan completion | $36,000 (for WECC2013013158, WECC2014014532, WECC2014014533, and WECC2014014534) | Self-Report | To mitigate this violation, WECC_URE2: 1) sent a one-time awareness email from the Director of HR (to all Managers/Supervisors) describing the importance of adhering to the termination process and timelines; 2) documented the procedures to include the formalization of a peer review by HR of all employee terminations looking for compliance-related items; 3) updated annual cyber security training to include a section on expectations of all parties involved for terminations of a NERC-covered position; 4) created formal training for managers and supervisors of NERC-covered employees, and working with WECC_URE2 training department, created new online training module; 5) launched training in WECC_URE2's learning management system for NERC-covered management; 6) conducted extensive review and updated Manager/Supervisor Policy and Procedures; 7) trained supervisors and managers with NERC-covered employees using learning management software; 8) drafted and disseminated out-of-band communication from NERC Program; 9) implemented procedure change for the replacement of existing card keys for personnel with WECC_URE2 facility access; and 10) conducted quality check of card keys created prior to procedure change. | 11/21/2014 | 2015-09-03 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014532 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R1. WECC determined that WECC_URE2 failed to follow its test procedures to ensure that new Cyber Assets and significant changes to existing Cyber Assets do not adversely affect existing cyber security controls within the production of the Electronic Security Perimeter (ESP). WECC_URE2 stated in its Self-Report that it installed one Cyber Asset, a Human Machine Interface (HMI) device, at the substation within the production ESP, and at that time, it failed to follow its testing procedures. The device remained on the workstation for 6 months. The second Cyber Asset HMI device was installed at another substation, and remained on the substaton supervisory control and data acquisition (SCADA) system for 1 month and 5 days. WECC determined that WECC_URE2 failed to follow its test procedures to ensure that new Cyber Assets do not adversely affect existing cyber security controls within the production ESP. Specifically, WECC_URE2 installed two HMI devices without testing to ensure the devices would not adversely affect existing cyber security controls. | CIP 007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to follow its test procedures to ensure that the new Cyber Assets did not have and adverse affect to existing cyber security contols. Failing to follow its test procedures could lead to a misconfiguration of the two HMI devices. Each HMI device provides read-only access to substation information through a single multi-function substation server device. WECC_URE2's data server devices manage the Energy Management System (EMS) by providing a view to its substation conditions and alarms on the HMI; each employee accesses the devices from the HMI. Therefore, if testing procedures are not completed to ensure the devices are configured correctly, WECC_URE2's visibility of the substations in scope could be compromised. WECC_URE2 implemented controls to prevent its visibility of the substations in scope from being compromised. Specifically, WECC_URE2's EMS operators can view substation information remotely from WECC_URE2's Control Centers over WECC_URE2's data network regardless of the presence or absence of HMI workstations in the substation. Therefore, incorrect configuration of either of the two HMI devices would not result in loss of WECC_URE2's visibility of the substations, because substation information would still be available to operators in WECC_URE2's Control Centers via a network connection to the EMS. WECC_URE2 implemented a Physical Access Control Systems (PACS) device that kept track of physical access logs to each facility. WECC_URE2 reviewed alarm and PAC system logs when both HMI devices were installed at each substation and there was no unauthorized physical access to either substation. The card readers, alarms, and controllers associated with the PACS were working properly. Normal detective controls would have alarmed if any unauthorized attempts were made to the PSP. Further, WECC_URE2 also implemented a System Event Manager within its ESP to collect logging. | when the initial HMI device was installed | Mitigation plan completion | $36,000 (for WECC2013013158, WECC2014014532, WECC2014014533, and WECC2014014534) | Self-Report | To mitigate this violation, WECC_URE2: 1) created a quick reference card/checklist job aid for NERC Change Controls for Telecom team; 2) conducted refresher training for the Telecom team on NERC CIP Change Controls; 3) updated telecom team website; 4) updated a website internal to IT with a link to the new quick reference card so that it is accessible to all; 5) drafted process for HMI builds and installs for desktop team; and 6) trained desktop team on HMI build process. | 1/28/2015 | 9/2/2015 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 R1 compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014533 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. WECC_URE2 failed to follow its test procedures and failed to verify that two Cyber Assets had their shared system accounts disabled, renamed, and/or deleted. WECC_URE2 stated in its Self-Report that it installed two Cyber Assets (Human Machine Interface (HMI) devices). The first HMI device was installed at a substation within the production Electronic Security Perimeter (ESP), and at that time, WECC_URE2 failed to follow its account management procedures. The device remained on the workstation for 6 months. The second HMI device was installed at a different substation and remained on the workstation for 1 month and 5 days. Both are workstations, Critical Asset facilities, and installed within the ESP as Cyber Assets at these facilities. During a post-change review of the change control documentation, WECC_URE2's Compliance team discovered that no testing of System Event Monitoring (SEM) logging was conducted on either HMI device even though it is a requirement of WECC_URE2's Change Control Process. During this review, it was identified that the change control documentation was not complete. WECC determined that WECC_URE2 failed to remove, disable or rename default accounts, where possible and change the password for default accounts that remained enabled, per CIP-007-3a R5.2. Specifically, WECC_URE2 installed two HMIs, but failed to verify that the shared system accounts (administrator accounts) were disabled, renamed or deleted. Further, WECC_URE2 did not test SEM logging on either HMI device per CIP-007-3a R5.1.2. | CIP 007-3a | R5 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to follow its test procedures and failed to verify that the HMIs had its shared system accounts disabled, renamed, and/or deleted. Each HMI device provides a method of read-only administrative access to substation information through a single multi-function substation server device. WECC_URE2's multi-function substation server devices manage the Energy Management System (EMS) by providing a view to its substation conditions and alarms on the HMI; each employee accesses them from the HMI. If shared system accounts are not disabled, renamed and/or deleted, then WECC_URE2 operators may not know of a malicious attempt to elevate privileges beyond read-only access on the HMI devices and other devices at the substation. Therefore, if operators are not aware of the alerts coming from the substations, then WECC_URE2's visibility of the substations in scope could be compromised. WECC_URE2 implemented controls to prevent its visibility of the substations from being compromised. Specifically, WECC_URE2's EMS operators can view substation information remotely from WECC_URE2's Control Centers over WECC_URE2's data network regardless of the presence or absence of HMI workstations in the substation. Therefore, incorrect configuration of either of the two in scope HMI devices would not result in loss of WECC_URE2's visibility of the substations in scope because substation information would still be available to operators in WECC_URE2's Control Centers via a network connection to the EMS. Further, WECC_URE2 has operators on-site at the Control Centers twenty-four hours a day and seven days a week, so an operator could have realized that the EMS application was removed from the primary HMI and could have contacted the IT SME on-call. The SME on-call could have restored the EMS application on the primary HMI device with no or little downtime. | when the intitial HMI device was installed | Mitigation plan completion | $36,000 (for WECC2013013158, WECC2014014532, WECC2014014533, and WECC2014014534) | Self-Report | To mitigate this violation, WECC_URE2: 1) created quick reference card/checklist job aid for NERC Change Controls to include reference to logging security events; 2) conducted refresher training for the telecom team on NERC CIP Change Controls; 3) added quick reference card to Telecom team website; 4) updated IT website with a link to the new quick reference card so that it is accessible to all of IT; and 5) sent a directive message from IT management to all of IT. | 1/28/2015 | 2015-09-02 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014534 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. WECC_URE2 failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) maintained logs of system events related to cyber security and retain them for 90 days. WECC_URE2 stated in its Self-Report that it installed two Cyber Assets (Human Machine Interface (HMI) devices). The first HMI device was installed at the substation within the production Electronic Security Perimeter (ESP) and remained on WECC_URE2's network for 6 months. The second HMI device was installed at a different substation and remained on WECC_URE2's network for 1 month and 5 days. Both are workstations, Critical Asset facilities, and installed within the ESP as Cyber Assets at these facilities. During a post-change review of the change control documentation, WECC_URE2's Compliance team discovered that it failed to enable logging on the System Event Manager (SEM). Specifically, since WECC_URE2 added the two new HMI devices to the SEM, the SEM should have been collecting logs for the required monitoring, but it did not. WECC determined that WECC_URE2 failed to follow its test procedures and verify that two HMIs were added to the SEM. Specifically, the SEM should have been receiving logs from the new HMIs, but WECC_URE2 did not configure the SEM to receive them, therefore, the log of system events was not captured by the SEM. Further, WECC_URE2 failed to retain all logs for ninety calendar days. | CIP 007-3a | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to maintain logs of system events related to cyber security and retain them for 90 days. Failure to follow its testing procedures and failing to verify and/or enable logging via the SEM device could lead to unknown alerts that are not captured. If unknown alerts are not captured, then WECC_URE2 operators may not know of a malicious attempt to elevate privileges beyond read-only access on the HMI devices and other devices at the substation. Therefore, if operators are not aware of the alerts coming from the substations, then WECC_URE2's visibility of the substations could be compromised. WECC_URE2 implemented controls to prevent its visibility of the substations from being compromised. Specifically, WECC_URE2 implemented a Physical Access Control Systems (PACS) device that kept track of physical access logs to each facility. WECC_URE2 reviewed alarm and PAC system logs when both HMI devices were installed at each substation, and there was no unauthorized physical access to either substation. The card readers, alarms, and controllers associated with the PACS were working properly. Normal detective controls would have gone off if any unauthorized attempts were made to the PSP. Further, WECC_URE2 also implemented a SEM within its ESP to collect logging. | when the intitial HMI device was installed | Mitigation plan completion | $36,000 (for WECC2013013158, WECC2014014532, WECC2014014533, and WECC2014014534) | Self-Report | To mitigate this violation, WECC_URE2: 1) created quick reference card/checklist job aid for NERC Change Controls to include reference to logging security events; 2) conducted refresher training for the telecom team on NERC CIP Change Controls; 3) added quick reference card to Telecom team website; 4) updated IT website with a link to the new quick reference card so that it is accessible to all of IT; and 5) sent a directive message from IT management to all of IT. | 1/28/2015 | 2015-09-02 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 R6 compliance history to be an aggravating factor in the penalty determination.
2015-12-30 | FERC | NP16-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014891 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-002-1 R3. WECC_URE3 conducted a Critical Cyber Asset (CCA) review at a WECC_URE3 facility. WECC_URE3 discovered that it failed to include a protocol converter device on its CCA list. The purpose of the device is to convert electronic messages from WECC_URE3's supervisory control and data acquisition (SCADA) system to the Remote Intelligent Gateway (RIG). The RIG provides for communication between WECC_URE3 and the neighboring Balancing Authority’s (BA) energy management system (EMS). The device is subject to CIP-002-1 R3 because the device has a routable protocol to communicate outside the Electronic Security Perimeter (ESP) to the RIG. The device was omitted from the CCA list when WECC_URE3 initially developed the list because WECC_URE3 personnel believed the device was exempt from the CIP Standards due to its serial connection. WECC_URE3 did not discover the oversight during subsequent annual reviews because until four years later, the part containing the protocol converter device was supported by a vendor and WECC_URE3 had no awareness that the vendor was not maintaining strong procedural or technical controls. WECC_URE3 assumed responsibility for supporting the entire RIG system four years after the device was originally omitted from the list. | CIP-002-1 | R3; R3.1 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE3 did not identify a protocol converter on its CCA list. The device is used to convert messages from WECC_URE3's generation SCADA system to a neighboring BA’s EMS. This failure to identify the device on WECC_URE3's CCA list could result in the protocol converter not receiving all of the required CIP protections, potentially leaving the device vulnerable to cyber security attacks that may include the protocol converter being used to send incorrect messages to the neighboring BA. The risk was mitigated as the device was located in the Physical Security Perimeter and monitored by WECC_URE3's Central Alarm 24 hours a day, seven days a week. Therefore any unauthorized physical access attempts would have been alerted to the central alarm operator. The device was also located inside an ESP and was protected by the customary ESP controls, such as electronic access points, logging, and monitoring. | when the Standard became mandatory and enforceable on WECC_URE3 | when WECC_URE3 added the device to the CCA list | $25,000 | Self-Certification | To mitigate this violation, WECC_URE3: 1) applied appropriate CCA controls to the omitted device; 2) added the device to the CCA list; and 3) added the device to existing TFEs. | 6/24/2015 | 10/26/2015 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-12-30 | FERC | NP16-1-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014397 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R3. Specifically, WECC_URE1 reported that it had failed to update a personnel risk assessment (PRA) for one employee at least every seven years after the initial PRA. WECC_URE1 further reported that the employee had unescorted physical access to a Critical Asset and had accessed the building on one occasion prior to the discovery of the late PRA. WECC_URE1 failed to complete an updated PRA after seven years for one employee. Once WECC_URE1 discovered the violation, WECC_URE1 immediately revoked the employee’s access until a PRA could be completed. The employee’s access was not reinstated until after the updated PRA was performed. The PRA was completed four months past the date that it should have been completed. WECC determined that WECC_URE1 failed to complete an updated PRA after seven years for one employee in violation of CIP-004-3a R3.2. The root cause of the violation was a lack of compliance process, as the violation occurred due to WECC_URE1 failing to review the spreadsheet used to monitor PRA renewal dates in a timely manner. | CIP-004-3a | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to conduct PRAs and keep them current could lead to improperly vetting the identity and criminal history of personnel managing Critical Cyber Assets (CCAs). This could result in malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the BPS which could negatively impact the BPS. WECC_URE1 failed to renew one employee’s PRA. This employee had physical access to the Primary Control Center and Backup Control Center, which contain Energy Management System (EMS) workstations, security information, and event management server and network equipment, such as routers, switches, and firewalls. However, WECC_URE1 implemented strong detective controls. Specifically, WECC_URE1 uses cameras to monitor CCAs and EMS operators around the clock. Also, EMS operators would have prevented a malicious individual from downloading malicious software onto the workstations because the individual did not have logical access and the EMS operator would have identified this issue. Further, this individual did not have logical access to the CCAs. Users who do have logical access to the CCAs are required to create complex passwords that are changed at least annually. Failed login attempts are logged and reported. Finally, this individual was a longstanding employee with WECC_URE1, and upon completion of the PRA there were no issues noted. | when WECC_URE1 should have completed the updated PRA | when WECC_URE1 completed the updated PRA | $0 | Self-Report | To mitigate this violation, WECC_URE1 implemented an automated solution for managing PRA renewals. With the implementation of this software, the appropriate departments are automatically notified (via an email message) of an approaching expiration date on all PRAs. This notification process eliminates reliance on the manual review of an excel spreadsheet. Also, it is important to note the notification must be acted upon by a member of the PRA renewal team within a specific timeframe or the software will continue to automatically send the email notification until the task has been completed. | 2014-09-15 | 2015-10-07 | Agrees/Does Not Contest | WECC reviewed WECC_URE1's internal compliance program and considered it to be a mitigating factor. WECC considered WECC_URE1's compliance history to be an aggravating factor in the disposition determination.
2015-12-30 | FERC | NP15-36-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014383 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R5. SERC_URE1 failed to implement the required procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) (PSP) 24 hours a day, 7 days a week. The SERC_URE1 control center houses one Critical Asset, the primary control center for SERC_URE1. The approved monitoring method for the control center building, which is designated as the PSP for the primary control center, is for human observation. Security personnel are stationed at the main entrance lobby for the control center building 24 hours a day, 7 days a week. The other four control center access doors are egress only and are monitored by video surveillance. All control center building doors are covered by video feeds going to a control center security guard station, as well as a video feed to the control center control room as a secondary monitoring option. The main entrance is a man-trap type entrance, requiring the station security guard to permit access through the second set of doors to gain further access to the control center building. While reviewing video footage to investigate a larceny at another building in the complex, SERC_URE1 discovered the control center security station was left unmanned for approximately 20 minutes each time on three separate occasions. The contract security guard was observed on the video footage exiting the building through a rear egress only door and blocking the door open to prevent the door from closing and locking upon exit. Blocking any secured door open is specifically prohibited within the SERC_URE1 physical security plan. The contract security guard returned through the same door approximately 20 minutes later in each of the three instances, and returned to the control center security station. SERC_URE1 later determined that the contract security guard was responsible for the larceny in the other building. After the Self-Report, SERC_URE1 conducted further reviews and found five additional instances in which the same contract security guard left the security station without making arrangements for monitoring of the PSP. In each of the five additional instances, the contract security guard again blocked the door open to permit undetected return to the control center security station. SERC_URE1 reported these additional discoveries as an expansion of scope to the Self-Report. The first instance was approximately two minutes in duration. The other four instances occurred during one day, with each instance being approximately two minutes each. SERC_URE1 reported that it appeared that the contract security guard left the assigned work area and the PSP monitoring duties to go to a car in the parking lot. After discovering the larceny, SERC_URE1 pressed charges against the contract security guard, to which the security guard pled guilty. The root cause of the violation was the lack of preventive controls to ensure the security officer performed its duties. SERC_URE1 did not ensure the security officer’s continuous presence at the guard station. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to properly implement physical access controls at the PSP could allow unauthorized individuals with malicious intent access to Critical Cyber Assets (CCAs), increasing the risk that CCAs or the energy management system could be compromised or degraded, possibly resulting in operational impacts. However, the ingress doors to the control center are man-trap type doors, where the on-site security personnel must permit access through the interior doors. Within the control center building (which is the SERC_URE1 established PSP), the area where the CCAs, non-CCAs within the Electronic Security Perimeter (ESP), and Electronic Access Control and Monitoring devices reside is segmented and secured by magnetic door locks which are controlled by badge readers that only permit access to those with approved and authorized access to Cyber Assets within the ESP. Access to the Cyber Assets is limited to users that have been approved and have user login accounts, which the guard at issue did not have. Gates to the control center are controlled by badge readers, reducing the likelihood of unauthorized personnel being able to gain access to the doors of the facility. The control center is staffed with regular and familiar operating personnel 24 hours a day, 7 days a week. | when the guard first left the security monitoring post unattended | the last date the guard left the security monitoring post unattended | 0 | Self-Report | To mitigate this violation, SERC_URE1: 1) removed the security officer in question and notified his employer that he is no longer allowed on any SERC_URE1 work location; 2) conducted and documented refresher training on CIP-006-3c and training on the new physical security controls for appropriate security officers; 3) installed a new security camera focused on the guard station in the subject facility and routed the feed to the central control station which can be monitored continuously or reviewed at a later time; 4) co-routed all other existing video surveillance feeds at the subject facility to the central control station which can be monitored continuously or reviewed at a later time; and 5) updated applicable procedures to include the new procedures related to the new security camera and video surveillance fields that were routed to the central control station. | 2014-10-20 | 2015-01-26 | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC took into consideration that fact that SERC_URE1 has approved and begun physical security updates at its facilities. As part of these upgrades, SERC_URE1 has already completed or will complete the following: (1) install a fully automated Physical Access Control System (PACS) at the control center which will serve as SERC_URE1's primary method of controlling access to the PSP and includes the use of two or more different physical access controls to allow authorized unescorted physical access into the PSP as required by Version 5 of the CIP Standards; (2) equip all exterior doors with alarming contacts and have high definition cameras focused on the interior and exterior of each door; (3) route the camera feeds and door alarms to the control center security guard station and to the primary security center; (4) expand the security center area, add monitoring stations, and hire an additional senior compliance specialist to manage the security center and the associated physical security countermeasures; and (5) link the exterior and interior man-trap style door used for ingress to require that one door be closed and secured before the other can open. SERC_URE1 will update SERC upon completion of the physical security updates. The following pre-existing controls will remain in place: (1) the armed guard currently used as the primary method of controlling access to the PSP will remain and serve as an additional internal control; (2) there will continue to be only one ingress point to the PSP; and (3) access to the control room will continue to be restricted by an additional card access system. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-12-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010813 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-1 R1. MRO_URE1's cyber security policy did not address at least 16 of the 41 requirements in Standards CIP-002-1 through CIP-009-1, as required by CIP-003-1 R1.1. For approximately six months, MRO_URE1 relied on its procedures, which only partially addressed the requirements in CIP-002-1 through CIP-009-1. Approximately 16 of the 41 CIP version 1 requirements were not covered by its procedures, and 18 of the 42 CIP version 2 requirements were not covered by the other processes. MRO_URE1 updated its cyber security policy to address all requirements in Standards CIP-002 through CIP-009. Additionally, MRO_URE1's cyber security policy was not readily available to all personnel with access to, or responsibility for Critical Cyber Assets (CCAs), as required by CIP-003-1 R1.2. MRO_URE1 did not post its cyber security policy on SharePoint until approximately thirty months after it was required by the Standard. MRO_URE1 had the cyber security policy available on internal drives, however, it was not readily available to all personnel with access to, or responsibility for, Critical Cyber Assets until approximately thirty months after it was required by the Standard. MRO_URE1 maintained a copy of its cyber security policy in the control room, but personnel had to request access and a process was not defined for how to make a request. Therefore, MRO determined that MRO_URE1's cyber security policy was not readily available. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-003-1 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 was following its procedures for approximately six months during the time it did not have a CIP compliant cyber security policy. MRO did not identify any significant gaps between its procedures and CIP system architecture standards. Additionally, MRO_URE1 addressed the cyber security policy updates until approximately six months after it was required by the Standard. Furthermore, although MRO_URE1's cyber security policy was not readily available to all personnel with access to, or responsibility for, Critical Cyber Assets, the system administrators and CIP program manager had access to the cyber security policy the entire time it was in place. The risk was mitigated because MRO_URE1 followed its procedures, and a copy of the cyber security policy was available in the control room. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 implemented its cyber security policy and posted it on the SharePoint site. | 2013-05-20 | 2015-02-03 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-12-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010814 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-1 R4. MRO_URE1 failed to implement its documented program to identify, classify, and protect information associated with Critical Cyber Assets (CCAs), as required by CIP-003-1 R4. MRO_URE1's documented program required that CCA information be labeled at all times. MRO_URE1 reported noncompliance because its network drawings were not labeled as in their electronic form, as required by MRO_URE1's program to identify, classify, and protect information associated with CCAs. The sensitive information did not comply with the MRO_URE1 program to mark all CCA information appropriately at all times. MRO_URE1's electronic system prevented the labeling of its network drawings in the electronic format, while its documented program required the labeling regardless of the document format. MRO_URE1 modified its program so that it only needed to identify CCA information "if and when it is printed" instead of at all times. MRO_URE1's policy continued to require that it classify, identify, and protect information associated with Critical Cyber Assets, regardless of media type. | CIP-003-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 treated the information that was printed without the label according to its documented program. MRO_URE1 revised its documented program so that it could electronically store CCA information without labeling it with the appropriate label (e.g. network diagrams) and only mark documents with the appropriate label if and when they are printed. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 modified its policy to not require the label on electronic documents kept in a secure location. | 2014-02-26 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-12-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010815 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-1 R5. MRO_URE1 did not maintain a list of designated personnel that were responsible for authorizing logical or physical access to protected information, as required by CIP-003-1 R5.1. MRO_URE1 was conducting quarterly reviews of authorization lists and provided evidence to MRO demonstrating that seven individuals signed off on the excel file that is used to track the access levels of each individual with access to the power plant control system. The excel file includes all users with both physical and cyber access. However, MRO_URE1 did not maintain a list of the designated personnel responsible for authorizing logical or physical access to protected information. The MRO_URE1 list of designated personnel was not documented until approximately eleven months after the Standard became enforceable. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-003-1 | R5; R5.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 did perform the reviews during the period of non-compliance, even though it did not document who was responsible for performing those reviews. The risk was mitigated because MRO_URE1 provided evidence that the same seven individuals, six plant managers and one NERC implementation manager, were conducting quarterly reviews throughout the period of noncompliance. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 formalized and documented designated personnel responsible for authorizing logical and/or physical access to protected information. | 2010-11-17 | 2015-01-22 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-09-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010817 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-004-2 R2. MRO_URE1 did not ensure that all personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including contractors and service vendors, were trained prior to their being granted access, as required by CIP-004-2 R2.1. There were approximately 130 people with authorized cyber or authorized unescorted physical access to 15 CCAs in six different Physical Security Perimeter (PSP) locations. Out of these 130 people, 14 individuals were granted access to CCAs or a PSP prior to receiving the required training. The average time of access before training was approximately two weeks. Two individuals had access for seven months before being trained. MRO_URE1's violation was due to plant managers not consistently requiring training for employees before giving them access. MRO_URE1 had a policy to train people before granting access, but the policy was not followed. | CIP-004-2 | R2; R2.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had not established central management of CIP user access. While providing CCA access to individuals who have not been properly trained could lead to inadvertent or malicious acts that expose vulnerabilities, this risk is reduced because MRO_URE1 requires employees to sign an acceptable use policy that includes cyber and physical access expectations with accompanying disciplinary actions. MRO also considered that MRO_URE1 self-identified the concern, has only 15 CCAs and 6 Critical Assets, and only connects to one neighboring entity. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) developed and implemented a procedure to be notified of personnel changes so that personnel are trained prior to having unescorted access to the PSP; and 2) completed a comprehensive review to ensure that all people are being trained before authorizing access. | 2014-07-02 | 2015-02-20 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-09-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010818 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-004-1 R3. MRO_URE1 failed to ensure that each personnel risk assessment (PRA) conducted include, at least, a seven-year criminal check, as required by CIP-004-1 R3.1, and also failed to update each PRA at least every seven years after the initial assessment as required by CIP-004-1 R3.2. Subsequent to the Self-Certification of noncompliance, MRO_URE1 notified MRO that it believed that it was compliant with CIP-004-1, R3 asserting that it was not capable of performing new (R3.1) or updated (R3.2) seven-year criminal background checks due to its procedures. MRO Enforcement staff held several conference calls with MRO_URE1 staff to discuss concerns related to PRAs and gain a better understanding of concerns raised by MRO_URE1 related to compliance with apparently conflicting regulations. MRO_URE1 administers its background check policy in accordance with its procedures and has implemented a background check policy. In accordance with its procedures, MRO_URE1 conducts a criminal background check on all individuals employed at its facilities regardless of whether those individuals have authorized cyber or authorized unescorted physical access. Further, under these provisions, MRO_URE1 is not capable of updating criminal background checks more frequently, although it currently conducts them for certain individuals every ten years. | CIP-004-1 | R3; R3.1; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 has a documented PRA program in accordance with federal law. However, the requirements governing the conduct of PRAs for MRO_URE1 certain personnel do not meet the minimum requirements of CIP-004-1 R3. MRO_URE1 is conducting initial PRAs that include a criminal background check for all personnel having authorized cyber or authorized unescorted physical access to CCAs. Additionally, MRO_URE1 is updating the PRA of certain individuals as provided under certain applicable regulatory processes. | when the Standard became mandatory and enforceable on MRO_URE1 | present | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 discussed this issue with its attorneys and any affected union regarding internal measures in place to manage access control. MRO_URE1 conducts quarterly access reviews to manage who has access, and that the access is appropriate. | 2015-04-24 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010819 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-004-1 R4. MRO_URE1 failed to maintain its list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs, as required by CIP-004-1 R4. MRO_URE1 had a list, but it did not update the list within seven calendar days of any change of personnel with authorized access to CCAs. Each of the six MRO_URE1 plant managers is authorized to provide physical or shared cyber access to CCAs without notifying the CIP Program Manager. Because the administration of physical and cyber access was not centralized, MRO_URE1 was not able to maintain an accurate list of personnel with authorized cyber or authorized unescorted physical access to CCAs, including their specific electronic and physical access rights to CCAs. As part of the mitigation process, MRO_URE1 conducted a comprehensive review of changes in personnel and determined that there were 15 instances where the list was not updated within seven days (14 personnel with physical access and 1 person with shared cyber access); in the next year, there were 21 instances where the list was not updated within seven days (19 personnel with physical access and 2 personnel with shared cyber access); and in the following year, there were 13 instances where the list was not updated within seven days (12 personnel with physical access and 1 person with shared cyber access.) Additionally, MRO_URE1 reported that it failed to revoke shared cyber access to CCAs within seven days of the individual no longer needing access, as required by CIP-004-1 R4.2. MRO_URE1 revoked the physical access card or key within seven days of personnel leaving, but it did not revoke the cyber access within seven days for those individuals with shared cyber access that no longer required such access. | CIP-004-1 | R4; R4.2 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had not established central management of CIP user access. While the failure to revoke access for personnel who no longer require access to CCAs could result in a former employee gaining access and causing a concern, this risk is reduced because MRO_URE1 was and is conducting the quarterly reviews as required under CIP-004-1, R4.1. This quarterly review allows MRO_URE1 to detect any users that are on the list of 'authorized users' and, while not within the prescribed seven-day timeframe, to make required updates to the list. Additionally, although MRO_URE1 was not revoking cyber access for shared accounts, MRO_URE1 was changing the shared passwords every 180 days. MRO also considered that MRO_URE1 self-identified the concern, has only 15 CCAs, and only six Critical Assets, and only connects to one neighboring entity. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 developed and implemented a procedure to be notified of personnel changes so that personnel lists can be modified within 24 hours or 7 days. | 2014-07-02 | 2015-02-13 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010820 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R1. MRO_URE1 failed to ensure that the Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) (ESPs) were afforded the protective measures as specified in CIP-004 R3 (Personnel Risk Assessments), and Standard CIP-007 R5 (Account Management) and R6 (Security Status Monitoring). Additionally, MRO_URE1 did not identify and maintain documentation of ESPs, all interconnected Critical and non-critical Cyber Assets within the ESPs, all electronic access points to the ESPs and the Cyber Assets deployed for the access control and monitoring of these access points, as required by CIP-005-1 R1.6. MRO_URE1 has six physical locations affected by this violation. MRO_URE1 did not identify and document the electronic access points to the ESP for approximately one year. MRO_URE1 was in the process of redefining its electronic access points to the ESP using firewalls and virtual local area networks (LANS) for the next three years. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-005-1 | R1; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For approximately 15 months, MRO_URE1 did not have any declared ESP access points. For the next year, MRO_URE1 redefined its electronic access points to the ESP using firewalls and virtual LANS. However, MRO_URE1 demonstrated that while the ESPs were being defined, the switches and firewalls were afforded some of the required protective measures. MRO reviewed evidence to confirm that MRO_URE1 had some of the required protective measures in place including CIP-007-1 R7 (Device Disposal or Redeployment) and CIP-003-1 R6 (Change Control). MRO_URE1 did not identify and document the ESP. During this timeframe, MRO_URE1 was allowing mixed-trust network traffic within the ESP. Allowing mixed-trust network traffic increases the risk that an adversary could have negatively impacted CCAs and Critical Assets. However, this risk was reduced because MRO_URE1 has only 15 Critical Cyber Assets (CCAs), with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. Further, per MRO_URE1, all switches and firewalls were treated as ESPs. Prior to firewall installation, routers with access control lists were used for access to system. Finally, the plant was locked at all times, and doors to computer rooms, where ESP devices were stored, were also locked and physically monitored via physical security system. | when the Standard became mandatory and enforceable on MRO_URE1 | present | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) created diagrams that establish that all critical and non-critical Cyber Assets are within the ESP; 2) updated its policies and procedures for account management and security status monitoring to include all Cyber Assets within the ESP; 3) provided evidence of required review of Cyber Asset accounts; and reviewed its access demonstrated that Cyber Assets used in the access control and monitoring of the ESP are afforded the protective measures specified in CIP-007 R5 and R6; and 4) must achieve compliance with CIP-004-1 R3 so as to comply with the requirements of CIP-005-1 R1. | 12/30/2015 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010821 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R2. MRO_URE1 documentation did not include a review process for authorization rights, in accordance with standard CIP-004 R4, as required by CIP-005-1 R2.5.3. MRO_URE1 did not have a documented review process to review the lists of its personnel who have authorized access to Critical Cyber Assets (CCAs) quarterly. This was a documentation issue. MRO_URE1 was conducting quarterly reviews, but did not have a formally documented process for doing so. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-005-1 | R2; R2.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While failing to document a review process for authorization rights for its Electronic Security Perimeters (ESPs) could result in potentially allowing unauthorized access, this risk was reduced because MRO_URE1 was performing reviews during the period of noncompliance. Further, MRO_URE1 demonstrated that it performed quarterly reviews every 90 days since the Standard became mandatory and enforceable. MRO_URE1 has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 updated, finalized, documented, and implemented the personnel access policy. The policy lists the procedure and approval for access, along with review steps. | 2014-02-27 | 2015-02-20 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010822 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R3. MRO_URE1 did not identify and maintain documentation of Electronic Security Perimeters (ESPs), therefore, MRO_URE1 did not implement and document an electronic or manual process for monitoring and logging access at access points to the ESP. MRO_URE1 has six physical locations affected by this violation. MRO_URE1 did not have firewalls in place to monitor and log access at access points to the ESP for approximately a year. MRO_URE1 did not have firewalls in place to monitor and log access points to the ESP until it implemented firewalls. However, MRO_URE1 failed to include a switch with mixed trust as part of its ESP access point definition until approximately three years later. Once firewalls were implemented, evidence demonstrated that MRO_URE1 was monitoring the firewall logs to detect unauthorized access attempts. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-005-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While failure to monitor and log access at access points to the ESP could result in unauthorized access and malicious or inadvertent acts being undetected, this risk was reduced because MRO_URE1 has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. Internally, MRO_URE1 uses read-only non-IP distributed network protocol serial connection for five facilities, with the remaining facility using Modbus Serial (legacy). MRO also considered that MRO_URE1 self-identified the concern. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) upgraded routers to firewalls which now have the ability to alert the entity of unauthorized access; 2) verified network diagrams are correct after upgrading routers; and 3) reviewed logs. | 2014-12-05 | 2015-04-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010823 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R4. MRO_URE1 failed to perform a cyber vulnerability assessment (CVA) of the electronic access points to the Electronic Security Perimeters (ESPs) at least annually, which included the minimum documentation requirements set forth in CIP-005-1 R4.1, R4.2, R4.3, R4.4, and R4.5. For approximately two years, MRO_URE1 did not have any documented CVA process. In the subsequent two years, MRO_URE1 had incomplete documentation for its CVA process. MRO_URE1 did not have a complete document identifying the CVA process until approximately four years after the Standard was enforceable. MRO_URE1 also did not perform a review to verify that only ports and services required for operations at access points were enabled, as required by CIP-005-1 R4.2. MRO_URE1 could not demonstrate that it performed any ports and services review. Additionally, MRO_URE1 did not discover all access points to the ESP, as required by CIP-005-1 R4.3, and MRO_URE1 did not review controls for default accounts, passwords, and network management community strings, as required by CIP-005-1 R4.4. Finally, MRO_URE1 did not document the results of the assessment, the action plan to remediate or mitigate vulnerabilities, and execution status of the action plan, as required by CIP-005-1 R4.5. MRO_URE1 did not provide evidence to demonstrate that the CVA occurred. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-005-1 | R4; R4.1; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 is required to adhere to its procedures. MRO_URE1's procedures require documentation to demonstrate that systems were assessed to mitigate vulnerabilities on a regular basis. MRO_URE1 provided evidence that it performed work related to its procedures vulnerability management, such as retina network scans, port and service reviews, and account reviews. However, MRO_URE1's procedures network scans and reviews only covered a portion of the accounts and devices that were required to meet the CIP-005-1 R4 requirements. By not performing the CVA, MRO_URE1 was subject to un-mitigated ports and services, access points, and account and password vulnerabilities. By not documenting the CVA process or the CVA results and action plans, MRO_URE1 was not able to demonstrate that it performed any CVA. MRO_URE1 did not have a complete documented CVA process until approximately four years after it was required by the Standard. MRO also considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) updated the CVA physical discovery process to comply with all requirements including a visual inspection of all ports; and 2) confirmed that there are no additional ESP access points other than those identified. | 2014-12-19 | 2015-06-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010824 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R5. MRO_URE1 did not ensure that all documentation required by Standard CIP-005 reflects current configurations and processes, and failed to review the documents and procedures referenced in Standard CIP-005 at least annually, as required by CIP-005-1 R5.1. MRO_URE1 was not able to review the documents and procedures referenced in CIP-005 annually, as required by CIP-005-1 R5.1, due to issues in the policies and procedures with CIP-005-1 R1 (MRO2012010820), R2 (MRO2012010821), R3 (MRO2012010822), and R4 (MRO2012010823) as described above. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-005-1 | R5; R5.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1 had partial policies and procedures in place for CIP-005. However, MRO_URE1 did not have adequate corresponding policies and procedures allowing adequate review and updating of documentation specified in CIP-005. There are accompanying CIP-005-1 R1, R2, R3, and R4 violations, which encompass the actual gap in the policies and procedures along with required documentation. The risk assessment for those violations qualifies the risk to the BPS that was introduced by MRO_URE1 not performing CIP-005-1 R5. Any policy and documentation deficiencies are being (or have been) addressed in the individual CIP-005-1 R1, R2, R3, and R4 Mitigation Plans and the individual risks are addressed in the individual CIP-005-1 R1, R2, R3, and R4 risk assessments. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) finalized all polices to support compliance with CIP-005-1 R1, R2, R3 and R4; and 2) maintained all documentation required by CIP-005-1. | 2014-12-12 | 2015-04-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010826 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R1. When it was required to be compliant, through approximately two and half years, MRO_URE1 failed to create, implement, and maintain cyber security test procedures that minimized adverse effects on the production system or its operation, as required by CIP-007-1 R1.1, and failed to document test results, as required by CIP-007-1 R1.3. MRO_URE1 did not document user and system accounts and passwords, logging, and ports and services test results until approximately two and half years after the Standard was enforceable. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R1; R1.1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the failure to implement cyber security test procedures that minimize adverse effects could result in inadvertent or malicious vulnerabilities being introduced to its system, this risk was reduced because MRO_URE1 adheres to its procedures. MRO_URE1's procedures require checking the baseline of the system after a change is applied. However, MRO_URE1's procedures do not address existing cyber security controls. By applying changes without testing cyber security controls, MRO_URE1 increased the risk of adversely impacting existing cyber security controls within its environment. MRO_URE1 had a CIP-003-1 R6 change management policy in place as of the enforceable date of the Standard. Since MRO_URE1 had an established change program, they were able to use ‘change request documents’ to troubleshoot any adverse effects on the system caused by changes. Because MRO_URE1 was managing changes per CIP-003-1 R6, the risk posed by this CIP-007-1 R1 violation was reduced. MRO also considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | present | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 will: 1) finalize and implement a written policy regarding what needs to be performed when making a significant change; and 2) retain documentation of test results. | TBD | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010827 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R2. MRO_URE1 did not establish and document a process to ensure that only those ports required for normal and emergency operations are enabled, as required by CIP-007-1 R2. MRO_URE1 did not include ports in its established and documented processes as required. However, MRO_URE1 did have established and documented processes to manage services. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the failure could result in inadvertent or malicious vulnerabilities being introduced to its system, this risk was reduced because MRO_URE1 adheres to its procedures. MRO_URE's procedures require documentation to demonstrate that ports, protocols, and services are being managed according to other standards, which includes checking the baseline of the system after a change is applied. For example, MRO_URE1 documented ports allowed in and out of the Electronic Security Perimeter (ESP) by the firewalls (boundary devices), however, it did not document the ports for each individual Critical Cyber Asset (CCA) in the ESP as required. Therefore, it did not fully address the requirements of CIP-007-1 R2. MRO observed evidence that MRO_URE1 has established and documented the processes to manage services. However, the processes do not include ports as required. This violation impacts all of the MRO_URE1 CCAs at the six different locations. There are currently twelve Solaris servers and three Windows operator workstations declared as CCAs. However, the risk to BPS reliability was reduced because MRO_URE1 was doing some port management. Additionally, MRO_URE1 had established firewall rules to monitor and limit ESP network traffic. MRO also considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 established and documented a process to ensure that only these ports required for normal and emergency operations are enabled | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) detailed what each port and service is used for; and 2) updated policy to ensure all non-CCAs and CCAs in ESP are addressed. | 2014-06-30 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010828 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R3. MRO_URE1 failed to establish and document a security patch management program that included the evaluation of cyber security patches for all Cyber Assets within the Electronic Security Perimeter, as required by CIP-007-1 R3. MRO_URE1 also failed to document the assessment of security patches within thirty calendar days of availability, as required by CIP-007-1 R3.1. Additionally, MRO_URE1 failed to document compensating measures applied to mitigate risk exposure or an acceptance of risk for patches that were not installed, as required by CIP-007-1 R3.2. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to evaluate security patches and document compensatory measures could pose a risk as most successful computer attacks exploit well-known vulnerabilities, however, while there was no evidence of the evaluation of patches, MRO_URE1 provided evidence patches were being applied. Additionally, there is a stand-alone server where patches were applied first, prior to installation on other systems. Patches applied were tested by first applying them to a backup test workstation, then applying them to non-critical Cyber Assets, before being applied to the Critical Cyber Assets (CCAs). The process of testing patches on a backup test workstation was assessed by MRO, and corroborated by scanning the process evidence from MRO_URE1. In addition, MRO_URE1 adheres its procedures that requires some level of patch management. MRO also considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) updated documentation and performed a comprehensive review for any necessary patches; 2) updated policy to better explain how the assessment is documented, and when patches will be applied or explain why they will not be applied; 3) updated policy to document how MRO_URE1 will represent mitigation when not applying patches; and 4) documented how many patches were not applied during the noncompliance period. | 2014-01-03 | 2015-02-03 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010829 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R4. MRO_URE1 failed to document and implement a process to address testing of antivirus signatures, as required by CIP-007-1 R4.2. MRO_URE1 only had a documented process for installing antivirus signatures. That process did not address testing the signatures. This affected all 15 MRO_URE1 Critical Cyber Assets (CCAs), including three Windows operator workstations and 12 Solaris primary and backup servers. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1 adheres its procedures which requires virus protection. However, MRO_URE1's procedures do not address the requirement of testing the signatures prior to installation. Applying antivirus signatures without testing increases the risk that MRO_URE1 may adversely impact existing cyber security controls within its environment. However, the risk to BPS reliability and security was reduced because MRO_URE1 was applying antivirus signatures to Solaris and Windows CCAs manually. MRO_URE1 manually installed the antivirus signatures and manually monitored the systems for issues. MRO also considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 added the required cybersecurity test to its antivirus procedure. | 2013-05-28 | 2015-04-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010830 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R5. MRO_URE1 failed to establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days for shared accounts, as required by CIP-007-1 R5.1.2. MRO_URE1 did not have logs for shared users that contained sufficient detail to identify the person that was using the shared account. MRO_URE1 was using a physical log book to denote the operator in charge at the time, but there could be more than one operator using the shared account at any given time. MRO_URE1 also failed to adequately identify and document those individuals with access to shared accounts, as required by CIP-007-1 R5.2.2. MRO_URE1 used a general overview statement to denote those individuals with access to shared accounts and did not: (1) identify those individuals with access by name or have a policy for managing the use of such accounts that limits access to only those with authorization; (2) have an audit trail of the account use (automated or manual); or (3) have steps for securing the account in the event of personnel changes (for example, change in assignment or termination) for shared accounts, as required by CIP-007-1 R5.2.3. MRO_URE1 did not manage shared user account access that allowed for audit trails and securing of the shared account when an individual no longer required cyber access. Any individual who knew the shared password would retain his or her logical access until the shared password was changed semi-annually. However, operators would need to be physically present in order to log in and there were procedures in place to remove physical access for individuals no longer authorized for physical access. After performing a comprehensive review, MRO_URE1 identified four instances where the shared password on three operator consoles at one facility were not timely changed to revoke logical access. However, physical access was revoked within seven days. All four incidents involved workstations at one facility. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R5; R5.1; R5.2.2; R5.2.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 cannot demonstrate it was adequately managing how shared user access was being administered to include the specific individual who had access, the logging of who used the shared account, and the revocation of the shared user account when logical access was no longer necessary. However, this risk was reduced because MRO_URE1 changed passwords to shared accounts semi-annually. Additionally, while the password is not changed within the seven days (or 24 hours) as required to revoke access to the shared account, the physical access required to log in to the shared accounts was revoked within the seven days (or 24 hours) as required. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) updated and established shared access processes and procedures; 2) updated policy to include a detailed statement to denote those individuals with access to shared accounts, by name; 3) finalized plans for personnel notifications; and 4) ensured shared password was changed since the last person left. | 2014-08-08 | 2015-06-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010831 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R6. MRO_URE1 did not implement and document the organizational processes and technical and procedural mechanisms for monitoring security events on Cyber Assets within the Electronic Security Perimeter (ESP), as required by CIP-007-1 R6.1. The MRO_URE1 security controls also failed to issue automated or manual alerts for detected cyber security incidents, as required by CIP-007-1 R6.2. MRO_URE1also failed to review logs of system events related to cyber security, as required by CIP-007-1 R6.5. Since when MRO_URE1 was required to demonstrate compliance with CIP-007-1 R6, MRO_URE1 had been in the process of implementing and documenting organizational process controls for system events related to cyber security, including creating the formal documentation to define what MRO_URE1 considered to be a cyber security incident. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R6; R6.1; R6.2; R6.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1 adheres its procedures, which requires documentation to demonstrate that audit trails and monitoring of systems occurs. For example, MRO_URE1 implemented firewalls to monitor and limit ESP network traffic. Evidence shows that MRO_URE1 was monitoring the firewall logs to detect unauthorized access attempts. However, this does not address the requirements of CIP-007-1 R6 related to monitoring and reviewing system events, or cyber security incidents. By failing to perform security status monitoring, MRO_URE1 was not aware of system events related to cyber security. Failing to alert for cyber security events increased the risk an adversary could have negatively impacted Critical Cyber Assets (CCAs) and Critical Assets. This violation impacts all of the MRO_URE1 CCAs at the six different locations. There are currently 12 Solaris servers and 3 Windows operator workstations declared as CCAs. MRO determined that this risk to BPS reliability was reduced because MRO_URE1 was doing some monitoring of systems as required under its procedures. MRO also considered that MRO_URE self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) configured firewalls to alert in the event of a Cyber Security incident; 2) implemented mechanism to allow monitoring of security event logs; and 3) verified successful implementation through review of monitored security event logs. | 2014-12-19 | 2015-06-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010833 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R8. MRO_URE1 did not perform annual cyber vulnerability assessments (CVAs). MRO_URE1 did not have a document identifying its CVA process, as required by CIP-007-1 R8.1. MRO_URE1 did not perform a review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter (ESP) are enabled, as required by CIP-007-1 R8.2. MRO_URE1 did not review controls for default accounts, as required by CIP-007-1 R8.3. And, MRO_URE1 did not document the results of the assessment, the action plan to remediate or mitigate vulnerabilities, and execution status of the action plan, as required by CIP-007-1 R8.4. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R8; R8.1; R8.2; R8.3; R8.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By not performing the CVA, MRO_URE1 may have un-mitigated ports and services, or default account vulnerabilities. By not documenting the CVA process or the CVA results and action plans, MRO_URE1 is not able to demonstrate clearly CVA work was performed. However, the risk posed to the BPS was reduced because MRO_URE1 adheres its procedures, which requires documentation to demonstrate that systems were assessed to mitigate vulnerabilities on a regular basis. While MRO_URE1 did not have a complete documented CVA process until approximately four years after the Standard was enforceable, MRO confirmed that MRO_URE1 had been performing work related to its procedures vulnerability management such as Retina network scans, ports and services reviews, and account reviews that covered a portion of the accounts and devices that were required to meet the CVA requirements in CIP-007-1 R8. Additionally, MRO considered that MRO_URE1 self-identified the concern and has only 15 CCAs with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) finalized documentation regarding CVAs to include documenting results of the CVA, assessing and reviewing any identified cyber vulnerabilities, and implementing action plans to mitigate any identified vulnerabilities; and 2) reviewed ports and services to confirm that only those ports and services required for operation of Cyber Assets within the ESP are enabled, and 3) reviewed and updated documentation related to user accounts; and 4) completed a CVA. | 2014-12-19 | 2015-06-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010834 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R9. MRO_URE1 did not annually review and update documentation specified in CIP-007 because MRO_URE1 did not have the required documented policies and procedures as described in the CIP-007-1 violations above. MRO_URE1 did not document changes resulting from modifications to the systems or controls within 90 calendar days of the change. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-007-1 | R9 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had partial policies and procedures in place for CIP-007. In addition, despite not having all the required formal CIP-007 policies and procedures, MRO_URE1 was taking steps to develop and document comprehensive policies and procedures for the CIP-007 requirements. The assessment for this CIP-007-1 R9 violation does not incorporate the risk associated with the related violations of CIP-007-1 R1, R2, R3, R4, R5, R6, and R8. There are accompanying CIP-007-1 R1, R2, R3, R4, R5, R6, and R8 violations, which encompass the actual gap in the policies and procedures along with required documentation. MRO also considered that MRO_URE1 self-identified the concern and has only 15 Critical Cyber Assets (CCAs) with one external serial connection to a neighboring entity from each of the six locations; and only one facility has control capability for the remaining five facilities. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1: 1) finalized all policies and maintain documentation to support compliance CIP-007; and 2) completed review of finalized policies to support compliance with CIP-007. | 2014-12-12 | 2015-04-23 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010837 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-006-1 R6. MRO_URE1 failed to implement a maintenance and testing program to ensure that all physical security systems under Requirements R2, R3, and R4 function properly, as required by CIP-006-1 R6. MRO_URE1 failed to document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) as required by R3, and further failed to implement and document the technical and physical mechanisms for logging physical entry points to the PSP as required by R4. MRO_URE1 was in the process of implementing the technical mechanisms (Physical Access Control Systems (PACS)) and did not have electronic logs until it completed implementation of its PACS system. Due to the PACS system not being completed, MRO_URE1 failed to ensure that all physical security systems required under R3 and R4 functioned properly, as required by R6. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-006-1 | R6; R6.1; R6.2; R6.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While failure to deploy technical controls for monitoring physical access could result in an unauthorized individual gaining access to Critical Cyber Assets (CCAs), the risk was reduced because MRO_URE1 was using partial procedural controls and was lacking the technical mechanism for monitoring physical access until the PACS came on line at the last location. Since the start of the mandatory compliance period, there have been physical locks on the external access points that require special keys, and in most cases, entry required PACS access to get into the gate perimeter and the inside door. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 implemented a PACS system and finalized and implemented a maintenance and testing program to ensure that the PACS system functions as required by R2, R3, and R4. | 2012-09-01 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010651 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1. MRO_URE1 did not have a process to identify all access points through each Physical Security Perimeter (PSP) and failed to document measures to control entry at those access points, as required by CIP-006-1 R1.2. MRO_URE1 did not document a PSP diagram for each PSP and did not indicate control measures to the access points in the physical security plan. Additionally, MRO_URE1 did not ensure that the Cyber Assets (Physical Access Control System (PACS)) used in the access control and monitoring of the PSPs were afforded the protective measures specified in Standard CIP-003, Standard CIP-004 R3, Standard CIP-005 R2 and R3, Standard CIP-006 R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009, as required by CIP-006-1 R1.8. MRO_URE1 did not have a complete PACS system for all Critical Assets until more than two years after the mandatory compliance date, therefore, compliance with the above standards and requirements was affected. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-006-1 | R1; R1.2; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had a documented physical security plan in place prior to when it was required to comply with CIP-006-1, however, it did not identify all control measures for each access point to the PSP. Additionally, MRO_URE1 had some controls in place for the PACS system, but it did not have a complete list of the controls as required. In addition, MRO_URE1 did not have a fully implemented PACS system in place until approximately two and half years after the Standard was enforceable. MRO considered that until the PACS came online MRO_URE1 utilized physical locks on the external access points (doors) that require special keys, and in most cases, entry required PACS access to get into the gate perimeter and the inside door. | when the Standard became mandatory and enforceable on MRO_URE1 | present | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 will: 1) determine required ports and services; 2) complete Cyber Vulnerability Assessments; 3) update PSP drawings with all access points identified; 4) test system logging on PACS software; 5) provide documentation demonstrating that PACS meets CIP-007 requirements; and 6) provide documentation showing that the PACS system is complying with R1.8. | 10/31/2015 (approved completion date) | TBD | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010652 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-006-1 R3. MRO_URE1 did not document and implement the technical controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) as required by CIP-006-1 R3. Additionally, MRO_URE1 did not have an alarm system to indicate a door, gate or window has been opened without authorization covering all PSPs as required by CIP-006-1 R3.1. MRO_URE1 was in the process of deploying a Physical Access Control System (PACS) system for all of its PSPs. During the implementation phase, MRO_URE1 did not electronically monitor access to the PSPs as required. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-006-1 | R3; R3.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While failure to deploy technical controls for monitoring physical access could result in an unauthorized individual gaining access to Critical Cyber Assets (CCAs), the risk was reduced because MRO_URE1 was using procedural controls. MRO_URE1 was lacking the technical mechanism for monitoring physical access until the PACS came on line at the last location. MRO also considered that until the PACS came online, MRO_URE1 utilized physical locks on the external access points (doors) that require special keys, and in most cases, entry required PACS access to get into the gate perimeter and the inside door. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 installed a PACS to monitor all PSPs via alarm and documented the technical controls provided by the PACS. | 2012-09-01 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010653 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-006-1 R4. MRO_URE1 failed to implement procedural and technical mechanisms for logging physical entry at all access points to the Physical Security Perimeter (PSP), as required by CIP-006-1 R4. MRO_URE1 only had manual logs that were not reviewed by security personnel. MRO_URE1 did not have electronic logs (technical mechanisms) for logging physical entry at all access points to the PSPs. MRO_URE1 was in the process of implementing the technical mechanisms (Physical Access Control System (PACS)) and did not have electronic logs until it completed implementation of its PACS system. MRO_URE1 did not hire or appoint any personnel to oversee access (security guards) at the PSP locations. Therefore, the logs were not maintained by security or other personnel authorized to control and monitor physical access as required by CIP-006-1 R4.3. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-006-1 | R4; R4.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 was using procedural controls and was lacking the technical mechanism for monitoring physical access until the PACS came on line at the last location. MRO also considered that until the PACS came online, MRO_URE1 utilized physical locks on the external access points (doors) that require special keys, and in most cases, entry required PACS access to get into the gate perimeter and the inside door. These keys were checked out to individuals (who required access) and who were required to sign for them. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 discontinued its use of manual paper logs at the PSP and installed technical mechanisms (PACS system) so that it can uniquely identify individual entry into the PSP. | 2012-09-01 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-32-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010654 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-006-1 R5. MRO_URE1 reported that it did not retain complete and adequate physical access logs for at least 90 calendar days until approximately three years after the Standard became enforceable. MRO_URE1 was in the process of implementing the Physical Access Control System (PACS) system and did not have electronic logs until it completed implementation of the PACS system. At the time of the self-certification, MRO_URE1 was not retaining complete physical access logs. Additionally, because MRO_URE1 did not hire or appoint independent employees to oversee access (security guards) at the Physical Security Perimeter (PSP) locations, MRO did not consider the manual logs to be a formal procedural control. The cause of MRO_URE1's violation was a failure to prioritize CIP compliance and devote the necessary resources to obtain and maintain compliance with CIP Reliability Standards in a timely manner. | CIP-006-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While failure to deploy technical controls for monitoring physical access could result in an unauthorized individual gaining access to Critical Cyber Assets (CCAs), the risk was reduced because MRO_URE1 was using partial procedural controls. MRO_URE1 was lacking the technical mechanism for monitoring physical access until the PACS came on line at the last location. MRO considered that until the PACS came online, MRO_URE1 utilized physical locks on the external access points (doors) that require special keys, and in most cases, entry required PACS access to get into the gate perimeter and the inside door. These keys were checked out to individuals (who required access) and who were required to sign for them. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | No Penalty (for MRO2012010813, MRO2012010814, MRO2012010815, MRO2012010817, MRO2012010818, MRO2012010819, MRO2012010820, MRO2012010821, MRO2012010822, MRO2012010823, MRO2012010824, MRO2012010826, MRO2012010827, MRO2012010828, MRO2012010829, MRO2012010830, MRO2012010831, MRO2012010833, MRO2012010834, MRO2012010837, MRO2012010651, MRO2012010652, MRO2012010653, MRO2012010654) | Self-Certification | To mitigate this violation, MRO_URE1 implemented a PACS system that allows it to retain physical access logs of individuals who enter the PSP. | 2012-11-30 | 2015-04-24 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-07-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011816 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R2.2. SERC_URE1 disabled firewall authentication during a network upgrade to troubleshoot communication issues and failed to re-enable firewall authentication following the network upgrade. This determination addresses multiple instances regarding SERC_URE1's violation of CIP-005 R2. Therefore, each instance is discussed separately. SERC learned SERC_URE1 disabled the firewall authentication approximately two weeks before it was required to be compliant with the CIP Standards, for troubleshooting purposes during a Supervisory Control and Data Acquisition (SCADA) upgrade. SERC_URE1 did not re-enable firewall authentication until approximately one and a half months after its mandatory and enforceable compliance date. SERC determined that SERC_URE1 failed to implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible, as required. The root cause of this issue was a failure to follow established change management and security controls procedures as explained in SERC2013011817 violation within this same agreement. While SERC was performing its assessment and determining the scope of the violation, it discovered an additional instance. SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 self-reported that it failed to ensure that only those ports and services required for normal and emergency operations were enabled for serial devices used as access points to the Electronic Security Perimeter (ESP). Given these facts, SERC determined that this violation should be addressed under CIP-005-3 R2.2. According to SERC_URE1, there were 21 radio access network devices involved that were from SERC_URE1's legacy SCADA system. SERC determined that SERC_URE1 did not scan, document, and disable unnecessary ports and services on these devices because they were initially thought to not have port and services capability. SERC determined that SERC_URE1 failed to enable only those ports and services required for operations and for monitoring Cyber Assets within the ESP at all access points, as required. The root cause of this issue was inadequate CIP experience. SERC determined that SERC_URE1 was in violation of CIP-005-3a R2 because it failed to implement organizational processes and technical procedures for control of electronic access at all electronic access points to the ESP. | CIP-005-3a | R2; R2.2; R2.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to implement technical and procedural mechanisms to control electronic access at all access points could have resulted in unrestricted access into the ESP, which increased the risk of Critical Cyber Assets being compromised and rendered inoperable. During the time user authentication was disabled, the SCADA system was protected by an intrusion detection system and the access control list on the firewall was restricting access to a limited set of IP addresses. Users accessing the SCADA system through the firewall had individual logins and passwords, the activity of which was being logged. All personnel with access had Personnel Risk Assessments and cyber security training. SERC_URE1 detected no incidents while the firewall authentication was turned off. The devices in the second incident were serially connected devices, which only allowed a one-way flow of information from the devices to the SCADA system. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) re-enabled the firewall authentication and adjusted the firewall rules; 2) documented the ports and services for the radio access network devices; and 3) issued reminders of its procedures. | 2013-05-21 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-07-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011817 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R1.4. SERC_URE1 had Cyber Assets within the Electronic Security Perimeter (ESP) that were not identified and protected pursuant to the requirements of Standard CIP-005-3a. SERC learned that SERC_URE1 had a network device, a hub, located within an ESP and Physical Security Perimeter that had four computer systems connected to it that were not previously identified or documented. The hub communicated between two front-end processors (FEP), a router, and the four non-critical computer systems. The four non-critical systems were used for administration of the router. SERC determined that SERC_URE1 failed to identify and protect four non-critical Cyber Assets pursuant to the requirements of Standard CIP-005-3. The root cause of this issue is inadequate preparation (documentation and thorough walk-throughs) prior to the compliance date. While SERC was performing its assessment and determining the scope of the violation, it discovered an additional instance. SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 self-reported that it connected a laptop computer to a Cyber Asset without performing its change control and configuration management procedures. SERC determined that by connecting the laptop inside an ESP, SERC_URE1 introduced a non-critical Cyber Asset within a defined ESP. Therefore, this device should have been identified and protected as required by CIP-005-3 R1.4. According to SERC_URE1, the laptop was performing port scanning on the centralized logging system. The laptop was disconnected the same day as it was discovered. SERC determined that SERC_URE1 failed to identify and protect a non-critical Cyber Assets pursuant to the requirements of Standard CIP-005-3. The root cause of this issue was insufficient training. SERC determined that SERC_URE1 was in violation of CIP-005-3a because it failed to identify and protect a non-critical Cyber Assets pursuant to the requirements of Standard CIP-005-3a. | CIP-005-3a | R1; R1.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious risk to the reliability of the bulk power system. Failing to identify and to protect Cyber Assets within the ESP could introduce vulnerabilities to the ESP and subsequently, the Critical Cyber Assets located therein. However, all of the devices involved were located in areas controlled with security card access. The non-critical computer systems did not support the energy management system (EMS) nor did they have direct access to the EMS. They were also protected by antivirus/malware software. The laptop did not have direct access to the Supervisory Control and Data Acquisition (SCADA) network and was utilized by personnel, who had undergone the required CIP training and had a completed Personnel Risk Assessments. Further, the SCADA network is monitored by a log analysis and intrusion detection system (IDS) which sends alerts to the cyber security team when it detects users attempting unsuccessful logins or unusual network traffic, where technically feasible. The laptop was only performing a ports and services scan of the centralized logging system and was not accessing the SCADA control system. The system administrator was performing the test, and had been properly processed for access to these systems and CIP-protected information. Neither the IDS nor SERC_URE1's antivirus system identified the occurrence of any security events during this session. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) unplugged the network cables from the undocumented devices; 2) reminded personnel involved that unauthorized devices cannot be connected to the ESP; 3) enhanced and implemented a checklist that reinforces the procedures for change management, the security controls and testing form, password management, and logging; 4) traced and labeled all cables connected to Cyber Assets in the ESP; 5) removed the maintenance laptop and any inappropriate network cables from the ESP; 6) provided additional guidance to the system administrator that was involved and with the other subject matter experts; 7) implemented an enhanced testing procedure process to ensure that all significant changes to Cyber Assets follow SERC_URE1 change management procedures; and 8) updated a document change control and security controls testing flow chart and included this process in in SERC_URE1's CIP change management procedures. | 2013-07-31 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-07-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011818 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R1.1. SERC_URE1 failed to deploy alternative measures to control physical access for Electronic Security Perimeter (ESP) wiring external to the Physical Security Perimeter (PSP). SERC learned that SERC_URE1 had one ESP with a fiber optic link, which spans two PSPs. Prior to its mandatory and enforceable compliance date, SERC_URE1 disabled the alternative measures (link encryption) it had in place due to communication and network issues experienced during its Supervisory Control and Data Acquisition (SCADA) system upgrade. The link encryption was scheduled to be restored as soon as the problem was resolved but was not until two months later. The change management ticket for the SCADA system upgrade did not contain enough details of all the items being addressed, so it did not capture the decision to disable the encryption, which was a part of the preparation and initial configuring of the SCADA system. Without a ticket to track the turning off and eventual turning back on of the encryption, this task was overlooked. SERC_URE1 submitted a Technical Feasibility Exception that required the link to be encrypted in order to mitigate the absence of the required physical six-wall border. The root cause of these issues was inadequate procedures (change management ticket system) and training. SERC determined that SERC_URE1 was in violation of CIP-006-3c R1.1 because it failed to deploy alternative measures to control physical access to such Cyber Assets where a completely enclosed (six-wall) border could not be established. | CIP-006-3c | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to protect communication links within the ESP could lead to an intruder intercepting network traffic to gain access to or disrupt communications between Critical Cyber Assets. However, the fiber line link could not have been modified without SERC_URE1 personnel being notified as it would have caused a network outage. In addition, the fiber link was not readily accessible as it was installed on top of electric distribution poles and/or buried underground. SERC_URE1 evaluated the protections it had in place and deemed these protections were sufficient until the encryption could be turned back on. SERC_URE1 has an intrusion detection system, the Cyber Assets inside the ESP have malware protection (where technically feasible), the endpoints of the fiber optic link are in an ESP and PSP, and the fiber optic link is wholly owned and controlled by SERC_URE1. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) scheduled a time for the encryption to be turned back on; 2) determined that a separate change management ticket will now be created to capture and track all details for each change to the ESP and/or Cyber Assets; and 3) continues to provide additional reminders emphasizing to system administrators the procedures for change management, security controls and testing form, password management, and logging to guide in the managing of complex projects like the upgrade in the instant violation. | 2012-12-19 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-07-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011819 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R1.6. An employee entered a Physical Security Perimeter (PSP) without authorized unescorted physical access. This determination addresses multiple instances regarding SERC_URE1's violation of CIP-006 R1.6. Therefore, each instance is discussed separately. A SERC_URE1 employee, who did not have authorized unescorted physical access, entered a PSP without the entry and the exit being documented. The employee, who tailgated behind two employees with authorized unescorted physical access, was continuously escorted. The employee had completed SERC_URE1's cyber security training and had a Personnel Risk Assessment (PRA) on file. The employee had been approved for access to a PSP but had not yet actually been granted that access. SERC determined that SERC_URE1 failed to document the entry and exit of a visitor, including the date and time to and from the PSP. While SERC was performing its assessment and determining the scope of the violation, it identified additional instances. SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 self-reported that it was in violation of CIP-006-3c R6. After further assessment, SERC determined that the violation should have been self-reported under CIP-006-3c R1.6. An employee with authorized unescorted physical access to a PSP escorted a visitor into the PSP but failed to log the visitor in, as required. SERC determined that SERC_URE1 failed to document the entry and exit of a visitor, including the date and time to and from the PSP. SERC_URE1 self-reported that it was in violation of CIP-006-3c R6. After further assessment, SERC determined that the violation should have been self-reported under CIP-006-3c R1.6. An employee without authorized unescorted physical access entered a PSP. While the power assist door for handicapped access door was open to allow passage of an authorized employee, the unauthorized employee tailgated into the PSP. The tailgating employee was not escorted while in the PSP. According to SERC_URE1, the unauthorized employee was inside the PSP for less than five minutes. SERC determined that SERC_URE1 failed to continuously escort and to document the entry and exit of a visitor, including the date and time to and from the PSP. The root cause for the three issues was inadequate training and awareness. SERC determined that SERC_URE1 was in violation of CIP-006-3c R1 because it failed to implement a physical security plan, as required. | CIP-006-3c | R1; R1.6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to adequately log visitors at the PSP access points created a risk that personnel were not properly supervised in the vicinity of Critical Cyber Assets (CCAs), which increased the risk of misuse or sabotage. However, the employee in the initiating instance had completed cyber security training and had a valid PRA on file. The employee in the second instance was continuously escorted and had completed cyber security training. For the third instance, the PSP was continuously manned; the individual in question was an SERC_URE1 employee, consistently observed, and was escorted out of the PSP within five minutes of entry. In each instance, the unauthorized personnel did not perform any activities involving CCAs while in the PSP. | when the first employee entered into a PSP without being logged appropriately | when the employee from second instance was escorted from the PSP | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) escorted the unauthorized employees or visitors out of the PSP and counseled employees that were involved; 2) trained management and employees on procedures for accessing PSPs; 3) conducted an investigation by the incident commander to improve its processes; 4) distributed material informing management and employees of the seriousness of violating its access control procedures; and 5) provided an additional visible component to situational awareness when visitors are in a PSP by using distinctive lanyards for visitors and escorts. Following the first instance, SERC_URE1 significantly upgraded its signage to remind employees about its procedures. After the second and third instances, SERC_URE1 made further adjustments to the signage, took disciplinary action against the employee involved in the second instance for ignoring training and the signage, and determined that the PSP awareness program needed to be expanded further. | 2013-06-28 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-07-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012550 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE1 failed to afford the protective measures specified in CIP-005-3 R2 and R3 to Cyber Assets used in the electronic access control and/or monitoring (EACM) of the Electronic Security Perimeter (ESP). This determination addresses multiple instances regarding SERC_URE1's violation of CIP-005 R1.5. Therefore, each instance is discussed separately. SERC learned that two EACM devices, an intrusion detection system and a syslog server, were not protected as specified in CIP-005-3 R2 and R3. SERC confirmed that the devices were on SERC_URE1's Cyber Asset list from the date of compliance and had been given the other protections listed in the requirements. A third device, an access control and monitoring management server, was included in the Self-Report. However, because it was a device used to authorize and log access to the Physical Security Perimeter (PSP), it will be addressed in SERC_URE1's CIP-006-3 R2.2 violation. SERC determined that SERC_URE1 failed to afford two EACMs the protective measures specified in CIP-005-3 R2 and R3. The root cause of this issue was inadequate training and CIP experience. While SERC was performing its assessment and determining the scope of the violation, it identified additional instances. SERC_URE1 self-reported that it did not ensure that the deployment of a new Cyber Asset within the ESP did not adversely affect existing cyber security controls as required by CIP-007-3 R1 (SERC2013-401726). SERC learned that SERC_URE1 installed a new network device within the ESP without following its established testing processes. SERC determined that SERC_URE1 failed to afford one EACM CIP-007-3 R1 protection, as required. The root cause of this issue was inadequate training, procedures, and CIP experience. SERC_URE1 self-reported that it failed to change a password annually on a Cyber Asset within the ESP as required by CIP-007-3a R5. According to SERC_URE1, a local user account on its centralized logging system had a password over a year old. According to SERC_URE1, it had reset the other passwords prior to its mandatory and compliance date but the process that was used to verify these actions did not identify this particular account. SERC_URE1 conducted a review and verified this was the only account with an overdue password. SERC determined that SERC_URE1 failed to change a password at least annually for one EACM, as required. The root cause of this issue was inadequate procedures. SERC_URE1 self-reported that it failed to submit a Technical Feasibility Exception (TFE) for two devices for which the use of antivirus software and other malicious software prevention tools was not technically feasible as required by CIP-007-3a R4. According to SERC_URE1, it discovered that two network devices installed could not implement antivirus or antimalware software and a TFE documenting the compensating measures that were in place had not been submitted. Approximately a month after the installation of the network devices, SERC_URE1 submitted a TFE for the network devices. SERC determined that SERC_URE1 failed to submit a TFE for EACM devices not capable of using antivirus software and other malicious software prevention tools as required. The root cause of this issue was inadequate training. SERC_URE1 self-reported that it discovered that it failed to review all user accounts at least annually as required by CIP-007-3a R5. SERC learned that SERC_URE1 did not review any of the user accounts on a remote authentication dial-in user service server. SERC determined that SERC_URE1 failed to review all user accounts at least annually, as required. The root cause of this issue was inadequate training and CIP experience. SERC_URE1 self-reported that it failed to ensure that only those ports and services required for normal and emergency operations were enabled as required by CIP-007-3a R2. SERC verified that SERC_URE1 had established and documented a process, but it failed to implement it before placing the central logging server into production. SERC determined that SERC_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled, as required. SERC determined that SERC_URE1 was in violation of CIP-005-3a R1.5 because it failed to afford Cyber Assets used in access control and/or monitoring of the ESPs the protective measures specified in CIP-005-3a R1.5. The root cause of this issue was inadequate processes and procedures. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to identify and to protect EACM devices could introduce vulnerabilities to the ESP and subsequently, the Critical Cyber Assets (CCA) located therein. In the initiating instance, the devices were deployed within a protected enclave and within a PSP. In addition, only authorized personnel had access. In the second instance, the device had no direct control, access, or monitoring capability of the BPS. In the third instance, all users on the systems in question had been authorized for access to SERC_URE1's CCAs and/or CCA information. There was only one authorized account found with an overdue password. In the fourth instance, compensating measures had been deployed upon commissioning of the Cyber Asset; however, SERC_URE1 failed to perform the administrative function of documenting the compensating measures through the TFE process. In the fifth instance, external access to the Cyber Assets within the ESP required strong two-factor authentication and all personnel with access had valid Personnel Risk Assessments and current cyber security training. In the last instance, the logging servers were deployed within an ESP and a PSP with limited electronic and physical access. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) replaced the central logging system with a new system inside the ESP and relocated its intrusion detection system inside the ESP for the first instance; 2) developed a comprehensive security controls testing form to ensure a more thorough review before new assets are placed into service; 3) disconnected the device that was prematurely installed in the ESP until all steps in the new procedure have been properly executed; 4) ran a complete baseline scan for the central logging solution server; 5) revised its security controls testing form to include a checklist for new assets; 6) filed a TFE regarding the antivirus issue; 7) conducted a review of user accounts; 8) updated the CIP access request form to separately indicate the RADIUS account; 9) changed the logging solution account's password and conducted a review on all Cyber Assets to review password changes; and 10) established periodic dates to check/change passwords on those systems that cannot automatically enforce SERC_URE1's password policy, set reminders of these dates were entered into compliance software to prompt administrators to perform this action prior to the due date, and included a check of password aging as part of the specifications for the annual cyber vulnerability assessment and provided the new process to system administrators and/or supervisors along with the notice to them of the annual password change. | 2013-08-23 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-06-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012551 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R3. SERC_URE1 failed to review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every 90 calendar days where alerting was not technically feasible. This determination addresses multiple instances regarding SERC_URE1's violation of CIP-005 R3. Therefore, each instance is discussed separately. SERC learned that two access points to the field devices were not retaining its event logs for 90 days due to excessive activity. The access points were two firewalls, which did not allow for automatic alerts or notifications and required a manual review at least every 90 calendar days. With the commissioning of SERC_URE1's automation project, excessive communication errors were being generated. These errors filled up the buffer faster than would occur during normal operation, which prevented the retention of the logs for the review of unauthorized access attempts. SERC determined that SERC_URE1 failed to review access logs for attempts at or actual unauthorized accesses at least every 90 calendar days, as required While SERC was performing its assessment and determining the scope of the violation, it found an additional instance. SERC_URE1 self-reported that it failed to perform monitoring of all of its access points to the Electronic Security Perimeter (ESP) twenty-four hours a day, seven days a week. As a result of the configuration of the access points, security events were not recorded for brief periods during system or network outages. According to SERC_URE1, since the fall the prior year, there had been approximately 15 minutes when monitoring of security events did not occur. This instance involved several devices inside the ESP that were configured in such a way that, in the event that the centralized logging solution server were restarted, their logs would not be captured during the few minutes of the rebooting process. SERC determined that SERC_URE1 failed to implement an electronic process for monitoring and logging access at access points to the ESP twenty-four hours a day, seven days a week. The root cause of this issue was deficient security controls and testing procedures as explained in SERC2013011817 violation within this same agreement. SERC determined that SERC_URE1 was in violation of CIP-005-3a R3 because it failed to implement electronic or manual processes for monitoring and logging access at access points to the ESP twenty-four hours a day, seven days a week. | CIP-005-3a | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to monitor and to log access to the ESPs twenty-four hours a day, seven days a week could have resulted in SERC_URE1 not being alerted to unauthorized attempts to access the ESP. Implementing monitoring and logging greatly reduces the risk of Critical Cyber Assets (CCAs) being compromised and rendered inoperable. However, all of the devices resided within a Physical Security Perimeters. Communication from the two firewalls to the distribution voltage level field devices was encrypted. Individuals with authorized access to the devices had an approved Personnel Risk Assessment and the required cyber security training. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) worked with the vendor to resolve the buffer issue; 2) manually pulled and checked the logs for both routers every 90 days; 3) ran the annual risk-based assessment methodology which resulted in the first instance's devices no longer being considered as CCAs. SERC_URE1 continued to work toward a solution to install a new firewall to completely separate this equipment from the ESP and then transferred the devices after the firewall was installed; 4) installed a redundant centralized logging server to ensure no gaps existed if the primary server was restarted; and 5) sent a refresher email to system administrators and reinforced the procedures for change management, security controls and testing form, password management, and logging. | 2014-10-23 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-06-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012555 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R6. SERC_URE1 failed to perform security status monitoring for two types of devices within the Electronic Security Perimeter (ESP). This determination addresses multiple instances regarding SERC_URE1's violation of CIP-007 R6. Therefore, each instance is discussed separately. According to SERC_URE1, three network-attached storage (NAS) devices and two encryption devices were not sending event logs to the central logging server. The NAS devices were Critical Cyber Assets (CCA) used for backing up the supervisory control and data acquisition (SCADA) data and server configurations. The encryption devices were non-critical Cyber Assets within the ESP used to encrypt data between the primary and backup SCADA systems. SERC determined that SERC_URE1 failed to ensure that all Cyber Assets within the ESPs, as technically feasible, implemented automated tools to monitor system events that are related to cyber security. The root cause of this issue was insufficient training and understanding of the CIP standards. While SERC was performing its assessment and determining the scope of the violation, it identified additional instances. SERC_URE1 self-reported that it failed to perform monitoring for Cyber Assets within the ESP during outages of the system log server. As a result of the configuration of four switches, security events would not be recorded for a brief period during system or network outages. According to SERC_URE1, since the fall the prior year, there had been approximately 15 minutes when monitoring of security events did not occur. SERC determined that SERC_URE1 failed to ensure that all Cyber Assets within the ESPs, as technically feasible, implemented automated tools to monitor system events that are related to cyber security. The root cause of this issue was insufficient understanding of the CIP standards and system capability knowledge. SERC_URE1 self-reported that it failed to perform security status monitoring for three printers. The three printers were non-critical Cyber Assets and were not capable of producing and forwarding security logs. However, SERC_URE1 did not file a Technical Feasibility Exception (TFE) for these devices. SERC_URE1 removed the printers from the ESP approximately two weeks prior to the submittal of the Self-Report. SERC determined that SERC_URE1 failed to file a TFE for the devices, as required. The root cause of this issue was insufficient understanding of the CIP standards and system capability knowledge. SERC determined that SERC_URE1 was in violation of CIP-007-3a R6 because it did ensure all Cyber Assets within the ESP, as technically feasible, implement automated tool or organizational process controls to monitor system events that are related to cyber security. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to monitor system events that are related to cyber security for its Cyber Assets within the ESPs could have resulted in a security breach going undetected. An undetected security breach may have compromised or rendered CCAs inoperable, which could significantly impact the BPS. However, all of the devices resided within an ESP and Physical Security Perimeters. The encryption devices encrypted traffic between two points within SERC_URE1's single ESP. The NAS was solely responsible for the historic storage of data. Individuals with authorized access to the devices had an approved Personnel Risk Assessments and the required cyber security training. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) removed all printers from within the ESP; 2) reconfigured the devices to forward logs to the centralized server; 3) installed a redundant centralized server so there will no longer be an issue during a reboot or failure of the syslog server; and 4) double-checked all devices in the ESP to ensure that those devices are either sending their logs to the centralized logging solution or are placed on a list for manual review. | 2014-08-01 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-06-30 | FERC | NP15-30-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012862 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R2.2. SERC_URE1 failed to afford Cyber Assets that authorize and/or log access to the Physical Security Perimeters (PSPs) the protective measures specified in Standard CIP-007-3a R8. This determination addresses multiple instances regarding SERC_URE1's violation of CIP-006 R2. Therefore, each instance is discussed separately. SERC_URE1 discovered that it failed to perform a Cyber Vulnerability Assessment (CVA) on two Physical Access Control Systems (PACS) control panels. According to SERC_URE1, it thought the control panels did not have ports and services capabilities so it did not create a baseline for the control panels. Because of this oversight, a CVA was not performed on the control panels. SERC determined that SERC_URE1 failed to afford two PACS devices CIP-007-3a R8 protection, as required. While SERC was performing its assessment and determining the scope of the violation, it identified additional instances. SERC_URE1 self-reported that a PACS device was not afforded the protective measures specified in CIP-005-3a R2 and R3. SERC_URE1 failed to implement the technical and procedural mechanisms to control access to the access control and monitoring management (ACM) server, which was used to authorize and log access to the PSP. In addition, SERC_URE1 failed to implement either an electronic or a manual process for monitoring and logging access to the device twenty-four hours a day, seven days a week. SERC determined that SERC_URE1 failed to afford the ACM CIP-005-3a R2 and R3 protections, as required. SERC_URE1 self-reported that it failed to set up automated logging or a manual logging process for several PACS devices as required by CIP-007-3c R6. SERC learned that logging was not being performed for two control panels and a server. Although the PACS server was transmitting its logs, SERC_URE1's central logging solution was not configured to capture the logs. The control panels were not capable of performing logging and SERC_URE1 had not submitted a Technical Feasibility Exception. SERC determined that SERC_URE1 failed to afford three PACS devices CIP-007-3a R6 protection, as required. SERC_URE1 self-reported that two control panels were not afforded the protective measures specified by CIP-007-3a R2. According to SERC_URE1, it did not know that the control panels had ports and services capabilities so it did not ensure that only those ports and services required for normal and emergency operations were enabled. SERC determined that SERC_URE1 failed to afford two PACS devices CIP-007-3a R2 protection, as required. SERC_URE1 self-reported that it discovered an unidentified non-critical Cyber Asset, a PACS control panel, which was directly connected to the Electronic Security Perimeter (ESP) and was not identified as a Cyber Asset within the ESP. SERC_URE1 discovered the Cyber Asset while performing a trace of its physical wiring as part of its mitigation activities for the violation reported in an earlier Self-Report (SERC2013011818). SERC determined that SERC_URE1 failed to identify and protect a non-critical Cyber Assets pursuant to the requirements of Standard CIP-005-3. The root cause of these issues was a lack of understanding of system capabilities. SERC determined that SERC_URE1 was in violation of CIP-006-3c R2.2 because it failed to afford Cyber Assets that authorize and/or log access to the PSP all of the protective measures specified in CIP-006-3c R2.2. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to protect PACS devices could leave those PACS devices vulnerable to disabling or misuse, resulting in unauthorized physical access to Critical Cyber Assets protected within the PSPs. However, no PSP access could be added or removed from the control panels themselves. In addition, the access control and monitoring management server was in a secured network zone protected by firewalls. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $0 (for SERC2013011816, SERC2013011817, SERC2013011818, SERC2013011819, SERC2013012550, SERC2013012551, SERC2013012555, and SERC2013012862) | Self-Report | To mitigate this violation, SERC_URE1: 1) ran a complete baseline scan for the PACS controlled panels and worked with the PACS vendor to document the baseline results; 2) set up automated logging to resolve the situation where the PACS server's logs were not being collected by the central logging server and prior to the automated logging being set up, SERC_URE1 conducted a manual review of the logs; 3) moved the directly-connected PACS control panel completely within the ESP and began a project to install a new server with a second instance of the existing PACS product; 4) expanded the review and approval of the annual CVA to include multiple reviewers to verify that all assets identified as NERC-CIP Cyber Assets will be included in the CVA; 5) included verification of logging capabilities and follow-through to ensure logs are collected in the security controls testing process; 6) implemented testing procedure process to ensure that all significant changes to Cyber Assets follow SERC_URE1's change management procedures; and 7) updated a document change control and security testing flow chart that encapsulates the process that further documented in the next revision of the CIP change management procedures. | 2014-03-25 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 will complete above-and-beyond actions to support SERC_URE1's transition to Version 5 of the CIP Standards. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. SERC determined that a zero dollar ($0) penalty was appropriate because SERC_URE1 has no prior CIP violations, and SERC_URE1 agreed to complete above-and-beyond actions.
2015-06-30 | FERC | NP15-30-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013772 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007 R5. Based on the information included in the CIP-007 R5 Self-Report and on interviews and data request responses provided by WECC_URE1, WECC determined WECC_URE1 was also in violation with CIP-006-3c R2. WECC_URE1 reported that it failed to provide protection of Physical Access Control Systems. WECC_URE1 mistakenly granted physical access for 18 individuals that did not have authorization for physical access. WECC determined that WECC_URE1 failed to follow its documented change control procedures for two devices during the transition to the new Physical Access Control and Monitoring (PACM) system. As a result of not following those procedures, WECC_URE1 failed to afford all the protective measures outlined in CIP-006-3 R2.2 to the two devices, specifically the protections of CIP-003 R6 and CIP-007 R1, R3, R4, R6, and R9. The two devices in scope included one workstation for guards to view alarms, and one physical access control server. The root cause of the violation was WECC_URE1's failure to follow its change control procedures. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to follow its documented change control procedures for one workstation for guards to view alarms and one physical access control server during a transition to a new system, resulting in those devices not receiving all the required CIP protections. Failure to follow change control and configuration management processes for the two devices could potentially allow adding or modifying hardware and software changes that could be harmful to PACM devices. Such malicious access to the workstation and physical access control server could be used to manipulate physical access to Physical Security Perimeters (PSPs), potentially giving the attacker physical access to restricted areas. However, WECC_URE1 implemented preventive controls to help prevent unauthorized physical access to the devices in scope. First, neither the workstation nor the physical access control server allowed physical access into the building, only into the cage where the Critical Cyber Asset (CCA) resided. A separate system was needed to gain access to the building, thus limiting the scope of potential unauthorized access to WECC_URE1 employees with authorized access to the building. Additionally, neither the workstation nor the physical access control servers were enabled with remote accessibility, thereby reducing the likelihood of malicious users gaining external access of these devices. | when the two devices were installed | when the two devices were provided CIP protections | $50,000 (for WECC2014013772, WECC2014013754, WECC2014013973, and WECC2014013628) | Self-Report | To mitigate this violation, WECC_URE1: 1) created change management requests (CMRs); 2) performed NERC testing; 3) received CMR approval; 4) implemented the CIP protections of CIP-003 R6 and CIP-007 R1, R3, R4, R6, and R9 for both devices; and 5) large scale project changes in the future will have a 100% validation, instead of a sampling for accuracy immediately following completion. | 2014-11-24 | 2015-01-28 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. WECC considered WECC_URE1's CIP-006 R1.8 compliance history to be an aggravating factor in the penalty determination.
2015-06-30 | FERC | NP15-30-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013754 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R1. WECC_URE1 reported that on commissioning of a program for automated alerting, four configuration issues arose that prevented automated alerting from working properly. The four Cyber Assets in scope are used in the logging and monitoring of Physical Security Perimeters (PSPs) and Electronic Security Perimeters (ESPs), collecting generator data, and network time server data. WECC determined that WECC_URE1 failed to verify that alerting for detected system events was properly functioning after a significant change. However, WECC determined that while the devices did not have automated alerting due to the change, WECC_URE1 was conducting manual review of the logs as allowed by CIP-007 R6 (the violation was originally reported as a CIP-007 R6). Because WECC_URE1 was not in violation of the Standard listed in the Self-Report, WECC determined a Self-Report for a possible violation of CIP-007-3a R1 was warranted to address WECC_URE1's failure to verify that new Cyber Assets or significant changes did not adversely affect existing controls. The root cause of the violation was a lack of training, personnel did not know how to properly configure the devices. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to verify that changes made to four Cyber Assets did not adversely affect existing security controls. The four Cyber Assets are used in the logging and monitoring of PSPs and ESPs, collecting generator data, and network time server data. Failure to implement security controls to monitor cyber security system events could allow unauthorized access to Cyber Assets to go unnoticed and unchecked. Specifically, as these devices are used to monitor Cyber Assets essential to the reliable operation of WECC_URE1's Critical Assets. If these devices were compromised by a malicious individual, the individual could use such access to disable logging and monitoring functionality for CCAs. Were that to happen, WECC_URE1 may be unaware of the compromised Cyber Asset, potentially allowing malicious access to these assets to go unnoticed and unchecked. However, WECC_URE1 implemented preventive measures to aid in the prevention of unauthorized or malicious access. Specifically, the devices in scope do not have remote access capability, or any direct control of CCAs. Also, the devices in scope were in both logically and physically secure areas surrounded by hardened and secure boundary devices. WECC_URE1 also had detective controls to aid in the early detection of unauthorized or malicious access. WECC_URE1 performed manual reviews of the system event logs on intervals of less than 90 days, thereby reducing the duration that system events would go unnoticed and unchecked. | when WECC_URE1 began utilizing the alerting program | when WECC_URE1 configured the devices for automated alerting | $50,000 (for WECC2014013772, WECC2014013754, WECC2014013973, and WECC2014013628) | Self-Report | To mitigate this violation, WECC_URE1: 1) configured the devices in scope to do automated alerting; and 2) implemented an automated solution for detecting loss of its automated alerting functionality to prevent future violations. | 2014-02-04 | 2014-05-07 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. WECC considered WECC_URE1's CIP-007 R1 compliance history to be an aggravating factor in the penalty determination.
2015-06-30 | FERC | NP15-30-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013973 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-007-1 R2. WECC determined that WECC_URE1's monthly ports and services scan results were different from its baselines. WECC_URE1's tool was misconfigured and therefore providing inaccurate information for all Windows based Cyber Assets. The tool was used for generating baselines and for asset scans to identify running ports and services. As such, WECC_URE1 failed to ensure that only those ports and services necessary for normal and emergency operations were enabled. The root cause of the violation was a failure in technology management in that the tool used for generating baselines was improperly configured. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE1 failed to ensure that only those ports and services required for normal and emergency operations are enabled. However, failing to ensure that only those ports and services necessary for normal and emergency operations are enabled poses an increased risk to WECC_URE1's Cyber Assets. This increased risk may allow for unauthorized internal and or external access, which could allow for successful cyber-attacks against Critical Cyber Assets (CCAs) essential to operation of the BPS, thereby disrupting the operation of the BPS. The risk was reduced because WECC_URE1 uses strong perimeter controls and active logging with third-party monitoring and alert generation to help prevent cyber attacks. The alert generation provides visibility to all activity on the networks. WECC_URE1 performs monthly ports and services scans and reviews so changes to the network are identified quickly. | when the Standard became mandatory and enforceable on WECC_URE1 | when WECC_URE1 confirmed that all device ports and services match the baseline of the properly configured tool | $50,000 (for WECC2014013772, WECC2014013754, WECC2014013973, and WECC2014013628) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) properly configured the tool; 2) verified that all ports and services matched the baseline from the newly configured tool; and 3) performed periodic scans and verifications of all Windows and non-Windows devices. | 2014-11-17 | 2015-01-27 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's CIP-007 R2 compliance history to be an aggravating factor in the penalty determination.
2015-06-30 | FERC | NP15-30-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013628 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. Specifically, WECC_URE1 reported that it had implemented a new security system for access to its Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). However, WECC_URE1 failed to input accurate information for some individuals thereby failing to ensure that individual and shared system accounts and authorized access permissions were consistent with the concept of “need to know” with respect to work functions performed. WECC determined that while WECC_URE1 was restructuring its Active Directory, WECC_URE1 failed to accurately input information for three individuals, leading to those individuals being granted logical access incorrectly. These three individuals were given administrative level privileges and logical access to the Core system which is typically used to control the entity’s generation. In doing so, WECC_URE1 failed to ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. The root cause of the violation was a lack of training on validating access requests. | CIP-007-3a | R5; R5.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to ensure that user accounts were implemented as approved by designated personnel for three individuals. The devices in scope are capable of manipulating turbines and disrupting communication. However, one of the individuals was unable to use the account they were granted access to because the person had no physical or logical way of accessing the device the account gave access to. None of the individuals were notified of the access they were granted and thus were unaware they had the ability to access the devices. Additionally all three individuals were authorized for access to other Critical Cyber Assets (CCAs) and thus had appropriate Personnel Risk Assessments (PRAs) and training, reducing the likelihood of misuse of CCAs. Also, WECC_URE1 conducts quarterly reviews of access rights to verify that accounts are implemented as authorized, thus limiting the possible duration of a similar issue. Finally, WECC_URE1 had active logging and alerting enabled on the devices to detect if incorrect passwords were input too many times. | when WECC_URE1 granted access to an ESP to personnel not authorized for such access | when all employees had the appropriate access | $50,000 (for WECC2014013772, WECC2014013754, WECC2014013973, and WECC2014013628) | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked access for Employee 1; 2) met with the administrator to discuss the importance of validating any and all changes; and 3) granted access for Employee 2 and Employee 3, as the access was required for job function. | 2014-02-20 | 2014-12-01 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. WECC considered WECC_URE1's CIP-007 compliance history to be an aggravating factor in the penalty determination.
2015-06-30 | FERC | NP15-30-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011657 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation CIP-002-1 R3. WECC_URE2 reported that it failed to identify three Critical Cyber Assets (CCAs) as being essential to the operation of three Critical Asset substations. WECC reviewed WECC_URE2's Self-Report and contacted the entity to request additional information. WECC determined that WECC_URE2 failed to identify three devices as CCAs essential to the operation of three Critical Asset substations. WECC determined that the devices in scope of the violation were three analog dial-up modems connected to remote terminal units (RTUs) that could be accessed through a dial-up connection. The root cause of the violation was lack of internal controls since these three CCAs could have been identified if the internal controls had been better. The RTUs were not classified as CCAs during the annual risk-based assessment methodology (RBAM) and CCA annual review as the review indicated that the RTUs only had non-routable connections. | CIP 002-1 | R3; R3.3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, WECC determined that WECC_URE2 failed to identify three dial-up modems provisioning dialup access to RTUs that controlled breakers at three substations. Left unprotected, these devices could be accessed and used to control breakers at any one of the three substations. In the event of a system event, breakers at two of the both the substations are identified as part of WECC_URE2 System Restoration Plan. Misuse or malicious attack rendering these breakers inoperable, therefore, could pose risks to system restoration. Unidentified CCAs are not afforded protective measures prescribed under CIP-003 through CIP-009. Further, unidentified CCAs that are located within integrated systems render the entire system vulnerable to attack. Electronic or physical access to these devices may not be controlled or monitored. Unidentified devices may be used as a gateway into Electronic Security Perimeters containing identified CCAs. The risks posed by WECC_URE2's noncompliance are limited given compensating measures in place during the violation period. Although the devices were not identified as CCAs, the devices were afforded a number of physical protective measures. All three devices were physically secured and afforded the protections of CIP-006. Each of the three devices were located within a Physical Security Perimeter (PSP). Physical access to the devices was limited to individuals who completed personnel risk assessments (PRAs) and cyber security training. Physical access was logged and monitored. Unauthorized physical access attempts would have triggered alarming notifying WECC_URE2 staff. Access to these devices required access to WECC_URE2's internal network. The devices were also afforded a number of electronic protective measures. Two of the devices could only be accessed after logging on to WECC_URE2's corporate network. Electronic access to the corporate network was restricted to WECC_URE2 staff. Access to the corporate network was logged and monitored and all three devices were electronically monitored on a 24 hour a day, seven day a week basis by WECC_URE2 operators via supervisory control and data acquisition (SCADA). In addition, none of the dial-in numbers for the devices were publicly listed. Lastly, all three facilities named in this violation are no longer considered critical facilities by application of newly adopted CIP-002 version 5 (v.5) critical asset determination methodology. Under the newly adopted v.5 methodology, these facilities are now rated “low.” | when the Standard became mandatory and enforceable on WECC_URE2 | when the modems were disconnected | 10000 | Self-Report | To mitigate this violation, WECC_URE2: 1) removed the modems; 2) had the compliance engineer and IT supervisor verify the removal of the dial up modems; 3) contracted with an independent consultant to review WECC_URE2's RBAM and associated CCA evaluation and identification process; 4) utilized the findings of this assessment to improve the internal controls which support the asset identification process; and 5) developed and provided training for employees and contractors who work at Critical Asset facilities on the appropriate use of routable protocols inside the PSP of Critical Assets. | 2013-06-30 | 2013-08-01 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition to the monetary penalty, WECC_URE2 submitted to WECC a narrative describing how WECC_URE2 developed procedures to: 1) ensure WECC_URE2 continues to foster a culture of compliance and awareness beginning with upper management; 2) incorporate compliance observations in the WECC_URE2 notifications; 3) continually incorporate compliance topics and updates into existing safety and weekly meetings; and 4) formalize a risk assessment process for NERC Reliability Standards. WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2015-06-30 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014014007 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4.2. Further review by FRCC determined this to be a violation of CIP-003-3 R1. A FRCC_URE1 janitorial contract supervisor failed to follow FRCC_URE1's cyber security policy regarding revocation and termination of physical access to Critical Cyber Assets (CCAs). In addition, a janitorial contractor (#1) failed to follow FRCC_URE1's cyber security policy and allowed an unauthorized individual to use their access badge. A FRCC_URE1 janitorial contractor (#1) was scheduled to begin a leave of absence. The janitorial contractor (#1) gave the FRCC_URE1-issued access badge to the janitorial contract supervisor at the conclusion of the work shift. On the following day, the janitorial contract supervisor was supposed to train a new janitorial contractor (#2), but was involved in a traffic accident. The janitorial contract supervisor contacted janitorial contractor (#1) and requested they retrieve the badge from them at the accident site, conduct the training to the new janitorial contractor (#2), and then turn the access badge over to a janitorial contractor (#3) for "safe-keeping" until it could be retrieved. Janitorial contractor (#1), however, handed the badge over to janitorial contractor (#2) and instructed them to "use that badge" until their badge arrived. This provided unauthorized access to janitorial contractor (#2), and violated FRCC_URE1's cyber security policy. A FRCC_URE1 administrator discovered the use of the janitorial contractor's (#1) access badge and was advised that the contractor (#1) was out of the country. Two days later, FRCC_URE1 administrator discovered that contractor's (#1) access badge had been used again at a non-CIP FRCC_URE1 facility. FRCC_URE1 then removed CIP access, and immediately disabled the badge. FRCC_URE1 retrieved the badge and it was provided to the access control office for destruction. The underlying root cause was the result of inadvertent behavior and poor management controls on the part of FRCC_URE1's janitorial company in following the established FRCC_URE1 cyber security policies. | CIP-003-3 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to follow cyber security policies with regard to revocation of access in a timely fashion as well as inappropriate sharing of access can result in unauthorized access to CCAs making them vulnerable to physical alteration or destruction. The risk was increased because the access badge to be revoked provided access to CCAs, and was given to an unauthorized contractor who did not have a NERC CIP-level personnel risk assessment on file, had completed no cyber security training, and subsequently used the access badge to gain access to a non-CIP FRCC_URE1 facility. The risk was reduced because the FRCC_URE1 is manned 24 hours a day, 7 days a week with authorized personnel who are aware of the duties performed by the janitorial staff, and as such would not expect nor allow physical contact to the CCAs by the janitorial staff. In addition, the janitorial staff did not have any electronic access to the CCAs. | date access badge was given to an unauthorized user | date access was removed | $13,000 (for FRCC2014014007 and FRCC2014014081) | Self-Report | To mitigate this violation, FRCC_URE1: 1) removed the CIP access privileges from the janitorial contractor (#1) badge and disabled the badge; 2) held a security “stand down” meeting between the FRCC_URE1 Facilities’ management company and the janitorial vendor regarding the inappropriate badge use incident and actions taken; 3) issued disciplinary notices to two of the janitorial contractors involved in the incident; 4) conducted an audit of the Facilities’ janitorial vendor badges that have access to determine if the janitorial contractors assigned to this site are in possession of their access badge, still employed by the vendor, and continue to require access to the Physical Security Perimeter (PSP); 5) performed a review of the existing cyber security training for contractors that have physical-only access; 6) released the new physical-only cyber security training to the appropriate FRCC_URE1 sites; 7) conducted a lessons-learned meeting with the management from the Facilities’ management company and janitorial vendor. 8) retrained all of its janitorial employees regarding FRCC_URE1's security requirements for access, each individual is now required to sign a certification document acknowledging training completion and understanding of the material; 9) reviewed its new hire package for the Facilities’ janitorial vendor to determine if the instructions regarding the use of the FRCC_URE1 issued access badge is clear and concise, FRCC_URE1 will continue to make recommendations for enhancements as appropriate and future updates to the package by the janitorial vendor will be reviewed and approved by FRCC_URE1 for implementation by the janitorial vendor; and 10) developed and released a Spanish version of the cyber security training for use by contractors that have physical-only access whose primary language is Spanish. | 2015-01-23 | 2015-03-09 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-06-30 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014014081 | Settlement Agreement | FRCC_URE1 submitted a Self-Report indicating that it was in violation of CIP-007-3a R6. FRCC_URE1 failed to review logs and retain them for the required 90 days related to a number of Cyber Assets. At one generation site, one local logging and monitoring device failed. The device was a Cyber Asset responsible for collecting and forwarding the logs for Critical Cyber Assets (CCAs) to the central logging and monitoring repository. The device failure resulted in an ability to collect and preserve CCA event logs for 21 hours. The device sustained an unrecoverable hardware failure. The failed Cyber Asset was replaced the next day. While logging and monitoring still occurred on the CCAs, the forwarding of these events to the central repository did not happen for 21 hours. Local logs were still available if any events needed to be investigated, but were never reviewed. The collector Cyber Asset only collected and forwarded new log events once it was back up and running. The root cause of this failure was a hardware failure, a lack of a manual process to review logs while the collector was unavailable, and the inability to collect logs for retention during the failure window. | CIP-007-3a | R6; R6.4; R6.5 | Lower | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because the CCAs continued to log cyber security events while the collector was down and the duration of the outage was only 21 hours. The risk was further reduced because all of the CCAs are within an Electronic Security Perimeter and a Physical Security Perimeter. | when logging and review of events failed | when logging and review of security events resumed | $13,000 (for FRCC2014014007 and FRCC2014014081) | Self-Report | To mitigate this violation, FRCC_URE1: 1) updated the CCA add-remove checklist to include steps to manually review logs in the event of a logging and monitoring device outage/failure; 2) communicated the updated changes to the CCA add-remove checklist to the responsible individuals; 3) updated the security status monitoring procedure; and 4) communicated the updated changes to the security status monitoring procedure to the responsible individuals. | 12/18/2014 | 3/9/2015 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC determined that FRCC_URE1's compliance history should not serve as a basis for aggravating the penalty.
2015-06-30 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014013853 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. FRCC_URE2 failed to provide protection from unauthorized physical access (R2.1) for 28 workstations used to change access to the Physical Access Control System (PACS), and also did not afford the protective measures specified under R2.2 The root cause for FRCC_URE2 failing to provide adequate protection from unauthorized physical access for the workstations was due to a mis-interpretation of CIP-006-3c R2 | CIP-006-3c | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to provide protection from unauthorized physical access for the workstations leaves the workstations vulnerable to physical attacks, which could lead to electronic cyber threats of the PACS servers and access control units. The risk of physical access to the workstations was reduced because all workstations were under video camera surveillence. Many were located in buildings requiring cardkey controlled access. The risk for electronic cyber threats is reduced because users must have an account on the domain in order to log into the workstations. Furthermore, users must have additional login credentials to access the cardkey system software on the workstations. No harm was known to have occurred. | when the workstations were put in service | expected Mitigation Plan completion | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) researched and determined virtual or remote options and application system requirements for PACS workstations; 2) removed non-NERC facility badging application from PACS workstations and selected, purchased, and installed stand-alone visitor badging workstations; 3) provided cyber and physical protections for badging workstations: 4) installed an application on the test virtualization option to ensure cardkey system/ and workstation functioned as expected; 5) provided monitoring capabilities for the workstation at the central monitoring station, on-boarded as a NERC protected device, and provided it physical protections; 6) developed job aids and training materials that will be used during implementation of the virtual or remote options; and 7) implemented selected approach for removing direct access to PACS, onboard workstations as NERC protected devices, and implement physical protections. | 2015-04-01 | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-06-30 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014013999 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R5.2.1 and R5.3. FRCC_URE2 failed to perform annual password changes for software accounts and failed to change passwords on default accounts before commissioning. In the first instance, during the annual password change for the software accounts at a power station, it was determined that 12 software account/password combinations on seven Critical Cyber Assets (CCAs) could not be changed because the previous passwords were not known due to a failure in the process for documenting passwords. FRCC_URE2 successfully changed the software account passwords by a later date. The affected devices made up fewer than 3% of the over 500 default account passwords annually across the NERC environment FRCC_URE2 manages. In the second instance, during a self-evaluation it was discovered by a cyber security analyst that the passwords for three default accounts on one storage array had not been changed upon commissioning of the CCA. This array provide storage capacity to four virtual machine hosts and virtual machines clients used as CCAs within an Electronic Security Perimeter (ESP). A review of documentation provided indicated that only three default accounts (i.e., ftp, monitor, and manage) are installed on the Cyber Assets as delivered. However, while investigating this instance, a subject matter expert (SME) discovered an article describing a fourth hidden "admin" account on storage arrays. This "admin" account was not disclosed by FRCC_URE2’s vendor compliance questionnaire. Upon further research, the SME located a customer advisory which indicates that the account has necessary privileges that are used by internal processes running on the array. The hidden "admin" account is only shown if a specific command, "show user admin" is issued through the command line. The account cannot be seen using the "show users" command or through the graphical user interface. The manage account passwords had been changed and verified prior to commissioning. However, the ftp and monitor accounts were overlooked and the passwords were not changed. Additionally, the password for the "admin" account was also not changed because it was unknown to the SME as commissioning time. All passwords were changed and unneeded default accounts were removed. The root cause of not performing the annual password change was failure to properly note the previous passwords, while the root cause of not changing the default passwords was determined to be an oversight by a subject matter expert (SME) for two of the accounts and incorrect disclosure by the vendor on the third account. The vendor had identified two of the default accounts on a vendor compliance questionnaire. However, the accounts were inadvertently overlooked by the SME and they were not disabled nor were the default password values changed. The third account was not disclosed and therefore unknown to FRCC_URE2 at the time of commissioning for the CCA. | CIP-007-3a | R5; R5.2.1; R5.3.3 | Lower | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to change the default password prior to commissioning could have resulted in unauthorized access being left open and created vulnerabilities to the identified CCAs, and failure to change passwords in a timely fashion could have resulted in unauthorized electronic access to CCAs. The risk was reduced for the first instance because access to the software accounts require a login with an account on the domain in order to access the software. Furthermore, only accounts on this domain can access the Cyber Assets and remote access to the Cyber Assets requires two-factor authentication from outside of the ESP. The potential risk was further reduced because these devices are in a Physical Security Perimeter (PSP) and would require that a user have access to the PSP to physically access the Cyber Assets. The risk was reduced for the second instance because access to the default accounts requires two-factor authentication into the ESP. Furthermore, two of the three default accounts have read-only access and do not have the ability to change the configuration of the Cyber Assets. The potential risk was further reduced because these CCAs are all located within an ESP and a PSP. No harm was known to have occurred. | when the default accounts should have been removed or had passwords changed | when FRCC_URE2 performed an 'extent of condition' review for all NERC assets, corrected any instances identified, and reported the additional instances to FRCC | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) reset the power station passwords for NERC protected assets; 2) removed the ftp and monitor accounts from devices; 3) changed the hidden account password; 4) reviewed and updated password compliance deliverables and assignments; 5) provided communications to all team members responsible for on-boarding new Cyber Assets on the requirements for securing default accounts. FRCC_URE2 distributed an email communication to team members responsible for onboarding new Cyber Assets on the requirements for securing default accounts. This was reinforced by email from the director of information security, risk & compliance. 6) redesigned and implemented a password management process to improve tracking of default accounts and accounts requiring manual password changes., and communicated password documentation updates and any process changes to relevant staff; 7) researched and performed 'extent of condition' review for all NERC assets, and corrected any instances identified, and reported the additional instances to FRCC; and 8) for any instance identified requiring an operational outage, scheduled and implemented mitigation of those instances. There were no additional instances that required mitigation beyond the instances reported to FRCC. Consequently, there was no need to notify FRCC of any scheduled mitigations requiring outages. | 2015-01-27 | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE2's compliance history to be an aggravating factor in the penalty determination.
2015-06-30 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014014157 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R8.2. FRCC_URE2 failed to complete a review of ports and services for Critical Cyber Assets (CCAs) and non-CCAs as part of its 2013 CIP-007-3a R8 cyber vulnerability assessment (CVA) process. The CVA process was reassigned to a new cyber security analyst. The timeframe for completing each component of the CVA was unclear to the new analyst based on the documented process. FRCC_URE2 did not assess that only the ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter (ESP) are enabled against established baselines at that time. The root cause of not completing the CVA was determined to be due to inadequate training and documentation, as the documentation was unclear to the new analyst. | CIP-007-3a | R8; R8.2 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to complete the review of ports and services as a part of the CVA in a timely fashion could have resulted in unauthorized ports and services being left open, and created vulnerabilities to the identified CCAs and non-CCAs. The risk was reduced because FRCC_URE2 had performed a full review of ports and services during the Mitigation Plan for FRCC2011007927. Additionally, FRCC_URE2 limited the software footprint on devices to only software required for business and emergency purposes. The risk did not exist on devices that were added after the completion of the Mitigation Plan. Furthermore, the potential risk was further reduced because these CCAs and non-CCAs are all located within an ESP and a Physical Security Perimeter. No harm was known to have occurred. | when FRCC_URE2 should have completed the CVA | Mitigation Plan completion | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) reviewed and updated process documentation to clarify assessment components related to ports and services and timeframe for completing each component and communicated through training sessions with relevant staff; 2) performed review of ports and services on all CCAs and non-CCAs within the ESP using updated process; and 3) documented previously identified vulnerabilities related to ports and services on action plan. | 2014-12-19 | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-05-28 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014014158 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. FRCC_URE2 failed to afford the required protections to Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). Specifically, FRCC_URE2 failed to complete a review of ports and services for electronic access control and monitoring (EACM) Cyber Assets as part of the annual CIP-007-3a R8 cyber vulnerability assessment (CVA) process. FRCC_URE2 also failed to afford the required protection of changing default passwords, CIP-007-3a R5.2.1 before commissioning two of the EACMs. For the first instance, the CVA process requires FRCC_URE2 to run port scans and compare them against the baselines established for the Cyber Assets. FRCC_URE2 ran port scans on 56 EACM Cyber Assets located within an ESP. FRCC_URE2 did not assess the results of the scans against the established baselines at that time. FRCC_URE2 performed the other requirements of CIP-007 R8 as part of the CVA and placed the assessment of the port scans on the action plan in a good faith effort to comply. The CVA process was reassigned to a new cyber security analyst. The timeframe for completing each component of the CVA was unclear to the new analyst based on the documented process. The new analyst believed that the assessment of the scans could be performed as part of the action plan with no time limitation. With that understanding, the new analyst placed the assessment of ports and services on the action plan with the intent to address vulnerabilities as they were discovered. The failure to complete the CVA was discovered through a self-evaluation during a mock audit exercise. The root cause of not completing the CVA was determined to be due to training and documentation, as the documentation was unclear to the new analyst. For the second instance, during a self-evaluation it was discovered by a cyber security analyst that the passwords for three default accounts on two storage arrays had not been changed upon commissioning of the EACM Cyber Assets. These arrays provide storage capacity to four virtual machine hosts and virtual machines clients used as EACMs within an ESP. A review of documentation indicated that only three default accounts (i.e., ftp, monitor, and manage) are installed on the Cyber Assets as delivered. However, while investigating this instance, a subject matter expert (SME) discovered an article describing a fourth hidden "admin" account on storage arrays. This "admin" account was not disclosed on FRCC_URE2’s vendor compliance questionnaire. Upon further research the SME located a customer advisory which indicates that the account has necessary privileges that are used by internal processes running on the array. The hidden "admin" account is only shown if a specific command, "show user admin" is issued through the command line. The account cannot be seen using the "show users" command or through the graphical user interface. The manage account passwords had been changed and verified prior to commissioning. However, the ftp and monitor accounts were overlooked and the passwords were not changed. Additionally, the password for the "admin" account was also not changed because it was unknown to the SME as commissioning time. All passwords were changed and unneeded default accounts were removed. The root cause of not changing the default passwords was determined to be an oversight by a SME for two of the accounts and incorrect disclosure by the vendor on the third account. The vendor had identified two of the default accounts on a vendor compliance questionnaire. However, the accounts were inadvertently overlooked by the SME and they were not disabled nor were the default password values changed. The third account was not disclosed and therefore unknown to FRCC_URE2 at the time of commissioning for the Cyber Assets. | CIP-005-3a | R1; R1.5 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to complete the review of ports and services as a part of the CVA in a timely fashion could have resulted in unauthorized ports and services being left open, and created vulnerabilities to the identified EACM Cyber Assets. The risk was reduced because FRCC_URE2 had performed a full review of ports and services during a past the Mitigation Plan. Additionally, FRCC_URE2 limited the software footprint on devices to only software required for business and emergency purposes. The risk is limited to devices that were added after the completion of the Mitigation Plan. Access to the accounts requires two-factor authentication into the ESP. Two of the three accounts have read-only access and do not have the ability to change the configuration of the Cyber Assets. The Cyber Assets devices provide storage for the jump host environment which allows remote access to the BPS, and therefore these devices do not directly impact the BPS. Furthermore, the potential risk was further reduced because these EACMs are all located within an ESP and Physical Security Perimeter. No harm was known to have occurred. | when the default accounts should have been removed or had passwords changed | Mitigation Plan completion | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) changed the passowerds to the default accouts; 2) removed the ftp and monitor accounts from the devices; 3) changed the password for the hidden admin account; 4) communicated to all team members responsible for onboarding new Cyber Assets on the requirements for securing default accounts, including the requirement to change passwords prior to on-boarding those devices; 5) reviewed and updated CVA process documentation to clarify assessment components related to ports and services and timeframe for completing each component and communicate to relevant staff, and updated the procedure and held a training session with relevant staff; 6) redesigned and implemented password management process to improve tracking of default accounts and accounts requiring manual password changes, and communicated password documentation updates and any process changes to relevant staff; 7) performed a review of ports and services on all Cyber Aassets supporting the EACMs using updated process; and 8) created an action plan to address vulnerabilities related to ports and services. | 2014-12-19 | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-05-28 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014014159 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it had a violation of CIP-006-3c R2.2. FRCC_URE2 failed to afford the required protection of completing a review of ports and services for Physical Access Control System (PACS) Cyber Assets as part of the annual CIP-007-3a R8 cyber vulnerability assessment (CVA) process. The CVA process requires FRCC_URE2 to run port scans and compare them against the baselines established for the Cyber Assets. A senior system security analyst ran port scans on 23 PACS Cyber Assets located within an Electronic Security Perimeter (ESP). The analyst did not assess the results of the scans against the established baselines at that time. FRCC_URE2 performed the other requirements of CIP-007 R8 as part of the CVA and placed the assessment of the port scans on the action plan in a good faith effort to comply. The CVA process was reassigned to a new cyber security analyst. The timeframe for completing each component of the CVA was unclear to the new analyst based on the documented process. The new analyst believed that the assessment of the scans could be performed as part of the action plan with no time limitation. With that understanding, the new analyst placed the assessment of ports and services on the action plan with the intent to address vulnerabilities as they were discovered. The failure to complete the CVA was discovered through a self-evaluation during a mock audit exercise. The root cause of not completing the CVA was determined to be due to training and documentation, as the documentation was unclear to the new analyst. | CIP-006-3c | R2; R2.2 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to complete the review of ports and services as a part of the CVA in a timely fashion could have resulted in unauthorized ports and services being left open, and created vulnerabilities to the identified PACS Cyber Assets. The risk was reduced because FRCC_URE2 had performed a full review of ports and services during a past the Mitigation Plan. Additionally, FRCC_URE2 limited the software footprint on devices to only software required for business and emergency purposes. The risk is limited to devices that were added after the completion of the mitigation plan. Furthermore, the potential risk was further reduced because these critical cyber assets (CCAs) and non-CCAs are all located within an ESP and Physical Security Perimeter (PSP). No harm was known to have occurred. | when FRCC_URE2 should have completed the CVA | Mitigation Plan completion | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) reviewed and updated process documentation to clarify assessment components related to ports and services and timeframe for completing each component and communicate to relevant staff: ,and updated the procedure and held a training session with relevant staff; 2) performed review of ports and services on all Cyber Assets supporting the PACS system using updated process; and 3) documented identified vulnerabilities related to ports and services on action plan. | 2014-12-19 | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-05-28 | FERC | NP15-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014014161 | Settlement Agreement | FRCC_URE2 submitted a Self-Report stating that it had a violation of CIP-005-3a R4.2. FRCC_URE2 failed to afford the required protection of completing a review of ports and services for access point Cyber Assets as part of the annual CIP-005-3a R4 cyber vulnerability assessment (CVA) process. The CVA process requires FRCC_URE2 to run port scans on the access points as well as review all ports and services in the access point rule sets, and compare them against the baselines established for the Cyber Assets. FRCC_URE2 completed a Mitigation Plan for CIP-005 R4, FRCC2011007931. The Mitigation Plan included an assessment of ports and services rule sets through the firewall and a milestone to update the CVA process. However, the firewall rule set assessment was not included in the documentation when the CVA process was updated. As a result of this omission, the ports and services rule set through the firewall were not reviewed when FRCC_URE2 performed the annual CIP-005 R4 CVA. A senior system security analyst ran port scans on six access point Cyber Assets. The analyst did not assess the results of the scans against the established baselines at that time. FRCC_URE2 performed the other requirements of CIP-005 R4 as part of the CVA and placed the assessment of the port scans on the action plan in a good faith effort to comply. The CVA process was reassigned to a new cyber security analyst. The timeframe for completing each component of the CVA was unclear to the new analyst based on the documented process. The new analyst believed that the assessment of the scans could be performed as part of the action plan with no time limitation. With that understanding, the new analyst placed the assessment of ports and services on the action plan with the intent to address vulnerabilities as they were discovered. The failure to complete the CVA was discovered through a self-evaluation during a mock audit. The root cause of not completing the CVA was determined to be due to training and documentation, as the documentation was unclear to the new analyst. | CIP-005-3a | R4; R4.2 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to complete the review of ports and services as a part of the CVA in a timely fashion could have resulted in unauthorized ports and services being left open, and created vulnerabilities to the identified Cyber Assets and those within the Electronic Security Perimeter (ESP). The risk was reduced because FRCC_URE2 had performed a full review of ports and services rule sets during a past Mitigation Plan. While the assessment conducted identified items to address in the action plan, no significant vulnerabilities or unauthorized ports were identified. Furthermore, the potential risk was further reduced because these access points are all located within a Physical Security Perimeter (PSP). No harm was known to have occurred. | when FRCC_URE2 should have completed the CVA | Mitigation Plan completion | $50,000 (for FRCC2014013853, FRCC2014013999, FRCC2014014157, FRCC2014014158, FRCC2014014159, and FRCC2014014161) | Self-Report | To mitigate this violation, FRCC_URE2: 1) performed review of ports and services through the firewall; 2) performed review of ports and services at the access points; 3) documented identified vulnerabilities related to ports and services on action plan; and, 4) reviewed and updated process documentation to clarify assessment components related to ports and services and timeframe for completing each component and communicate to relevant staff: ,and communicated the update to other members of the Security Operations team. | 2014-09-01 | 2014-01-05 | Neither Admits nor Denies | FRCC reviewed FRCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC200800463 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Certification stating that it was in violation of CIP-001-1 R2. RFC_URE1 failed to have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-001-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on RFC_URE1's failure to have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. While RFC_URE1 did have communication plans and procedures in place, these plans and procedures did not specifically involve interconnection entities. The risk posed by this violation was mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities and the fact that the RFC_URE1 had significant security oversight, intrusion and sabotage detection, protective forces, security training and detailed response tactics and procedures in place. No harm is known to have occurred. The risk to transmission posed by RFC_URE1's location within the BPS decreased during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, RFC_URE1: 1) incorporated into its procedures the recognition of sabotage events on BES equipment, requirements to communicate information concerning sabotage events to appropriate parties in the Interconnection, and sabotage response guidelines for reporting disturbances due to sabotage events; 2) trained affected plant personnel on revised sabotage recognition procedures; and 3) reinforced communications contacts with the Federal Bureau of Investigation. | 2011-04-30 | 2011-08-16 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC200800464 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Certification stating that it was in violation of CIP-001-1 R3. RFC_URE1 failed to provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-001-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the RFC_URE1's failure to provide operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. The risk of the violation was partially mitigated by RFC_URE1's implementation of communication plans, however, these plans did not specifically involve interconnection entities. The risk of the violation was further mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities. No harm is known to have occurred. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, RFC_URE1: 1) incorporated into its procedures the recognition of sabotage events on BES equipment, requirements to communicate information concerning sabotage events to appropriate parties in the Interconnection, and sabotage response guidelines for reporting disturbances due to sabotage events; 2) trained affected plant personnel on revised sabotage recognition procedures; and 3) reinforced communications contacts with the Federal Bureau of Investigation. | 2011-04-30 | 2011-08-16 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC200900462 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Certification stating that it was in violation of CIP-001-1 R1. RFC_URE1 failed to have procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities oriented towards Bulk Electric System (BES) elements. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-001-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the RFC_URE1's failure to implement specific procedures for the recognition of and for making their operating personnel aware of sabotage events on its facilities oriented towards BES elements. The risk of this violation was mitigated by RFC_URE1's existing security oversight, intrusion and sabotage detection programs and procedures. The risk was also mitigated by the fact the relatively small size of the RFC_URE1's BES facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, RFC_URE1: 1) incorporated into its procedures the recognition of sabotage events on BES equipment, requirements to communicate information concerning sabotage events to appropriate parties in the Interconnection, and sabotage response guidelines for reporting disturbances due to sabotage events; 2) trained affected plant personnel on revised sabotage recognition procedures; and 3) reinforced communications contacts with the Federal Bureau of Investigation. | 2011-04-30 | 2011-08-16 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000698 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Certification stating that it was in violation of CIP-001-1 R4. RFC_URE1 failed to establish communications contacts, as applicable, with local Federal Bureau of Investigation officials and develop reporting procedures as appropriate to its circumstances. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-001-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the RFC_URE1's failure to establish communications contacts, as applicable, with local Federal Bureau of Investigation officials and develop reporting procedures specific to BPS elements. The risk was partially mitigated by the fact that the RFC_URE1 did, however, have established communication contacts in place with Federal Bureau of Investigation officials (that were not BPS specific). The risk of this violation was further mitigated by the relatively small size of the RFC_URE1's bulk electric system (BES) facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Self-Certification | To mitigate this violation, RFC_URE1: 1) incorporated into its procedures the recognition of sabotage events on BES equipment, requirements to communicate information concerning sabotage events to appropriate parties in the Interconnection, and sabotage response guidelines for reporting disturbances due to sabotage events; 2) trained affected plant personnel on revised sabotage recognition procedures; and 3) reinforced communications contacts with the Federal Bureau of Investigation. | 2011-04-30 | 2011-08-16 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000699 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-3 R1. RFC_URE1 failed to identify and document a risk-based methodology to use to identify its Critical Assets. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-002-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the inherent risk of the violation itself, which is RFC_URE1's lack of a risk-based methodology to identify Critical Assets, the foundation of compliance with the CIP Standards. However, upon subsequent application of a documented risk-based methodology, RFC_URE1 had no Critical Assets that were identified. The risk posed by this violation was also partially mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | when RFC_URE1 developed and documented a risk-based assessment methodology to identify Critical Assets | No penalty | Self-Report | To mitigate this violation, RFC_URE1: 1) developed and documented a risk-based assessment methodology to identify Critical Assets and identified Critical Assets by applying that methodology; 2) determined whether it needed to develop a list of Critical Cyber Assets; and 3) obtained management approval of its assessment and methodology and evaluation. | 2011-06-06 | 2011-09-15 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000700 | Notice of Confirmed Violation | RFC_URE1submitted a Self-Report stating that it was in violation of CIP-002-3 R2. RFC_URE1 failed to develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in CIP-002-3 R1 and by failing to review this list at least annually. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-002-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the inherent risk of the violation itself, which is the RFC_URE1's failure to review of the list of identified Critical Assets developed from a documented risk-based methodology. However, upon subsequent application of a documented risk-based methodology, RFC_URE1 had no Critical Assets that were identified. The risk posed by this violation was also partially mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | when RFC_URE1 applied its risk-based assessment methodology and identified its null list of Critical Assets | No penalty | Self-Report | To mitigate this violation, RFC_URE1: 1) developed and documented a risk-based assessment methodology to identify Critical Assets and identified Critical Assets by applying that methodology; 2) determined whether it needed to develop a list of Critical Cyber Assets; and 3) obtained management approval of its assessment and methodology and evaluation. | 2011-06-06 | 2011-09-15 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000701 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-3 R3. RFC_URE1 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of the Critical Assets using the list of Critical Assets developed pursuant to CIP-002-3 R2. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-002-1 | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the nature of the violation itself, that is the RFC_URE1's failure to develop a list of CCAs associated with the operation of its Critical Assets. However, upon subsequent application of a documented risk-based methodology, RFC_URE1 had no Critical Assets that were identified, therefore no CCAs associated with Critical Asset operation would have been identified. The risk of this violation was partially mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | when RFC_URE1 identified no Critical Assets | No penalty | Self-Report | To mitigate this violation, RFC_URE1: 1) developed and documented a risk-based assessment methodology to identify Critical Assets and identified Critical Assets by applying that methodology; 2) determined whether it needed to develop a list of CCAs; and 3) obtained management approval of its assessment and methodology and evaluation. | 2011-06-06 | 2011-09-15 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000702 | Notice of Confirmed Violation | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-002-3 R4. RFC_URE1 failed to have its senior manager approve annually the risk-based assessment methodology, the list of Critical Assets, and the list of Critical Cyber Assets (CCAs). The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-002-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk determination is based on the nature of the violation itself, that is the RFC_URE1's failure to obtain the annual approval of the risk-based methodology, the list of Critical Assets, and the list of CCAs. Upon subsequent application of a documented risk-based methodology, RFC_URE1 had no Critical Assets and further, no CCAs associated with Critical Asset operation. The risk of this violation was partially mitigated by the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | when RFC_URE1 obtained senior manager approval of the risk-based assessment methodology | No penalty | Self-Report | To mitigate this violation, RFC_URE1: 1) developed and documented a risk-based assessment methodology to identify Critical Assets and identified Critical Assets by applying that methodology; 2) determined whether it needed to develop a list of CCAs; and 3) obtained management approval of its assessment and methodology and evaluation. | 2011-06-06 | 2011-09-15 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001222 | Notice of Confirmed Violation | During a Compliance Audit, RF determined that RFC_URE1 was in violation of CIP-003-1 R2. RFC_URE1 did not properly identify individuals that were delegated responsibility for CIP Reliability Standard compliance. RFC_URE1 named four individuals as delegates but did not state the specific responsibilities that it delegated to those individuals. In addition, the individuals' titles were not listed. The cause of this deficiency is the lack of specificity in the existing delegation of authority letters to address the ClP standards. Specifically, while the delegation of authority letters for compliance to the NERC standards were issued and addressed overall responsibility for NERC Compliance, they did not assign specific responsibility for compliance to CIP-002-3 through CIP-009-3 as required by CIP-003-3 R2. The root cause of this violation was RFC_URE1's incorrect belief that it was not subject to the NERC Reliability Standards because a separate entity had exclusive control over RFC_URE1's original switchyard. Additionally, RFC_URE1 incorrectly believed that a third entity would be responsible for RFC_URE1's compliance with all applicable Reliability Standards. | CIP-003-1 | R2.1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). There were four individuals named as delegates with overall responsibility for adherence to the CIP Standards CIP-002 through CIP-009. The violation was in documenting the proper identification of those individuals and their exact responsibilities. The minimal risk determination is based on the relatively small size of the RFC_URE1's Bulk Electric System (BES) facilities and that this was a documentation issue where RFC_URE1 had actually identified individuals as delegates but had failed to properly document them with all required information. The risk to transmission posed by RFC_URE1's location within the BPS has decreased during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | No penalty | Compliance Audit | To mitigate this violation, RFC_URE1 reissued the letter delegating authority for CIP Reliability Standard compliance that included all required information. | 2011-11-01 | 2013-05-02 | Does Not Contest | RFC considered RFC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-05-28 | FERC | NP15-28-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012851 | Settlement Agreement | WECC_URE1 submitted Self-Reports stating that it was in violation of CIP-004-3a R4. In the first instance, covered under the initial Self Report, WECC_URE1 failed to revoke access for two retired employees within seven days (the access was revoked six days late). In the second instance, covered under the second Self Report, one employee was provisioned with cyber access, but the access list was not updated within seven days (the list was updated five days late). In the third instance, covered under the third Self Report, the access list was not updated within seven days after one employee's access was revoked (the list was updated 13 days late). WECC Subject Matter Experts (SMEs) reviewed the Self-Reports and issued Data Requests (DR), seeking information on the devices in scope and the type of employee access. WECC_URE1 responded to the DR, stating that the devices in scope were "non-CCA.'' Because of WECC_URE1's response, WECC determined the facts were more appropriately covered under CIP-007-3 R5. A WECC SME requested an interview to discuss the last two Self Reports, but WECC_URE1 did not respond to the interview request. WECC issued a Notice of Find, Fix and Track (FFT) for CIP-007. However, WECC_URE1 rejected the FFT, requesting that the violation be processed under CIP-004-3a R4, because the devices in scope include Critical Cyber Assets (CCAs). A WECC SME discussed the FFT rejection. During that conversation, WECC_URE1 stated that despite its previous response, the devices in scope did include CCAs, and that these should be included within the scope of CIP-004 R4, and requested that the WECC SME issue a Data Request for clarification in writing. WECC_URE1 responded to that DR and stated: "none of these facilities ... are defined as WECC_URE1 Critical Assets," and "none of the devices ... are CIP Cyber Assets." WECC_URE1 also responded further, stating that "these four devices are classified as WECC_URE1 Critical Cyber Assets." This response further added to the confusion of whether the devices in scope were CCAs or not. WECC issued an additional three Data Requests and conducted an interview with WECC_URE1 to determine the scope of this violation. Finally, WECC issued a NOAV, alleging noncompliance with both CIP-004-3a R4 and CIP-007 R5. WECC_URE1 responded and provided even further information again several months later. A WECC SME reviewed the additional information provided by WECC_URE1. WECC determined that WECC_URE1 used non-CCAs to gain remote access to CCAs, and that the individuals in scope did have access to CCAs through the non-CCA workstations. The entity failed to maintain an accurate list of personnel with electronic access rights to CCAs. Given this information, WECC determined that the violation was properly within CIP-004-3a R4, rather than CIP-007 R5. The root cause was a lack of compliance processes to ensure the CIP list was updated in a timely manner. WECC_URE1 has the processes, but they failed to employ them in this instance. As a tool for future prevention, WECC_URE1 is implementing an automated system to prevent future occurrences. | CIP-004-3a | R4 | Lower | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to maintain and update CCA access lists may lead WECC_URE1 to be unaware of who should or should not have access to those CCAs. Such a lack of knowledge could allow unauthorized access to go unnoticed. An unauthorized individual with malicious intent could manipulate the workstations and potentially disrupt operations. However, there were mitigating factors in place during the duration of the violation. All individuals in scope were in good standing within WECC_URE1, had completed personnel risk assessments, and were current on training. In two instances, WECC_URE1 had collected the employees' access cards prior to their departure. | when WECC_URE1 should have updated its access list for the first instance of noncompliance | when the last access list was updated | $30,000 (for WECC2013012851 and WECC2013013110) | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked the employees' CIP access; 2) revised its CIP Access List; and 3) implemented an automated tool to prompt the access list review/revocation requirements. | 2014-11-24 | 2015-04-10 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 agreed to implement several reliability-focused terms. WECC_URE1 will revise its Self-Reporting process to require that submitted Self-Reports contain more information regarding the reported violation, internal controls relevant to the reported violation, mitigating factors regarding the reported violation, and other relevant information. WECC_URE1 will formalize a process for better response to data requests, identifying relevant information, who should be included in meetings, and schedules for answering data requests. The process will also include a standing time slot on the agenda for the compliance senior manager of the Division of Operations and Maintenance's weekly meetings to bring up an potential issues arising from the process or data requests. WECC_URE1 will develop a process to elevate issues that arise from answering data requests. The person responsible for responding to the data request will complete the request. WECC_URE1 senior management will be notified and will respond to the questions or concerns raised by WECC, if there are further concerns about the adequacy of the response, then senior management will notify either the compliance senior manager or the chief compliance officer who will then respond. WECC_URE1 will develop a policy to ensure that WECC_URE1's ownership matrix is updated as necessary. WECC_URE1 will also include backup owners of Standards in the matrix to ensure those individuals are properly trained and have the requisite knowledge should they be called upon to respond to WECC during the absence of the primary Standard owner. WECC_URE1 will institute advance internal deadlines into policies to reduce the need for extension requests. WECC_URE1 will foster a culture of partnership with WECC through encouragement of communication and collaboration during weekly and monthly meetings. WECC_URE1 will expand its 'lessons learned' to include compliance with its own internal policies and procedures. WECC_URE1 will include an agenda item during the compliance senior manager's monthly meetings to assess communications between WECC_URE1 and WECC. WECC_URE1 will conduct internal spot-check/audits for 20% of applicable Standards each year. WECC_URE1 will conduct yearly internal spot-check/audits on its internal procedures that relate to WECC compliance to ensure WECC_URE1 is adhering to its own procedures. WECC considered WECC_URE1 compliance history to be an aggravating factor in the penalty determination.
2015-05-28 | FERC | NP15-28-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013110 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1. WECC_URE1 failed to identify and provide Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP) the appropriate protective measures. While reviewing evidence of completion of a Mitigation Plan for another violation of the same Reliability Standard, WECC determined that WECC_URE1 has four control panels that it does not consider part of its Physical Access Control System (PACS). However, WECC determined that these control panels are PACS, and should be provided the protections mandated by CIP-006-1 R1.8. In making this determination, WECC spoke with WECC_URE1 on several occasions and reviewed data request responses submitted by WECC_URE1. Because WECC_URE1 does not consider the control panels as PACS, WECC_URE1 personnel did not have a willingness to wrap these into the open Mitigation Plan. In order to address the lack of protection on the control panels, WECC determined that a Self-Report for a possible violation of CIP-006-1 R1.8 was warranted. The four control panels in scope authorize access into and/or log access to all of WECC_URE1's PSPs. Within these PSPs are numerous Critical Cyber Assets (CCAs), Electronic Access Control and Monitoring devices (EACMs), PACS, and other non-CCA devices. WECC determined that the control panels are Cyber Assets and that because the panels had not been classified as such, WECC_URE1 failed to provide the panels with all the protective measures identified in the Standard in violation of CIP-006-1 R1.8. | CIP·006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to identify four control panels as Cyber Assets and therefore failed to provide the control panels with all CIP-006 R1.8 protections. These four control panels authorize and/or log access to all of WECC_URE1's PSPs which contain CCAs, EACMs, PACS and other non-CCA devices. Failing to identify and provide all CIP protections to these four control panels could have allowed unauthorized access into these devices, If successful, unauthorized personnel could have gained physical access to the control panels, allowing personnel to tamper with or physically manipulate the devices to then gain unauthorized logical access. This logical access could then be used to gain unauthorized physical access to all of the WECC_URE1's CCAs. However, WECC_URE1 implemented detective measures to help detect unauthorized access to these devices. Specifically, WECC_URE1 uses tamper detection switches that generate alarms when control panel doors are opened. Security guards monitor these alarms around the clock and regularly review logs. Second, the hallways containing the control panel doors are monitored around the clock via video by security guards. Third, WECC_URE1 provides training upon hiring and annual training on monitoring alarms that signify unauthorized or actual access attempts. Finally, as preventative controls, the control panels are located within secured buildings that require keycards for entry. Entrances are monitored continuously by security guards. Also, room keys are required to enter the telecommunications rooms where three of the four control panels are located. These keys are only provided to authorized personnel. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $30,000 (for WECC2013012851 and WECC2013013110) | Self-Report | To mitigate this violation, WECC_URE1: 1) added the four PACS keycard door controller devices to the list of CIP controlled Cyber Assets; 2) determined who has been granted physical access to the devices, verified that such access was authorized and that all persons have current personnel risk assessments; 3) included the devices in WECC_URE1's annual CIP-005 Electronic Security Perimeter self-assessment; 4) included the devices in WECC_URE1's CIP security patch management program; 5) prepared and filed a Technical Feasibility Exception (TFE) with WECC regarding CIP-007 R4 to support the inability of these devices to use antivirus/antimalware software; 6) updated CIP Cyber Asset configuration documentation to include the devices; 7) updated PACS security log review methods; 8) tested devices to verify correct functioning of entry alarms, and included such testing in the annual Cyber Vulnerability Assessment (CVA) process; and 9) updated WECC_URE1 CIP policies and procedures to include the devices. | 2014-12-19 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC_URE1 agreed to implement several reliability-focused terms. WECC_URE1 will revise its Self-Reporting process to require that submitted Self-Reports contain more information regarding the reported violation, internal controls relevant to the reported violation, mitigating factors regarding the reported violation, and other relevant information. WECC_URE1 will formalize a process for better response to data requests, identifying relevant information, who should be included in meetings, and schedules for answering data requests. The process will also include a standing time slot on the agenda for the compliance senior manager of the Division of Operations and Maintenance's weekly meetings to bring up an potential issues arising from the process or data requests. WECC_URE1 will develop a process to elevate issues that arise from answering data requests. The person responsible for responding to the data request will complete the request. WECC_URE1 senior management will be notified and will respond to the questions or concerns raised by WECC, if there are further concerns about the adequacy of the response, then senior management will notify either the compliance senior manager or the chief compliance officer who will then respond. WECC_URE1 will develop a policy to ensure that WECC_URE1's ownership matrix is updated as necessary. WECC_URE1 will also include backup owners of Standards in the matrix to ensure those individuals are properly trained and have the requisite knowledge should they be called upon to respond to WECC during the absence of the primary Standard owner. WECC_URE1 will institute advance internal deadlines into policies to reduce the need for extension requests. WECC_URE1 will foster a culture of partnership with WECC through encouragement of communication and collaboration during weekly and monthly meetings. WECC_URE1 will expand its 'lessons learned' to include compliance with its own internal policies and procedures. WECC_URE1 will include an agenda item during the compliance senior manager's monthly meetings to assess communications between WECC_URE1 and WECC. WECC_URE1 will conduct internal spot-check/audits for 20% of applicable Standards each year. WECC_URE1 will conduct yearly internal spot-check/audits on its internal procedures that relate to WECC compliance to ensure WECC_URE1 is adhering to its own procedures. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2015-05-28 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012654 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R2. WECC_URE1 issued temporary access badges to three employees so the employees could build a kitchen within a Physical Security Perimeter (PSP) where Critical Cyber Assets (CCA) were located. WECC_URE1's authorizing employee mistakenly believed that the three employees had received CCA training during the previous calendar year. However, the three employees last received CCA training two years prior. The three employees had physical access to eleven CCAs and one non-critical Cyber Asset at WECC_URE1's control center. As a result, WECC_URE1 was in violation of CIP-004-3a R2.1 for failing to ensure the three employees were trained prior to being granted access to the CCAs. The root cause of this violation was human error when WECC_URE1 verified the training dates for the three employees. | CIP-004-3a | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure that three employees received training prior to being granted physical access to eleven CCAs and one non-CCA at WECC_URE1's control center. WECC_URE1's failure to train its employees on the proper use of Critical Assets increased the opportunity for the employees to improperly use the CCAs. Although WECC_URE1 granted access to the three employees, WECC_URE1 implemented preventive and detective controls. Specifically, WECC_URE1 implemented live video monitoring of the PSP 24 hours a day seven days a week. Additionally, each of the personnel involved in the violation had received prior CCA training. Furthermore, in this instance, the employees involved only had access to the PSP on a limited basis after receiving temporary access badges. Moreover, the PSP had a minimum of eight authorized, trained personnel inside at all times. The personnel and cameras minimized or prevented physical access to the CCAs and therefore would have prevented any unauthorized access to the supervisory control and data acquisition system. | when the three employees were granted access to the CCAs | when the three employees no longer had access to the CCAs | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Self-Report | To mitigate this violation, WECC_URE1: 1) started documenting the actual date of last CIP training in the Temporary Access Badge Log; 2) distributed a Bulk Operation Guide to all responsible senior load dispatchers responsible for issuing temporary badges and managing the Temporary Access Badge Log; 3) revised its Energy Control Centers (ECC) instructions for issuing temporary ECC badges that instructs entry of last CIP training date in the Temporary Access Badge Log; and 4) updated its training program for the load dispatcher with revised procedure related to issuing temporary ID badges for access to restricted areas of the ECC. | 2013-08-16 | 12/20/2013 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's CIP-004 R2 compliance history to be an aggravating factor in the penalty determination.
2015-05-28 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013374 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-005-3a R2. WECC_URE1 performed troubleshooting that affected a router identified as an access point. During the troubleshooting, WECC_URE1 personnel issued a command that negated WECC_URE1's configured access list leaving the router without CIP-005 R2 controls. As a result, WECC_URE1 failed to use an access control model that denies access by default, such that explicit permissions were specified on the access point. WECC_URE1 also failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) at one access point. The scope of this violation includes one access point and one ESP. The root cause of this violation was lack of training when conducting work on access points and by a lack of appropriately configured firewall that inherently denies access by default. | CIP-005-3a | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For three years, one WECC_URE1 access point lacked the protections required by CIP-005-3a R2.1 and R2.2. This exposed WECC_URE1 to the potential risk of unauthorized individuals using the unprotected access point to gain access to WECC_URE1's other devices and networks. Although one of WECC_URE1's access points lacked the protections required by CIP-005-3a R2.1 and R2.2, WECC_URE1 did implement and document organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the ESP. Additionally, WECC_URE1 implemented a defense-in-depth architecture of physical and logical cyber security controls, including physical security mechanisms, special locks, and closed circuit television. WECC_URE1 also implemented internal cyber security controls including firewalls, vulnerability scanning tools, and a Security Information Events Management system. | when WECC_URE1 issued the command | when WECC_URE1 activated the Access Control List (ACL) on the router in scope | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) activated the ACL on the router; 2) retrained its technical personnel on the proper procedure to follow when conducting work at non-firewall access point devices and to ensure that ACLs are reapplied once work is completed; 3) checked all Access Points for instances where non-firewall devices are used as access points and ensured that the device denies access by default; and 4) implemented a firewall that inherently denies access by default. | 5/9/2014 | 11/21/2014 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-05-28 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013375 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-006-3a R2. WECC_URE1 failed to identify fourteen Cyber Assets that authorize and log access to the Physical Security Perimeter and afford them CIP protection outlined in Standard CIP-006-3a R2. WECC_URE1 has eleven Physical Access Control System (PACS) panels capable of providing access, monitoring, and logging independent of WECC_URE1's PACS servers. The control panels in scope are capable of controlling access to all fourteen of WECC_URE1's Physical Security Perimeters (PSPs). WECC_URE1 also has three workstations capable of provisioning access to all of WECC_URE1's PSPs. WECC_URE1 did not provide the eleven panels and three workstations all of the protections identified in CIP-006-3a R2. The root cause of this violation was WECC_URE1's misunderstanding of whether the devices in scope were subject to the Reliability Standards. | CIP-006-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not provide three workstations and eleven panels with all of the protections identified in CIP-006-3a R2 potentially exposing WECC_URE1's Critical Cyber Assets to access by unauthorized individuals. However, the panels in scope were protected by the inherent protections of the PACS network through WECC_URE1's PACS servers. WECC_URE1 installed the panels in either a PSP or a location protected from unauthorized physical access. WECC_URE1 also installed the workstations in either a PSP or located protected from unauthorized physical access, such as WECC_URE1 Central Monitoring Station or Badging Office. Furthermore, the 14 devices in scope were provided some of the protections identified in CIP-006-3a R2.2. Specifically, the panels and workstations were afforded the protections required by CIP-003 R1-R5, CIP-004, CIP-006 R4-R5, CIP-007 R7, and CIP-008. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) completed the change management form to include PACS workstations as devices afforded the protections of CIP-006 requirements (where applicable) and other requirements denoted in CIP-006 R2; 2) modified the change control management procedure and form to better detail when PACS devices must be added to the CIP Cyber Asset inventory; 3) reviewed the list of PACS devices to be afforded the protections of CIP-006 requirements (where applicable) and other requirements denoted in CIP-006 R2, verified the counts are correct and determined if Technical Feasibility Exceptions (TFEs) are required; 4) submitted TFEs (if required) to WECC; 5) developed an implementation schedule for bringing the PACS devices into compliance; 6) trained affected personnel on the modifications to the change control procedure; and 7) completed and signed off on change management forms demonstrating completion of implementation schedule for the PACS devices in scope. | 11/12/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-04-30 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013373 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-007-3a R8. Specifically, WECC_URE1 did not perform a Cyber Vulnerability Assessment (CVA) on each Cyber Asset in 2011 and 2012. Instead, WECC_URE1 used a representative system model to perform CVAs of representative devices. As a result, WECC_URE1 omitted 13 Cyber Assets from the 2012 CVA. Ten of the devices were Critical Cyber Assets (CCAs), two were non-critical Cyber Assets, and one was an Electronic Control and Monitoring device. WECC_URE1 also omitted 11 Cyber Assets from the 2011 CVA. Eight of the devices were CCAs, two of the devices were non-Critical Cyber Assets, and one of the devices was a Physical Access Control System device. The root cause of this violation was WECC_URE1's reliance on a representative system model to perform CVAs. | CIP-007-3a | R8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not perform CVAs on all Cyber Assets in 2011 and 2012. This could have exposed WECC_URE1 to successful cyber-attacks against WECC_URE1's Cyber Assets. However, WECC_URE1 implemented compensating measures to decrease the risk associated with only performing CVAs on representative devices. Specifically, WECC_URE1 implemented a defense-in-depth architecture of physical and logical cyber security controls. This defense-in-depth architecture includes physical security mechanisms with guards, special locks, closed circuit television, and logical perimeter controls. WECC_URE1 also implemented internal cyber security controls including firewalls, vulnerability scanning tools, and a Security Information Events Management system. WECC_URE1 Tripwire reports also confirmed that the baselines of the devices in scope matched those of the representative devices. | when WECC_URE1 used the representative system model during the 2011 CVA | when WECC_URE1 performed the CVA on all required Cyber Assets | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) assessed devices currently with Tripwire to assure that baselines of devices omitted from the CVA have no applicable deviation from the devices used as the representative sample when performing the CVA; 2) developed the WECC_URE1 plan for CVA requiring the individual testing of all devices and ensured all required activities were performed; 3) trained appropriate personnel on the new CVA plan; 4) implemented the new CVA plan against all required Cyber Assets; and 5) performed a quality assurance review for the implementation of the CVA Plan. | 12/15/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-04-30 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013750 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-3 R6. WECC_URE2 reported that its CIP-003-3 R6 procedure required the creation of a security control checkout form for every significant change. The security control checkout form documents a breakdown of how a significant change affects all applicable CIP-002 through CIP-009 requirements and ensures that all applicable CIP controls are applied prior to the change being put into production. WECC_URE2 reported there is no evidence of the form being created and filled out for the 23.85% change tickets that occurred in the year. WECC determined WECC_URE2 failed to follow its change control and configuration management process for 23.85% changes. WECC determined these changes affected 116 devices, and that the changes made by WECC_URE2 were patches and upgrades to servers, workstations, and other networking equipment. The root cause of the violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 had inadequate oversight due to a lack of peer review or management review of change controls. WECC_URE2 did not have a dedicated quality assurance employee to verify results of change control. There was also a lack of training because some individuals did not know the change control and configuration management process. | CIP-003-3 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2's failure to follow its change control and configuration management process could allow for adding or modifying hardware and software changes that could compromise WECC_URE2's reliable operation of it transmission lines. Although WECC_URE2 failed to follow its change control and configuration management process, it did implement preventive controls. WECC_URE2 ensured that all CIP applicable devices resided within Electronic Security Perimeters (ESPs). WECC_URE2's devices were configured with tightly restricted ingress Access Control Lists and ports and services. WECC_URE2 disabled all dial-up access to assets within the ESP and required two-factor authentication for all external interactive access. WECC_URE2 also implemented detective controls. WECC_URE2 implemented Tripwire file integrity checker to verify no unauthorized functional changes occurred. Tripwire was configured to issue pop-up alerts to responsible personnel when a detected unauthorized change occurred. WECC_URE2 also conducted annual Cyber Vulnerability Assessments on all of its devices residing within an ESP. WECC_URE2's Cyber Vulnerability Assessment did not find any unaccounted ports and services or any default user accounts on the systems in scope. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Further, all personnel with access to Cyber Assets in the 23.85% change management tickets had CIP training and had current personnel risk assessments. | when WECC_URE2 failed to follow its change control process | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) created a security control checkout form training plan for the applicable group and delivered that training plan to the applicable group's quality assurance manager; 2) completed security checkout form documentation and training for the applicable group; and 3) completed security checkout form training for the applicable operations team. The training covered proper usage for the security checkout form as it relates to the NERC CIP-003-3 R6 process. | 8/29/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-003 compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013890 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-004-3a R4. WECC determined that on two occasions WECC_URE2 failed to revoke access to Critical Cyber Assets (CCAs) within seven calendar days for personnel who no longer require access to CCAs. In the first instance, a contractor no longer required access to WECC_URE2's CCAs. WECC_URE2 revoked access 28 days later. In the second instance, a WECC_URE2 employee verbally resigned. WECC_URE2 revoked access 14 days later. After the audit, WECC_URE2 reported a third instance of noncompliance. In that instance, a WECC_URE2 employee verbally resigned. WECC_URE2 revoked access 11 days later. The root cause of this violation was due to improper communication with vendors when a contractor has left employment and lack of management training and awareness regarding effect of certain human resources policies as applied to the voluntary separation of employees having access to a CIP environment. | CIP-004-3a | R4; R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to revoke access to CCAs in a timely manner could allow unauthorized individuals to have malicious physical access to WECC_URE2's CCAs. Although WECC_URE2 failed to revoke access to CCAs within seven calendar days, this violation was limited to three occasions that involved three individuals, none of whom were terminated for cause. WECC_URE2 verified the individuals did not attempt access after their separation. Additionally, the periods for these three occasions were of short duration, lasting 28 days, 14 days, and 11 days respectively. No harm is known to have occurred. | eight calendar days after the contractor in the first instance of noncompliance no longer required access | when WECC_URE2 terminated the employee's access in the third instance of noncompliance | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Compliance Audit | To mitigate this violation, WECC_URE2: 1) revised the separation and exit policy and procedures, along with accompanying supervisor's exit checklist, to provide emphasis on entering termination transactions early and adding language specific to NERC CIP areas; 2) incorporated the policy, including termination transactions and retirements, into periodic reminders sent to supervisors; 3) updated vendor contract language to comply with NERC Standards; and 4) reviewed master agreements and Individual Task Assignments for inclusion of the new language once the agreements expired. | 2015-02-16 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-004 compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013503 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-005-3a R5. WECC_URE2 made 13 changes to its networks or controls. The changes included adding and removing devices and updating firewalls. All 13 devices in scope are classified as Electronic Access Control and Monitoring devices responsible for protecting devices essential to a WECC_URE2 control center department. WECC_URE2 failed to update four pieces of documentation within 90 calendar days of the change. The root cause of this violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 used a change control checklist, but the checklist did not include an explicit step to update relevant documentation as a result WECC_URE2 staff involved did not update relevant documentation. | CIP-005-3a | R5; R5.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to update relevant documentation after the 13 changes were made could have led to inaccurate documents that contain information regarding the CIP-005 protections of the Electronic Security Perimeters inside which the Critical Cyber Assets reside. Although WECC_URE2 failed to update the documentation, WECC_URE2 did implement preventive controls. WECC_URE2 followed all security related change controls when modifying, adding, or removing devices. As a result, devices were tested and approved prior to implementation of the change. No harm is known to have occurred. | 91 calendar days after WECC_URE2 made changes to its network or controls | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) updated the four pieces of documentation; and 2) updated the checklist to include steps for updating documentation. | 1/9/2014 | 10/20/2014 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013504 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1. WECC_URE2 failed to conduct Cyber Vulnerability Assessments (CVAs) on 13 controls panels. WECC_URE2 never conducted full CVAs on three control panels. WECC_URE2 attempted to scan the three control panels, but the scan caused the control panels to crash. WECC_URE2's 16 control panels were not afforded the protective measures specified in Standards CIP-007-3 and CIP-009-3. WECC_URE2 also failed to verify that no default accounts resided on the panels on an annual basis. Additionally, two unauthorized personnel were left unescorted in an area containing WECC_URE2's Physical Access Control and Monitoring (PACM) server for the generating station's Physical Security Perimeters (PSPs) and a control panel. WECC also determined that WECC_URE2 failed to ensure that Cyber Assets that authorize or log access to the PSPs were protected from unauthorized physical access as required by CIP-006-3c R2.1. The root cause of this violation was equipment failure, lack of process and training issues as some of the WECC_URE2 personnel were not adequately trained on WECC_URE2's escorting procedures. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 uses the PACM devices in scope to implement physical controls required to protect WECC_URE2's devices. Unauthorized physical access to WECC_URE2's control panels could allow for physical compromise of the devices controlling all of WECC_URE2's transmission and generating systems which would affect WECC_URE2's peak load and generation. Although WECC_URE2 failed to ensure the 16 control panels classified as PACM devices were afforded the protective measures specified in CIP-006-3c R2, WECC_URE2 did implement preventive and detective controls. WECC_URE2 personnel responsible for recovering the devices were knowledgeable of the devices and had the vendors' contact information in the event the devices needed to be recovered. The control panels' functionality was limited by design which restricted malicious opportunities. Every year WECC_URE2 verified that no default accounts were enabled on the devices. WECC_URE2's PACM devices were all located in restricted facilities staffed 24 hours a day, seven days a week by personnel who only allowed access to authorized individuals. The two individuals left unescorted were discovered by staff who noticed the unescorted individuals and immediately notified WECC_URE2 management. WECC_URE2 confirmed that no harm occurred to the devices the unescorted individuals had access. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) met with the escort employee who did not follow procedures and retrained him on PSP escorting procedures; 2) revised the Emergency Situations section of the CIP Cyber Security Policy to ensure that the situation in question is adequately covered for future occurrences; 3) updated and installed new signage at the generating station data center PSP; 4) updated the process and/or any other processes deemed necessary to ensure that if an information security emergency occurs in a CIP-protected area, the CIP Cyber Security Policy's emergency must be followed; 5) updated the CIP Cyber Security Training course; 6) developed procedures for performing a CVA on the PACS field panels; 7) performed and documented the results of a CVA on the PACS field panels; 8) updated the Recovery Plan procedures to include the PACS field panels; and 9) conducted the annual Recovery Plan exercise to include PACS field panels, documented the results of the exercise, and reviewed meeting minutes. | 8/30/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-006-3c compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013751 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-3a R1. WECC_URE2 failed to implement the proper test procedures described in CIP-007-3a R1 for 31 change management tickets. The CIP-007 procedure states that a security control checkout form document is to be created for every significant change as this form helps ensures that all applicable CIP controls are applied, prior to the change being put into production. The security control checkout form was not filled out for the 31 significant change tickets. Further, WECC determined that WECC_URE2 were unable to confirm that testing was performed per the CIP-007 test procedure prior to the 31 significant changes being placed into production. These changes made by WECC_URE2 included patches and upgrades to servers, workstations, and other networking equipment that impacted 116 devices. The root cause of this violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 had inadequate oversight due to a lack of peer review or management review of change controls. WECC_URE2 did not have a dedicated quality assurance employee to verify results of change control. There was also a lack of training because some individuals did not know the change control and configuration management process. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to complete its security check out form could have allowed for the adding or modifying hardware and software changes that are harmful to Critical Cyber Assets essential to the operation of the BPS. Although WECC_URE2 failed to complete its security check out form, WECC_URE2 did implement preventive controls. WECC_URE2 ensured that all CIP applicable devices resided within Electronic Security Perimeters (ESPs). WECC_URE2's devices were configured with tightly restricted ingress Access Control Lists and ports and services. WECC_URE2 also disabled all dial-up access to assets within the ESP and required two-factor authentication for all external interactive access. WECC_URE2 also implemented detective controls. WECC_URE2 implemented Tripwire File Integrity Checker to verify no unauthorized changes occurred. Tripwire File Integrity Checker was configured to issue pop-up alerts to responsible personnel when a detected unauthorized change occurred. WECC_URE2 also conducted annual Cyber Vulnerability Assessments (CVA) on all its devices residing within an ESP. WECC_URE2's CVA did not detect any unaccounted ports and services or any default user accounts on the systems in scope. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Further, all personnel with access to Cyber Assets in the 31 change management tickets had CIP training and had current personnel risk assessments. | when WECC_URE2 first failed to follow proper test procedures | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) configured Tripwire Enterprise System to show all applicable security controls have been tested and passed to prevent occurrence of similar future issues; 2) created security control checkout form training plan for the applicable group and delivered it to the applicable group's manager; 3) completed security control checkout form documentation and training for the applicable group; and 4) completed security control checkout form training for the operations team. | 8/29/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013505 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-3a R3. WECC_URE2's procedures required WECC_URE2 to review security patches within 30 days of their release and apply security patches within 90 days of their evaluation if the security patches are determined to be applicable. A Java patch was released and WECC_URE2 determined it was applicable and should be applied. Specifically, WECC_URE2 attempted to install the patch, but due to technical limitations the patch failed. Specifically, WECC_URE2 applied the patch to the workstation, but the update broke the Oracle Forms software. To fix this problem WECC_URE2 needed to install an update to the Oracle Forms on the backend server. The Oracle Forms update would not work until WECC_URE2 installed additional RAM on the backend server. WECC_URE2 did not install the Java patch until approximately three months after the patch should have been applied. The root cause of the violation was failure to include in its procedure a process to deal with software issues. WECC_URE2 had an established procedure, but waited too long to find a solution for the software issue so that it could follow its procedures within the 90 day time period. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to install the patch impacted one workstation used by the operators to control WECC_URE2's energy management system (EMS). This failure could have allowed vulnerabilities on the workstation to remain unnoticed and unchecked for a longer duration. Although WECC_URE2 failed to install the patch within 90 days, WECC_URE2 did implement compensating controls. WECC_URE2 was aware of the patch and the associated vulnerabilities addressed by the patch. WECC_URE2 did install the patch as soon as technically feasible. The Electronic Security Perimeter (ESP) for the EMS is protected behind a Physical Security Perimeter with adequate controls, monitoring, and logging in accordance with CIP-006 R4, R5, and R6. All Cyber Assets within the ESP are protected with antivirus and anti-malware controls. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Finally, all personnel with access to the Windows workstation had CIP training and had current personnel risk assessments. | 91 days after WECC_URE2 determined the Java patch was applicable | when WECC_URE2 installed the Java patch | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) upgraded server memory to allow for successful back-end application updates; 2) upgraded Oracle Forms and performed Java updates; 3) documented the update in the CIP-007-3 R3 patch tracking spreadsheet; 4) updated the Technical Feasibility Exception (TFE) template to reflect different TFE options; and 5) trained operations IT subject matter experts on the new procedure. | 6/26/2014 | 11/24/2014 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013897 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-007-3a R8. WECC_URE2 failed to annually perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets in the Electronic Security Perimeters (ESPs) and failed to perform a complete CVA because not all ports and services on all Cyber Assets were assessed. WECC_URE2 used ports and services information gathered from one Cyber Asset as a representative sample to satisfy the vulnerability for 38 other Cyber Assets. WECC_URE2 only scanned one device to collect current ports and services information and the information was gathered from a test system and not from the actual Cyber Assets in question. WECC_URE2 also failed to gather current ports and services information from an additional 23 Cyber Assets. This led to a violation that included 21 Critical Cyber Assets (CCAs) and 41 non-critical Cyber Assets. The root cause of the violation was a process deficiency. Specifically, the technical team involved was not able to perform the CVA scan due to device and system outage limitations and felt that a scan on a representative sample would be sufficient. | CIP-007-3a | R8; R8.2; R8.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2's failure to conduct CVAs on 21 CCAs and 41 non-critical Cyber Assets led to a situation where WECC_URE2 put the 62 Cyber Assets at risk of compromise and unauthorized manipulation. Although WECC_URE2 failed to conduct the CVAs, WECC_URE2 did implement compensating measures. WECC_URE2 implemented a defense-in-depth strategy including physical and logical cyber security controls such as physical security mechanisms with guards and closed-circuit television. WECC_URE2 also implemented logical perimeter and other cyber security controls including firewalls, intrusion detection systems, and least-privilege account management practices. | the day after WECC_URE2 completed its Mitigation Plan for a prior violation of this Standard | present | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Compliance Audit | To mitigate this violation, WECC_URE2 will: 1) begin to transition to compliance with some or all of the CIP V5 Standards; 2) split the entire network to where all in-scope systems will be on two separate networks, two in each network; and 3) declare all Cyber Assets and systems at the generating facility to be part of one or more low impact Bulk Electric System cyber systems (LIBCS), as a result the LIBCS at the facility will no longer be in scope for any requirements pertaining to the execution of a CVA. | 11/5/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-23-000 | Western Electricity Coordinating Council (WECC) | WECC_URE3 | NCRXXXXX | WECC2014014001 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. WECC_URE3 reported that it failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) implemented automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3a R6. Specifically, WECC_URE3 failed to properly maintain and review logs for three Supervisory Control and Data Acquisition (SCADA) switches and to retain logs for 90 days for two Energy Management System (EMS) servers. As a result, WECC_URE3 reported that it had a violation of CIP-007-3a R6. WECC determined that WECC_URE3 failed to ensure that all Cyber Assets within the ESP implemented automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3a R6. The root cause involving the three switches was human error in that one employee did not add the devices to the Security Incident and Event Management (SIEM) for monitoring. The root cause for the servers not retaining 90 days worth of logs was due to technical errors as a result of a mis-configuration after a re-installation on a client after testing was performed. | CIP-007-3a | R6; R6.4; R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events that are related to cyber security. Specifically, WECC_URE3 failed to maintain and review logs for three SCADA switches which provide internal communication between SCADA workstations and SCADA servers. WECC_URE3 also failed to retain logs for 90 days for two EMS servers. Failing to implement, maintain, and review a logging system and failing to retain logs for 90 days could lead to undetected security incidents. A malicious person could scan these devices to discover vulnerable ports and services and launch an attack against any discovered vulnerabilities. WECC_URE3 implemented strong preventative controls to prevent undetected security incidents from occurring. Specifically, WECC_URE3 configured the operating system on these switches to limit which ports and services are allowed to open and start prior to adding them to the ESP. In other words, this configuration restricts any unauthorized ports and services outside of their current configuration, reducing the likelihood of an unauthorized user from leveraging a vulnerable port or service and gaining remote access to the SCADA switches. WECC_URE3 also implemented strong detective controls to detect any security incidents. Specifically, WECC_URE3 implemented a SIEM device that is used to monitor the logs of the SCADA devices. If someone were to gain control of the switches and attempt to then gain control of other SCADA devices, the security information and event management (SIEM) could detect that attempt. Since the SIEM monitors the SCADA devices 24 hours per day, seven days a week, an email would have been sent to security personnel alerting them about an unauthorized access attempt. The security personnel on-call would likely investigate, review the logs, and determine the unauthorized ports and services to shut them down. This would stop the network connection of the unauthorized personnel by shutting down the unauthorized ports and services, preventing unauthorized access to the SCADA devices. As further compensation, WECC_URE3 implemented strong compensating controls. Specifically, WECC_URE3 implemented a Cisco operating system (IOS) configuration to prevent unknown Media Access Control (MAC) addresses from connecting to the network. This MAC address restriction would likely prevent remote logging into the SCADA switches and attempt to access other SCADA devices. WECC_URE3 implemented additional strong compensating controls. Specifically, WECC_URE3 implemented locks on cabinets that contain these switches which would likely prevent a malicious person from physically damaging the three switches in scope. The locked cabinets prevent employees from getting physical access to the switches and not be able to access the switches via a serial cable and its console port. WECC_URE3 also added a firewall to restrict network access within the ESP and provide access point protections. | the date that WECC_URE3 put the switches into production without the appropriate monitoring tools | Mitigation Plan completion | 15000 | Self-Report | To mitigate this violation, WECC_URE3: 1) WECC_URE3 submitted evidence of the new switches being added as data sources within its SIEM and its log collection occurring; and 2) WECC_URE3 configured the alarm/notification to notify WECC_URE3 personnel when a “data source” client has stopped forwarding logs. | 2014-08-01 | 2014-11-14 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-03-31 | FERC | NP15-21-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2014013576 | Settlement Agreement | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. NPCC_URE1 failed to annually update passwords on Critical Cyber Assets and protected assets, most of which were relays. The substations have an automated password management system to handle the password changes. The root cause was ongoing functional issues with the automated password management system which did not allow NPCC_URE1 to properly update the passwords. A manual password change was instituted after NPCC_URE1 was unable to correct the automated password management system. | CIP-007-3a | R5; R5.3.3 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substation risk to the reliability of the bulk power system (BPS). Although the passwords were not changed, as required by CIP-007-3a R5.3.3, there are several levels of local physical protection that would have to be overcome for this to impact the BPS. Specifically, gate locks and badge access control provided physical security to the control house. In addition, there are several levels of remote cyber protection systems that would have to be overcome for this to impact the BPS; Firewalls, VLAN tunnels, and 2 levels of user authentication. Also, all passwords in use meet the password requirements. | When NPCC_URE1 failed to annually update the passwords. | When NPCC_URE1 completed its review of the passwords. | $0 (for NPCC2014013576 and NPCC2014013398) | Self-Report | To mitigate this violation, NPCC_URE1: 1) conducted monthly reviews of the date of last change of the station devices using the control system's password status report; 2) trained system administrators in the proper process to manually change passwords, using the system with minimal impact to the BPS; 3) developed and expanded on procedures to change and track the password changes using the built in functions of the vendor's system. | 2014-04-15 | 2015-01-09 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a Neutral factor in the penalty determination. In addition to the formal mitigation plan submitted, NPCC_URE1 agreed to implement additional mitigation activity. NPCC_URE1 has agreed to additional enhancements to their password manager system for their legacy devices. The enhancement is scheduled to be finished by the end of 2015. NPCC determined that NPCC_URE1’s compliance history was an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-21-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2014013398 | Settlement Agreement | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. During their quarterly review of their data center door badge access, it was discovered that a few individuals did not have their access removed as requested and within the 7 day period for transfers. A request to remove access from the PSP owner was sent to security through a non-standard procedure. Security revoked physical access on the old badging system. However, as the request did not occur through the normal process, during the cut-over to the new badging system, this individual’s access was effectively re-instated. Access for this individual was revoked upon discovery approximately three months later. A request from the PSP owner to remove access for a different individual was sent to security through a non-standard procedure, and access was not revoked in the badging system until discovery approximately three weeks later. An individual was granted access to both the data center and control center in error in the new badging system. The person in question was given access in error. The root cause was due to the provisioner’s limited experience of the new system. Upon further review of access, it was discovered that additional employees were also given access during the badging system cut-over. The root cause of the additional employees was due to requests that were made outside of the standard process. All individuals have had their access removed within approximately three months. | CIP-004-3a | R4. | Lower | Moderate | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Of the areas affected, the area that had Critical Cyber Assets (CCA) used in real-time operation of the BPS, and this area is staffed 24/7. In addition, there is an off-site alternate control center used to back up another control center. The individuals at issue did not have cyber access to any CCAs, only physical access. A physical attack on the CCAs used in real-time operation of the BPS would result in an automatic switch-over to the back-up system. During the violation duration, these individuals did not attempt to gain access to the PSPs.The individuals are still employed at the company and are in good standing. | When the first individual's access was incorrectly re-instated. | When the last individual's access was revoked. | $0 (for NPCC2014013576 and NPCC2014013398) | Self-Report | To mitigate this violation, NPCC_URE1: 1) removed physical access for those individuals identified as not having approved access to CIP areas; 2) centralized the physical access provision and revocation process that is accessible to security personnel with the rights to provision and revoke access in the physical security system; 3) revised the physical access provision and revocation process to add a checker step to make sure that the access changes match the access requests; 4) performed training for security personnel regarding the access provisioning/revoking process. Communication was sent to access requesters reminding them of the use of the online access request form as the only acceptable way to request access or revoke access. | 2014-04-25 | 2014-12-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a Neutral factor in the penalty determination. In addition to the formal mitigation plan submitted, NPCC_URE1 agreed to implement additional mitigation activity. NPCC_URE1 is in the process of developing a CIP access provisioning system within their compliance software. This system will be used to request and approve access to CIP physical security perimeters and revocation of such access. The system will provide a consistent method of provisioning CIP physical access across all companies. The result will be the elimination of the manual tracking process for CIP access provisioning at NPCC_URE1 and the multiple database system. NPCC determined that NPCC_URE1’s compliance history was an aggravating factor in the penalty determination.
2015-03-31 | FERC | NP15-21-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013012894 | Notice of Confirmed Violation | On August 27, 2013, NPCC_URE2 submitted a Self-Report stating that it had a violation of CIP-007-3a R4. The anti-virus software used for servers at NPCC_URE2 was transitioned. Updates for the old anti-virus stopped earlier during the month of transition. Due to an oversight by administrative staff managing the systems in question, some systems were missed in the transition and continued to run old anti-virus software without updates to the signatures identifying malware. Specifically, teams did not communicate clearly when and who had responsibility to update the systems’ anti-virus software. The systems affected were Linux servers used to monitor status of ICCP network availability, and virtual guest hypervisors running virtual desktops to support desktop access for IT support functions. NPCC_URE2 maintains a business process which involves use of an automated set of tests for server and desktop compliance to policies. The issue was discovered during a review of the automated compliance testing results. | CIP-007-3a | R4; R4.2 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected systems in question were running variants of Linux with limited account access and no externally exposed services. The remaining systems were Windows based systems that had anti-virus software with malware signatures 52 days out of date. Cyber assets within the same environment had functioning and updated anti-virus software with regular malware signature updates. All systems in question did not provide functions critical to the operation of the power system and were within an electronic security perimeter. No harm is known to have occurred. | when NPCC_URE2 failed to update signatures identifying malware | when NPCC_URE2 submitted a TFE for the appropriate assets | 0 | Self-Report | To mitigate this issue, NPCC_URE2: 1) transitioned the anti-virus software on the Linux systems in question 2) confirmed that regular updates to the malware signatures are applied with weekly testing via automated compliance test software. 3) replaced the systems with new ones that require Technical Feasibility Exceptions 4) developed a new system for automated testing and reporting on system configuration compliance. | 2014-11-06 | 2014-12-11 | Does Not Contest | NERC encourages internal discovery of noncompliance. Such identification should mark the beginning of coordination and partnership between the registered entity and the Regional Entity to remove outstanding risk to the BPS. This coordination and partnership should include timely identification, communication, and completion of mitigating activities. The failure of a registered entity to perform in this reliability-enhancing manner is the basis for the treatment of this violation as a Spreadsheet Notice of Penalty instead of a Find, Find, Track and Report or Compliance Exception.
2015-03-31 | FERC | NP15-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013058 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1.6. SERC_URE1 failed to log visitor access to Physical Security Perimeters (PSP) during two separate incidents. This determination addresses multiple incidents regarding SERC_URE1's violation of CIP-006 R1. Therefore, each incident is numbered and discussed separately. With regard to the first incident, SERC learned that a visitor to a PSP was not logged during the time of an outage of the Physical Access Control System (PACS). The outage affected two physical access points to the PSP. At 11:25, a SERC_URE1 security officer was dispatched to the PSP to monitor and validate access to the two access points during the outage. At 13:30, a contracted security technician entered the PSP to begin troubleshooting the issue with the PACS. Due to the layout of the communications closet, the security officer posted at the PSP was able to maintain line of sight of the technician. This enabled the security officer to serve as the escort for the security technician as well as perform the monitoring and access validations. However, the security officer did not manually log the technician’s entry (13:30) and exit (14:45) in the visitor control log per SERC_URE1's visitor control program. The root cause was human error. The security officers are trained on the proper procedures. However, the security officer here failed to follow the documented procedure. With regard to the second incident, a contracted security technician was performing work within the same PSP to replace a processor board. The security technician did not have authorized unescorted access privileges to the operations center PSP and was considered a visitor. The security technician was escorted by a SERC_URE1 employee during the time that work was being performed (15:53 to 16:36). The employee did not manually log the technician’s access in the visitor control log per SERC_URE1's visitor control program. SERC staff determined that SERC_URE1 was in violation of CIP-006-3c R1.6.1 because it failed to use logs to document the entry and exit of visitors, including the date and time, and to and from the PSPs. The root cause was human error. The SERC_URE1 employee failed to follow established procedures. While SERC was performing its assessment and determining the scope of the violation, the following additional issues were found: 1. While reviewing the PSP visitor logs for the two months, SERC_URE1 discovered there were some illegible entries and some information was missing in the logs (e.g., date, entry and exit times). As a result, SERC_URE1 reviewed the logs for a three month time period at the same PSP. SERC_URE1 identified a total of 55 visitors without PSP exit times, three visitor entries were missing a date, two visitors without a PSP date and entry time, one visitor without a PSP entry time, and some visitor names that were difficult to identify due to illegible writing and/or the first or last name was not included. SERC staff determined that SERC_URE1 was in violation of CIP-006-3c R1.6.1 because it failed to use logs to document the entry and exit of visitors, including the date and time, and to and from PSPs. The root cause was human error. The SERC_URE1 employees failed to follow established procedures. 2. SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report that it failed to document alternative measures to control physical access to Cyber Assets within an Electronic Security Perimeter (ESP). According to SERC_URE1, it discovered that there were two sites that had wiring outside the PSPs and a completely enclosed six-wall border could not be established. SERC staff determined that SERC_URE1 was in violation of CIP-006 R1.1 because it failed to document and to deploy alternative measures to control physical access to Cyber Assets where a six-wall border could not be established. The root cause was a misinterpretation issue. SERC_URE1's initial interpretation was that the wiring being exposed outside the ESP was not access to CCAs. Therefore, it did not protect it as such. However, when the CIP-005 Compliance Assessment Report was released SERC_URE1 modified their interpretation based on statements within the NERC document. | CIP-006-3c | R1; R 1.1; R1.6; R1.6.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to adequately log visitors at the PSP access points could create a risk that personnel were not properly supervised in the vicinity of Critical Cyber Assets. With regard to the visitor logs, the visitors were continuously monitored and escorted during the time they were in the PSP. A fenced barrier surrounds the two PSPs and monitoring is provided by security personnel twenty four hours a day, seven days a week. In addition, electronic monitoring of the wiring is provided by operational personnel, who maintain situational awareness of the network connectivity at the sites. | when the Standard became mandatory and enforceable for SERC_URE1 | present | $20,000 (for SERC2013013058, SERC2013013082, SERC2014013341, SERC2014013342, and SERC2014013620) | Self-Report | To mitigate this violation, SERC_URE1: 1) issued an email to the console operators and supervisors to reinforce SERC_URE1's procedures for monitoring and logging - the email included a copy of the procedure and instructions from the procedure regarding controlling access points, monitoring access points and logging access into the PSP; 2) issued a security awareness reinforcement publication focused on access control for the PSP; 3) updated its cyber security training to include a section on visitor logs and instructions for completion; 4) reviewed the security command center procedures for visitor management, alternative measures, and operability testing to make sure specific instructions were provided in regards to logging visitors; 5) filed a Technical Feasibility Exception for the two sites identified by operations; 6) developed a security awareness reinforcement publication around visitor management and update the visitor management poster; 7) conducted a counseling session between SERC_URE1 facilities management, SERC_URE1's vendor, and the affected facilities contractor to discuss the findings from the incident; 8) issued communications to all facilities employees and contractors reiterating the requirement for visitor control and logging. All personnel will be required to sign an acknowledgement form acknowledging receipt of the information and certifying their understanding of SERC_URE1's requirements for visitor management; 9) provided refresher training to SERC_URE1 security officers in the areas of visitor management and alternative measures to reinforce logging requirements; 10) evaluated the visitor logs to determine if there is a trend with a particular group and provide additional training and/or communications regarding the requirements for CIP-006 R1.6.1 to those particular group(s); and 11) developed a visitor control enterprise procedure to provide specific verbiage regarding: 1) completion of visitor logs, 2) logging requirements due to forgotten, lost/stolen or awaiting new badge, and 3) requirements and instructions for visitor log reviews by the business units. To mitigate this violation, SERC_URE1 will: 1) develop a standard enterprise manual log form and visitor badge tag to be used by the business units at SERC_URE1 PSP access points; 2) issue the new enterprise manual log forms and visitor tags to the business units; 3) implement the use of the new enterprise manual log forms; and 4) implement the monthly manual log review process. | 4/27/2015 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-03-31 | FERC | NP15-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013082 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4. SERC_URE1 failed to maintain a list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) and failed to revoke access to CCAs within seven calendar days for individuals, who no longer required such access. The Self-Report contained two incidents. SERC_URE1 added two new CCAs. While performing a review of the access list, the reviewer noticed two unfamiliar names. After further investigation, it was confirmed that the two employees did not need access to the two CCAs. Neither individual had physical access to the workstations nor had they been informed how to setup remote access to the workstations. The employees’ access was removed. When adding the CCAs, an additional active directory admin group was inadvertently added, so it brought in additional employees who would then have access. The root cause was a lack of technical understanding or oversight where the system administrator failed to realize the consequences of the move. With regard to the second incident, a manager requested the removal of electronic access from an employee, who no longer needed access. According to SERC_URE1, a workflow ticket was created, which indicated that access was removed for one domain group and twelve days later for the second domain group. However, while verifying the removal, it was discovered that access to the first domain had not been removed as previously indicated. The employee’s access was removed approximately two weeks later. The root cause was human error. The administrator who was performing the work made a mistake and hit the cancel button instead of save to complete the removal process. | CIP-004-3a | R4 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to grant and revoke access in a timely fashion, as well as failure to maintain the accuracy of the access list could leave the Cyber Assets unprotected and vulnerable to a cyber threat. For the first incident, the two individuals had electronic access to CCAs but had not set up remote access and did not have physical access. The individuals did not access the CCAs during the period they had access. For the second incident, the individual did not access the CCAs during the time that access should have been removed. The three individuals had each completed the required cyber security training and personnel risk assessment. | the date the employees were granted access | when the access was removed | $20,000 (for SERC2013013058, SERC2013013082, SERC2014013341, SERC2014013342, and SERC2014013620) | Self-Report | To mitigate this violation, SERC_URE1: 1) removed electronic access for the two employees; 2) required the manager in question to complete training on the NERC cyber security awareness E-learning course; 3) notified the IT Analyst that the access to the domain had not been removed as stated in the workflow ticket. The IT Analyst removed the access and confirmed via email to the NERC access services team; and 4) conducted a counseling session with the IT Analyst to review SERC_URE1's procedures for compliance with CIP-004 R4.2. | 2013-11-20 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2015-02-26 | FERC | NP15-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013341 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4. SERC_URE1 failed to revoke access to Critical Cyber Assets (CCA) within seven calendar days for one contract employee, who no longer required such access. A security officer resigned rather than transition to the new contract security services provider. The part-time security officer was not terminated in the SERC_URE1 system at the time the new contract security provider took over the security contract. The security officer retained authorized unescorted physical access to three Electronic Security Perimeters (ESPs). The security officer retained possession of the access badge. The security officer’s access was discovered and physical access was removed. A review of the security officer’s badge activity showed there has been no access since three weeks prior to the resignation. The root cause of this issue was an oversight by staff. | CIP-004-3a | R4; R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to grant and revoke access in a timely fashion, as well as failure to maintain the accuracy of the access list could leave the Cyber Assets unprotected and vulnerable to a cyber threat. However, the security officer was in good standing when he left, had a current personnel risk assessment, and had completed the required cyber security training. A review of the badge activity showed no access since prior to the security officer’s departure. | seven calendar days after the security guard’s CCA access should have been revoked | when all logical and badging system access was deactivated for the security officer | $20,000 (for SERC2013013058, SERC2013013082, SERC2014013341, SERC2014013342, and SERC2014013620) | Self-Report | To mitigate this violation, SERC_URE1: 1) removed access for the security officer; 2) reviewed and evaluated the procedure(s) for maintaining contractor access; 3) created and sent an awareness communication detailing the termination process and requirements to all managers with reports with NERC CIP access and to all contract firm contacts that manage contingent workers with NERC CIP access; and 4) developed and deployed manager training for termination processes which will address all termination/retirement scenarios, including contingent workers. | 2014-10-15 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2015-02-26 | FERC | NP15-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013342 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R5. SERC_URE1 failed to implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeters (PSPs) twenty-four hours a day, seven days a week, as required. At 9:33 p.m., SERC_URE1 began receiving communication failure alarms for 16 substation PSPs. According to SERC_URE1, the communication loss was between the Physical Access Control System (PACS) central server and the regulated remote field devices. The loss of communication occurred when SERC_URE1 executed a software upgrade on a network device around 9:00 p.m. the same day. The remote devices provided localized physical security access control, alarming, and access logging at the SERC_URE1's substation facilities. SERC_URE1 followed its response process by deploying alternative measures in accordance with SERC_URE1 procedures. SERC_URE1's procedures called for it to deploy alternative measures within 24 hours of a system outage to these sites. SERC_URE1 elected to deploy security officers to each of the 16 affected sites. Security officers were unable to arrive at two of the 16 substations within the 24-hour timeframe. The two substations contained a total of 4 Critical Cyber Assets out of 314 assets. These alternative measures, however, did not allow for monitoring of physical access to these PSPs twenty-four hours a day, seven days a week. The root cause of this issue was that IT performed a change on networking gear outside of the ESP without fully understanding the consequences if it shall fail. | CIP-006-3c | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to monitor physical access at 16 substation sites for approximately 25 hours meant SERC_URE1 would not have been able to respond to any unauthorized access attempts immediately. However, SERC_URE1 had documented procedures to deploy alternative monitoring methods and deployed those resources according to its procedure for 14 out of the 16 sites. The remote devices at SERC_URE1's substations operate in a stand-alone mode, and the card readers were still functioning properly during the time of the communication loss. All access and alarm activity was cached at the devices and downloaded to the server once the communication was reinstated. There were no unauthorized access attempts during the duration of the violation. | when loss of physical access monitoring occurred | when security arrived at the last substation and began monitoring physical access | $20,000 (for SERC2013013058, SERC2013013082, SERC2014013341, SERC2014013342, and SERC2014013620) | Self-Report | To mitigate this violation, SERC_URE1: 1) issued an email updating its process for communicating planned outages, equipment installations, major projects, etc., for any site identified on SERC_URE1's Critical Asset list. SERC_URE1 protection services was added to the distribution for future communications; 2) reviewed the security command center procedure for PACS issues to determine if there are any deficiencies, updated the procedure, and trained the appropriate SERC_URE1 personnel on entering PACS-related incident tickets; 3) updated the Physical Security Plan to provide clarity in the language regarding the deployment of alternative measures. A communication was issued to appropriate SERC_URE1 personnel detailing the changes along with a copy of the update; 4) evaluated the alternative measures site list spreadsheet to determine the necessary components needed to support a deployment; and 5) updated the alternative measures site list with the enhancements identified and provided training to appropriate SERC_URE1 personnel regarding its use. | 2014-07-21 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2015-02-26 | FERC | NP15-21-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013620 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5.3.3. SERC_URE1 found that one user had two accounts with passwords that had not been changed annually as required by CIP-007 R5.3.3. These accounts were associated with 11 Critical Cyber Assets (CCAs). SERC learned that the Cyber Assets had a technical password control deployed to force a password change after 365 days. However, the control would only force a password change if there was an attempted login. The accounts were not accessed within the annual timeframe. Therefore, the deployed policy and control did not enforce the annual change. SERC_URE1 has a documented NERC CIP cyber requirement procedure requiring passwords to be changed every 365 days. However, the procedure does not explicitly require the user to access the account for the sole purpose of changing the password. SERC learned that the accounts in question were local administrator accounts deployed on the 11 workstations. SERC_URE1 changed the password approximately sixteen months after the previous password changes following the discovery. | CIP-007-3a | R5; R5.3: R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to annually change account passwords could leave the system vulnerable to compromise for an extended period of time through unauthorized use of a password. However, SERC_URE1 had technical and procedural controls in place to enforce annual password changes. SERC_URE1 verified that the accounts had not been accessed since the date of expiration. Therefore, the deployed controls did not enforce the required password changes. If someone did try to access an account, the controls would have forced a password change. Also, this issue affected one generation site. All affected devices were protected by a Physical Security Perimeter and Electronic Security Perimeter. | the first day of the calendar year following the year requiring the password change | when the password was changed | $20,000 (for SERC2013013058, SERC2013013082, SERC2014013341, SERC2014013342, and SERC2014013620) | Self-Report | To mitigate this violation, SERC_URE1: 1) changed passwords for user accounts that did not have the password reset as required; 2) performed an extent of conditions analysis; and 3) created a reporting mechanism to capture and verify password age of Cyber Assets. | 2014-06-30 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2015-02-26 | FERC | NP15-21-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014210 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP 005-3a R2. WECC_URE1 failed to implement strong access controls for remote interactive access from five workstations to one server within the Electronic Security Perimeter (ESP). Auditors reviewed the change history of WECC_URE1's Network Address Translation (NAT) architecture for a server. The Audit team found that WECC_URE1 implemented an access rule change allowing access from five workstations outside the ESP. The five workstations did not utilize two-factor authentication. The failure to utilize strong access controls resulted in the violation. The root cause was human error and a lack of strong access controls. | CIP 005-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to implement strong access controls for remote interactive access to one server within the ESP. WECC_URE1's failure to implement strong access controls at the electronic access points to the ESP could result in an unauthorized individual exposing it to known vulnerabilities and gain unauthorized access to devices. The risk was mitigated because WECC_URE1 maintains multiple layers of protection for ESP assets, including multi-factor authentication, strict user account controls, change control and configuration management, and monitoring of system events. Furthermore, WECC_URE1 has established and documented appropriate ESP architecture and identified all access points which reside within the defined ESPs. At all access points to the ESPs, WECC_URE1 enables only ports and services required for operations and for monitoring Cyber Assets within the ESP. WECC_URE1 also documents the configuration of those ports and services. Only specific ports and services required for operations and monitoring have been enabled, and in all other cases access to and from any ESP is denied by default. WECC_URE1 has documented all open ports and services enabled on any access point into a designated ESP, including the business justification. Where interactive access into a designated ESP has been enabled, the processes to request and review authorization rights, authentication methods used, and appropriate use banner content, have been documented. | when WECC_URE1 implemented the application | Mitigation Plan completion | $30,000 (for WECC2014014210 and WECC2014014214) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) migrated the server out of the ESP and into a dedicated secure demilitarized zone; and 2) drafted updates to the change control procedures and forms to specifically call out changes requiring interactive access into or out of the ESP to better ensure appropriate controls are in place. | 9/8/2014 | TBD | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-02-26 | FERC | NP15-21-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014214 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP 007-3a R8. WECC_URE1 was unable to provide evidence to auditors that it reviewed its ports and services or conducted a review of its controls for approximately 15 Critical Cyber Assets (CCAs) and 5 Electronic Access Control and Monitoring (EACM) devices. Further, WECC_URE1 failed to provide files or output documentation of any kind demonstrating the performance of an annual Cyber Vulnerability Assessment (CVA). The root cause is human error and from a lack of internal controls/process for maintenance and testing documentation and records. Since WECC_URE1 did not have adequate controls in place to ensure it was reviewing and maintaining its system documentation properly. | CIP 007-3a | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to perform a CVA on all CCAs inside the ESP could potentially allow unauthorized ports and default user accounts to go unnoticed and uncontrolled, thus exposing the system to unauthorized connections and/or access, negatively impacting BPS operations. WECC_URE1 maintains multiple layers of protection for ESP assets, including multi-factor authentication, strict user account controls, change control and configuration management, and monitoring of system events. Furthermore, WECC_URE1 has established and documented appropriate ESP architecture and identified all access points which reside within the defined ESPs. At all access points to the ESPs, WECC_URE1 enables only ports and services required for operations and for monitoring Cyber Assets within the ESP. WECC_URE1 also documents the configuration of those ports and services. Only specific ports and services required for operations and monitoring have been enabled, and in all other cases, access to and from any ESP is denied by default. WECC_URE1 has documented all open ports and services enabled on any access point into a designated ESP, including the business justification. Where interactive access into a designated ESP has been enabled, the processes to request and review authorization rights, authentication methods used, and appropriate use banner content, have been documented. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $30,000 (for WECC2014014210 and WECC2014014214) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) developed and tested one or more automated methods to regularly capture and document active ports and services; 2) drafted changes to the security checklist form and associated processes used during change control activities to better tie this information back into the annual CVA process; 3) drafted changes to the overall change control and testing programs to better tie these back into the annual CVA process; 4) developed and tested ways to utilize internal scanning tools within the environment without impact to the Energy Management System (EMS); and 5) is also in the process of setting up a server within a DMZ to help manage the documentation for a number of EMS processes. | 2014-10-03 | TBD | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-02-26 | FERC | NP15-19-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013427 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-002-1 R3. RFC_URE1 reported that during an internal compliance review, it discovered at a RFC_URE1 Critical Asset substation two Ethernet cables connecting two managed Ethernet switches to a Ethernet switch. The switch was connected via fiber to an internet protocol (IP) ring that connected several non-critical substations. Other Cyber Assets were connected to the managed Ethernet switches. None of the Cyber Assets at the Critical Asset substation were classified as Critical Cyber Assets (CCAs) despite the use of routable protocol by the two managed Ethernet switches. In addition, during the Compliance Audit, RF discovered two storage devices that were not declared as CCAs. RFC_URE1 later reported in its Mitigation Plan for CIP-002-1 R3 that it had identified a physical Ethernet cable connection from these two external storage devices to servers that run a database. The assets were initially classified as protected Cyber Assets, but not NERC CCAs. After confirming the function of the storage devices, RFC_URE1 assessed them using its CCA identification process and classified them as CCAs. RFC_URE1 determined that, in part, the root cause of the violation is that its annual assessments did not include a separate step to identify the use of routable protocol. RFC_URE1 made a strategic decision prior to CIP mandatory enforcement to remove routable protocol from Critical Asset substations. Based on this earlier decision, RFC_URE1’s annual assessments did not include a separate step to identify routable protocol as it assumed that no routable protocol was being used in Critical Asset facilities. As a result, isolated devices, which used routable protocol, were not identified as CCAs. Further, RFC_URE1 also determined that a procedure utilized in the CCA identification process included a form that was pre-populated and relied on historical answers, which increased the possibility of misclassifying an asset. Finally, RFC_URE1 determined that the evaluation of Cyber Assets needed someone that has IT experience and would have an adequate understanding of how the Cyber Assets are connected to the network equipment and relevant configurations and protocols being used. | CIP-002-1 | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although RFC_URE1 disconnected the relevant Ethernet cables and the external storage devices are located within a Physical Security Perimeter, assets not protected by the full suite of CIP-007 security controls may have been vulnerable to misuse or compromise. The long duration of the violation – over four years – also increased the risk to the BPS. In addition, although RFC_URE1 conducted annual assessments those reviews assumed that routable protocol had been removed from all substations and therefore the RFC_URE1 reviewer, who also did not have information technology expertise, did not recognize assets that were subject to CCA classification. As a result, the internal controls in place prior to mitigation of this violation were not fully effective. The risk to the BPS was mitigated for the following reasons. The external network connection is a RFC_URE1 private network behind a firewall, which is not part of the Electronic Security Perimeter (ESP), and is not exposed to the internet. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2014013427 and RFC2014013705) | Self-Report | To mitigate this violation, RFC_URE1: 1) unplugged the network connection at the Critical Asset substation; 2) investigated and assessed all Cyber Assets in all Critical Asset substations; 3) developed, updated and supplemented documentation to any existing processes and procedures to address non-BPS Cyber Assets at Critical Asset substations, including new asset identification templates, configuration guides, ESP diagrams, and recovery plans; 4) conducted an investigation to determine the root cause, extent of condition, and corrective actions; 5) submitted technical feasibility exceptions for controls that were not technically feasible to apply; 6) included personnel with the technical expertise needed to complete an effective annual assessment; and 7) applied protective measures of the CIP Standards to the newly-identified CCAs. | 9/30/2014 | TBD | Neither Admits nor Denies | RFC reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although the risk determinations for the violations were not minimal, RFC_URE1 has been cooperative through the enforcement process and has voluntarily and timely mitigated the violations. RF determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE1’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1’s response to the audit findings is behavior that RF seeks to encourage, as these are positive, proactive steps to prevent recurrence of noncompliance. In light of this response, RF determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability. RF also considered that the violations were not indicative of systemic issues in RFC_URE1’s compliance program, or resulting from a significant lack of internal controls. Although both violations are classified as “moderate” risk issues, these assessments were based solely on the risk inherent in violations of those particular Standards, and were not related to the implementation of RFC_URE1’s compliance program. Furthermore, the root causes of the violations are not likely to be repeated; the CIP-002-1 R3 violation was an incomplete effort prior to the mandatory compliance date that led to an assumption of the status of the affected devices, and the CIP-009-1 R4 issue involved RFC_URE1’s faulty interpretation of the Standard made in good faith and quickly corrected upon notice of RF’s interpretation. RFC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
2015-02-26 | FERC | NP15-19-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013705 | Settlement Agreement | During the Compliance Audit, RF determined that RFC_URE1 was in violation of CIP-009-1 R4. RFC_URE1 failed to provide evidence of backup of information required to successfully restore Critical Cyber Assets for network-attached storage (NAS) servers. Instead, RFC_URE1 stated that it uses mirroring, which is real-time replication of data on a backup system, as a backup method. However, mirroring is insufficient for CIP-009-1 R4 compliance because it does not provide a reliable method of recovery under all circumstances. For example, accidentally modified or deleted files, corrupted files, and malicious code would be replicated to the backup source, leaving no recovery files in such events. RFC_URE1 determined that, in part, the root cause of the violation is that RFC_URE1 failed to recognize that its chosen method for backup was insufficient for recovery. | CIP-009-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE1 allowed a risk to the BPS to exist over a period of more than four years by not developing a functional backup and recovery plan for the NAS servers. This lack of recovery planning meant that these servers were vulnerable to a wide array of potential harm including accidental and intentional data manipulation and corruption. The risk to the BPS was mitigated for the following reasons. The NAS servers were classified as CCAs and are afforded the protections required in CIP-002-3 through CIP-009-3 standards. Additionally, the NAS servers reside within Physical Security Perimeters and a segregated Electronic Security Perimeter (ESP). Finally, elevated authorized electronic access is required to access the NAS servers. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2014013705 and RFC2014013427). | Compliance Audit | To mitigate this violation, RFC_URE1: 1) established a procedure for backing up and recovering the NAS servers; 2) performed the backup of the NAS server system configuration; 3) updated the training and reference material document regarding the backup and restoration procedures for CCAs within the Electronic Security Perimeter to ensure it included instructions for backing up and restoring the NAS server configuration; and 4) conducted training for relevant personnel, including how to achieve compliance with the standard and provide example of good compliance evidence. | 2014-11-24 | TBD | Neither Admits nor Denies | RFC reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although the risk determinations for the violations were not minimal, RFC_URE1 has been cooperative through the enforcement process and has voluntarily and timely mitigated the violations. RF determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE1’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1’s response to the audit findings is behavior that RF seeks to encourage, as these are positive, proactive steps to prevent recurrence of noncompliance. In light of this response, RF determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability. RF also considered that the violations were not indicative of systemic issues in RFC_URE1’s compliance program, or resulting from a significant lack of internal controls. Although both violations are classified as “moderate” risk issues, these assessments were based solely on the risk inherent in violations of those particular Standards, and were not related to the implementation of RFC_URE1’s compliance program. Furthermore, the root causes of the violations are not likely to be repeated; the CIP-002-1 R3 violation was an incomplete effort prior to the mandatory compliance date that led to an assumption of the status of the affected devices, and the CIP-009-1 R4 issue involved RFC_URE1’s faulty interpretation of the Standard made in good faith and quickly corrected upon notice of RF’s interpretation.
2015-02-26 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010644 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. Specifically, SPP_URE1 had not included a Cyber Asset in its patch management program and was unable to provide evidence that patches were assessed for another Cyber Asset, per R3.1. Accordingly, no compensating measures were applied to these Cyber Assets to mitigate risk per R3.2. With regard to SPP_URE1's failure to include the server in its patch management program, the root cause was that during its installation, SPP_URE1's configuration management policy for ensuring that new devices are fully documented with procedures covering applicable security controls, including patching, was not followed. Due to employee oversight, patches were not assessed for the device. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The lack of patch assessment and installation, and the failure to apply compensating measures, where appropriate, creates the risk that SPP_URE1's Cyber Assets would be susceptible to vulnerabilities that would have otherwise been prevented by patching. The risk posed by this violation was mitigated by SPP_URE1's policy to deny access to devices that attempt to communicate with its Cyber Assets from outside its Electronic Security Perimeter (ESP), and no Cyber Assets or Critical Cyber Assets within SPP_URE1's ESPs have internet access. Therefore, the probability of unauthorized access to SPP_URE1's Cyber Assets within its ESPs is remote. SPP_URE1 has installed an antivirus application on its Cyber Assets and its ESP networks are continuously monitored by a network intrusion detection system. These activities increase the likelihood that SPP_URE1 would detect unauthorized access of its ESPs. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) moved the functions performed by both Cyber Assets to an existing Cyber Asset that is patched according to SPP_URE1's security patch management program; and 2) decommissioned both Cyber Assets. | 2013-01-02 | 2013-06-12 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-02-26 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010645 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.8. Two of SPP_URE1's Physical Access Control System (PACS) Cyber Assets used for physical security monitoring were not afforded the protective measures required by CIP-003 R1, R6; CIP-005 R2, R3; CIP-007 R2, R3, R4, R5.1.2, R5.2.3, R5.3.2, R5.3.3, R6; and CIP-009 R1. SPP_URE1 failed to include two PACS Cyber Assets in the Cyber Asset security policy, it failed to apply a change control process to the PACS Cyber Assets, it failed to capture system event logs for the PACS Cyber Assets and review the logs every 90 days. SPP_URE also failed to submit Technical Feasibility Exceptions (TFEs) for the PACS Cyber Asset that could not meet patching requirements, and for the PACS Cyber Assets that could not meet password complexity nor password change requirements. The root cause of the violation was that the SPP_URE1 employees supporting these assets were not originally within the IT Department and were not aware of the specific NERC requirements. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to afford all the protective measures of CIP-006-1 R1.8 to the two PACS Cyber Assets presented the risk that if the assets were compromised, SPP_URE1's incident response may not have been alerted of an unauthorized attempt to access SPP_URE1's Physical Security Perimeter (PSP). During the period of noncompliance, SPP_URE1 had several security controls in place which mitigated the risk posed by this violation. Both PACS Cyber Assets reside within a PSP and an Electronic Security Perimeter (ESP). All personnel who interacted with the PACS Cyber Assets were authorized for unescorted physical and/or electronic access to Critical Cyber Assets. SPP_URE1 utilizes a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access, and to detect malware. SPP_URE1's NIDS is monitored during office hours by qualified personnel and is configured to send alerts to authorized personnel on a 24 x 7 basis. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) performed a compliance status assessment for the two PACS Cyber Assets to determine the required mitigating activities in order to meet compliance with CIP-006-3 R2.2/CIP-006-1 R1; 2) added the Cyber Assets to SPP_URE1's Cyber Security Policy; 3) included the Cyber Assets in SPP_URE1's Change Control Process 4) included the Cyber Assets in SPP_URE1's mitigation for dial-up devices; 5) began capturing the Cyber Assets logs on SPP_URE1's logging server, and included the logs in its 90-day review process; 6) established, documented, and implemented a process to ensure that only ports and services required for normal and emergency operations were enabled; 7) applied SPP_URE1's security patch management process to one of the Cyber Assets, and submitted a Technical Feasibility Exception (TFE) for the other Cyber Asset that cannot meet patching requirements ; 8) updated the anti-virus and malware signature files on the Cyber Assets; 9) for one of the Cyber Assets, established a log to track shared account use; 10) set up account logging for the shared account; 11) submitted TFEs for the Cyber Asset that cannot meet password complexity nor password-change requirements; 12) performed log reviews for the two PACS Cyber Assets; and 13) included the two PACS Cyber Assets in SPP_URE1's recovery plan. | 2013-10-30 | 2014-04-29 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-02-26 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011085 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1. SPP_URE1 failed to identify a Remote Terminal Unit (RTU) test server as an Electronic Access Point (EAP). The test server, which resides inside an Electronic Security Perimeter (ESP), was directly connected to RTU test equipment residing outside the SPP_URE1 ESP, but no electronic access point was identified between the server and the test equipment. The root cause of the violation was that this configuration existed prior to the mandatory compliance date. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to identify the RTU test server as an access point meant SPP_URE1 failed to institute appropriate access controls to prevent unauthorized access to the SPP_URE1 ESP. The risk posed by the violation was mitigated by SPP_URE1's implementation of a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access within its network. SPP_URE1's NIDS is monitored during office hours by qualified personnel, and is configured to send alerts to authorized personnel on a 24x7 basis. Technicians who work with the test server and RTUs have authorized physical access to the SPP_URE1 Physical Security Perimeters and hold current Personnel Risk Assessments. Applicable patches have been applied to the test server; anti-virus is installed; and security logs are reviewed. | when SPP_URE1 failed to identify an EAP | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) added a firewall between the test server and the test RTU equipment located outside the ESP to create an access-controlled EAP between the two locations; and 2) improved its annual vulnerability assessment process to include a physical walk-through and cable trace to identify all access points to the ESP. | 2012-10-12 | 2013-07-12 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE determined that SPP_URE1's compliance history should not serve as a basis for aggravating the penalty.
2015-01-30 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011410 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-2a R1. Specifically, SPP_URE1 was unable to provide evidence showing that cyber security testing was performed prior to installation of several Cyber Assets. SPP_URE1 did not maintain sufficient documentation to demonstrate that testing occurred on newly built workstations and a virtual environment host server. Adequate evidence was not maintained to demonstrate that the associated security controls were properly configured prior to placing the Cyber Assets into production. Subsequent to the audit and during mitigation of the aforementioned noncompliance, SPP_URE1 identified an additional instance of non-compliance. A set of firewalls were added to the outer boundary of two servers bringing the servers into the SPP_URE1 Electronic Security Perimeters (ESPs), but SPP_URE1 could not demonstrate that CIP-007-3 R1 testing was conducted on the two servers prior to introduction into SPP_URE1 ESPs. SPP_URE1 also discovered that a third-party software upgrade was performed on a Cyber Asset without properly testing security controls and documenting the results. The instances described resulted from a lack of staff training with regard to configuration management and change control. | CIP-007-2a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to test the introduction of new Cyber Assets, or significant changes to Cyber Assets in the ESP creates a risk that SPP_URE1's security controls may have been weakened due to the modification, thereby exposing the SPP_URE1 ESP and its associated network to malicious attack. The risk posed by this violation is mitigated because the implicated devices were afforded the CIP required protections (including security patching and anti-malware). The security controls of the Cyber Assets in scope of this violation were checked during SPP_URE1's annual Cyber Vulnerability Assessments and whenever significant changes were implemented to these Cyber Assets. Additionally, SPP_URE1's access control and monitoring devices are configured to deny all access attempts originating from outside its ESPs, thereby significantly limiting the risk that actual unauthorized access could occur. SPP_URE1's ESP networks are continuously monitored by a network intrusion detection system, which provides a redundant detection mechanism in the event that SPP_URE1 failed to identify an unintended change in its security controls. | when new workstations and/or a new server were installed | Mitigation Plan completion | None | Compliance Audit | To mitigate the violation, SPP_URE1: 1) replaced the two servers in 2013 to bring them into compliance; 2) performed a comparison scan of the third party software upgrade to the asset's baseline to review and assess security controls; 3) provided refresher training to IT staff on NERC requirements for Cyber Assets; 4) provided training to IT staff on use of the testing templates, and added the templates to the Configuration Management Plan for easy access; and 5) added an additional review step to its change control process. | 2013-08-02 | 2013-09-11 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-01-30 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011415 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-1 R5 (5.1.2, 5.1.3, 5.2.3, 5.3.3). SPP_URE1 was unable to provide evidence to demonstrate that historical audit trails of individual user account access activity for Windows systems was adequately logged as required by R5.1.2. While login failures were logged, successful logins were not. After the audit, SPP_URE1 found that three network switches and two routers were not logging all individual account access activity as required by R5.1.2. Access failures and successes were not being logged as a result of the lack of staff training with regard to configuration management. SPP_URE1 did not review all user accounts at least annually to verify access privileges are in accordance with CIP-003 R5, and CIP-004 R4 as required by CIP-007 R5.1.3. Specifically, the audit team discovered that although SPP_URE1 was reviewing shared user accounts, access privileges for individual user accounts were not reviewed. The noncompliance was due to employee oversight during the annual review of account access. SPP_URE1 was unable to provide evidence of an audit trail of shared account use as required by R5.2.3. Specifically, the audit team discovered that all Supervisory Control and Data Acquisition (SCADA) and Energy Management System (EMS) operators and the system/network administrator used the same shared user account, but a log was not maintained to identify the individual who was accessing the shared account at any particular time. The noncompliance resulted from employee oversight. SPP RE found that SPP_RE failed to change the domain password for a SCADA service account annually as required by R5.3.3. SPP_RE had not changed the password because doing so would have resulted in a system error. Although the password change was technically infeasible, SPP_RE had not requested a Technical Feasibility Exception (TFE) nor documented compensating measures. | CIP-007-1 | R5; R5.1.2, R5.1.3, R5.2.3, R5.3.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to adequately track the use of the accounts in question (individual windows accounts, shared operator accounts, and switch/router accounts) creates a risk that an unauthorized person could have accessed the SPP_URE1 Electronic Security Perimeter (ESP). Such unauthorized access could have negatively impacted SPP_URE1's network, its operator workstations, and its EMS devices. Additionally, the failure to adequately review access potentially increases the risk of an insider attack because the scope of individuals with access to critical systems may have included more individuals than was required. During the period of noncompliance, SPP_URE1 had several security controls in place which mitigated the risk of this violation. Individuals with access to the Physical Security Perimeter (PSP) and ESP have completed physical and cyber security training as well as Personnel Risk Assessments. SPP_URE1 maintains policies to remove access when personnel leave or transfer to other departments. Information Technology staff utilize an electronic work order system for work assignment and activity tracking (which could be cross referenced against access times to narrow potential abuse of account privilege); and the SPP_URE1 ESP is continuously monitored by an intrusion detection system, which increases the likelihood that potentially malicious activity in the environment would be detected. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Audit | To mitigate the violation, SPP_URE1: 1) revised its logging policy to include login and logoff successes and failures, and updated its log management document to include the new account logging policy; 2) created a spreadsheet of accounts to include individual user accounts. The spreadsheet is utilized as a template to identify accounts requiring review during SPP_URE1's annual accounts audit; 3) implemented an electronic log in order to maintain a record of shared user account access in which shared account users log their account use time; 4) filed a TFE with SPP RE to address the inability to change the service account password; and 5) migrated the functionality of the Windows cluster to a virtual server and disabled the service account password. | 2014-09-15 | 2014-10-08 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-01-30 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011416 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-1 R6. Specifically, SPP_URE1 did not implement automated tools or organizational process controls to monitor specific system events related to cyber security for certain Supervisory Control and Data Acquisition (SCADA) system accounts, and no compensating measures were applied to mitigate risk. The root cause of the non-compliance was that SPP_URE1 did not log specific events for certain SCADA system accounts because the frequency of these logged events degraded server functionality. | CIP-007-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to ensure that sufficient logging was enabled reduced SPP_URE1's awareness of system cyber security events within its Electronic Security Perimeters (ESP). However, SPP_URE1 utilizes a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access. SPP_URE1's NIDS is monitored during office hours by qualified personnel, and is configured to send all network traffic alerts to authorized personnel on a 24x7 basis, which increases the likelihood that SPP_URE1 would detect unauthorized access attempts into the SPP_URE1 ESPs. SPP_URE1 denies access to devices that attempt to communicate to its ESPs from outside the ESP, thereby limiting the risk that unauthorized access could occur. In addition, no devices within SPP_URE1's ESPs have internet access. These SCADA Cyber Assets reside within SPP_URE1's defined ESPs and Physical Security Perimeters (PSPs), with access limited to only authorized personnel. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Audit | To mitigate this violation, SPP_URE1: 1) developed a script to allow for collating of security events; the collated list is reviewed quarterly, as required by CIP-007-3 R6; 2) submitted a Technical Feasibility Exception for security event logging of certain system accounts; and 3) updated its Log Management document to address security event logging for the applications related to this violation. | 2014-01-02 | 2014-06-06 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-01-30 | FERC | NP15-19-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010987 | Settlement Agreement | SPP_URE1 was in violation of CIP-005-1 R2.1, R2.2, and R2.4. SPP_URE1 failed to document and implement organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to its Electronic Security Perimeter(s) (ESP). Specifically, two switches, one at the Primary Control Center (PCC) and one at the Backup Control Center (BCC), were not capable of being configured to explicitly permit authorized data traffic into the ESP and deny other traffic by default as required by CIP-005-1 R2.1. The switches could not be configured such that only the ports and services required for operations and monitoring Cyber Assets within the ESP were enabled as required by CIP-005-1 R2.2. Furthermore, the switches were not capable of supporting strong technical controls at the access points to ensure authenticity of the accessing party as required by CIP-005-1 R2.4, and SPP_URE1 had not sought a Technical Feasibility Exception. The root cause of the violation was SPP_URE1's oversight that the devices were not technically capable of being configured to meet the requirement. | CIP-005-1 | R2; R2.1; R2.2; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because the switches lacked the specified configuration and technical controls, there was the risk that unauthorized electronic access into SPP_URE1's ESP might occur. However, SPP_URE1 had procedural, organizational, and technical mechanisms in place for control of electronic access via the switches. SPP_URE1's access control and monitoring devices are configured to deny all access attempts originating from outside the ESP, thereby limiting the risk that unauthorized access could occur. SPP_URE1's ESP network is continuously monitored by a network intrusion detection system, which increases the likelihood that SPP_URE1 would detect unauthorized access attempts into the SPP_URE1 ESPs. Network traffic between the two switches flows over a communications path owned and controlled by SPP_URE1. The switches are located within Physical Security Perimeters (PSPs) and physical access is restricted to authorized personnel with cyber security training and Personnel Risk Assessments. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Investigation | To mitigate this violation and prevent recurrence, SPP_URE1 installed two pairs of stacked firewalls as ESP access point devices between its PCC and BCCs. The firewalls are configured to explicitly permit authorized data traffic into the ESP, deny unauthorized data traffic by default, are configured such that only required ports and services are enabled, and support strong technical controls. | 2014-06-06 | 2014-09-23 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
2015-01-30 | FERC | NP15-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012741 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-003-3 R6. A RFC_URE1 IT network consultant (Network Consultant) was escorted by authorized security personnel to a RFC_URE1 in order to fix a software encryption certificate to allow remote access to a network device. The Network Consultant was authorized to access the NERC CIP IT device. However, while at the site, the Network Consultant applied unapproved network changes that resulted in a loss of network communication to the site, in violation of RFC_URE1’s change management process. The changes applied by the Network Consultant were still being analyzed by RFC_URE1’s IT engineering group and had not yet been approved at the time the Network Consultant applied them. The Network Consultant was contacted immediately and directed to revert to the original approved configuration. However, communication was lost with a device for approximately 45 minutes. RFC_URE1 IT conducted a root cause analysis of the issue. During this analysis, RFC_URE1 identified that the same IT Network Consultant made an additional change without following RFC_URE1’s change management process approximately two weeks after the first incident. The second incident involved a change that was applied on multiple other non-CIP devices and did not result in any harm to the network. Upon discovery of this additional process failure by the Network Consultant, the Network Consultant’s access to the CIP infrastructure was removed until the investigation was completed to prevent further incidents. RFC_URE1 also determined during its root cause analysis that the Network Consultant was aware of RFC_URE1’s change management process, but chose not to follow it in both cases. Ultimately, the Network Consultant was terminated. RFC_URE1 failed to follow its change management procedure on two occasions, one of which resulted in a 45-minute period of reduced security of the network. RFC_URE1 promptly detected the issue, conducted a root cause analysis, effectively mitigated it, and timely self-reported it. | CIP-003-3 | R6 | Lower | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Network Consultant’s failure to follow the RFC_URE1 change management process resulted in a 45-minute loss of visibility to a device . Although RFC_URE1 failed to implement its change management procedure in this instance, all other testing procedures were followed for the erroneous application of the unapproved network changes. In addition, protective relays, which do not depend on network connectivity, continued to function, and the control center was able to monitor the lines affected by the communication outage via monitoring equipment at neighboring stations. Lastly, cybersecurity logging was still occurring locally during this period and the review of the logs did not show any reportable cybersecurity incident during the noncompliance, during which time the devices on the network were isolated. | when RFC_URE1 failed to follow its change control and configuration management process | Mitigation Plan completion | 0 | Self-Report | To mitigate this violation, RFC_URE1: 1) revised its change management process to require a RFC_URE1 IT staff member to be present at the control center and deployed in the field while changes are implemented in case an outage occurs; 2) conducted training on its revised change management process for its IT personnel; 3) instituted a pre- and post-implementation peer review of significant changes to RFC_URE1’s NERC CIP Networks; and 4) also updated its change request form to reflect the new, pre- and post-implementation peer review. | 2013-07-24 | 2014-08-13 | Admits | RF considered certain aspects of the RFC_URE1’s compliance program as mitigating factors. RF also considered that the violation was caused by a rogue employee and did not indicate a systemic problem at RFC_URE1 such as a lack of awareness and training on RFC_URE1’s change management process. RF considered this fact a mitigating factor in the penalty determination. However, because RFC_URE1’s failure to implement its change management procedure resulted in harm to its operations, and because RFC_URE1’s initial response to the violation allowed a second failure to occur that was caused by the same employee, RF determined that the violation did not qualify for Find, Fix, Track and Report (FFT) or Compliance Exception disposition. The need for a monetary penalty was eliminated by the significant credit given for RFC_URE1’s timely detection, correction and reporting, and its well-established history of doing so in prior matters.
2015-01-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011812 | Settlement Agreement | SERC_URE1 submitted a Self-Certification to SERC stating that it was in violation of CIP-006-3c R4. SERC_URE1 failed to implement controls to manage physical access at an emergency egress door to a Physical Security Perimeter (PSP). According to SERC_URE1, it received a door forced open alarm for an emergency egress door to a PSP. SERC learned that corporate security was conducting the annual testing on all physical access points to the PSP and inadvertently left the door unsecured. An employee was onsite performing authorized work in the area and opened the unsecured door, generating the alarm. Upon learning that the door was unsecure, SERC_URE1 had it physically monitored until the appropriate employee arrived and secured the door. The door was an emergency egress door that required a key to open it from the outside. The root cause of this issue was human error. SERC_URE1 personnel performed tests and failed to re-secure the door. | CIP-006-3c | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the PSP door was unsecured, it was configured to alarm when opened and was in working condition. The Cyber Assets were located within a facility that was protected by a perimeter fence that required restricted card access to enter, as well as cameras throughout the location. | when the door was left unsecure | when the door was secured | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Certification | To mitigate this violation, SERC_URE1: 1) locked the door and ensured it was secure; and 2) disabled the locking mechanism to prevent the ability to unlock the door. | 12/5/2012 | 2014-03-05 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-01-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012154 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R2.2. SERC_URE1 had Cyber Assets that authorized and/or logged access to the Physical Security Perimeter (PSP) that were not afforded the protections specified in CIP-007-3 R3 and CIP-007-3 R5.1.3. The Self-Report contained two incidents. In the first incident, SERC_URE1 discovered that the alerting feature it previously used for two servers regarding security patch monitoring stopped working after it failed to renew an extended support contract with a vendor. SERC_URE1 failed to assess the security patches and security upgrades in accordance with CIP-007-3 R3. With regard to the second incident, SERC_URE1 discovered that two operator accounts had not been suspended in accordance to CIP-007-3 R5.1.3. Both operator accounts were associated with contracted security guards assigned to SERC_URE1. SERC learned that neither security guard had been terminated for cause. Accordingly, the access list should have been updated within the seven calendar days of any change. SERC_URE1 submitted a second Self-Report to SERC stating that it was in violation of CIP-004-1 R4. SERC determined that this violation was reported incorrectly under CIP-004-1 R4 and instead should have been reported under CIP-006-3c R2.2 and CIP-005-3a R1.5. SERC determined that a portion of the previous Self-Report involved the same Standard and Requirement as and has decided to treat it as an expansion of scope. SERC_URE1 reported that it failed to identify and document four administrator accounts that provided cyber access to two physical access control systems (PACS). The root cause of these issues was human error when extending the contract. SERC_URE1 failed to ensure the alerting feature was included when they extended their contract. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to remove access to and update the access lists for PSPs could have allowed unauthorized access to go unnoticed, potentially allowing malicious access. Further, failure to track and maintain a list of personnel with cyber access to PACS could have allowed individuals with cyber access to PACS to manipulate or alter physical access authorizations to Critical Cyber Assets (CCAs), either purposefully or by mistake, resulting in disruption or loss of control of the energy management system or SERC_URE1's portion of the BPS. However, neither operator account had permission levels that could affect the integrity of the CIP infrastructure. In addition, failing to assess and to implement security patches and security upgrades, where applicable, combined with the failure to document compensating measures if not installed, could have left software on the affected Cyber Assets vulnerable, increasing the risk of a cyber-attack that could result in operational impacts and potential degradation of the BPS. However, the affected Cyber Assets were behind corporate firewalls and intrusion detection and intrusion protection systems were deployed on the network. Also, the individuals in question would not have cyber access because automated processes would have removed access within 24 hours. | 30 days following the first patch release | when the administrator accounts to PACS were documented | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Report | To mitigate the first incident in this violation, SERC_URE1: 1) subscribed to an alerting feature for extended support of notifications; 2) conducted a meeting to determine the extent of condition; 3) implemented patches; and 4) updated documentation. To mitigate the second incident in this violation, SERC_URE1: 1) suspended the 1st and 2nd operator accounts; and 2) developed a security officer termination process. | 2014-09-30 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2015-01-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012155 | Settlement Agreement | SERC_UREX submitted a Self-Report to SERC stating that it was in violation of CIP-005-1 R1. SERC_URE1 failed to identify serially connected devices as electronic access points, and it failed to afford the protective measures for Cyber Assets used in the access control and/or monitoring of Electronic Security Perimeter(s) (ESP) as specified in CIP-007-1 R5 and CIP-005-1 R2, as required by CIP-005-1 R1.5. SERC_URE1 reported four instances of non-compliance with CIP-005-1 R1. SERC verified the instances listed in the Self-Report. SERC_URE1 reviewed its ESP documentation and acknowledged that it failed to identify 20 out of 45 (44%) total access points. The root cause was that prior to the release of the Compliance Analysis Report, SERC_URE1 decided to not include the devices in question. With regard to Cyber Assets used in the access control and/or monitoring of ESPs, SERC learned that SERC_URE1’s change management process failed to require that designated personnel approve user accounts prior to the installation of the new Cyber Assets as mandated by CIP-007 R5.1.1. A total of 263 individual and shared user accounts were involved. The devices at issue were electronic access control and/or monitoring systems (EACM) devices. The root cause was an insufficient change management process. Also, SERC_URE1 reported that while decommissioning an EACM server a security analyst discovered that the virus definition deployment folder on the server allowed anonymous access. SERC learned that the folder was utilized by SERC_URE1 to install updated virus definitions for anti-virus and malware protection. SERC determined that by allowing anonymous access to the folder, SERC_URE1 failed to implement the technical and procedural controls that enforce access authentication of, and accountability for, all user activity as required by CIP-007 R5. The root cause was human error. SERC_URE1 failed to reconfigure the default settings that allowed anonymous access. With regard to CIP-007 R5.1.3, SERC_URE1 failed to revoke a user account on another EACM server within the seven day required time period. SERC learned that the individual had access to 18 out of 47 EACMs. The root cause was human error. An individual failed to take action on a notification to remove access. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to properly identify access points greatly increases the risk of Critical Cyber Assets (CCAs) being compromised and rendered inoperable, which could have caused the loss of monitoring and control of numerous BPS elements. A violation of CIP-005-1 R1.5 has the potential to affect the reliable operation of the BPS by providing the opportunity for cyber intrusions to occur on CCAs located within the established ESP. However, the unidentified access points were serially connected which utilized non-routable protocols and were protected inside a Physical Security Perimeter (PSP). All personnel with access to the PSP had NERC CIP training and current personnel risk assessments. Also, SERC_URE1 had a defense in-depth strategy of protection that an intruder would have to overcome to gain access to the devices. These protections include corporate firewalls, intrusion detection systems, and intrusion prevention systems. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Report | To mitigate the first incident in this violation, SERC_URE1: 1) conducted an inventory and developed a list of serial electronic access points; and 2) determined a compliance approach for serial electronic access points and included them in the EACM inventory. To mitigate the second incident in this violation, SERC_URE1: 1) developed a list of all EACM accounts which were opened without proper approvals; 2) obtained account approvals; 3) submitted a survey to peer utilities on best practices for obtaining account approvals; and 4) assessed the survey results to determine if updates were needed to electronic access control and account management procedure. To mitigate the third incident in this violation, SERC_URE1: 1) correctly set security control configuration settings on the replacement asset; 2) decommissioned the asset; and 3) published a policy to ensure continued compliance. To mitigate the fourth incident in this violation, SERC_URE1 removed the user's access and updated the user access review procedures to indicate the need to escalate tickets requesting removal or change of access by following up all ticket requests with a direct email to the user administration personnel responsible for access removal and changes. | 2013-08-13 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1’s CIP-005 R1 compliance history to be an aggravating factor in the penalty determination.
2015-01-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012520 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE1 failed to afford the protections specified in CIP-005-3a R3 to two Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). SERC_URE1 relocated two firewalls serving as electronic access control and/or monitoring systems (EACMS) to a new network at a data center. SERC_URE1 discovered that the configuration and connector were not updated with the correct internet protocol (IP) address on the two firewalls. Without the correct IP address, SERC_URE1 could not capture security-specific logs. The cause of the issue was failing to follow the change management worksite documentation (CIP-003a R6). According to SERC_URE1, the devices were properly configured and began to transfer the logs to the centralized logging and monitoring tool, which collects the logs, monitors, detects, and alerts for attempts at or actual unauthorized access. The front-end device behind the firewalls had locally retained the access logs to the involved remote terminal units (RTUs). SERC_URE1 submitted a second Self-Report to SERC. SERC decided to treat the Self-Report as an expansion of scope. SERC_URE1 reported that it had three additional issues, described below, where accounts were not properly documented on the user access list. For the first issue, SERC_URE1 implemented but did not document 24 accounts. SERC_URE1 implemented 16 accounts on the integrated lights-out servers, which granted cyber access to four EACMS. SERC_URE1 resolved this issue when the servers were retired. In addition, SERC_URE1 identified four administrator accounts on NERC CIP systems that were not adequately documented which provided access to 62 EACMs. Also, SERC_URE1 identified four Windows server database accounts that were not documented. SERC_URE1 implemented the accounts on the system in a previous review but they were not documented on the user access list. The accounts provided cyber access to four EACMs. For the second issue, SERC_URE1 reported that it granted one user access to a CIP administrator account which provided the individual cyber access to 20 EACMs. However, it failed to document the access on the user access list. For the third issue, SERC_URE1 identified two instances where it failed to remove personnel from the access list within seven calendar days of a change in the need for access. In the first occurrence, an employee’s job responsibilities changed and access removal was not performed in a timely manner. The employee had cyber access to nine EACMs. For the second occurrence, SERC_URE1 discovered during its quarterly review that an employee had retired but cyber access had not been removed. SERC_URE1 removed access on and the employee had access to two EACMs. | CIP-005-3a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1’s failure to follow its change control and configuration management processes resulted in it failing to perform monitoring and alerting on two access points, which could have allowed a Cyber Security Incident to go undetected. Further, failure to track and maintain a list of personnel with cyber access to EACMS could have allowed individuals with cyber access to EACMS to manipulate or alter logical access authorizations to Critical Cyber Assets (CCAs), either purposefully or by mistake, resulting in disruption or loss of control of the energy management system or SERC_URE1's portion of the BPS. However, the firewalls were operational and did not permit unauthorized traffic into the ESP and the front-end device behind the firewalls had locally retained the access logs to the involved remote terminal units. Also, for the third issue, the individuals in question would not have cyber access because automated processes would have removed access within 24 hours. | seven days past when the accounts were implemented on the device | when the individuals access was revoked and the list was updated | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Report | To mitigate this violation, SERC_URE1: 1) had its networking engineers update the address in the firewall configuration manager and reconfigure the connector; and 2) had its networking management review the connector status and similar issues as part of daily operation meetings by the cyber security operations team. To mitigate this violation, SERC_URE1 will communicate with various groups that are responsible for creating accounts to make them aware of the requirement to notify the personnel that need to update the user account list. | 2014-09-30 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012994 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-3 R4. SERC_URE1 granted an individual authorized cyber access to Critical Cyber Assets (CCA) but failed to update the cyber access list, as required. SERC_URE1 performed a quarterly review of its lists of individuals having cyber access to CCAs. It discovered that one individual was granted access a year prior , but the cyber access list was not updated until the same day as the discovery. SERC verified that SERC_URE1 had been performing quarterly reviews of its access lists, as required. | CIP-004-3 | R4 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual had a completed personnel risk assessment, the required cyber security training, and was authorized to have cyber access. | the eighth day after the individual was granted authorized cyber access to CCAs | when the cyber access list was updated | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Report | To mitigate this violation, SERC_URE1: 1) added the individual at issue to the Cyber Access List; 2) added an item to the employee entrance checklist to ensure a cyber request form is provided to the hiring management if an employee’s job function will require cyber access. Hiring management must complete the cyber approval form and provide the form to the cyber access approver. This is done prior to approving physical access; 3) informed affected management of the updated processes; and 4) moved responsibility for performing the quarterly access review from plant operations into the generation compliance group. The physical access approver provides the required physical documents. The cyber access approver, physical access approver, and the generation compliance representative perform the quarterly review together. | 2013-09-17 | 2014-08-06 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1’s CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013403 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-002-1 R3. SERC_URE1 discovered two devices within the Electronic Security Perimeter (ESP) that were not identified and protected as Critical Cyber Assets (CCAs). SERC_URE1 discovered two switches that it had not identified as CCAs. According to SERC_URE1, the root cause of the violation was that the switches were not mounted in the standard location for similar devices in other cabinets, making it difficult to identify these devices from a physical perspective and had not been configured with internet protocol (IP) addresses. SERC learned that SERC_URE1 utilized network scanning tools to collect information about its CCAs and without the IP addresses associated with the switches, they were not discovered. SERC_URE1 reports that there were five Cyber Assets connected to the switches for communication purposes. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The switches were serially connected to devices that converted Ethernet to serial communications and could not be electronically accessed due to the lack of an IP address, which decreased their risk of being compromised and rendered inoperable from an attack. No harm is known to have occurred. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 replaced the devices | $29,000 (for SERC2013011812, SERC2013012154, SERC2013012155, SERC2013012520, SERC2013012994, and SERC2014013403) | Self-Report | To mitigate this violation, SERC_URE1: 1) installed layer two devices which do not allow for IP configuration, identifying the devices as non-critical cyber systems; and 2) reviewed the CCA Classification procedure and conducted a training session on the proper identification of CCAs and non-CCAs. | 2014-02-04 | 2014-04-04 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's CIP-002 R3 compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007222 | Settlement Agreement | SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-007 R6. SERC_URE2's agent failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP), as technically feasible, implemented automated tools or organizational process controls to monitor system events that are related to cyber security. Several switches that were used to connect servers to disk arrays were within the ESP. SERC learned that the switches were not configured to capture and log cyber security events and had been in production since SERC_URE2’s mandatory compliance date. The Ethernet maintenance cables were removed from the fiber switches. This action eliminated the fiber switches from being Critical Cyber Assets (CCAs) or Cyber Assets within the ESP, since they no longer had communications outside of the ESP. SERC determined that SERC_URE2's agent failed to implement cyber security automated tools or organizational process controls to monitor system events on four Cyber Assets. While SERC was performing its assessment and determining the scope of this violation, the following additional issue was found: During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-1 R6. SERC_URE2's agent failed to have its cyber security logs reviewed either manually or through an automated process, in addition to not maintaining the logs for 90 days, as required. Specifically, several Cyber Assets, consisting of remote power controllers, consoles, a centralized logging and security analyzer, and a switch, were not configured to send logs to the central logging server for automated review, and the logs were not maintained for 90 days. SERC determined that SERC_URE2's agent failed to implement cyber security automated tools or organizational process controls to monitor system events on the Cyber Assets. SERC determined that SERC_URE2 was in violation of CIP-007 R6 because it failed to ensure that all Cyber Assets within the ESP, as technically feasible, implemented automated tools or organizational process controls to monitor system events that are related to cyber security. | CIP-007-1 | R6 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All of the Cyber Assets, including those involved with this violation, were secured within an established Physical Security Perimeter and ESP. In addition, any external access to the Cyber Assets required strong two-factor authentication. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Self-Report and Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) for the first issue: a) removed the affected Cyber Assets' ability to use a routable protocol within a control center by disconnecting the network cable. In addition, the Cyber Assets were tagged with a warning stating “do not connect to any network.” This action prevents any possible misuse of the Cyber Assets; b) updated the CCA list to reflect the removal of the fiber channel switches; c) added a hardware lock to each network port on each of the fiber channel switches to prevent installation of network cables; d) improved applicable internal policies and procedures for adding new Cyber Assets to the ESP. The updates included more diligent analysis of requirements and guidelines for submitting technical feasibility exceptions (TFEs); e) evaluated and selected replacement Cyber Assets that are supported by the chosen vendor and comply with all required NERC CIP Standards; f) requested funding for the selected replacement Cyber Assets during next budget cycle; g) purchased replacement Cyber Assets once approved for the budget; h) communicated to and trained personnel, responsible for adding Cyber Assets to the ESP, on the updated policies and procedures; i) tested the acquired replacement Cyber Assets; j) ensured Cyber Assets were compliant with all applicable NERC CIP Standards; k) installed the replacement Cyber Assets into the ESP; and 2) for the second issue: a) completed inventory of applicable Cyber Assets and validated logging was functional; b) filed TFEs as necessary; c) completed a review of current process and controls for remaining Critical Assets to identify gaps; d) updated processes and controls as necessary to close gaps identified; and e) trained personnel on updated processes and controls. | 2012-10-17 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007238 | Settlement Agreement | SERC_URE2 submitted a Self-Report stating that it was in violation of CIP-004-3 R4. SERC_URE2's agent failed to revoke access within seven calendar days for an employee who no longer needed access to Critical Cyber Assets (CCAs) as required. An employee was transferred and no longer needed authorized cyber and authorized unescorted physical access to CCAs. SERC determined that SERC_URE2's agent failed to revoke access within seven calendar days for personnel who no longer required such access to CCAs. While SERC was performing its assessment and determining the scope of this violation, the following additional issue was found: During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-004-3 R4. Personnel with authorized cyber access to CCAs were omitted from the lists of personnel with authorized cyber or authorized unescorted physical access to CCAs. SERC learned two individuals were granted authorized cyber and authorized unescorted physical access to CCAs without being added to the appropriate lists within seven calendar days. As a result of the audit finding, SERC_URE2's agent performed and internal review and discovered that five additional personnel, who were not properly updated on the access lists within seven calendar days of a change. SERC_URE2's agent granted authorized cyber and authorized unescorted physical access rights. However, the lists were not updated on time. SERC_URE2's agent granted a fourth individual authorized unescorted physical access rights, but it did not update the physical access list according to the Standard. SERC_URE2's agent granted the fifth individual authorized cyber access but was not updated on the cyber access list according to the Standard. SERC determined that SERC_URE2's agent failed to update lists within seven calendar days of any change of personnel with such access to CCAs. SERC determined that SERC_URE2 was in violation of CIP-004-3 R4 because its agent failed to maintain lists of personnel with authorized cyber and authorized unescorted physical access to CCAs. | CIP-004-3 | R4 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the individuals involved possessed a valid personnel risk assessment and had the required cyber security training. | when SERC_URE2's agent failed to remove the individual from the access lists | when SERC_URE2's agent added users to the access lists | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Self-Report and Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) for the first issue: a) revoked CCA access; b) verified employees' CCA access; c) verified other business units' employees' CCA access; d) conducted a review of all current processes, procedures, and training in support of CIP-004 R4 to identify improvements reducing the probability of reoccurrence; e) revised CIP-004 processes as needed; f) investigated and implemented a local solution that incorporated automatic notification escalation of pending revocation requests; and g) trained impacted supervisors on updated processes; and 2) for the second issue: a) validated its access list used to track personnel to ensure that the list was consistent with existing access authorization and/or revocation documentation and its other departments conducted an extent of condition analysis to validate their respective access lists were consistent with existing access authorization and/or revocation documentation; b) performed a review of its current processes for maintenance of its access lists and, as necessary, identified process improvements focused on automating the generation of the access list and enhancing the existing technical and procedural controls for the maintenance of the access lists; c) revised processes and procedures for each department where improvements were identified; and d) trained affected employees on the revised processes and procedures. | 2012-10-31 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009709 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-002-1 R1. SERC_URE2 failed to document a complete and comprehensive risk-based assessment methodology (RBAM) that considered all assets in accordance with R1. According to SERC_URE2, it did not consider the Critical Assets required when documenting its RBAM. SERC_URE2’s RBAM failed to consider the assets listed in R1.2. In addition, SERC_URE2 failed to include procedures as required in R1.1 to adequately perform the risk-based assessment and to document the results. SERC determined that SERC_URE2 was in violation of CIP-002-1 R1 because it failed to identify and to document a RBAM to use to identify its Critical Assets. | CIP-002-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to consider required asset types when developing the RBAM could have resulted in Critical Assets not being correctly identified and afforded protective measures required by the CIP Standards. The proper identification of Critical Assets is crucial to the reliable operation of the BPS. Without this, Critical Cyber Assets (CCAs) upon which the Critical Assets rely for functionality are not afforded all of the protective measures of the CIP Standards. Without these protective measures, the CCAs were at a greater risk of being compromised and rendered inoperable, which increases the risk to Critical Assets becoming compromised and/or rendered inoperable. However, SERC_URE2's agent had developed an RBAM for its registered functions that considered the required asset types and had identified the CCAs used in the course of performing SERC_URE2's registered functions. The CCAs were protected pursuant to the SERC_URE2 agent’s CIP program. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2: 1) revised its RBAM document used to identify its Critical Assets to include all of the asset categories required by R1.2. | 2011-11-10 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009712 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-003-1 R2. SERC_URE2 failed to document a change to the senior manager within 30 calendar days of the effective date, as required. SERC determined that SERC_URE2 was in violation of CIP-003-1 R2 because it did not document the designation of a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, the Standards CIP-002 through CIP-009. | CIP-003-1 | R2 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to document the designation of a senior manager could have resulted in unauthorized personnel approving CIP documents. However, there was an employee acting as the senior manager. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2: 1) created a new change in senior manager assignment document. | 2011-11-10 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009713 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP 005-1 R1.5. SERC_URE2's agent failed to identify a Cyber Asset used to control and monitor access to the Electronic Security Perimeter (ESP) and failed to afford it all of the protective measures specified in CIP-005-1 R1.5. SERC learned that the Cyber Asset SERC_URE2's agent failed to identify was an authentication server. SERC_URE2's agent failed to include the authentication server in the annual cyber vulnerability assessments in accordance with CIP-007-1 R8. However, the remaining protective measures listed in CIP-005 R1.5 had been given to the Cyber Asset. SERC determined that SERC_URE2 was in violation of CIP-005-1 R1.5 because it did not afford all of the protective measures to a Cyber Asset used in access control and/or monitoring of the ESP, as required. | CIP-005-1 | R1; R1.5 | Medium | Severe | The violation posed a moderate risk to the reliability of the bulk power system. Failing to identify and to protect electronic access control and monitoring devices could introduce vulnerabilities to the ESP and subsequently, the Critical Cyber Assets located therein. However, the device had been afforded the other protective measures listed in CIP-005-1 R1.5. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) performed an assessment and extent of condition review of asset type classification for Cyber Assets in scope of CIP-005 R1.5; 2) performed a cyber vulnerability assessment (CVA) per CIP-007 R8 for the Cyber Asset identified in the Compliance Audit as being improperly classified and, thus, did not have a CVA completed. Additionally, performed an extent of condition review of CIP-007 R8 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs; 3) performed training and education on the applicability of standards and requirements associated with Cyber Assets used in the access control and/or monitoring of the ESPs as per CIP-005 R1.5; and 4) implement corrective actions as identified in action plans created in the milestones for applicable Cyber Assets used in the access control and/or monitoring of the ESPs across business units. | 2013-07-11 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009714 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-005-1 R3. SERC_URE2's agent failed to implement security monitoring processes to detect and alert for actual unauthorized access into Electronic Security Perimeters (ESPs). SERC learned that SERC_URE2's agent only logged denied access attempts. It failed to perform logging and monitoring of actual access through firewalls into the ESPs. SERC determined that SERC_URE2 was in violation of CIP-005-1 R3.2 because it failed to implement monitoring processes to detect and alert for actual unauthorized accesses. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to monitor access to the ESP may result in unauthorized access going undetected. However, the firewalls were configured to log denied traffic, which provided the ability to alert to unsuccessful unauthorized access attempts. In addition, interactive access into the ESP required strong two-factor authentication. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) researched how to technically implement a mechanism to detect and alert for actual unauthorized accesses or determine if a procedural process can be implemented should a technical solution not be available; 2) submitted a Technical Feasibility Exception (TFE) for Cyber Assets that could not detect and alert for actual unauthorized accesses. In addition, SERC_URE2's agent's remaining departments that operate the rest of its Critical Assets conducted an extent of condition analysis on their Cyber Assets and confirmed that those assets could detect and alert for actual unauthorized accesses; 3) created procedures to detect and alert for actual unauthorized accesses for any Cyber Assets on which it is not technically feasible to do so. In addition, SERC_URE2's agent's remaining departments that operate the rest of its Critical Assets will submit a TFE for Cyber Assets that cannot detect and alert for actual unauthorized accesses identified in the previous milestone as needed; 4) performed a review of build/test plans for Cyber Assets subject to CIP-005 R3 to ensure that they included steps for validating that the Cyber Assets are configured to detect and alert for attempts at or actual unauthorized accesses 24 hours a day, seven days a week. Additionally, language will be enhanced to ensure that when automated alerting is not technically feasible, a TFE will be filed and the Cyber Assets will be subject to processes and procedures created in the previous milestone to assess access logs for attempts at or actual unauthorized accesses at least every 90 calendar days; 5) trained all personnel responsible for performing the new procedures created in the previous milestone as needed; and 6) implemented any new processes created in the previous milestone. | 2013-06-27 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009715 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-006-1 R1.8. SERC_URE2's agent, failed to afford the protective measures of CIP-007 R3 and CIP-007 R5 to Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP). SERC learned that several servers were involved in the violation. With regard to CIP-007-1 R3.1, security patches for the servers were not assessed for applicability within 30 days of availability, as required. The servers had a total of 14 security patches related to the operating system that were not assessed until approximately 120 days after they became available With regard to CIP-007 R5, SERC learned that SERC_URE2's agent did not technically enforce special characters in the servers’ passwords and did not change the servers’ passwords at least annually. SERC determined that SERC_URE2 was in violation of CIP-006 R1.8 because it failed to afford the protective measures of CIP-007-1 R3 and CIP-007-1 R5 to Cyber Assets used in access control and monitoring of the PSP, as required. | CIP-006-1 | R1; R1.8 | Medium | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to protect Physical Access Control System (PACS) devices could result in unauthorized individuals gaining access to Critical Cyber Assets, which could impact the BPS. However, the affected Cyber Assets were secured within a PSP with access control and monitoring and required two-factor authentication to access. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) collaborated with manufacturer via email and phone to confirm the operator table and password history table should be in sync and that SERC_URE2's agent’s results could be replicated in the manufacturer’s lab to ensure it was not specific to the SERC_URE2 agent’s environment; 2) created a script that will automatically notify users via email if their password has not been changed in 305 days (60 days before 365 days limit), 335 days (30 days before 365 days limit) and 358 days (7 days before the 365 days limit); 3) created a script that will automatically notify via email the access control intrusion detection system application administrators if any account password has not been changed in 359 days or more and request the administrator to terminate and/or disable the account; 4) updated corporate security document to reflect the notifications outlined in previous two milestones. The on-call administrator will delete the account and record in a service ticket upon receipt of the notification of account passwords exceeding 359 days; 5) trained corporate security personnel responsible for the updates made to corporate security systems security management document; 6) communicated to users in the access control intrusion detection system the requirement to change their password annually and failure to change their password annually would result in their account being terminated before their annual date; 7) conducted an extent of condition analysis of the PACS devices in regards to the protective measures in CIP-007-3 and determined if there are any gaps that needed to be addressed with the outlined protective measures; 8) reviewed the results of the extent of condition analysis in the previous milestones to develop a corrective action plan to address any identified gaps; 9) completed the corrective action plan developed in previous milestone; 10) communicated to and trained affected personnel on the changes from the corrective action plans completed in the previous milestone; 11) information management performed an extent of condition review for the PACS servers in relation to CIP-007 R3 controls, and established a corrective action plan to address any issues or improvements identified during the reviews; and 12) performed an extent of condition review of account management controls for the PACS servers in regards to CIP-007 R5 (including need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews. SERC_URE2's agent implemented corrective actions as identified in action plans created in previous two milestones for PACS Cyber Assets across business units. | 2013-07-11 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC determined that SERC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009716 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-1 R2. SERC_URE2's agent failed to implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. SERC learned that several devices were involved, consisting of switches, routers, terminal servers, and network devices. SERC confirmed that SERC_URE2's agent had a process in place. However, SERC_URE2's agent was unable establish that only those ports and services required for normal or emergency operations were enabled on these devices. SERC determined that SERC_URE2 was in violation of CIP-007-1 R2 because it failed to implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2; R2.2 | Medium | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to disable ports and services that are not required for emergency or normal operations could allow unauthorized users to gain access and control of Cyber Assets or provide an opportunity for malware to be introduced. However, the devices resided in an Electric Security Perimeter and a Physical Security Perimeter, In addition, any external access to the Cyber Assets required strong two-factor authentication. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) ascertained required ports and services for normal and emergency operations; 2) determined if any updates to procedures were needed; 3) updated process documents as needed from prior milestone; 4) trained personnel; 5) reviewed current CIP assets and validated required ports for normal and emergency operations of the asset were correctly documented; and 6) reviewed current CIP assets and validated that the cyber vulnerability assessments performed were adequate and update any discrepancies identified. | 2013-03-31 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC determined that SERC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009717 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-1 R4. SERC_URE2 failed to use anti-virus software and other malicious software prevention tools, where technically feasible. Several Cyber Assets, specifically remote power controllers, were involved. SERC learned that it was not possible for the Cyber Assets to run anti-virus/malware prevention software. However, SERC_URE2's agent had not requested a Technical Feasibility Exception (TFE) to document the compensating measures it had in place for this deficiency. A TFE was submitted after the Compliance Audit. SERC determined that SERC_URE2 was in violation of CIP-007-1 R4 because it failed to file a TFE on the inability to install malware and anti-virus protection tools on the identified Cyber Assets, as required. | CIP-007-1 | R4 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Cyber Assets involved were power distribution devices for servers at a manned site and could be bypassed immediately to maintain operations if they had become compromised. In addition, the Cyber Assets resided behind firewalls with access controls that restricted unauthorized traffic and resided within Physical Security Perimeter. | when the Standard became mandatory and enforceable on SERC_URE2 | when SERC_URE2's agent submitted a TFE | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) submitted appropriate TFEs; 2) performed an inventory of Cyber Assets related to the affected location; 3) completed TFEs for any Cyber Assets identified as needed; 4) reviewed current process and identified any potential gaps in evaluating the need for a TFE; and 5) updated policies and procedures, and trained personnel. | 2013-01-29 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009718 | Settlement Agreement | During a Compliance Audit, SERC determined that, SERC_URE2 was in violation of CIP-007-1 R3. SERC_URE2's agent, failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for three Cyber Assets within the Electronic Security Perimeter (ESP). SERC learned that there was a patch management program in place. However, SERC_URE2's agent failed to implement the program for several Cyber Assets. SERC determined that SERC_URE2 failed to provide a documented security patch assessment program for several non-critical Cyber Assets within the ESP. | CIP-007-1 | R3 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Cyber Assets resided within a Physical Security Perimeter and ESP, and all personnel with access had valid Personnel Risk Assessments and current cyber security training. | when the Standard became mandatory and enforceable on SERC_URE2 | when SERC_URE2's agent implemented the patch management program for the affected Cyber Assets | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) performed a review of current patch management procedures; 2) conducted an analysis of all applicable Cyber Assets and categorized applicable security patches; 3) performed an analysis to determine what operating system, software, applications, and firmware were not currently included in the procedure(s) for formal tracking; 4) updated associated patch management procedures for any identified gaps; 5) updated and released new versions of all applicable patch management programs; and 6) conducted training. | 2012-11-30 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009719 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-1 R5.3. SERC_URE2's agent failed to ensure that passwords consisted of a combination of alpha, numeric, and “special” characters, as technically feasible and failed to change all passwords at least annually. SERC learned that, for several devices, SERC_URE2's agent could not establish that the required password complexities had been implemented. An additional device could not meet the password complexity requirement. While compensating measures were in place, SERC_URE2's agent had not submitted a Technical Feasibility Exception (TFE). SERC staff also learned that SERC_URE2's agent failed to change account passwords on several Cyber Assets at least annually, as required. SERC determined that SERC_URE2 was in violation of CIP-007-1 R5.3 because it failed to implement enhanced passwords and failed to change account passwords annually. | CIP-007-1 | R5; R5.3 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Cyber Assets resided in an ESP and a Physical Security Perimeter. Any external access to the Cyber Assets required strong two-factor authentication. For the Cyber Assets that could not enforce password complexity, passwords were still in place. For those passwords that were not changed annually, the accounts were locked by the system as they were not accessed within the required timeframe. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) completed the TFE documentation and submitted the TFEs; 2) performed a review of account(s) for CIP assets and ensured that passwords have been changed within the annual requirement; 3) reviewed remaining accounts for annual password changes and changed any passwords that needed to be changed; 4) completed a review of current processes and controls to identify gaps; 5) completed and submitted TFEs for any assets identified in previous milestones as needed; and 6) updated the processes and controls as identified, and completed training of personnel. | 2013-01-15 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009721 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-007-1 R8.2. SERC_URE2's agent, failed to verify during an annual cyber vulnerability assessment (CVA) that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. SERC learned that SERC_URE2's agent failed to verify that only ports and services required for operation were enabled on several Cyber Assets during a prior CVA. In addition, SERC_URE2’s agent's CVA a year earlier missed verifying the ports and services on a different Cyber Asset. SERC determined that SERC_URE2 was in violation of CIP-007-1 R8.2 because its CVAs failed to verify that only ports and services required for operation of all of its Cyber Assets were enabled. | CIP-007-1 | R8; R8.2 | Lower | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review ports and services during the annual CVA could allow unnecessary ports and services to remain open and vulnerable to exploit. However, logging was properly configured, which alerted to security events. In addition, all of the involved Cyber Assets were within an ESP and a Physical Security Perimeter. | when SERC_URE2's agent had to complete the annual CVA properly | Mitigation Plan completion | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) ascertained required ports for normal and emergency operations of the assets; 2) reviewed processes and procedures related to required ports and services; 3) updated procedures based on results of prior milestone; 4) trained personnel; 5) performed review of current CIP assets and validated required ports for normal and emergency operations are correctly documented; and 6) performed a review of current CIP assets and validated CVAs were adequate and updated discrepancies identified. | 2013-03-31 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009722 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE2 was in violation of CIP-006-3a R1.7. SERC_URE2's agent failed to update its physical security plan within 30 calendar days of a new installation. SERC learned that a site physical security system was installed and tested at separate sites. However, the physical security plan was not updated until 70 days past the required 30 calendar days. No additional CIP-006 R1 violations were identified during the audit. SERC determined that SERC_URE2 was in violation of CIP-006-3a R1.7 because it failed to update its physical security plan within 30 calendar days of the completion of any physical security system redesign or reconfiguration. | CIP-006-3a | R1; R1.7 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2's agent updated the physical security plan within 70 days of the change and the site security system was functioning properly. | 30 days after SERC_URE2's agent should have updated the physical security plan | when SERC_URE2's agent updated the physical security plan | $0 (for SERC2011007222, SERC2011007238, SERC2012009709, SERC2012009712, SERC2012009713, SERC2012009714, SERC2012009715, SERC2012009716, SERC2012009717, SERC2012009718, SERC2012009719, SERC2012009721, and SERC2012009722) | Compliance Audit | To mitigate this violation, SERC_URE2's agent: 1) conducted an extent of condition analysis of physical security perimeters at designated Critical Assets to determine whether there were other instances in which the physical security plan was not updated within 30 days following a reconfiguration or redesign change; 2) reviewed results of extent of condition analysis. If additional instances were identified in which the physical security plan was not updated following a reconfiguration or redesign change, added all necessary updates to the next revision of the physical security plan; 3) collected all applicable physical security drawings related to physical security perimeters for designated Critical Assets from each of the respective business areas; notified business areas that corporate security would assume custodianship and retention responsibilities of the physical security drawings going forward to include within the updated physical security plan; 4) updated physical security plan to include language stating that the physical security plan will be updated and signed by the director of corporate security, as the Senior Manager delegate for CIP-006, to incorporate any physical security redesign or reconfiguration changes (including, but not limited to, additional or removal of access points through the physical security perimeter, physical access controls or monitoring/logging controls) within 30 days. The updates to the physical security plan also specified that it is corporate security’s responsibility to be the custodian of all applicable the physical security drawings related to physical security perimeters for designated Critical Assets which will be included within the physical security plan; 5) updated corporate security’s workflow documentation for CIP-006 R1.7 to include a notification to the director of corporate security, as a checkpoint when a physical security configuration change ticket is closed out for any physical security reconfiguration or redesign of physical security perimeters at designated Critical Assets; 6) communicated to corporate security personnel the updated workflow for CIP-006 R1.7; and 7) communicated and conducted training to the applicable business areas regarding the changes to the enterprise physical security plan implemented. | 2012-04-27 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. In addition, SERC_URE2 and SERC_URE2's agent completed the following actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 revised its RBAM, Critical Asset list, and CCA list to clearly indicate that SERC_URE2's agent's RBAM, Critical Asset list, and CCA list identify the relevant Cyber Assets necessary to support SERC_URE2's registered functions. In addition, SERC_URE2's agent provided SERC with documentation that clearly identifies all Critical Assets, CCAs, Electronic Access Control or Monitoring Systems, and Physical Access Control Systems involved in supporting SERC_URE2's registered functions. These updated documents will enable SERC to more quickly identify any CIP issues that involve SERC_URE2's registered functions and minimize the impact on SERC_URE2's agent if future possible violations are discovered. SERC determined that SERC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012824 | Settlement Agreement | SERC_URE3 submitted a Self-Report stating that it was in violation of CIP-004-3 R4. On three separate occasions, SERC_URE3 failed to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). This determination addresses multiple incidents regarding SERC_URE3's violation of CIP-004-3 R4, each instance involving a different Physical Security Perimeter (PSP). Each instance is discussed separately. SERC_URE3 maintained an internal access list of individuals with authorized cyber or authorized unescorted physical access to CCAs in a centralized repository. In the first instance, SERC_URE3 failed to implement its documented procedures to ensure its access list of personnel with authorized unescorted physical access to the PSPs was maintained. SERC_URE3 performed an assessment of its internal processes, and discovered that 0.79% individuals was erroneously listed as having authorized unescorted physical access to a single PSP. The individual’s name was extracted from a database and manually added in error to the list of personnel with authorized unescorted physical access in the centralized database. Although the individual did not have physical access to the PSP, the individual’s name remained on the access list for approximately one year and three months. In the second instance, SERC_URE3 failed to implement its documented procedures to update its access list within seven calendar days of a change of personnel with access to CCAs. SERC_URE3 In this instance, an individual verbally notified the corporate security department that he or she no longer required authorized unescorted access to a second PSP. SERC_URE3 management failed to submit an electronic access request form to remove the access. corporate security revoked the individual’s physical access on the same day the individual verbally requested the access be removed. However, corporate security did not update records housed in the centralized repository to reflect that the individual no longer required access. Therefore, the access list was not updated accordingly. This instance occurred because SERC_URE3 failed to adhere to its internal processes to utilize the centralized repository as a mechanism to update any access changes to the PSP. SERC_URE3 removed the individual from the access list approximately four months after the individual no longer required access. In the third instance, SERC_URE3 failed to implement its documented procedures to update its access list with seven calendar days of a change of personnel with access to CCAs. SERC_URE3 performed an internal review of individuals with authorized unescorted access to its PSPs. SERC_URE3 discovered that 0.59% individuals that had authorized unescorted physical access to a third PSP remained on its access list after the individual’s physical access rights were revoked. SERC_URE3 initially submitted a request form to revoke the individual’s physical access that was no longer required to certain PSPs. Corporate security inadvertently revoked the individual’s physical access to all PSPs but failed to remove the individual from the physical access list. The access list was corrected by removing the individual from the access list approximately four days after the internal review was performed. The root cause of these instances was a human performance in regards to a new tool. | CIP-004-3 | R4; R4.1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All three instances were documentation errors and all individuals’ physical access were removed despite the failure to update the access list. Additionally, all individuals involved had cyber security training, had a completed personnel risk assessments, were in good standing, and had not been terminated for cause. | when the first individual was added to the access list in error | when the last individual was removed from the access list | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) conducted a line-by-line review of the printed reports from the source system and the access list; 2) remedied all identified discrepancies in the existing CCA access lists; 3) conducted periodic line-by-line reviews of the printed source reports from the source system and the access list; 4) held a formal training session that included all employees responsible for using the access/install/moves (AIM) tool to grant and remove physical access; 5) circulated an email to affected personnel describing a more detailed AIM report to use for adding and removing access and the importance of following this process; and 6) fully implemented an automated program that checks for discrepancies between the source system and the access list every evening. | 2013-10-18 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012825 | Settlement Agreement | SERC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-3a R1. SERC_URE3 failed to implement adequate cyber security test procedures to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls. SERC_URE3 tested and deployed a new Cyber Asset, a network switch, into production within the ESP. A security controls testing checklist was used during the initial installation to ensure adding or replacing Cyber Assets would not adversely affect existing cyber security controls. The network technician who deployed the new network switch followed the documented test procedures and disabled a generic account prior to deployment. However, the documented test procedures did not include specific guidance stating that modifications must be saved to permanent memory. Approximately four months later, SERC_URE3 experienced a power emergency interruption, which resulted in the network switch being powered off and on. Due to the failure to save system configurations to permanent memory, the system configuration for the network switch reverted back to the previous settings as a result the power interruption, thus re-enabling the generic account. Had the network technician saved the system configurations to permanent memory, a power interruption would not have caused the configurations to revert back to previous settings. On the same day, a network technician discovered a generic local user account was enabled on the network switch. Four days after the power emergency interruption, SERC_URE3 resolved this incident by disabling the generic account on the device and ensured that all configuration settings were saved to permanent memory. The root cause of this violation was SERC_URE3's procedures failed to include steps for saving the modifications to permanent memory. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk of the violation was reduced by the following factors. The generic account was discovered on the same day it was re-enabled as a result of the power interruption. The generic account was disabled four days later with the configuration saved to permanent memory, ensuring the issue would not recur. SERC_URE3 tested its cyber security controls when it first deployed the network switch and found no adverse effects. The switch was located within a protected Physical Security Perimeter and ESP. Additionally, there were other protective measures in place such as network segmentation, isolation of security zones, firewalls, intrusion detection and prevention systems, and 24 hours a day, seven day week monitoring provided by a security services provider. There were no Cyber Security Incidents reported during the violation. | when the network switch was deployed | when the configuration was appropriately saved | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) removed the unapproved generic account from the network switch; 2) added a step to the checklist to prompt the saving of the configuration to an extensively detailed, step-by-step checklist for preparation and deployment of every CIP Cyber Asset; and 3) circulated an email to affected personnel describing the new work instruction that was added to the checklist and the importance of saving the configuration. | 2014-06-06 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012826 | Settlement Agreement | SERC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. SERC_URE3 failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) implemented automated tools or organizational process controls to monitor system events that are related to cyber security. SERC_URE3 discovered that monitoring and logging for 0.20% of Cyber Assets within the ESP did not occur for 28 days. The access control lists (ACLs) on the firewall were deployed into production approximately 28 days prior to the discovery. At this time, the ACLs were correctly configured to allow for communication with the system information and event management (SIEM) tool. A technician rearranged the order of the ACL rule sets during a quarterly firewall ACL review. This change inadvertently resulted in communication loss for 0.20% of Cyber Assets that were being routed through the firewall to the SIEM monitoring tool for logging and monitoring. SERC_URE3 corrected the communication failure on the same day it discovered the violation. The root cause was a lack of change controls and awareness tools. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation affected a single generation facility which was not in operation during the violation. Therefore, the six Cyber Assets involved were not functionally utilized during the violation. There were no reportable Cyber Security Incidents during the violation. Further, the Cyber Assets were within a protected ESP and Physical Security Perimeter. Additionally, there were other protective measures in place such as network segmentation, isolation of security zones, firewalls, intrusion detection and prevention systems, and 24 hour a day, seven day week monitoring provided by a security services provider. | when the firewall configuration was changed and logging and monitoring stopped for the six devices | when the firewall configuration was modified to ensure logging resumed | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) corrected the ruleset to allow alerting; and 2) created alarms to notify support personnel of potential loss of logging. | 2013-11-17 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012941 | Settlement Agreement | SERC_URE3 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. SERC_URE3 failed to identify an Electronic Access Control Monitoring (EACM) device in the Electronic Security Perimeter (ESP), and did not ensure it was afforded the protective measures as required by CIP-005-3a R1.5. This determination addresses multiple instances regarding SERC_URE3's violation of CIP-005-3a R1. Each instance is discussed separately. In the first instance, SERC_URE3 self-reported that it failed to identify and document firewalls as access points to the ESP. An access point EACM firewall was configured with a bypass option to allow pass through communication to a second firewall. The access point EACM firewall was configured as a Virtual Private Network (VPN) termination point and protected as an EACM. This firewall provided access to the ESP from the corporate network and a Demilitarized Zone (DMZ). The protected firewall was configured to allow the communication bypass, which permitted VPN traffic to bypass the protected firewall and its access control lists. As a result, communication could be routed directly to the second firewall, therefore making it an access point to the ESP. This second firewall was not identified as an access point on SERC_URE3's network diagram and it was not fully protected as an EACM. Specifically, ports and services associated with the second firewall were not documented pursuant to CIP-007 R2 and the firewall was not included in the Cyber Vulnerability Assessment. The root cause of this violation was SERC_URE3's failure to identify and document EACMs pursuant to SERC_URE3 processes and procedures. A total of 13 network engineers had electronic access to the EACM device in question. SERC_URE3 resolved the issue by removing the bypass function and prohibiting its use going forward. In the second instance, SERC_URE3 discovered that it did not include two EACM devices in the scope of the annual disaster recovery plan exercise. Personnel responsible for the execution of the recovery plan(s) assumed that these devices did not need to be included in the class of Cyber Assets scheduled for testing during the initial year of compliance. SERC_URE3tested the disaster recovery plan, but it failed to include the two EACMs in the scope for testing as required by CIP-009 R2. The two EACMs were included in the disaster recovery plan exercise that occurred the following year. The root cause for the second instance was a human oversight and a lack of controls that would have caught the missing devices. In the third instance, an engineer accidently installed an operating system service pack on an intrusion prevention system/intrusion detection management system, an EACM device, without performing tests to ensure existing cyber security controls were not impacted as required by CIP-007 R1. SERC_URE3 tested the service pack the following day. The root cause of third instance was human performance. The individual involved failed to follow established testing procedures. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A lack of processes, procedures, and proper tools to identify and document electronic access points greatly increased the risk of Critical Cyber Assets (CCAs) being compromised and rendered inoperable. In addition, failing to identify and protect EACM devices could introduce vulnerabilities to the ESP and subsequently, the CCAs located therein. However, for the first instance, electronic access was restricted to 13 network engineers that had a completed personnel risk assessment and cyber security training. For the second instance, procedures were in place and staff was trained and prepared to perform the disaster recovery plan test for the two EACM devices. Further, SERC_URE3 performed a disaster recovery plan test for other Cyber Assets within the ESP. For the third instance, the failure to test in the test environment was identified and mitigated the following day. Also, although the service pack was not tested prior to implementation, the subsequent testing of the service pack confirmed that the content of the updates was not critical to the management system. No identified cyber incidents occurred during the duration of the violation. All devices involved in this violation were protected within a secure Physical Security Perimeter and ESP. Further, the devices in question could only be electronically accessed by individuals with two-factor authentication and SERC_URE3 has signature and behavioral based intrusion detection system devices in place to alert personnel in the event of suspicious activity. | when the firewall began acting as an access point | present | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) modified site-to-site VPN tunnels peering with existing ESP access points to not allow interface access control lists on ESP access points to be bypassed; 2) updated the checklist for adding or replacing CIP assets to specify that new access point firewalls using VPN tunnels should not be configured in a manner that allows VPN sessions to bypass interface access control lists; 3) completed the CIP-009 R2 annual recovery exercise for the two EACM systems not previously included; 4) updated the checklist for adding or replacing CIP Assets to specify that the annual recovery plan exercise and backup media testing must be performed in the initial year; 5) tested the service pack after-the-fact to determine that it had no adverse effects to the cyber security controls; 6) made technical enhancements to servers to ensure that administrators could easily distinguish between test and production server console sessions; 7) made enhancements to the managed security service provider (MSSP) internal procedures used in applying security patches to the servers; 8) the MSSP completed training of all engineers that have access to the SERC_URE3 network; 9) performed scoping of all CIP environments to ensure no other instances of access point firewalls using VPN tunnels configured in a manner that allows VPN sessions to bypass interface access control lists exists; 10) developed technical enhancement to automatically audit configurations to ensure there is no bypass checkbox checked; and 11) developed and provided training on access point and site-to-site VPN tunnel configuration. To mitigate this violation, SERC_URE3 will uncheck the bypass checkbox in all CIP environments. | 2/10/2015 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012942 | Settlement Agreement | SERC_URE3 submitted a Self-Report stating that it was in violation of CIP-005-3 R2. SERC_URE3 failed to properly configure a virtual private network (VPN) device that controlled remote access to the Electronic Security Perimeter (ESP) to deny access by default, resulting in unrestricted access for authenticated VPN users to three ESPs. This determination addresses multiple instances regarding SERC_URE3's violation of CIP-005-3a R2. Each instance is discussed separately. A network engineer started a phased upgrade of VPN client software on all interactive remote Cyber Assets (laptops, computers, iPads, etc.). A lack of knowledge of the new upgrade features resulted in improper configurations that created a new Electronic Access Control or Monitoring (EACM) device out of a corporate server that was not covered by SERC_URE3's CIP program. This EACM device configuration did not support an access control model that denied access by default. As a result, 1,305 SERC_URE3-approved interactive access users had the potential to authenticate into three ESPs. After reviewing all firewall logs and intrusion detection system (IDS) activity, SERC_URE3 discovered that only three of the 1,305 interactive access users accessed the corporate VPN remote access server to authenticate into the three ESPs. These individuals were granted electronic access but not physical access. SERC_URE3 mitigated this issue by modifying the access control list (ACL) associated with the VPN group policy. SERC_URE3 performed a review of external interactive access into its ESPs and discovered that an ACL was directing authentication attempts into an IDS/intrusion protection system secure network that was not protected as an ESP. SERC_URE3 failed to modify the ACL to ensure traffic was routed to the correct authentication server. Modifications to the ACL permitted traffic to be routed to the authentication server that was not classified nor protected as an EACMS device. Fourteen SERC_URE3 support personnel had external interactive access to the EACMS device. SERC determined that SERC_URE3 failed to implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible (CIP-005 R2.4). SERC_URE3 performed an internal review of individuals with external interactive access into ESPs. SERC_URE3 discovered that three employees were granted access to ESPs without authorized approval because they used the wrong process to request approval for external interactive access. These three employees were not on the access list to the ESPs. The process the employees used was created as a part of SERC_URE3's change management procedure to document and approve changes to corporate and CIP assets. This process should not have been used to request access to the ESPs. The root cause for these instances was human performance and a failure to follow established procedures. | CIP-005-3a | R2; R2.1; R2.4; R2.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to establish processes and mechanisms that use an access control model that denies access by default gave approximately 1,305 users unauthorized access to the energy management system (EMS) network, increasing the risk of Critical Cyber Assets (CCAs) being accessed, compromised, and rendered inoperable. In addition, failing to implement and to document organizational processes and strong technical and procedural mechanisms to ensure the authenticity of users accessing the ESPs could have resulted in unauthorized individuals gaining access to the ESP and CCAs therein. However, access to the EACM (firewall) configurations (ACLs) was restricted to authorized personnel only and was based on job function. In all three instances, SERC_URE3 reviewed log files to confirm that no suspicious activity occurred. A managed security services provider was monitoring for detected security events throughout the network 24 hours per day, 7 days per week. No Cyber Security Incidents were reported during this violation. SERC_URE3 had protective controls in place on CCAs and Cyber Assets inside of established ESPs and two-factor authentication was required for all remote access to SERC_URE3 systems. In instance one, most of the users were unaware of their ability to access the EMS network. The three employees that accessed the EACM server were network administrators and had access to network devices but did not have local access to devices inside of the network. Accessing CCAs within the ESPs would require user accounts and passwords for the relevant CCAs. The three employees were authorized for electronic access to CCAs, had valid personnel risk assessments, and had undergone cyber security training. SERC_URE3 reviewed logs and confirmed that the three individuals did not attempt to access any CCAs via the EACM server during the violation. Also, two-factor authentication was required to access the VPN, making it difficult for a malicious individual to take advantage of the misconfigured ACL associated with the VPN group policy. For instances two and three, no employees used the access that they had been granted. | when an EACM device was installed without a deny-by-default configuration | when the electronic access list in instance one was modified | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) modified the VPN group policy to include an ACL with a default deny rule; 2) removed the CIP subnet from the ACL; 3) corrected the access discrepancies for the three individuals mentioned in the self-report; 4) created a separate business to business (B2B) VPN remote access server specifically for use with CIP Assets and migrate to that server the remote access function for EACM systems; 5) created a separate B2B VPN remote access server specifically for use with CIP Assets and migrated to that server the remote access function for ESPs and Physical Access Control Systems; 6) created alerts that trigger when specific changes are made in the configuration of network equipment, specifically switches, routers, and firewalls; and 7) developed and provided training on the processes and requirements specific to granting and removing external interactive access into ESPs. To mitigate this violation, SERC_URE3 will enhance existing technical controls to further delineate the type and level of access privileges for administrative access to network equipment (specifically switches, routers, and firewalls) and will enhance the granularity of role based authentication and authorization policies for network administrators. | 2/10/2015 (approved completion date) | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2014013882 | Settlement Agreement | SERC_URE3 submitted a Self-Report to SERC stating that it was in violation of CIP-004-3a R4. SERC_URE3 failed to update access lists within seven calendar days of any change in the access rights of personnel with access to Critical Cyber Assets (CCAs). While performing quarterly access reviews, SERC_URE3 identified a discrepancy between an access/install/moves (AIM) tool electronic access list and the actual electronic access rights. Specifically, one user had been approved and granted electronic access to the Windows domain, but the access was not reflected in the associated access list. This issue lasted eight days after the individual was granted access until when the access list was updated. SERC_URE3 determined that the root cause was a synchronization issue with a proprietary database that is used as the centralized repository for SERC_URE3's access control lists. The entry was in the access request database table, but upon approval, this entry was not copied correctly to the appropriate table. SERC_URE3 submitted a second Self-Report to SERC stating that it was in violation of CIP-004-3a R4. SERC determined that the Self-Report represented an expansion of scope to the above-mentioned Self-Report and consolidated the violations. A vendor employee with authorized unescorted physical access into a Physical Security Perimeter (PSP) voluntarily resigned from the vendor. The vendor did not notify SERC_URE3 of the separation until approximately four and half months later. Additionally, the individual did not return the physical access card which gave access to one PSP containing four Electronic Access Control Monitoring (EACM) devices. SERC_URE3 removed the badge access and updated the appropriate access lists the same day it was notified that the vendor employee had resigned. SERC_URE3 conducted a review of the former vendor employee’s physical access and confirmed that the vendor employee never attempted to access a PSP after resigning. SERC_URE3 determined that the root cause of the issue was an improper communication and implementation of the physical access removal policy established by SERC_URE3 for vendors. This issue lasted from eight days after the vendor employee resigned until when SERC_URE3 removed the vendor employee’s access and updated the access list. SERC_URE3 reported an additional violation of CIP-004-3a R4. SERC determined that this violation represented an expansion of scope to the second above-mentioned Self-Report and consolidated the violations. SERC_URE3's parent company notified its vendor that it was canceling the contract between the two parties. However, SERC_URE3's parent company did not notify SERC_URE3 that it was cancelling the contract. At the time, a vendor employee had authorized unescorted physical access into the same PSP identified in the second above-mentioned Self-Report. Because SERC_URE3's parent company did not notify it of the cancellation of the contract, SERC_URE3 did not remove the vendor employee’s unescorted physical access within seven days of the individual not needing the access. SERC_URE3 was notified that the vendor employee no longer needed physical access, and it immediately processed the request to remove physical access for the vendor employee in question. When SERC_URE3 makes a change in its centralized repository, the access list is automatically updated to reflect the change. Therefore, the access list reflected the removal of the vendor employee’s access. Additionally, SERC_URE3 conducted an assessment to track the actual access of the vendor employee during the two month period and it confirmed that the vendor employee had not attempted or gained access during the timeframe. SERC determined that the root cause of the issue was a lack of communication between SERC_URE3 and its parent company. | CIP-004-3a | R4; R4.1; R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individuals involved had cyber security training and completed personnel risk assessments. For the first issue, the individual involved was authorized for the access that was granted. The error in the access list was corrected two days after discovery. Also, this issue affected 0.04% of those who were listed accurately on the access list. Finally, the domain that the user was granted access to had electronic monitoring. For the second issue, the individual involved resigned in good standing and the physical access logs for the PSP revealed that the vendor employee’s card was not used to access the PSP during the violation. For the second and third issue, the PSP in question was manned 24 hours a day, 7 days a week by SERC_URE3 personnel. This PSP contains no CCAs, only EACMs and non-CCAs. For the third issue, SERC_URE3 was in possession of the access card since its creation. The vendor employee had not visited the SERC_URE3 site and never had possession of the access card. Therefore, the vendor employee had no means to access the PSP, which contained EACM devices but no CCAs. | eight days after the first individual was granted access | Mitigation Plan completion | $30,000 (for SERC2013012824, SERC2013012825, SERC2013012826, SERC2013012941, SERC2013012942, and SERC2014013882) | Self-Report | To mitigate this violation, SERC_URE3: 1) remedied the identified discrepancy in the existing access list; 2) implemented a technical enhancement to identify a discrepancy between the two tables in the future and thus prevent a potential violation in the future; 3) removed physical CIP Access for the vendor employee in the second issue; 4) removed physical CIP Access for all vendor employees in the second issue; 5) removed physical CIP Access for the vendor employee in the third issue; and 6) removed physical CIP Access for all parent company employees and parent company vendor employees. | 2014-07-29 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE3's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE3's compliance history to be an aggravating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011963 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1, was in violation of CIP-005-3 R2. The Audit Team identified three devices serving as Electronic Security Perimeter (ESP) access points on which WECC_URE1 failed to disable ports and services that were not needed for operations or for monitoring Cyber Assets within the ESP. The Audit Team determined that the three devices were firewalls that served as access points to the primary energy control center ESP. The root cause of the violation was control management, because WECC_URE1 failed to timely disable appropriate ports and services. WECC determined that additional ports and services not needed for operations or for monitoring Cyber Assets within the ESP were enabled on three firewalls serving as ESP access points. | CIP-005-3 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, WECC_URE1 failed to ensure that only ports and services required for operations and monitoring of Cyber Assets within the ESP were enabled on three firewalls. This violation posed potential harm to WECC_URE1, because additional points of vulnerability to the ESP could be created, due to WECC_URE1's failure to disable ports and services. However, the risk posed by WECC_URE1's failure is limited given compensating measures in place during the violation period. WECC_URE1 has a “defense-in depth” cybersecurity strategy. Each of the three devices was configured to deny access by default, such that explicit access permissions must be specified. Electronic access to the devices was limited to individuals who required such access to perform their job function. Access through each ESP access point was monitored and logged 24-hours a day, seven days a week. Unauthorized access attempts would have triggered an alarm that alerted designated personnel. | when the Standard became mandatory and enforceable on WECC_URE1 as a "Table 1" entity | Mitigation Plan completion | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) disabled the non-required ports and services; and 2) created a checklist to be used when any future significant changes occur. | 2013-03-20 | 2013-06-14 | Agrees | WECC reviewed WECC_URE 3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011964 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-3a R4. The Audit Team reviewed WECC_URE1's 2011 and 2012 Cyber Vulnerability Assessments (CVAs). The 2011 CVA failed to identify open ports and services on one ESP access point. The 2012 CVA incorrectly identified ports and services for three ESP access points, as enabled. The 2012 CVA correctly identified ports and services as being enabled on the access point incorrectly identified in 2011 as being disabled. The Audit Team, therefore, determined that WECC_URE1 failed to conduct a CVA that included a review that ensured only ports and services required for operations were enabled, for 2011 and 2012. The root cause of the violation was control management, because WECC_URE1 failed to follow its CVA procedure annually . WECC determined that CVAs conducted by WECC_URE1 in 2011 and 2012 did not verify that only ports and services required for operations at access points were enabled for four ESP access points. | CIP-005-3a | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation posed potential harm to WECC_URE1, because WECC_URE's failure to conduct timely CVAs could affect the stability and availability of WECC_URE1's immediate operational area of coverage. The risk posed by WECC_URE1's noncompliance is, however, offset given compensating measures in place during the violation period. WECC_URE1 implemented a defense-in-depth architecture of administrative, physical and logical cyber security controls. Electronic access through each firewall was limited to individuals who completed Personnel Risk Assessments and cybersecurity training. The four ESP access points were configured to deny access by default, such that explicit access permissions must be specified. Electronic access to the devices was limited to individuals who required such access to perform their job function. Access through each ESP access point was monitored and logged 24-hours a day, seven days a week. Unauthorized access attempts would have triggered an alarm that alerted designated personnel. | when WECC_URE1 failed to conduct an annual review | The last day of the noncompliant CVA year | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) updated its CVA processes to include additional reviews; 2) created a correction statement to address the error in the 2011 report; and 3) reviewed the 2011 and 2012 CVAs for potential issues using the new review process. | 2013-06-21 | 2013-10-18 | Agrees | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011875 | Settlement Agreement | WECC issued to WECC_URE1 a Notice of Compliance Audit. Prior to the Compliance Audit, WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R2. WECC_URE1 reported that it had not created a list of known ports and services for servers located in its Physical Access Control and Monitoring System (PACS) ESP. A WECC subject matter expert determined that the facts and circumstances of WECC_URE1's Self-Report were more appropriately reviewed under CIP-006-1 R1.8. For that reason, WECC filed a Self-Report on WECC_URE1's behalf under CIP-006-1 R1.8. The root cause of this violation was control managment, because WECC_URE1 failed to manage the required controls for access to its PSP. WECC Enforcement determined that WECC_URE1 failed to afford the required controls defined in CIP-006-1 R1 for 19 PACS devices used in the access control and monitoring of its Physical Security Perimeter (PSP). WECC Enforcement determined that WECC_URE1 failed to afford 19 PACS devices the protections described in CIP-006-1 R1.8. | CIP-006-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to ensure that only ports and services required for normal and emergency operations were enabled on 19 devices used in the access control and monitoring of the PSP. This violation posed potential harm to WECC_URE1 because the access control and monitoring devices to its PSP could have been vulnerable to misuse of malicous cyber attacks. The potential risks associated with this violation were however, limited due to WECC_URE1's additional procedures and policies. Specifically, WECC_URE1 had limited communication through the firewall to only necessary communication. Additionally, the PACS ESP does not contain any Critical Cyber Assets (CCAs) and is not connected to a CCA ESP. Individuals with electronic access to the ESP completed Personnel Risk Assessments and cyber security training. | when the Standard became mandatory and enforceable on WECC_URE1 as a "Table 1" entity | Mitigation Plan completion | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Self-Report | To mitigate this violation, WECC_URE1: 1) addressed PACS servers’ known ports and services to complete CIP controls implementation; 2) addressed deficiencies; and 3) updated its Cyber Asset Security Checklists for each device with final status to validate CIP Controls Implementation. | 3/13/2014 | 2014-03-22 | Agrees | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011493 | Settlement Agreement | WECC issued to WECC_URE1 a Notice of Compliance Audit. Prior to the Compliance Audit, WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R2. The Audit Team identified four devices within the energy managment system (EMS) ESP, and WECC_URE1 identified another three devices during the mitigation review process for which WECC_URE1 failed to accurately identify ports and services required for normal and emergency operations. The root cause of the violation was WECC_URE's failure to create a list of known ports and services to define and manage its assets. WECC reviewed the mitigation activities and determined that WECC_URE1 had failed to enable only ports and services required for normal and emergency operations for seven devices located within its EMS ESP. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure that ports and services required for normal and emergency operations were enabled on seven devices located within its EMS ESP. This violation posed potential harm to WECC_URE1 because its non-compliance created opportunities for unauthorized internal cyber attacks. The potential risks associated with this alleged violation were, however, limited due to WECC_URE1's additional procedures and policies. Specifically, the EMS network devices have technical and procedural controls for electronic access at all access points. Additionally, passwords are required to access the devices and all EMS devices are located within a Physical Security Perimeter PSP which is monitored 24 hours a day, 7 days a week. | when the Standard became mandatory and enforceable on WECC_URE1 as a "Table 1" entity | Mitigation Plan completion | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Self-Report | To mitigate this violation, WECC_URE1: 1) identified, validated, and documented authorization of ports and services for PACS and EMS devices; 2) listed authorized ports and services, including dynamic ranges; 3) create a new testing checklist for changes to applicable Cyber Assets; and 4) train WECC_URE1's subject matter experts on the new procedures. | 2013-10-31 | 2014-02-18 | Agrees | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011494 | Settlement Agreement | WECC issued to WECC_URE1 a Notice of Compliance Audit. Prior to the Compliance Audit, WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. WECC_URE1 reported that it did not include non-operating system legacy applications installed on its energy management system (EMS) and Physical Access Control System (PACS) in its patch management program. Therefore, patches for these applications were not assessed pursuant to CIP-007-1 R3. The root cause of this violation was WECC_URE1's lack of compliance processes and its failure to implement its patch management program. WECC reviewed the mitigation activities and determined that WECC_URE1 failed to assess patches for 27 EMS devices, and three PACS devices. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, WECC_URE1 failed to assess patches for legacy applications installed on 27 EMS devices and three PACS devices. This violation posed potential harm to WECC_URE1 because its noncompliance created opportunities for unathorized internal cyber attacks. However, the devices in scope of the violation did not have internet connectivity. In the event that software vulnerabilities existed, they could not be accessed nor exploited externally from the internet. Further, legacy programs were not running during the violation period and could not be accessed internally, limiting the risk during the violation. The risk of internal misuse was offset given compensating measures in place during the violation period. Internal electronic access to the devices was limited to individuals who completed Personnel Risk Assessments and cybersecurity training. The devices were physically secured within Physical Security Perimeters PSP and ESP Electronic Security Perimeters. All access was logged and monitored. Unauthorized physical or electronic access attempts would have triggered an alarm, alerting appropriate WECC_URE1 personnel. | the day after WECC_URE1 completed the mitigation of its first violation of the Standard | Mitigation Plan completion | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Self-Report | To mitigate this violation, WECC_URE1: 1) scoped and mitigated PACS systems, network devices, and EMS systems; 2) updated patch program to include application patch requirements; and 3) verified that there were no more unknown patches that require assessing and scheduling of patch deployment. | 2014-09-05 | 2014-09-18 | Agrees | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012008 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-007-3a R5. WECC_URE1 disclosed to the Audit Team that WECC_URE1 could not locate electronic access logs of individual user account successful access attempts for a total of 12 Critical Cyber Assets (CCAs). Six of the 12 assets were not logging failed access attempts. In addition, although logging on each device was enabled, logging for successful attempts was not functioning. The root cause of the violation was WECC_URE1's lack of compliance processes to ensure that logging for successful attempts was functioning. WECC reviewed the Audit findings, and determined WECC_URE1 failed to ensure that logs of individual user account access are generated and maintained for 90 days, and that these access logs were generated and maintained for twelve devices identified as CCAs. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation posed potential harm to WECC_URE1, because if unauthorized access to the Cyber Assets is not logged, and is unnoticed and unchecked, it could allow potentially malicious access to these assets. The risk posed by WECC_URE1's noncompliance is limited given the compensating measures in place during the violation period. Each of the 12 devices were located within an Electronic Security Perimeter (ESP). Although access logs for the individual CCAs were not maintained for 90 days, access logs for the ESP were generated, maintained and reviewed during the violation period. Unauthorized access through the ESP would have been detected through WECC_URE1's use of alarms. Unauthorized access attempts would have triggered an alarm alerting WECC_URE1 information technology staff. Additionally, electronic access to the ESP and CCAs in scope of the violation was restricted to individuals who completed Personnel Risk Assessments and cybersecurity training. | the day after WECC_URE1 completed the mitigation of its first violation of the Standard | Mitigation Plan completion | $65,000 (for WECC2013011963, WECC2013011964, WECC2013011875, WECC2012011493, WECC2012011494, and WECC2013012008) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) fixed its logging procedures to server for user authentication; 2) reviewed logs from the devices; 3) removed one device,; and 4) created a Cyber Asset Security Checklist. | 2013-05-20 | 2013-09-27 | Agrees | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013727 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-005-3a R1. Specifically, WECC_URE2 failed to test annually the backup media for Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP) as required by CIP-009-3 R5. While WECC_URE2 stated it performs monthly testing of all backup media types in addition to annual sample testing, WECC_URE2 failed to create and retain evidence of such testing and therefore, WECC could not verify that WECC_URE2 was in fact performing the testing on an annual basis. WECC determined that WECC_URE2 failed to demonstrate how it afforded Cyber Assets with all the specified protective measures of CIP-005-3a R1.5. The root cause of this violation was that WECC_URE2's procedure failed to include procedures on the creation and retention of evidence of monthly testing that meets the requirements of the Standard. WECC_URE2 identified the Electronic Access Control and Monitoring (EACM) devices within the class of assets categorized as servers but did not specifically label an asset type of EACM. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2 failed to provide evidence of annual testing of backup media for Cyber Assets used in the access control and/or monitoring of the ESP. However, WECC_URE2 implemented alternative procedures to help detect corrupt backup disks and to help prevent the use of outdated information for restoration. Specifically, WECC_URE2 implemented an enterprise media backup and management system for the testing of backup disks. While this system only conducts tests on samples of Cyber Asset systems, the testing is done monthly which aids in the detection of corrupt data. Further, WECC_URE2 ensured that every CCA resided within an Electronic Security Perimeter (ESP) and that WECC_URE2 identified and documented the ESPs and all access points to the perimeter. WECC_URE2 performs monthly testing of all backup media types in addition to annual sample testing. | the first day of the calendar year in which WECC_URE2 cannot demonstrate compliance with the Standard | when WECC_URE2 had evidence of testing of backup media for EACM devices | 0 | Compliance Audit | To mitigate this violation, WECC_URE2: 1) modified the procedure for annual testing of backup media to specifically include EACMs as an asset type; and 2) enhanced the process for conducting monthly verification of backup media images in a manner that results in appropriate evidence retention and comprehensive coverage of all applicable Cyber Assets. | 2014-06-13 | 2014-09-22 | Neither Admits nor Denies | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC also considered two other mitigating factors. First, WECC_URE2 provided an affidavit to WECC stating that it was actually performing monthly testing of backup images for all asset types, but that WECC_URE2 failed to create and maintain evidence of such testing. Second, WECC_URE2 underwent a prior Compliance Audit. During that audit, WECC_URE2's procedure for annual testing of backup media was in effect, but WECC did not find deficiencies with WECC_URE2's backup media testing program, thereby perpetuating WECC_URE2's determinations with respect to the satisfactory nature of its compliance documents regarding testing of backup media, resulting in the current violation.
2014-12-30 | FERC | NP15-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014013752 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-005-3a R1. Specifically, WECC_URE3 failed to test annually the backup media for Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP) as required by CIP-009-3 R5. While WECC_URE3 stated it performs monthly testing of all backup media types in addition to annual sample testing, WECC_URE3 failed to create and retain evidence of such testing and therefore, WECC could not verify that WECC_URE3 was in fact performing the testing on an annual basis. WECC determined that WECC_URE3 failed to demonstrate how it afforded Cyber Assets with all the specified protective measures of CIP-005-3a R1.5. The root cause of this violation was WECC_URE3's procedure failed to include procedures on the creation and retention of evidence of monthly testing that meets the requirements of the Standard. WECC_URE3 identified the Electronic Access Control and Monitoring (EACM) devices within the class of assets categorized as servers but did not specifically label an asset type of EACM. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 failed to provide evidence of annual testing of backup media for Cyber Assets used in the access control and/or monitoring of the ESP. However, WECC_URE3 implemented alternative procedures to help detect corrupt backup disks and to help prevent the use of outdated information for restoration. Specifically, WECC_URE3 implemented an enterprise media backup and management system for the testing of backup disks. While this system only conducts tests on samples of Cyber Asset systems, the testing is done monthly which aids in the detection of corrupt data. Further, WECC_URE3 ensured that every CCA resided within an Electronic Security Perimeter (ESP) and that WECC_URE3 identified and documented the ESPs and all access points to the perimeter. WECC_URE3 performs monthly testing of all backup media types in addition to annual sample testing. | the first day of the calendar year in which WECC_URE3 cannot demonstrate compliance with the Standard | when WECC_URE3 had evidence of testing of backup media for EACM devices | 0 | Compliance Audit | To mitigate this violation, WECC_URE3: 1) modified the procedure for annual testing of backup media to specifically include EACMs as an asset type; and 2) enhanced the process for conducting monthly verification of backup media images in a manner that results in appropriate evidence retention and comprehensive coverage of all applicable Cyber Assets. | 2014-06-13 | 2014-09-22 | Neither Admits nor Denies | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC also considered two other mitigating factors. First, WECC_URE3 provided an affidavit to WECC stating that it was actually performing monthly testing of backup images for all asset types, but that WECC_URE3 failed to create and maintain evidence of such testing. Second, WECC_URE3 underwent a prior audit. During that Compliance Audit, WECC_URE3's procedure for annual testing of backup media was in effect, but WECC did not find deficiencies with WECC_URE3's backup media testing program, thereby perpetuating WECC_URE3's determinations with respect to the satisfactory nature of its compliance documents regarding testing of backup media, resulting in the current violation.
2014-12-30 | FERC | NP15-8-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010574 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-004-1 R4. MRO_URE1 failed to maintain its lists of personnel with authorized unescorted physical access to Critical Cyber Assets (CCAs) and failed to revoke access within seven days for personnel who no longer require such access to CCAs. This violation involved four individuals who had unauthorized access: two were employees of MRO_URE1's contractor and two were MRO_URE1 employees. The contractor failed to notify MRO_URE1 within 24 hours of voluntary terminations, as contractually obligated, and MRO_URE1 did not remove the two contractor employees from MRO_URE1 list of personnel who had physical access to CCAs within seven days. Each contractor employee remained on the personnel list for approximately two to three months after ending employment with the contractor. The initial discovery of the first individual led to a comprehensive review that led to the discovery of the second individual. The two MRO_URE1 employees changed roles within MRO_URE1 and no longer required access to CCAs, but physical access was not revoked within seven days. MRO_URE1 personnel responsible for processing access revocations updated the change in the MRO_URE1 list of personnel with authorized access, but failed to complete the process by removing the employees’ access rights from the Physical Access Control System. The first employee was discovered when the individual unsuccessfully attempted to access the Physical Security Perimeter (PSP). The second employee was discovered as part of a comprehensive review in response to the discovery of the first employee. The first employee had accessed the PSP numerous times and subsequently was determined to have a continued business need for such access. Both MRO_URE1 employees continued to have access to the PSP between two and three years after access was required to be revoked. | CIP-004-1 | R4; 4.1; 4.2 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was due to misconfigured access credentials to MRO_URE1's PSP of its primary transmission control center for four individuals for a considerable length of time. MRO considered this concern a systemic problem for three reasons. First, 9.5% of contractor employees and 1.1% MRO_URE1 employees had unauthorized unescorted access to the control center, which is a Critical Asset that poses more risk to the BPS than substations or power plants. One of the the two MRO_URE1 employees accessed the control center on numerous occasions. Second, the unauthorized individuals were discovered inadvertently and at different times. Third, the duration of the violation was lengthy and ranged from several months for the contractor employees to several years for MRO_URE1 employees. While the actual risk in this instance was low, MRO’s assessment of moderate risk is based on potential risk to the BPS due to process weakness. MRO_URE1 failed to confirm that the list used for physical unescorted access contained correct information. During this lengthy time period, if the list was modified, MRO_URE1 would not be able to detect unauthorized unescorted access to the control center because it relied on incorrect documentation. The following mitigated the risk to the BPS. The contractors did not attempt to physically access CCAs following the date when they left the employment of the contractor and the badges that the contractor employees used could only be used during regular business hours. Further, the two contractor employees only had limited authorized physical security access and did not have electronic access to the CCAs. The two MRO_URE1 employees were in good standing and had current personnel risk assessments. One of the two MRO_URE1 employees did not access nor attempt to access the PSP during the time their access was assumed to have been revoked. The other employee did have a legitimate need to access the PSP and would have been granted unescorted physical access to the PSP | when the first employee should have had access revoked | when MRO_URE1 revoked access for the last employee | $0 (for MRO2012010574, MRO2012010804, MRO2012010805, and MRO2012010806) | Self-Report | To mitigate this violation, MRO_URE1: 1) improved its access verification and revocation processes for MRO_URE1 employees and contractor employees; 2) revoked the access of the terminated contractor employees; 3) implemented an interim practice to verify the employment status of all contract employees; 4) revised the revocation process to reflect that contractor employees' authorized access will be revoked unless their employment status is confirmed within the timeframe specified by MRO_URE1; 5) removed MRO_URE1 employees' authorized access until the investigation concluded; 6) confirmed the employees' need for authorized access: 7) improved quarterly review of personnel with authorized access to the PSP by reconciling the list of personnel in the Physical Access Control System to the MRO_URE1 authorized personnel list; and 8) added a quality review step to the access revocation process and checklist to compare the authorized personnel access list to the Physical Access Control System database when access rights changes are made. | 2012-08-31 | 2012-10-24 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. Further, MRO gave credit to MRO_URE1 for its commitment to improve its CIP compliance through the retention of an independent consultant. The scope of the engagement with the independent consultant included both an assessment of the strength and maturity of MRO_URE1's internal controls related to CIP compliance and the development of a risk and control matrix related to the internal controls for physical security access management processes. As a result of the independent consultant’s engagement throughout the third quarter of 2013, MRO_URE1 implemented enhancements to its internal controls related to CIP compliance and physical access control. The MRO_URE1 Board of Directors Audit Committee supported the retention of the independent consultant, which MRO considered as demonstrating a high level of engagement of senior management in MRO_URE1's compliance program. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-8-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010804 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1.5. MRO_URE1 failed to afford the protective measures of CIP-005-1 R1.5 for Cyber Assets used in the access control and montoring of the Electronic Security Perimeter (ESP). Specifically, MRO_URE1 failed to change passwords on an annual basis for Critical Cyber Assets (CCAs) and Cyber Assets within the ESP pursuant to CIP-007-1 R5.3.3, and as referenced by CIP-005-1 R1.5. MRO_URE1 conducted an internal review and assessment of shared accounts to improve documentation and processes performed by an internal review group. The review group identified a total of 70 shared accounts for CIP Cyber Assets, 15 shared accounts did not have their passwords updated annually. The discovery led MRO_URE1 to initiate an additional review that found a total of 70 shared accounts, 15 of which did not have their password updated annually. | CIP-005-1 | R1; 1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). There were a total of 15 shared accounts which provided access to Cyber Assets used in the control and monitoring of ESPs and PSPs that did not have their passwords changed annually. All accounts went at least 16 months without a password change and some accounts went as long as ten years and three months (123 months) without a password change. While these accounts were provisioned to exclusively provide system to system application access, they also could have been used for interactive access to the Cyber Assets which may have posed a serious or substantial risk to reliability of the BPS. With access to these accounts, it would be possible for unauthorized deletion, disruption, or download of the encrypted database that stored the configuration of the access to the ESPs and PSPs. However, this potential risk was mitigated because the accounts do not propagate to the domain servers within the ESP and the accounts do not provide access to CCAs. Additionally, robust firewall configuration limited the external use of the accounts. For the shared accounts at issue, access control and monitoring servers could only be accessed from the domain controller. General corporate workstations did not provide access to the protected servers with these shared accounts. Further, two-part authentication is required to access the application used for configuration changes to the ESP and PSP. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 changed the passwords on the shared accounts | $0 (for MRO2012010574, MRO2012010804, MRO2012010805, and MRO2012010806) | Self-Report | MRO_URE1 submitted a single Mitigation Plan for violations for CIP-005-1 (MRO2012010804), CIP-006-1 (MRO2012010805), and CIP-007-01 (MRO2012010806). To mitigate this violation, MRO_URE1: 1) staff immediately changed the passwords or disabled the subject shared accounts; 2) revised the Electronic Access List document to identify all shared accounts utilized on CCAs and Cyber Assets located within an ESP; 3) verified passwords had been changed at least annually for all other shared accounts relating to CCAs and Cyber Assets residing within an ESP; 4) staff conducted a review of CCAs and Cyber Assets to ensure all administrator, shared, and other generic accounts were properly identified; 5) verified that passwords had been changed at least annually for all administrator, shared, and other generic accounts relating to CCAs and Cyber Assets; and 6) removed the 15 shared accounts from its Domain account locations and moved them to new administrative groups to improve control and accountability. | 2012-07-13 | 2012-10-25 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. Further, MRO gave credit to MRO_URE1 for its commitment to improve its CIP compliance through the retention of an independent consultant. The scope of the engagement with the independent consultant included both an assessment of the strength and maturity of MRO_URE1's internal controls related to CIP compliance and the development of a risk and control matrix related to the internal controls for physical security access management processes. As a result of the independent consultant’s engagement throughout the third quarter of 2013, MRO_URE1 implemented enhancements to its internal controls related to CIP compliance and physical access control. The MRO_URE1 Board of Directors Audit Committee supported the retention of the independent consultant, which MRO considered as demonstrating a high level of engagement of senior management in MRO_URE1's compliance program.
2014-12-30 | FERC | NP15-8-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010805 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1. Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP) were not afforded the protective measures in CIP-007-1 R5. MRO_URE1 conducted an internal review and assessment of shared accounts to improve the documentation and processes performed by an internal review group. The review identified a subset of shared accounts used for Critical Cyber Assets (CCAs) and Cyber Assets located within an Electronic Security Perimeter (ESP) that did not have their passwords changed on an annual basis. As a result of a cross-functional team review of the shared account concerns, MRO_URE1 initiated an extent of conditions review to determine the full scope of noncompliance. Another internal review group for MRO_URE1's also identified a subset of shared accounts used for CCAs and Cyber Assets located within an ESP which did not have their passwords updated annually. Out of a total of 70 shared accounts for CIP Cyber Assets, 15 shared accounts did not have their passwords updated annually. Cyber Assets on which these shared accounts were used include the Information Management System (IMS) system. | CIP-006-1 | R1; 1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). There were a total of 15 shared accounts which provided access to Cyber Assets used in the control and monitoring of ESPs and PSPs that did not have their passwords changed annually. All accounts went at least 16 months without a password change and some accounts went as long as ten years and three months (123 months) without a password change. While these accounts were provisioned to exclusively provide system to system application access, they also could have been used for interactive access to the Cyber Assets, which may have posed a serious or substantial risk to reliability of the BPS. With access to these accounts, it would be possible for unauthorized deletion, disruption, or download of the encrypted database that stored the configuration of the access to the ESPs and PSPs. However, this potential risk was mitigated because the shared accounts do not propagate to the domain servers within the ESP and the accounts do not provide access to CCAs. Additionally, robust firewall configuration limited the external use of the accounts. For the shared accounts at issue, access control and monitoring servers could only be accessed from the domain controller. General corporate workstations did not provide access to the protected servers with these shared accounts. Further, two-part authentication is required to access the application used for configuration changes to the ESP and PSP. In making its risk determination, MRO also considered the greater risk this vulnerability to the PSP of lack of password changes for an extended period of time posed in conjunction with the violation of CIP-004-1 R4 (MRO2012010574), where individuals continued to have access to the PSP due to improper configuration of the Physical Access Control System. It was possible that an individual could have knowledge of one of these passwords and could have gained unauthorized unescorted physical access to CCAs and directly harmed CCAs. However, this risk was mitigated because all individuals had undergone a personnel risk assessment and had completed the required cyber security training. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 changed the passwords on the shared accounts | $0 (for MRO2012010574, MRO2012010804, MRO2012010805, and MRO2012010806) | Self-Report | MRO_URE1 submitted a single Mitigation Plan for violations for CIP-005-1 (MRO2012010804), CIP-006-1 (MRO2012010805), and CIP-007-01 (MRO2012010806). To mitigate this violation, MRO_URE1: 1) staff immediately changed the passwords or disabled the subject shared accounts; 2) revised the Electronic Access List document to identify all shared accounts utilized on CCAs and Cyber Assets located within an ESP; 3) verified passwords had been changed at least annually for all other shared accounts relating to CCAs and Cyber Assets residing within an ESP; 4) staff conducted a review of CCAs and Cyber Assets to ensure all administrator, shared, and other generic accounts were properly identified; 5) verified that passwords had been changed at least annually for all administrator, shared, and other generic accounts relating to CCAs and Cyber Assets; and 6) removed the 15 shared accounts from its Domain account locations and moved them to new administrative groups to improve control and accountability. | 2012-07-13 | 2012-10-25 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. Further, MRO gave credit to MRO_URE1 for its commitment to improve its CIP compliance through the retention of an independent consultant. The scope of the engagement with the independent consultant included both an assessment of the strength and maturity of MRO_URE1's internal controls related to CIP compliance and the development of a risk and control matrix related to the internal controls for physical security access management processes. As a result of the independent consultant’s engagement throughout the third quarter of 2013, MRO_URE1 implemented enhancements to its internal controls related to CIP compliance and physical access control. The MRO_URE1 Board of Directors Audit Committee supported the retention of the independent consultant, which MRO considered as demonstrating a high level of engagement of senior management in MRO_URE1's compliance program.
2014-12-30 | FERC | NP15-8-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010806 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R5. MRO_URE1 failed to require passwords to be changed at least once a year as required by Reliability Standard CIP-007-1 Requirement 5.3.3. MRO_URE1 had a total of 26 accounts in the Energy Management System (EMS) in the active directory domain located within an Electronic Security Perimeter (ESP) that did not have their passwords changed annually. All accounts went at least 19 months without a password change and some accounts went as long as 43 months without a password change. While none of these accounts had domain-level administrator privileges, 15 accounts had local administrative privileges on devices located within an ESP. | CIP-007-1 | R5; 5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because none of the 26 accounts in the EMS active directory domain located within an ESP that did not have their passwords changed annually provided access to CCAs. Although these assets were located within the ESP, these accounts were ordinary user accounts of which some accounts had local administrative rights on non-critical Cyber Assets, primarily devices supporting the video wall. | when MRO_URE1 failed to change its passwords at least annually | when MRO_URE1 changed the passwords on the shared accounts | $0 (for MRO2012010574, MRO2012010804, MRO2012010805, and MRO2012010806) | Self-Report | MRO_URE1 submitted a single Mitigation Plan for violations for CIP-005-1 (MRO2012010804), CIP-006-1 (MRO2012010805), and CIP-007-01 (MRO2012010806). To mitigate this violation, MRO_URE1: 1) staff immediately changed the passwords or disabled the subject shared accounts; 2) revised the Electronic Access List document to identify all shared accounts utilized on CCAs and Cyber Assets located within an ESP; 3) verified passwords had been changed at least annually for all other shared accounts relating to CCAs and Cyber Assets residing within an ESP; 4) staff conducted a review of CCAs and Cyber Assets to ensure all administrator, shared, and other generic accounts were properly identified; 5) verified that passwords had been changed at least annually for all administrator, shared, and other generic accounts relating to CCAs and Cyber Assets; and 6) removed the 15 shared accounts from its Domain account locations and moved them to new administrative groups to improve control and accountability. | 2012-07-13 | 2012-10-25 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. Further, MRO gave credit to MRO_URE1 for its commitment to improve its CIP compliance through the retention of an independent consultant. The scope of the engagement with the independent consultant included both an assessment of the strength and maturity of MRO_URE1's internal controls related to CIP compliance and the development of a risk and control matrix related to the internal controls for physical security access management processes. As a result of the independent consultant’s engagement throughout the third quarter of 2013, MRO_URE1 implemented enhancements to its internal controls related to CIP compliance and physical access control. The MRO_URE1 Board of Directors Audit Committee supported the retention of the independent consultant, which MRO considered as demonstrating a high level of engagement of senior management in MRO_URE1's compliance program. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-12-30 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011507 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1, specifically R1.5. WECC Enforcement (Enforcement) determined that WECC_URE1 failed to afford 57.1% of the Electronic Access Control and Monitoring (EACM) devices all the protection required by CIP-005-3a R1, specifically R1.5. The security information and event management and network security manager EACM devices were commissioned for use in monitoring WECC_URE1's generation control network Electronic Security Perimeter (ESP). WECC_URE1 failed to afford the following protections to 57.1% of EACM devices: CIP-003-3 R5 and R6; CIP-005-3 R2 and R3; CIP-006-3 R3, CIP-007-3 R1, R3, R4, R5, R6, R7, R8, and R9; CIP-008-3 R1; CIP-009-3 R1, R2, R3, R4, and R5. The root cause of this violation was WECC_URE1's lack of process to ensure that a third-party vendor provided all protections required by the Standard. | CIP-005-3a R1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, WECC_URE1 failed to afford 57.1% of EACM devices 19 of the 25 protective measures specified in CIP-005-3a R1.5. The 57.1% of the EACM devices involved in the violation are used for access control and/or monitoring of the generation control network ESP and the primary and back-up System Operations Control Center ESPs. The violation may have created a situation where WECC_URE1's Critical Cyber Assets could have been compromised. Specifically, WECC_URE1's failure to properly protect 57.1% of the EACM devices placed its operations control room in a position where it could have faced malicious cyber attacks. Moreover, the number of protections not afforded to 57.1% of the EACM devices increased the ways and means that a malicious cyber attack could have occurred and created a situation where potential attacks would not have been discovered by WECC_URE1. Although WECC_URE1 failed to afford certain protections required by CIP-005-3a R1.5, WECC_URE1 kept 57.1% of the EACM devices in a facility that was access controlled. WECC_URE1 also managed and audited the facility to ensure no unauthorized personnel had access to the EACM devices. Additionally, all personnel with access to the facility had personnel risk assessments as required by CIP-004-3 R3. Moreover, WECC_URE1 has established procedures for responding to EACM alerts and cyber security incidents. Furthermore, WECC_URE1 reviewed and maintained access logs to the EACM devices. No Cyber Security Incidents occurred during the period of violation. | when the EACM devices were commissioned and not afforded all the protections under the Standard | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Self-Report | To mitigate this violation,WECC_URE1: 1) developed and implemented a checklist as a procedural control that will help ensure that the protections required under CIP-005 R1.5 are in place prior to commissioning EACM devices; and 2) provided evidence it had afforded the protections specified in R1.5 to the four EACM devices. Specifically, WECC_URE1 (i) identified its data center in a Physical Security Perimeter; (ii) updated its CIP-007 R8 program document to address the subject EACM devices and performed a cyber vulnerability assessment of the devices; (iii) updated its CIP-003 R5 access control program to address the EACM devices and conducted a review of the access control privileges; (iv) submitted a technical feasibility exception for CIP-007 R3; and (v) placed documentation addressing the EACM devices as required by the Standard. | 2012-12-13 | 2014-05-12 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012248 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-3 R2. WECC Enforcement (Enforcement) determined that WECC_URE1 failed to implement an access control model that denies access by default, such that explicit access must be specified for Access Points or supplemental Electronic Access Control and Monitoring (EACM) devices that could allow for authorized access to or through the Electronic Security Perimeter (ESP) for access points (switches), as required by CIP-005 R2.1. Additionally, WECC_URE1 failed to enable only ports and services required for operations and for monitoring Cyber Assets within an ESP and failed to document the configuration of those ports and services. Specifically, WECC_URE1 failed to enable 18.2% of access points with the default community string public configured, as required by CIP-005 R2.2. WECC also determined that where external interactive access into the ESP had been enabled, WECC_URE1 failed to implement strong procedural or technical controls at a number of EACM systems prior to or upon deployment to ensure authenticity of the accessing party, where technically feasible, as required by CIP-005 R2.4. The root cause of this violation was WECC_URE1's lack of strong procedural and technical controls at all electronic access points to the ESP. | CIP-005-3 | R2; R2.1; R2.2; R2.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to fulfill three out of the six sub-requirements pertaining to this Standard, resulting in it being unable to certify that its Critical Cyber Assets (CCAs) were adequately protected in the event of a malicious cyber attack. Furthermore, WECC_URE1's failure increased the opportunity for malicious cyber attacks to occur without WECC_URE1 knowledge. However, WECC_URE1 employed several compensating measures. Specifically, WECC_URE1 implemented a defense-in-depth architecture of physical and logical cyber security controls, including physical security mechanisms with guards, special locks, closed-circuit television, and logical perimeter and internal cyber security controls, including firewalls, vulnerability scanning tools, intrusion detection systems, and a security incident and events management system. No Cyber Security Incidents occurred during the period of violation. | when WECC completed its prior Compliance Audit of WECC_URE1 and found it compliant | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) upgraded and reconfigured its supervisory control and data acquisition network; 2) disabled the internet protocol capability of three switches; 3) removed the firewall on the simple network management protocol service; and 4) submitted a technical feasibility exception regarding the R2.4 issue. | 2014-04-30 | 2014-10-13 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012249 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-3 R4. WECC Enforcement (Enforcement) determined that Cyber Vulnerability Assessments (CVAs) conducted by WECC_URE1 were deficient. WECC_URE1's CVAs did not verify that ports and services required for operations at access points were enabled (R4.2), and did not identify deficiencies related to enabled network management community strings (R4.4). The root cause of this violation was WECC_URE1's lack of a compliance process to ensure CVAs were conducted for the electronic access points to its ESP. | CIP-005-3 | R4; R4.2; R4.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's failure to conduct comprehensive CVAs may have increased the likelihood for malicious cyber attacks to go unnoticed. Specifically, WECC_URE1's failure to ensure that ports and services required for operations at access points were enabled increased the potential for uncontrolled information to enter the Electronic Security Perimeter (ESP). Additionally, because WECC_URE1 failed to identify deficiencies related to enabled network information about the contents which may be used to gain access to Critical Cyber Assets. However, WECC_URE1 did employ various compensating measures. Specifically, WECC_URE1 deployed additional physical security protections to prevent unauthorized physical access to access points. Additionally, WECC_URE1 used procedural and technical controls for logical access at access points. Further, it was determined that there were no unauthorized access attempts during the violation period. | when WECC completed its prior Compliance Audit of WECC_URE1 and found it compliant | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) disabled the internet protocol capability of the switches in scope; and 2) removed the firewall on the simple network management protocol service. | 2014-04-30 | 2014-10-13 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012201 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-006-3c R3. WECC Enforcement (Enforcement) determined that pursuant to CIP-006-3c R3, WECC_URE1 is required to keep Electronic Access Control and Monitoring (EACM) devices involved in the monitoring of an Electronic Security Perimeter (ESP) within a Physical Security Perimeter (PSP). In this instance, WECC_URE1 did not keep 30.8% of EACM devices involved in the monitoring of an ESP in a PSP. The root cause of this violation was WECC_URE1's failure to identify its data center as a PSP in its Physical Security Plan. | CIP-006-3c | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to ensure that 30.8% of EACM devices used to monitor access to its ESPs resided within a PSP. WECC_URE1's failure resulted in the devices being potentially accessible to unauthorized individuals who may not have had appropriate training or screenings prior to accessing the devices. The risks associated with WECC_URE1's failure were limited due to additional procedures employed by WECC_URE1. Specifically, the EACM devices involved were located in a facility where access was controlled, managed, and audited and all personnel with access to the facility had personnel risk assessments in place. Additionally, WECC_URE1 had procedures in place for responding to EACM alerts and cyber security incidents. It was determined that there were no EACM alerts or cyber security incidents during the violation period. Finally, WECC_URE1 maintained and reviewed access logs to the EACM devices. | when the EACM devices were commissioned | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1 created a PSP to house the EACM devices. | 2012-10-01 | 2014-08-21 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012203 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-006-3c R4. WECC Enforcement (Enforcement) determined that WECC_URE1 failed to implement operational and procedural controls to manage physical access to all access points of its Physical Security Perimeters (PSPs). Specifically, WECC_URE1 experienced a physical access control system outage at its Systems Operating Office (SOO) that caused a breach of its implementation of its operational and procedural controls for its PSP. While working, WECC_URE1 employees noticed chemical fumes emanating from the HVAC system of the building. The employees opened one outside door and one inside door of the SOO PSP to help dissipate the chemical fumes. Enforcement determined that WECC_URE1 opened two access points to its SOO PSP and did not apply proper operational or procedural controls to manage physical access to the subject PSP. The root cause of this violation was human error that caused WECC_URE1's failure to adequately secure its PSP. | CIP-006-3c | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to implement access control mitigation during a physical access control system outage in a PSP, and that WECC_URE1's failure resulted in a situation where unauthorized individuals could have accessed the PSP without proper logging and without proper authorization. The potential risks associated with this violation were limited due to additional compensating measures in place during the pendency of the violation. Specifically, WECC_URE1 had the PSP fully staffed for the duration of the violation. During the event, two system operators were on-site and controlling physical access to the access points at issue. One of the two access points also had security measures in place that made that access point only useable for egress. A security camera was installed and was monitoring the other access point that was only useable for ingress. Additionally, in this instance, the violation had a minimal duration of approximately three hours. However, WECC_URE1 did not have a method to control access to the PSP during the duration of the violation. Further, it was determined that there were no unauthorized physical access attempts during the incident. | when WECC_URE1 opened two access points to its PSP without proper operational or procedural controls | when WECC_URE1 closed the two access points | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) closed the two access points to its SOO PSP; 2) updated its PSP procedural controls; and 3) provided training to its System Operators. | 2013-12-18 | 2014-06-06 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012204 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-006-3c R5. WECC Enforcement (Enforcement) determined that WECC_URE1 failed to document a valid, deployed, and repeatable process or procedure to monitor physical access to all access points to the subject Physical Security Perimeters (PSP). Specifically, when it commissioned the subject PSP, WECC_URE1 included technical controls for monitoring access but failed to document valid, deployable, and repeatable procedures for monitoring physical access to the subject PSP. Enforcement determined that WECC_URE1 did not have a procedure for monitoring the subject PSP. The root cause of this violation was human error and a lack of process. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to have a procedure to monitor physical access at all access points to the subject PSP 24 hours a day 7 days a week. WECC_URE1's failure created the opportunity for unauthorized physical access to Critical Cyber Assets (CCAs) to go unnoticed or unchecked. Due to these failures, Enforcement determined that WECC_URE1 could not ensure that all its CCAs located within the subject PSP were properly protected from potential malicious attacks. The potential risks associated with the violation were, however, limited. Although Enforcement determined that WECC_URE1 failed to have documented procedures, WECC_URE1 did employ different technical measures to protect the subject PSP. WECC_URE1 employed an alarm system at its PSP access points and instituted security information and event management to monitor logical access to the subject PSP. | when the subject PSP was commissioned | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1 modified its log monitoring procedure for the subject PSP. | 2013-09-25 | 2014-06-27 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012226 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-007-3a R2. WECC Enforcement (Enforcement) determined that WECC_URE1 was required to establish, document and implement a process to ensure that only those ports and services required for normal and emergency operation are enabled. In this case, WECC_URE1 had enabled ports and services on a number of devices that were not required for normal and emergency operation. The root cause of this violation was human error and lack of process. | CIP-007-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's failure to properly ensure that only ports and services required for normal and emergency operations were enabled, created several potential risks related to WECC_URE1's Critical Assets. In this instance, WECC_URE1 failed to ensure that only ports and services required for normal and emergency operations were enabled. Due to WECC_URE1's failure, the devices in question were susceptible to unauthorized internal and or external access. Enforcement determined that without proper monitoring of the ports and services, WECC_URE1's Critical Assets could have been exposed to malicious cyber attacks which in turn could have impacted WECC_URE1's operations. The potential risks associated with the violation were limited due to additional measures implemented by WECC_URE1 during the pendency of the violation. WECC_URE1 has implemented various cyber security controls to properly monitor any suspicious activity. Specifically, WECC_URE1 employs firewalls, vulnerability scanning tools, and a security incident and events management system to monitor, track, and notify WECC_URE1 if any potential cyber attacks occur. | when WECC completed its prior Compliance Audit of WECC_URE1 and found it compliant | Mitigation Plan completion | $38,000 (for WECC2012011507, WECC2013012248, WECC2013012249, WECC2013012201, WECC2013012203, WECC2013012204, and WECC2013012226) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) disabled the ports on one device that was associated with a software management system service no longer in use during the Compliance Audit; 2) updated its security controls baseline and conducted a Cyber Vulnerability Assessment for all applicable devices, including the subject devices; 3) incorporated lessons learned from the Audit into the security controls and CVA methodology; 4) removed the devices from production; and 5) performed a scan to verify that only ports and services required for operations were enabled. | 2014-10-03 | 2014-10-13 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013490 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R2. WECC_URE2 failed to develop a list of its Critical Assets or Critical Cyber Assets (CCAs) during the calendar year. WECC_URE2 applied its risk-based assessment methodology (RBAM) but failed to develop the null lists of Critical Assets as required by the Standard. WECC further determined that WECC_URE2 failed to perform the annual review of the null list of Critical Assets as it did not create the list. The root cause was human error and lack of procedure. The personnel involved in gathering the documentation addressed the requirement to have the null lists by creating the redacted appendices as placeholders for the actual lists. However, they did not properly store the approved null lists. The personnel involved understood the requirements; however, in an effort to heighten the security of cyber asset information, only the redacted version was properly stored. | CIP-002-3 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to develop a list of Critical Assets could potentially result in non-identification of Critical Assets and CCAs. Therefore, the critical systems would not be afforded all the CIP protections and could have allowed WECC_URE2's peak load to be lost or misused. WECC_URE2 has 230 kV transmission lines and no Special Protection Systems. The risk was mitigated because in the prior year, WECC_URE2 did not identify any Critical Assets and therefore no CCAs. Further, WECC_URE2 did apply its RBAM and stated that it did not have any Critical Assets or CCAs, but failed to document the null lists for the year in its procedure. No harm is known to have occurred. | when WECC_URE2 failed to develop and review its null list of Critical Assets | when WECC_URE2 created and had its null list of Critical Assets approved by the compliance manager | $5,000 (for WECC2014013490, WECC2014013491, and WECC2014013492) | Self-Certification | To mitigate this violation, WECC_URE2: 1) created and had its null list of Critical Assets approved by the compliance manager; and 2) established additional procedures for future annual reviews to ensure that these lists are always created and properly stored, including a checklist that requires verifications from four members of WECC_URE2's compliance team, and adding these steps to its compliance calendar and reminder system. | 2014-02-28 | 2014-11-04 | Agrees/Stipulates | In addition to the monetary penalty, WECC_URE2 will submit to WECC, a narrative describing how WECC_URE2 plans to complete the following additional terms of settlement: Violation Prevention and Detection Controls: 1) Augment or improve processes and procedures for preventing violations - a. Include an improved process for identifying new standards/versions and their applicability to WECC_URE2. For example, include improvements to WECC_URE2's processes, systems, or tools to detect possible violations or repeat violations; b. Enhance WECC_URE2's CIP-002 procedures "to require duplicative review" associated with CIP-002 compliance. For example, develop peer review checklist, training associated with conducting peer reviews, and procedures for ensuring WECC_URE2 maintains applicable, timely, CIP-002 reviews and documentation 2) Augment or improve processes and procedures for detecting violations - a. Develop, implement, or enhance internal self-audit of WECC_URE2's compliance with all applicable NERC Reliability Standards 3) Develop and Implement an electronic calendar and reminder system for Compliance - a. The system will contain at a minimum, enforcement dates for future applicable NERC and WECC Standards, NERC and WECC events that will be attended by the WECC_URE2 Compliance Team, internal compliance meetings, and scheduled WECC_URE2 compliance activities, including annual reviews of procedures, training, testing, and drafting. CIP Version 5 Transition : 1) Prepare for transition to CIP Version 5 - a. Train applicable employees, contractors, and vendors on CIP Version 5 applicability to WECC_URE2; b. Create templates and associated tools for tracking CIP Version 5 employee responsibilities. For example, assign review and associated compliance responsibilities to accountable WECC_URE2 employees or contractors; c. Define a security procedure and protocol to determine modifications and enhancement needed to comply with CIP version 5 - Consultant for Mock Audit and Gap Analysis. WECC_URE2 will hire an outside consultant to perform a mock audit and gap analysis. For budgetary reasons, this will not be performed until 2015. Internal Compliance Program (ICP): 1) Fill out WECC's ICP Assessment (ICPA); 2) Based on results or weaknesses identified by WECC_URE2 in its ICPA, develop, augment, or improve and implement ICP; and 3) Distribute the ICP to all applicable employees, contractors, and vendors. Attendance and Participation at WECC and NERC Events: 1) Attend Compliance User Group and Critical Infrastructure Protection User Group Meetings for 2014 and 2015; 2) Attend NERC Risk-Based Registration workshop in Sacramento-October; and 3) Attend other WECC and NERC sponsored events/training. Deliverable: 1) Submit ICPA to WECC; 2) Submit a narrative to WECC describing how WECC_URE2 implemented or plans to implement the above reliability-focused proposals; and 3) Submit a list of potential consultant candidates for mock audit and gap analysis. WECC considered WECC_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013491 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R3. WECC_URE2 failed to develop a list of Critical Cyber Assets (CCAs) that were essential to the operation of the Critical Asset during the calendar year. WECC determined that WECC_URE2 failed to develop the list of CCAs using the list of Critical Assets developed pursuant to CIP-002-3 R2. WECC further determined that WECC_URE2 failed to perform the annual review of the null lists of CCAs as it did not create the list. The root cause was human error and a lack of procedure. The personnel involved in gathering the documentation addressed the requirement to have the null lists by creating the redacted appendices as placeholders for the actual lists. However, they did not properly store the approved null lists. The personnel involved understood the requirements; however, in an effort to heighten the security of cyber asset information, only the redacted version was properly stored. | CIP-002-3 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to develop a list of Critical Assets could potentially result in non-identification of CCAs. Therefore, the critical systems would not be afforded all the CIP protections and could have allowed WECC_URE2's peak load to be lost or misused. WECC_URE2 has 230 kV transmission lines and no Special Protection Systems. The risk was mitigated because in the prior year, WECC_URE2 did not identify any Critical Assets and therefore no CCAs. Further, WECC_URE2 applied its risk-based assessment methodology and stated that it did not have any Critical Assets or CCAs, but WECC_URE2 failed to document the null lists for the year in its procedure. No harm is known to have occurred. | when WECC_URE2 failed to develop and review its null list of CCAs | when WECC_URE2 created and had its null list of CCAs approved by the compliance manager | $5,000 (for WECC2014013490, WECC2014013491, and WECC2014013492) | Self-Certification | To mitigate this violation, WECC_URE2: 1) created and had its null list of CCAs approved by the compliance manager; and 2) established additional procedures for future annual reviews to ensure that these lists are always created and properly stored, including a checklist that requires verifications from four members of WECC_URE2's compliance team, and adding these steps to its compliance calendar and reminder system. | 2014-02-28 | 2014-11-04 | Agrees/Stipulates | In addition to the monetary penalty, WECC_URE2 will submit to WECC, a narrative describing how WECC_URE2 plans to complete the following additional terms of settlement: Violation Prevention and Detection Controls: 1) Augment or improve processes and procedures for preventing violations - a. Include an improved process for identifying new standards/versions and their applicability to WECC_URE2. For example, include improvements to WECC_URE2's processes, systems, or tools to detect possible violations or repeat violations; b. Enhance WECC_URE2's CIP-002 procedures "to require duplicative review" associated with CIP-002 compliance. For example, develop peer review checklist, training associated with conducting peer reviews, and procedures for ensuring WECC_URE2 maintains applicable, timely, CIP-002 reviews and documentation 2) Augment or improve processes and procedures for detecting violations - a. Develop, implement, or enhance internal self-audit of WECC_URE2's compliance with all applicable NERC Reliability Standards 3) Develop and Implement an electronic calendar and reminder system for Compliance - a. The system will contain at a minimum, enforcement dates for future applicable NERC and WECC Standards, NERC and WECC events that will be attended by the WECC_URE2 Compliance Team, internal compliance meetings, and scheduled WECC_URE2 compliance activities, including annual reviews of procedures, training, testing, and drafting. CIP Version 5 Transition : 1) Prepare for transition to CIP Version 5 - a. Train applicable employees, contractors, and vendors on CIP Version 5 applicability to WECC_URE2; b. Create templates and associated tools for tracking CIP Version 5 employee responsibilities. For example, assign review and associated compliance responsibilities to accountable WECC_URE2 employees or contractors; c. Define a security procedure and protocol to determine modifications and enhancement needed to comply with CIP version 5 - Consultant for Mock Audit and Gap Analysis. WECC_URE2 will hire an outside consultant to perform a mock audit and gap analysis. For budgetary reasons, this will not be performed until 2015. Internal Compliance Program (ICP): 1) Fill out WECC's ICP Assessment (ICPA); 2) Based on results or weaknesses identified by WECC_URE2 in its ICPA, develop, augment, or improve and implement ICP; and 3) Distribute the ICP to all applicable employees, contractors, and vendors. Attendance and Participation at WECC and NERC Events: 1) Attend Compliance User Group and Critical Infrastructure Protection User Group Meetings for 2014 and 2015; 2) Attend NERC Risk-Based Registration workshop in Sacramento-October; and 3) Attend other WECC and NERC sponsored events/training. Deliverable: 1) Submit ICPA to WECC; 2) Submit a narrative to WECC describing how WECC_URE2 implemented or plans to implement the above reliability-focused proposals; and 3) Submit a list of potential consultant candidates for mock audit and gap analysis. WECC considered WECC_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-11-25 | FERC | NP15-8-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013492 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R4. WECC_URE2 failed to include the null lists of Critical Assets and Critical Cyber Assets (CCAs) in its procedure and therefore no senior manager approved the list of Critical Assets and CCAs during the calendar year. The root cause was human error and lack of procedure. The personnel involved in gathering the documentation addressed the requirement to have the null lists by creating the redacted appendices as placeholders for the actual lists. However, they did not properly store the approved null lists. The personnel involved understood the requirements; however, in an effort to heighten the security of cyber asset information, only the redacted version was properly stored | CIP-002-3 | R4 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to develop a list of Critical Assets and CCAs and have it approved by senior management could potentially result in non-identification and protection of Critical Assets and CCAs. Therefore, critical systems would not be afforded all the CIP protections and could have allowed WECC_URE2's peak load to be lost or misused. WECC_URE2 has 230 kV transmission lines and no Special Protection Systems. The risk was mitigated because in the prior year, WECC_URE2 did not identify any Critical Assets and therefore no CCAs. Further, WECC_URE2 did apply its risk-based assessment methodology and stated that it did not have any Critical Assets or CCAs, but failed to document the null lists and have them approved for the year in its procedure. No harm is known to have occurred. | when WECC_URE2 failed to have the senior manager approve the null lists of Critical Assets and CCAs | when WECC_URE2 created and had its null list of Critical Assets and CCAs approved by the compliance manager | $5,000 (for WECC2014013490, WECC2014013491, and WECC2014013492) | Self-Certification | To mitigate this violation, WECC_URE2: 1) had its null lists of Critical Assets and CCAs approved by the compliance manager; and 2) established additional procedures for future annual reviews to ensure that these lists are always created and properly stored, including a checklist that requires verifications from four members of WECC_URE2's compliance team, and adding these steps to its compliance calendar and reminder system. | 2014-02-28 | 2014-11-04 | Agrees/Stipulates | In addition to the monetary penalty, WECC_URE2 will submit to WECC, a narrative describing how WECC_URE2 plans to complete the following additional terms of settlement: Violation Prevention and Detection Controls: 1) Augment or improve processes and procedures for preventing violations - a. Include an improved process for identifying new standards/versions and their applicability to WECC_URE2. For example, include improvements to WECC_URE2's processes, systems, or tools to detect possible violations or repeat violations; b. Enhance WECC_URE2's CIP-002 procedures "to require duplicative review" associated with CIP-002 compliance. For example, develop peer review checklist, training associated with conducting peer reviews, and procedures for ensuring WECC_URE2 maintains applicable, timely, CIP-002 reviews and documentation 2) Augment or improve processes and procedures for detecting violations - a. Develop, implement, or enhance internal self-audit of WECC_URE2's compliance with all applicable NERC Reliability Standards 3) Develop and Implement an electronic calendar and reminder system for Compliance - a. The system will contain at a minimum, enforcement dates for future applicable NERC and WECC Standards, NERC and WECC events that will be attended by the WECC_URE2 Compliance Team, internal compliance meetings, and scheduled WECC_URE2 compliance activities, including annual reviews of procedures, training, testing, and drafting. CIP Version 5 Transition : 1) Prepare for transition to CIP Version 5 - a. Train applicable employees, contractors, and vendors on CIP Version 5 applicability to WECC_URE2; b. Create templates and associated tools for tracking CIP Version 5 employee responsibilities. For example, assign review and associated compliance responsibilities to accountable WECC_URE2 employees or contractors; c. Define a security procedure and protocol to determine modifications and enhancement needed to comply with CIP version 5 - Consultant for Mock Audit and Gap Analysis. WECC_URE2 will hire an outside consultant to perform a mock audit and gap analysis. For budgetary reasons, this will not be performed until 2015. Internal Compliance Program (ICP): 1) Fill out WECC's ICP Assessment (ICPA); 2) Based on results or weaknesses identified by WECC_URE2 in its ICPA, develop, augment, or improve and implement ICP; and 3) Distribute the ICP to all applicable employees, contractors, and vendors. Attendance and Participation at WECC and NERC Events: 1) Attend Compliance User Group and Critical Infrastructure Protection User Group Meetings for 2014 and 2015; 2) Attend NERC Risk-Based Registration workshop in Sacramento-October; and 3) Attend other WECC and NERC sponsored events/training. Deliverable: 1) Submit ICPA to WECC; 2) Submit a narrative to WECC describing how WECC_URE2 implemented or plans to implement the above reliability-focused proposals; and 3) Submit a list of potential consultant candidates for mock audit and gap analysis. WECC considered WECC_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-11-25 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013346 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R3.2. FRCC_URE1 failed to detect and alert for attempts at or actual unauthorized accesses during the period. A FRCC_URE1 firewall unexpectedly stopped functioning as a result of a hardware failure. A detailed review of the failure indicated that earlier FRCC_URE1 personnel became aware that the parsing of the logs for the firewall on the device had stopped. Corrective actions including troubleshooting and contacting the vendor for support were initiated. The vendor recommended corrective actions which were taken, and it was believed that the system would recover. However, an incident ticket in the FRCC_URE1 help desk system was not created, and as a result, there was not confirmation that the logging issue had been resolved. As a result of the firewall hardware failure incident, the vendor was contacted again for additional support. The root cause of the violation was the failure of the device and lack of clarity on expectations when performing CIP compliance activity, which resulted in an improper documentation and hand-off of responsibility. | CIP-005-3a | R3; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, during the parsing failure, FRCC_URE1's loss of the ability to monitor access through the firewall and any ability to respond to potential alarms or alerts from that Cyber Asset could leave the Cyber Assets within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. The risk was mitigated because the firewall is protected behind a corporate firewall, and all Cyber Assets within the ESP are located inside a Physical Security Perimeter. The risk was further mitigated as only monitoring functions were impaired and all other preventive and protective security controls were in effect. FRCC_URE1 reviewed all the firewall logs and concluded that as a result of this violation, there was no actual risk to the BPS. Furthermore, the failure of firewall (hardware), completely eliminated any external risk as all communication was severed from outside systems. | when the logging for the firewall stopped | when the logging issue resolved | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this violation, FRCC_URE1: 1) discussed the parsing problem with the vendor and implemented the corrective actions; 2) established inactivity alerts so that if firewall logs fall more than 30 minutes behind a medium alarm is created and the team receives an alert; 3) established health alerts for the SIEM appliance that generate a high alarm and alert the team; 4) discussed the compliance issue with subject personnel to sensitize issue of accountability and lessons learned; and 5) installed an additional logging server to provide backup for the logs from the firewall. | 2014-02-18 | 2014-09-15 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-11-25 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013354 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-008-3 R1. FRCC_URE1 failed to implement its documented Cyber Security Incident Response Plan (CSIRP) when detecting a potential cyber security incident. Corrective actions including troubleshooting and contacting the vendor for support were initiated for the parsing error and the vendor recommended corrective actions which were taken. It was believed that the system would recover; however, the security analyst did not create an incident ticket in the FRCC_URE1 help desk system as required by the FRCC_URE1 incident response plan. As a result, there was no follow-up to confirm that the logging issue had been resolved. The root cause of the violation was a FRCC_URE1 security analyst was not clear that the procedure called for the creation of a FRCC_URE1 CIP Incident Ticket, even after logging an incident with the product support vendor. | CIP-008-3 | R1; R1.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, FRCC_URE1's failure to implement the CSIRP during the parsing failure led to its loss of the ability to monitor access through the firewall and any ability to respond to a potential alarms or alerts from that Cyber Asset could leave the Critical Cyber Assets within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. The risk was reduced because the firewall is protected behind a corporate firewall, and all Cyber Assets within the ESP are located within a Physical Security Perimeter. The risk was further reduced as only monitoring functions were impaired and all other preventive and protective security controls were in effect. FRCC_URE1 reviewed all the firewall logs and concluded that there was no actual risk to the BPS. | when FRCC_URE1 failed to implement its CSIRP | Mitigation Plan completion | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this violation, FRCC_URE1: 1) conducted training for incident response; 2) performed verbal counseling with the analyst to reiterate incident response processes and requirements; and 3) met with all CIP technicians to review and clarify CIP incident response processes and requirements. | 2014-04-04 | 2014-09-30 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-11-25 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013355 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1; R1.1, and R1.6. FRCC_URE1 discovered during a third-party cyber vulnerability assessment (CVA) that it had four Critical Cyber Assets (CCAs) that were not documented and defined as access points. Additionally, FRCC_URE1 discovered it had not maintained its documentation for the Electronic Security Perimeter. The root cause of the violation was inaccurate guidance that since the devices only communicate serially to the outside devices, access control lists were not required. | CIP-005-3a | R1; R1.1; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, FRCC_URE1's failure to identify all access points could leave the Cyber Assets within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. The incorrect documentation could cause incorrect decisions to be made without a full understanding of the network topology. The risk was mitigated because the access points are protected behind a corporate firewall, subject to the FRCC_URE1 change management process, and all Cyber Assets are located in a Physical Security Perimeter. The risk was further reduced as the devices were properly configured to block all inbound traffic, FRCC_URE1 personnel authorized to administer the switches is limited, and all other preventive and protective security controls were in effect. | when the devices should have been documented and treated as access points | completion of mitigating activity #3 | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this violation, FRCC_URE1: 1) reclassified the devices as access points and updated the documentation; 2) updated the network diagram to properly reflect the access points; 3) relocated the devices to the original logical location by changing the configurations on the switches and firewalls; 4) updated the Cyber Asset classification on the Cyber Asset list spreadsheet; 5) recertified the ESP configuration and documentation; and 6) updated the CCA identification procedure to address a review of access point changes for prevention of recurrence. | 2014-07-15 | 2014-10-17 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-11-25 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013357 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R2; R2.1, R2.2, and R2.3. As discovered during the third-party cyber vulnerability assessment (CVA) FRCC_URE1 discovered it failed to document some of the ports and services required for normal and emergency operations on 64 Cyber Assets. While a baseline was documented and was very detailed, some ports mostly user datagram protocol ports and dynamically assigned ports that are required for normal and/or emergency operations were not included in the FRCC_URE1 baselines. Furthermore, FRCC_URE1 discovered that for one Cyber Asset, one port and its associated service not being used, and it was not properly disabled during the install process as a result of an oversight by the subject matter expert. The root cause of the violation was that dynamic network ports in use for operational and emergency use by Critical Cyber Assets were not documented. | CIP-007-3a | R2; R2.1; R2.2; R2.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, FRCC_URE1's failure to enable and document only those ports and services required for normal and emergency operations could leave the Cyber Assets within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. The risk was reduced because all devices were located in an ESP and within a Physical Security Perimeter (PSP). Subsequent review of all 64 Cyber Assets showed only ports and services required for normal and emergency operations were enabled and that this was a documentation-only issue except for one Cyber Asset. The risk on the Cyber Asset with the port and service not disabled was negated as the service was never configured to communicate to any device, internal or external, and hence rendered unavailable. Furthermore, the firewall did not allow any communication for this service, rendering it harmless. | when FRCC_URE1 completed the prior Mitigation Plan to establish baselines | when FRCC_URE1 disabled the service in mitigating activity #2 | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this violation, FRCC_URE1: 1) updated documentation for all 64 Cyber Assets discovered with incomplete baselines; and 2) removed one service that was discovered but not required for normal and emergency operation of the subject Critical Cyber Asset; 3) reviewed and refined the roles and responsibilities for the CIP subject matter experts in regards to monitoring for ports and services; 4) conducted a lessons learned session with all subject matter experts to address conditions that led to this violation and share results with FRCC_URE1 management; and 5) updated procedures to enforce any lessons learned as applicable. | 2014-06-17 | 2014-09-15 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1’s compliance history to be an aggravating factor in the penalty determination.
2014-11-25 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013414 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R3 and R3.1. During an internal compliance review, it was discovered that a security analyst failed to complete the documentation of the assessment of the patches for the applicability to the FRCC_URE1 Cyber Asset environment. Multiple security patches were released but the analyst documentation was not sufficient to demonstrate the compliance with the requirement within the required 30 days for the following four software products. The root cause of the violation was the lack of clarity on required documented information in order to demonstrate compliance with evaluation for applicability of released patches. | CIP-007-1 | R3; R3.1 | Lower | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was increased because some of the applicable patches were not applied because they were not assessed. The risk was reduced because most of the systems were updated with current applicable patches and only lacked documentation of assessment of the applicable security patches or updates. | 30 days from when the Standard became mandatory and enforceable on FRCC_URE1 | date when assessment activity was corrected | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this issue, FRCC_URE1: 1) reformatted its patch tracking spreadsheet; 2) completed assessment of missed activity and updated the spreadsheet; 3) performed a compliance review to confirm information updated in the spreadsheet; and 4) conducted lessons learned sessions with subject matter experts and shared results with FRCC_URE1 management. | 2014-04-10 | 2014-10-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1’s compliance history to be an aggravating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013420 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R2; and R2.3. FRCC_URE1 discovered that not all of the required personnel had completed their annual CIP cyber security training. FRCC_URE1 believed that 37 FRCC_URE1 personnel who were required to complete their CIP annual training as required by CIP-004 R2, took incorrect cyber security training (general cyber security training). Although both the training courses are designed to address cyber security, the training taken by these subject personnel was not the required approved CIP cyber security compliance training. Similarly, 14 FRCC_URE1 personnel were believed to not have completed the required CIP cyber security annual training. When the problem was detected, FRCC_URE1 technology staff required the subject personnel to retake the appropriate cyber security training. The root cause of the violation was a result of the internal training system incorrectly tracking the general cyber security training as the required CIP cyber security training, which resulted in the individuals being depicted as having already taken required cyber security training. After completing the detailed review and the mitigation, FRCC_URE1 revised the number of personnel who did not complete required annual training. Three personnel in one year and seven personnel in another year did not complete their annual CIP cyber security training. | CIP-004-3a | R2; R2.3 | Lower | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because all identified personnel had completed all previous initial and required annual CIP cyber security training. Furthermore, the FRCC_URE1 CIP cyber security training course had no significant updates as the policy and procedures remained unchanged. | when the annual training was missed | when the annual training was completed in mitigating activity #1 | $25,000 (for FRCC2014013346, FRCC2014013354, FRCC2014013355, FRCC2014013357, FRCC2014013414, and FRCC2014013420) | Self-Report | To mitigate this violation, FRCC_URE1: 1) retrained the eight identified FRCC_URE1 personnel with the correct CIP training and terminated unneeded access for two additional individuals; and 2) corrected the technical control in identity manager to ensure that only correct CIP approved training is recognized; 3) verified training program correction was effective, and records were accurate and complete; and 4) implemented a review of the training material when modified in learning management system to ensure it is properly posted as required CIP training. | 2014-07-31 | 2014-09-30 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011244 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-005-3a R2.1. SPPRE_URE1 did not use an access control model that denied access by default for all access points to SPPRE_URE1's Electronic Security Perimeter (ESP). Specifically, explicit access permissions were assigned for inactive Internet Protocol (IP) addresses on SPPRE_URE1's ESP access points (firewalls). The violation stemmed from SPPRE_URE1's decision to forgo the removal of the explicit access permissions once the IP addresses became inactive under an assertion that its implemented “deny all” firewall rules were sufficient to be compliant with CIP-005-3 R2.1. | CIP-005-3a | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to remove inactive IP addresses presented a risk of unauthorized access to Cyber Assets located within SPPRE_URE1's ESP. Such a risk, if exploited via IP spoofing, could have resulted in the loss of highly sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. However, SPPRE_URE1 confirmed that no unauthorized access to the ESP occurred by use of the inactive IP addresses. In addition, SPPRE_URE1 had protective measures in place to protect Cyber Assets inside the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions; Control Point to protect, analyze, and control the user accounts of its SharePoint environment; password and lockout policies; personnel physical and cyber access reviews and control processes; as well as the isolated nature of SPPRE_URE1's network without Internet connectivity. | the earliest date of a permit statement being assigned to an inactive IP address | when SPPRE_URE1 removed the explicit access permissions for the inactive IP addresses from the SPPRE_URE1 firewalls | $10,000 (for SPP2012011244, SPP2012011245, SPP2012011246, SPP2012011247, and SPP2012011248) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) removed the explicit access permissions for the inactive IP addresses from the SPPRE_URE1 firewalls during the audit; and 2) revised its change control process to include additional steps for the update of firewall rules when devices with permitted access are removed from service. | 2013-04-26 | 2013-05-28 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered as a mitigating factor SPPRE_URE1's commitment to create nine new CIP compliance positions in response to instances of noncompliance discovered during the Compliance Audit.
2014-10-30 | FERC | NP15-7-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011245 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-005-3 R1, R1.4, R1.5, and R1.6. The Remote Terminal Units (RTUs) that are serially connected to SPPRE_URE1 field protective relays and the encryption devices that reside within a defined Electronic Security Perimeter (ESP) and are connected to external management interface devices, were neither identified nor documented as access points to the ESP as required by R1. The root cause of noncompliance was SPPRE_URE1’s failure to recognize these devices as access points to the ESP. SPPRE_URE1 had always considered these devices that are connected via non-routable serial connections to be excluded by the routable traffic requirement. SPPRE_URE1 did not consider these devices to be a non-critical Cyber Asset connected to the ESP because the serially connected device did not have a logical or physical network connection the ESP. SPPRE_URE1's host server for its virtual machines, and a supervisory control and data acquisition (SCADA) administrative workstation were not identified as non-critical Cyber Assets within a SPPRE_URE1 ESP per R1.4. The administrative workstation used by the Network Security department as a client device within the ESP network and was not used for administering the SCADA system. The root cause of noncompliance was SPPRE_URE1's oversight of not properly identifying these devices as non-critical Cyber Assets within the affected ESP. The electronic access control and monitoring (EACM) servers used to authenticate interactive access to Cyber Assets within ESPs and the SCADA administrative workstation were not identified on SPPRE_URE1's master asset list. As a result, logging and monitoring of electronic access per CIP-005-3 R3 could not be demonstrated for three of the EACM servers, and testing per CIP-007-3 R1, security patch management per CIP-007-3 R3, malware prevention per CIP-007-3 R4, account management per CIP-007-3 R5, security status monitoring per CIP-007-3 R6, and assessment for cyber vulnerabilities per CIP-007-3 R8 could not be demonstrated for the SCADA administrative workstation. The Active Directory servers (EACM) in question were not used to authenticate interactive access to Cyber Assets within the ESPs. They were used to authenticate access to Jump Hosts used to access the ESP. The Active Directory servers had been performing the external authentication role since before the effective date for CIP Version 3. The administrative workstation was used by the Network Security department as a client device within the ESP network and was not used for administering the SCADA system. The root cause of noncompliance was SPPRE_URE1's failure to recognize these devices as non-critical Cyber Assets within an ESP. SPPRE_URE1 did not identify the devices as access points or non-CCAs because of its interpretation of the standard. They did not believe they qualified as access points or non-CCAs and disagreed with Compliance’s interpretation of the standard. SPPRE_URE1 did not document the installation of a circuit providing a data communication link between two control center ESPs on its network diagram per R1.6 until approximately 21 months after the installation. SPPRE_URE1 was required to update its documentation within 90 days from the date of the installation per CIP-005-3 R5.2. SPPRE_URE1 did not have a formal step within the change management process to ensure the network team was notified of changes to the network. SPPRE_URE1 has added to its change control process steps to ensure the network team is informed of changes to devices and connections to the ESP network. The root cause of noncompliance was due to SPPRE_URE1 oversight of not ensuring that the network diagram was updated within 90 days from the date of the installation of the circuit which was due to SPPRE_URE1 failing to communicate effectively between departments about the link between sites. | CIP-005-3 | R1; R1.4; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not identifying the encryption devices and RTUs as access points to the ESP presented the risk that access to the ESP could occur without proper access controls in place to protect Cyber Assets within the ESP. The encryption devices, however, were documented in SPPRE_URE1's network topology demonstrating its awareness of the location of such devices. Notwithstanding, SPP RE determined that the devices had been afforded all of the protections prescribed in CIP-005. The failure to properly document the host server for its virtual machines and SCADA administrative workstation as non-critical Cyber Assets within a SPPRE_URE1 ESP and the RTUs that are serially connected to SPPRE_URE1 field protective relays as access points to a substation ESP, presented a risk that such devices would not be afforded all the CIP-005 protective measures, which could allow unauthorized electronic access to devices within the ESP. Notwithstanding, SPP RE determined that the devices were identified as Critical Cyber Assets (CCAs) and afforded all of the protections prescribed in CIP-005. Not identifying the EACM servers used to authenticate interactive access to Cyber Assets within ESPs and the SCADA administrative workstation on SPPRE_URE1's master asset list presented a risk that such devices would not be afforded the protective measures specified in CIP-005-3 R1.5. Nevertheless, despite the deficiencies of protective measures per CIP-005-3 R3, CIP-007-3 R1, R3 through R6, all other protective measures specified in CIP-005-3 R1.5 had been afforded. Not timely updating SPPRE_URE1's network diagram to reflect the installation of the circuit presented a risk that affected staff would not have made appropriate decisions regarding the protection of assets within the network environment due to an incorrect understanding of the network’s design. However, despite the failure to update the documentation, interviews with SPPRE_URE1's staff during the audit demonstrated that they had maintained an appropriate awareness of the network environment. Common to all above-listed instances of noncompliance, SPPRE_URE1 had protective measures in place to protect CCAs inside the ESP and access points to the ESP, including Microsoft Domain User and Security Group permissions controlling access to network resources based on job functions, password and lockout policies, personnel physical and cyber access reviews and control processes. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $10,000 (for SPP2012011244, SPP2012011245, SPP2012011246, SPP2012011247, and SPP2012011248) | Compliance Audit | To mitigate this violation, SPP RE_URE: 1) updated its CCA identification process to ensure all access points to its ESPs are identified; 2) moved the external management interface devices within the affected substation ESP, effectively removing them as access points, and identified and documented them as non-critical Cyber Assets within the affected ESP; 3) identified and documented the RTUs that are serially connected to the SEL protective relays as access points to the affected substation ESP (R1); 4) identified and documented its host server for its virtual machines and SCADA administrative workstation as non-critical Cyber Assets within the affected substation ESP (R1.4, R1.5); 5) documented the installation of the affected circuit, which provides a data communication link between the two affected ESPs (R1.6); and 6) updated its change management process and change request form to require notification to Network Security personnel each time a device is added and removed from an ESP (R1.6). | 2013-04-30 | 2013-05-28 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered as a mitigating factor SPPRE_URE1's commitment to create nine new CIP compliance positions in response to instances of noncompliance discovered during the Compliance Audit.
2014-10-30 | FERC | NP15-7-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011246 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-006-3a R2.2. Specifically, SPP RE_URE's Physical Access Control System (PACS) servers were not afforded all the protective measures specified in CIP-007-3a R3.2 and R4.2. CIP-007-3a R3.2 requires SPPRE_URE1 to “document the implementation of security patches” and “[i]n any case where the patch is not installed, [SPPRE_URE1] shall document compensating measure(s) applied to mitigate risk exposure.” Although security patches were assessed for applicability on the PACS servers within 30 calendar days of availability per CIP-007-3a R3.1, one patch was neither tested nor installed, and multiple patches, with a combination of tested/not tested, were installed but not within one year after the expiration of the 30-day patch assessment period, and there were no documented compensating measures applied to mitigate risk exposure for any of these patches as required by CIP-007-3a R3.2. SPPRE_URE1's noncompliance of CIP-007-3a R3.2 stemmed from its failure to document the implementation of compensating measures under an assertion that the Standard does not prescribe a timeline for installing applicable patches and SPPRE_URE1 anticipated applying the patches at some future date. CIP-007-3a R4.2 requires SPPRE_URE1 to “document and implement a process for the update of anti-virus and malware prevention ‘signatures[ ]’, which “must address testing and installing the signatures.” SPPRE_URE1 had documented and implemented a process for updating anti-virus and malware prevention signatures for its PACS servers. For the non-windows SCADA servers, SPPRE_URE1 tested the anti-virus signatures in a test environment before placing them on production servers. Although SPPRE_URE1 did not test Windows operating system anti-virus signatures before deploying them into production as required by its anti-malware management process, SPPRE_URE1 did have measures in place that would have alerted them to any problems caused by the anti-virus definitions on a windows machine after it was deployed. SPPRE_URE1's noncompliance of CIP-007-3a R4.2 stemmed from its failure to require the testing of anti-virus signatures prior to implementation in the production environment. | CIP-006-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to provide the protective measures specified in CIP-007-3a R3.2 and R4.2 (as made applicable by CIP-006-3a R2.2) to SPPRE_URE1's PACS servers presented a risk of exposing them to cyber vulnerabilities and malfunctions, which could have rendered the servers inoperable, thereby placing the reliability of the BPS at risk. However, physical and electronic access to the PACS servers and Cyber Assets residing within the Physical Security Perimeter (PSP) was limited to only those individuals with authorized physical and/or electronic access rights. Additionally, SPPRE_URE1 attested that there were no system failures resulting from delayed patch installation or the failure to test signature updates prior to implementation; and, even had the PACS servers failed, the PACS panels would have continued to restrict unauthorized access to the PSP based on the local memory of the PACS panels. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $10,000 (for SPP2012011244, SPP2012011245, SPP2012011246, SPP2012011247, and SPP2012011248) | Compliance Audit | To mitigate this violation, SPPRE_URE1 : 1) documented compensating measures to mitigate risk exposure for applicable patches yet to be installed within six months from their release dates; 2) installed an updated version of its anti-virus and malware software; 3) implemented configuration changes to the anti-virus and malware software to allow the installation of prevention signature updates to a test environment before installing them in the production environment; 4) revised its system management process to require either the installation of applicable security patches or documentation of applied compensating measures to mitigate risk exposure for uninstalled patches within six months of their release date; and 5) advised all affected personnel of the revised system management process. | 2013-04-26 | 2013-06-24 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered as a mitigating factor SPPRE_URE1's commitment to create nine new CIP compliance positions in response to instances of noncompliance discovered during the Compliance Audit.
2014-10-30 | FERC | NP15-7-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011247 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-3a R4.2. SPPRE_URE1 utilized Windows and Linux operating systems for its supervisory control and data acquisition (SCADA) servers. For the Windows operating systems, which provide SCADA communication with neighboring utilities, the anti-virus and malware software was configured to automatically install all applicable software prevention signature file updates on the associated SCADA servers upon their availability, without testing. Thus, SPPRE_URE1 was unable to ensure that the SCADA servers would adequately detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter (ESP) until sometime after the installation of the software updates. This violation stemmed from SPPRE_URE1's decision to forgo the implementation of procedures for testing anti-virus signatures prior to installation in the production environment. SPPRE_URE1 had incorrectly determined that doing so increased the risk of compromise to the SCADA servers due to the unique risks associated with the servers’ operating system. | CIP-007-3a | R4; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test anti-virus and malware prevention signatures prior to production implementation presented a risk that SPPRE_URE1's SCADA servers could malfunction. Because these servers are utilized in the communication of system statuses with neighboring entities, such an event could have weakened SPPRE_URE1's situational awareness, thereby placing the reliability of the BPS at risk. However, multiple redundant servers are in place to mitigate the loss of any of the SCADA servers. Additionally, SPPRE_URE1 maintains back-ups for restoration of the SCADA servers. Moreover, although the SCADA servers are relied upon for communications with neighboring entities, they are not utilized for real-time operations on the SPPRE_URE1 system. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $10,000 (for SPP2012011244, SPP2012011245, SPP2012011246, SPP2012011247, and SPP2012011248) | Compliance Audit | To mitigate this violation and to prevent recurrence, SPPRE_URE1: 1) documented compensating measures to mitigate risk exposure for applicable patches yet to be installed within six months from their release dates; 2) installed an updated version of anti-virus and malware software; 3) implemented configuration changes to its anti-virus and malware software to allow the installation of applicable signature file updates to a test host before installing them on the SCADA servers; and 4) revised its system management process and change control process to provide more clarity as to the testing processes. | 2013-04-26 | 2013-05-29 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered as a mitigating factor SPPRE_URE1's commitment to create nine new CIP compliance positions in response to instances of noncompliance discovered during the Compliance Audit. SPP RE considered SPPRE_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011248 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-3a R3.2. Specifically, although security patches for Cyber Assets within the Electronic Security Perimeter (ESP) were assessed for applicability within thirty calendar days per CIP-007-1 R3.1, a number of patches were not installed within one year of the 30-day patch assessment period. While SPPRE_URE1's security patch management program addressed assessing the applicability of the security patches within thirty calendar days of release, it did not address the timing of installing the security patches. Additionally, although SPPRE_URE1 attested that compensating measures were applied to mitigate the risk exposure for uninstalled patches, SPPRE_URE1 was unable to produce any supporting documentation as required by R3.2. This violation stemmed from SPPRE_URE1's decision to forgo the implementation of compensating measures because the Standard does not prescribe a timeline for installing applicable patches and SPPRE_URE1 anticipated applying the patches at some future date. | CIP-007-3a | R3; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE1's failure to implement all available security patches or updates presented a risk that ESP Cyber Assets could be compromised via the unmitigated system vulnerabilities, thereby placing the reliability of the BPS at risk. However, approximately 55% of the released patches were timely installed. Additionally, SPPRE_URE1's ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Moreover, all Cyber Assets within the ESP were only accessible to those with authorized physical and/or electronic access rights. SPPRE_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | the date the earliest released patch was required to be installed | Mitigation Plan completion | $10,000 (for SPP2012011244, SPP2012011245, SPP2012011246, SPP2012011247, and SPP2012011248) | Compliance Audit | To mitigate this violation and to prevent reoccurrence, SPPRE_URE1: 1) revised its patch management processes to require that applicable patches be installed or compensating measures be documented within six months from their release dates; and 2) installed all outstanding applicable patches. | 2013-04-26 | 2013-05-29 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered as a mitigating factor SPPRE_URE1's commitment to create nine new CIP compliance positions in response to instances of noncompliance discovered during the Compliance Audit. SPP RE considered SPPRE_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013515 | Settlement Agreement | TRE_URE1 submitted a Self-Report to Texas RE stating that it had an issue with Reliability Standard CIP-007-3a R5. Specifically, TRE_URE1 determined there were 23 user accounts for which passwords were not changed at least annually per R5.3.3. TRE_URE1 failed to change the passwords on the 23 accounts in over 500 days. These accounts include local administrator accounts, energy management system (EMS) support accounts, and service accounts used for Network Time Protocol. The cause of the violation is that TRE_URE1 did not have sufficiently strong or sufficiently specific procedural controls to manage passwords. | CIP-007-3a | R5; R5.3.3 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Particularly, TRE_URE1's cyber access process did not specifically address management of passwords for accounts that were disabled and later re-enabled, potentially increasing risk of unauthorized access due to aged passwords, which Standard CIP-007-3a R5 addresses. The risk is mitigated because TRE_URE1 has an in-depth security policy which covers all security measures for protecting Cyber Assets and Critical Cyber Assets. All of the accounts at issue had complex passwords known only to TRE_URE1 EMS administrators. There was no attempted use of these accounts detected during prior years. The accounts were only accessible from within TRE_URE1's Physical Security Perimeter, and were thus still secured. | The date the accounts were re-enabled after the effective date of the annual requirement of R5.3.3 | The date TRE_URE1 disabled all accounts after they were detected on the Cyber Vulnerability Assessment (CVA)) | 0 | Self-Report | To mitigate this violation, TRE_URE1: 1) promptly disabled the applicable accounts upon discovery; 2) added a process to flag and review the password age of any password over the age of 90 days in its CVA; 3) included the specific computers or items which require attention in the action plan instead of having the action plan refer back to the CVA report. This will make it less likely that a flagged item will be overlooked during implementation of the action plan; 4) revised its cybersecurity policy to address re-enabling accounts that have been disabled; and 5) documented a process to further reduce the possibility of missed items on the CVA action plan; TRE_URE1 will perform a review of the implementation of all CVA action plan items prior to closing out the action plan for the year. | 2014-05-03 | 2014-05-20 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TRE_URE1 has a dedicated compliance manager, sufficient resources, a robust self-assessment program, and the compliance program is available to all employees. Texas RE determined a penalty was not warranted in this case because TRE_URE1 took the following actions above and beyond those necessary to mitigate the instant violation: 1) developed a compliance task manager program that includes an annual password reminder; 2) contracted with a third party to perform its Cyber Vulnerability Assessment in order to lend outside perspective to its CIP program; and 3) retained a CIP consultant to provide services when needed.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013013144 | Settlement Agreement | TRE_URE2 submitted a Self-Report stating that it was in violation of CIP-003-3 R6. TRE_URE2 did not implement its documented change control process for two circuits that were decommissioned and for one Critical Asset. Specifically from the two decommissioned circuits, two Critical Cyber Assets (CCAs) relays were removed, a hardware modification; from the circuit conversion, one CCA relay was electrically reconfigured and had a parameter table updated, a modification of hardware and software; and serving the three circuits at issue, two CCA transceivers had parameter tables updated, comprising a software modification. The root cause was the assumption by staff that since no cyber security controls were impacted, there was no need to follow the change control process. This occurred as a result of inadequate controls. | CIP-003-3 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A failure to follow a change control and configuration management process could introduce potential cyber security vulnerabilities to CCAs. However, the risk was mitigated due to the following factors: the violation arose because the TRE_URE2 staff was aware that the relay network integrity was not modified, and no cyber security controls were impacted; no firewalls, ports and services, passwords, or account management settings were changed; no actual adverse impacts resulted from the absence of following the change control procedure; and all impacted equipment involved included redundancy. There was primary and backup relaying in place. Furthermore, each end of the new circuit had local breaker relaying. | when TRE_URE2 first did not implement its documented change control process | when TRE_URE2 completed its change control documentation pursuant to its change control process | $56,000 (for TRE2013013144, TRE2014013983, TRE2013012881, TRE2013012882, and TRE2014013369) | Self-Report | To mitigate this violation, TRE_URE2 : 1) completed its change control documentation pursuant to its change control process; 2) added evaluations in its TRE_URE2 relay construction and maintenance group procedures that require checking with the reliability and power quality group for the latest documentation and recording requirements; and 3) added evaluations to its TRE_URE2 relay engineering group relay design and setting checklists regarding how to address documentation situations when relay CCA work is involved. | 2014-05-07 | 2014-06-03 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014013983 | Settlement Agreement | After a Compliance Audit, Texas RE determined that TRE_URE2 was in violation of CIP-005-1 R1.5. Specifically, TRE_URE2 failed to afford the protective measures for three Cyber Assets used in the access control and monitoring of its Electronic Security Perimeters (ESPs) as specified in Standard CIP-007 R5. Based upon the review of the documentation provided by TRE_URE2, Texas RE determined that TRE_URE2 did not implement any local account technical controls and did not have an applicable Technical Feasibility Exception (TFE) in place for CIP-007 R5.3.1 or and R5.3.3. Additionally, TRE_URE2 did not change local account passwords at least annually for the three subject Cyber Assets. The root cause of the violation was inadequate commissioning controls for new devices. As a result, not all new devices were incorporated fully into TRE_URE2’s regular processes, and requirements related to technical controls and password changes were subsequently overlooked. | CIP-005-1 | R1; R1.5 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although no actual harm is known to have occurred, TRE_URE2’s failure to implement fully its policies related to passwords and its associated technical controls on three Cyber Assets could have allowed an attacker to access or compromise a system, potentially leading to loss of load. The failures for the last four and a half years included: not implementing local account technical controls without a TFE in place; and not changing passwords annually. The risk to the BPS was mitigated by the following factors. TRE_URE2 employs protection in-depth to secure its in-scope Cyber Assets. TRE_URE2 employs technical controls for remote access to the subject devices. All Cyber Assets reside within security-controlled Physical Security Perimeters that are monitored 24 hours a day, seven days a week. Additionally, TRE_URE2 either requires individual log-in accounts on all in-scope devices or controls shared accounts through password changes. TRE_URE2 provides passwords to shared accounts only to employees with a need to have access to the device. TRE_URE2 also revokes account access for personnel who no longer need access to in-scope devices, and, upon the termination or departure of any such employees, changes shared and default account passwords. | when the Standard became mandatory and enforceable on TRE_URE2 | when Texas RE approved TRE_URE2’s new TFE | $56,000 (for TRE2013013144, TRE2014013983, TRE2013012881, TRE2013012882, and TRE2014013369) | Compliance Audit | To mitigate this violation, TRE_URE2: 1) changed the password on the shared account in accordance with its policy of changing shared passwords; 2) filed a new TFE to include all the requirements in CIP-007 R5.3 for all applicable Cyber Assets. The previous TFE only included CIP-007 R5.3.2; and 3) developed a documented workgroup-level procedure to change passwords on all NERC CIP in-scope devices at least annually. | 2014-09-30 | 2014-10-13 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012881 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-1 R1.2. TRE_URE2 conducted testing to ensure that new Cyber Assets and significant changes to existing Cyber Assets did not affect existing cyber security controls. However, while TRE_URE2 conducted testing in a manner that reflected production environments, TRE_URE2 stated that it failed to document that testing was performed in a manner that reflected production environments on 10 occasions. The root cause of the CIP-007 R1.2 violation was human error and lack of adequate procedural controls. | CIP-007-1 | R1; R1.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). According to TRE_URE2, no issues were noted during testing, and the violation is documentation only. Failure to perform required testing could have compromised a Critical Cyber Asset, with a risk of substantial harm (loss of load). The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE2 employs protection in-depth to secure its Cyber Assets. All Cyber Assets reside within security-controlled Physical Security Perimeters that are monitored 24 hours a day, seven days a week. Additionally, TRE_URE2 requires either individual log-in accounts on all in-scope devices or controls shared accounts through password changes. TRE_URE2 provides passwords to shared accounts only to employees with a need to have access to the device. TRE_URE2 also revokes account access for personnel who no longer need access to in-scope devices, and, upon the termination or departure of any such employees, changes shared and default account passwords. | when the Standard became mandatory and enforceable on TRE_URE2 | when the documentation illustrating that test environments reflected production environments was created | $56,000 (for TRE2013013144, TRE2014013983, TRE2013012881, TRE2013012882, and TRE2014013369) | Self-Certification | To mitigate this violation, TRE_URE2: 1) documented test environments for each in-scope asset; 2) demonstrated and documented how test environments reflect production environments by comparing configurations; and 3) implemented a procedural control into its procedure to update the test environment documentation when changes affecting test environments are performed on in-scope systems. | 2014-02-21 | 2014-04-08 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012882 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-1 R4.2. Specifically, TRE_URE2 failed to document a process for the update of anti-virus and malware prevention signatures that addressed testing and installing the signatures. TRE_URE2 only had a process document that instructs the asset owner or delegate(s) to comply with R4.2. The root cause of the violation was human error and inadequate controls that have since been bolstered. | CIP-007-1 | R4; R4.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2 represents that signatures were duly assessed as required and that no issues were noted during testing. However, TRE_URE2 failed to document the process. Thus, the issue is documentation only. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE2 employs protection in-depth to secure its Cyber Assets. In addition to account access controls, all ESP Cyber Assets are monitored with alerting for attempts at actual or unauthorized access. Further, TRE_URE2 employs anti-virus and other malware prevention tools to detect, prevent, deter, and mitigate the introduction, exposure and propagation of malware. | when the Standard became mandatory and enforceable on TRE_URE2 | when TRE_URE2 created an anti-virus and an anti-malware process document that addressed testing and installation | $56,000 (for TRE2013013144, TRE2014013983, TRE2013012881, TRE2013012882, and TRE2014013369) | Self-Certification | To mitigate this violation, TRE_URE2: 1) developed a workgroup-level process for updating, testing and installing anti-virus and anti-malware prevention signatures; 2) documented the workgroup-level procedure for updating, testing and installing anti-virus and anti-malware prevention signatures; and 3) developed requirements for an automated solution for delivering, installing and testing anti-virus and anti-malware signatures that enhances the newly-developed workgroup-level process. | 2014-04-07 | 2014-04-08 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE considered TRE_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-10-30 | FERC | NP15-7-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014013369 | Settlement Agreement | During a Compliance Audit, Texas RE determined that TRE_URE2 was in violation of CIP-007-1 R5. Based upon the review of the devices sampled, Texas RE determined that TRE_URE2 failed to implement relevant annual password change technical controls for one Critical Cyber Asset as required by CIP-007-1 R5. A technical control was in place for the Critical Cyber Asset, but it was set to “never expire.” The root cause of the violation was determined to be inadequate commissioning controls. When the server was built, no procedure or work instruction was written as a guide for standing up this in-scope device, and no quality checks or technical controls were in place. | CIP-007-1 | R5 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE2 changed passwords annually as required, TRE_URE2’s failure to implement fully its policies related to associated technical controls could have allowed an attacker to access or compromise a system, potentially leading to loss of load. The risk to the BPS was mitigated by the following factors. TRE_URE2 employs protection in-depth to secure its in-scope Cyber Assets. All Cyber Assets reside within security-controlled Physical Security Perimeters that are monitored 24 hours a day, seven days a week. Additionally, TRE_URE2 either requires individual log-in accounts on all in-scope devices or controls shared accounts through password changes. TRE_URE2 provides passwords to shared accounts only to employees with a need to have access to the device. TRE_URE2 also revokes account access for personnel who no longer need access to in-scope devices, and, upon the termination or departure of any such employees, changes shared and default account passwords. | when the Standard became mandatory and enforceable on TRE_URE2 | when the technical control was enabled | $56,000 (for TRE2013013144, TRE2014013983, TRE2013012881, TRE2013012882, and TRE2014013369) | Compliance Audit | To mitigate this violation, TRE_URE2: 1) enabled a password expiration technical control; 2) conducted a comprehensive CIP-007 R5 compliance assessment of all in-scope devices; and 3) documented and implemented commissioning control procedures for firewalls, routers, and switches. | 2014-05-01 | 2014-06-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012782 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-005-3 R1.4. SERC_URE1 failed to identify a non-critical Cyber Asset within a defined Electronic Security Perimeter (ESP) and to protect it pursuant to the requirements of Standard CIP-005-3. SERC learned that SERC_URE1 had installed a device within the ESP to perform Cyber Vulnerability Assessments (CVAs). The device was used to scan vulnerabilities for all Cyber Assets in the ESP. SERC learned that the device did not appear on SERC_URE1's protected non-critical Cyber Asset list pursuant to R1.4. In addition, the device was not afforded any of the protective measures pursuant to CIP-005-3. SERC learned that the device was associated with approximately 52 access points and electronic access was granted to three information technology (IT) support personnel. | CIP-005-3 | R1; R1.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to identify and to protect devices in the ESP could lead to unprotected devices being compromised and used to exploit Critical Cyber Assets (CCAs). However, the device in question was an appliance utilized by three IT support staff to perform CVAs and had no interactive access to CCAs. In addition, the data collected during the CVA was transported and encrypted in transit. The data was transmitted from the device was outbound only, inbound communication was not allowed. Additionally, SERC_URE1 utilizes firewalls, intrusion detection systems, malicious software prevention, and encryption which mitigates the risk from externals threats. No harm is known to have occurred. | when the device was installed into production | when the device was removed from the ESP | $5,000 (for SERC2013012782, SERC2013012783, SERC2013012784, and SERC2014013637) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) removed the device from the ESP and from the list of non-critical Cyber Assets; 2) updated and revised NERC CIP programs, plans and processes, the change control and configuration management program and the NERC CIP Cyber Security testing program to include actions and test frameworks to ensure NERC compliance for new Cyber Assets being added to an ESP; and 3) made use of a vulnerability scanner to replace the functionality of the device in question. | 2013-10-17 | 2014-07-26 | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012783 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-005-3 R2. SERC_URE1 failed to enable only ports and services required for operations and for monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). SERC learned that SERC_URE1 failed to ensure that only ports and services required for operations and for monitoring of Cyber Assets between two ESPs. Communication between the ESPs occurred through a secured virtual private network, which allowed ingress and egress traffic. Although communications between the ESPs were secured, SERC_URE1 failed to disable the ports and services that were not required. | CIP-005-3 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to disable unnecessary ports and services could have resulted in unrestricted access into the ESP. This increased the risk of Critical Cyber Assets being compromised and rendered inoperable. However, the ports and services in question were configured to allow secure communications between two trusted networks for continuity. The communication path was secured via encrypted tunneling and was established between the trusted control center ESPs. In addition, the firewalls within the ESPs were configured to filter all inbound traffic originating from external networks. No harm is known to have occurred. | when the access control lists were configured | when the ports and services that were not required for operations were disabled | $5,000 (for SERC2013012782, SERC2013012783, SERC2013012784, and SERC2014013637) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) leveraged existing knowledge of the required ports and services for operations and monitoring of Cyber Assets within the ESP to determine the required ports and services between the ESPs; 2) modified the existing configuration rules for the primary site firewall(s) and the backup site firewall to include egress access rules allowing only the required ports and services; 3) conducted testing pursuant to its NERC CIP cyber security testing program to ensure that configuration changes do not adversely affect existing cyber security controls; and 4) conducted testing to ensure that proposed changes restrict ESP to ESP traffic to the required ports and services. | 2013-11-18 | 2014-06-05 | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012784 | Settlement Agreement | During a Compliance Audit, SERC determined that SERC_URE1 was in violation of CIP-006-3c R1. SERC_URE1 failed to ensure all Cyber Assets within an Electronic Security Perimeter (ESP) resided within an identified Physical Security Perimeter (PSP). SERC learned that the opening existed due to an unrestricted power supply (UPS) being replaced by a contractor. The location of the opening was above the drop ceiling and was approximately 16” x 36”, which was large enough to allow unauthorized entry into the PSP. During the timeframe of this occurrence, 27 Cyber Assets were located in the PSP and were considered essential to the control of the bulk power system (BPS). Although the opening was located in the corridor of the main building, the opening was not easily accessible because it required the use of a ladder and the removal of ceiling tiles. | CIP-006-3c | R1; R1.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Failing to completely enclose the PSP with a six-wall border could have allowed unauthorized physical access to Critical Cyber Assets. However, a ladder was required to gain entrance into the PSP from the hallway corridor, which was located in the main building, and monitored by physical security personnel. During the timeframe of the violation, monitoring and logging of the PSP was performed twenty four hours a day, seven days a week. No harm is known to have occurred. | when a vendor created the opening in order to complete an upgrade to the UPS | Mitigation Plan completion | $5,000 (for SERC2013012782, SERC2013012783, SERC2013012784, and SERC2014013637) | Compliance Audit | To mitigate this violation, SERC_URE1 installed dimensioned lumber secured from inside the PSP in such a fashion as to reduce the opening size below 96 square inches. | 2013-07-24 | 2014-06-05 | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013637 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R2. SERC_URE1 failed to disable unnecessary ports and services required for normal and emergency operations. SERC_URE1 hired a third-party service provider to perform its annual Cyber Vulnerability Assessment (CVA). Results from the CVA indicated that two ports were enabled on five Cyber Assets (two non-critical Cyber Assets and three electronic access control and monitoring (EACM) devices) that were not documented as being required for normal or emergency operations. In addition, 19 unnecessary services were enabled on approximately 22 devices, including the five Cyber Assets mentioned previously, that were not required for normal and emergency operations. The 22 devices included 14 Critical Cyber Asset (CCA) workstations, 4 EACM devices, 2 physical access control system (PACS) devices, and 2 non-critical Cyber Assets. According to SERC_URE1, the ports and services were enabled on the 22 devices when they were deployed into production. SERC_URE1 had documented procedures and had established a process to ensure ports and services required for normal and business operations were enabled. | CIP-007-3a | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Undocumented ports and services left Cyber Assets within the Electronic Security Perimeters (ESPs) susceptible to security vulnerabilities. However, the two ports that were enabled on the five Cyber Assets were associated with a service that was not required for operations Therefore, the service was not configured and the potential to exploit the open ports and un-configured service was limited. In addition, all but one of the other identified services did not open ports on the network interface of the devices in question. The one service that could open ports would have opened the two ports that were open on the five Cyber Assets. The affected CCAs, EACM devices, PACS device, and other Cyber Assets resided behind secured firewalls. Access was restricted to three information technology support personnel who had valid personnel risk assessments and had completed the required cyber security training. Logging and monitoring of these devices is centralized and occurs 24 hours, 7 days a week. SERC_URE1 had no known Cyber Security Incidents during the violation period. No harm is known to have occurred. | when SERC_URE1 deployed the Cyber Assets into production | Mitigation Plan completion | $5,000 (for SERC2013012782, SERC2013012783, SERC2013012784, and SERC2014013637) | Self-Report | To mitigate this violation, SERC_URE1: 1) followed its change control and testing processes to disable the port(s) and service(s) on each identified host; and 2) ensured the service status of each port and service is documented appropriately. | 3/28/2014 | 2014-07-22 | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-10-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012977 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R1.6. SERC_URE2 failed to document all Critical Cyber Assets (CCAs) and a non-critical Cyber Asset within an Electronic Security Perimeter (ESP). The devices at issue were not documented on an ESP diagram for approximately two years. The four CCAs were servers and the Cyber Asset was an integrated lights-out network interface. The devices were removed from the ESP diagram as part of a change request to decommission the devices. However, the decommissioning of the devices was canceled and the ESP diagram was not updated to reflect that the devices were still within the ESP. Approximately two years later, the five devices were decommissioned, making the ESP diagram accurate. | CIP-005-3a | R1; R1.6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were being protected in accordance with the CIP Standards, were included on the CCA list, and were reviewed annually with the Cyber Vulnerability Assessment (CVA) during the time that the ESP diagram was incorrect. Further, defense in depth was achieved through a combination of controls consisting of detailed operating procedures; personnel risk assessments; network controls such as firewalls and intrusion detection and prevention devices; and use of Physical Security Perimeters. | when the ESP diagram became inaccurate as a result of a result of the decision not to decommission the CCAs and non-critical Cyber Asset within the ESP | when the five devices were decommissioned and the ESP diagram became accurate | $0 (for SERC2013012977 and SERC2014013393) | Self-Report | To mitigate this violation, SERC_URE2: 1) decommissioned the devices from the ESP; 2) implemented interim guidance to provide additional details on the proper process for the update, approval, and publication of ESP drawings; 3) implemented a revision to the change evaluation team checklist item related to the ESP drawing update requirement to state that drawings shall be updated in draft form; 4) added a task within the change management system for the change coordinator to notify document librarian when work is completed and the proposed drawing update is approved for publication; 5) implemented a revision to the procedure for creating and updating ESP drawings to provide specific guidance regarding the proper sequence for updating, approving and publishing ESP drawings; 6) trained relevant information technology, network engineering, and security groups on the revision to the procedure for creating and updating ESP drawings; 7) performed an extent of condition review to determine if additional conditions exist which require updates to ESP drawings; and 8) performed corrective actions as appropriate based on results of the extent of condition review. | 2/28/2014 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE2 conducted other activities in addition to the mitigating activities previously described to help prevent recurrence of the CIP-005-3a R1 violation, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 has committed to conduct an annual comparison of SERC_URE2's official ESP drawings with its unofficial record from its change management database to ensure that the Cyber Asset inventory in each are aligned and that there are no discrepancies. In addition, the SERC_URE2 CVA vendor will conduct a separate annual comparison of the inventories in the official ESP drawings and the unofficial change management database during the annual CVA. Furthermore, the CVA vendor will compare these inventories to active network scans performed during the CVA to ensure inventory alignment. SERC_URE2 has also centralized its CIP compliance efforts, which SERC considered to be a mitigating factor in the penalty determination. The compliance personnel report directly to SERC_URE2's chief operating officer through the vice president, NERC/CIP Compliance. Key centralization activities have included developing NERC/CIP compliance business goals, performance metrics, and leading indicators; consolidating multiple internal NERC-related websites into a single NERC repository; centralizing SERC_URE2's review of compliance-related condition reports in SERC_URE2's corrective action system; consolidating all internal assessments; rewriting policies and procedures to ensure consistency and efficiency; centralizing SERC_URE2's review of and response to NERC alerts and advisories; and integrating NERC CIP into SERC_URE2's enterprise-wide business continuity exercise and program.
2014-09-30 | FERC | NP14-50-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2014013393 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R1. SERC_URE2 discovered gaps at two Physical Security Perimeters (PSPs) that did not have the required enclosed six-wall border or alternative measures where a complete enclosure was not physically possible. A facilities contractor began work on a PSP. A vent was added to a newly constructed office adjacent to the PSP, which created a gap of 13 inches by 13 inches. Approximately six weeks later, SERC_URE2 discovered and corrected the gap. The facilities contractor was performing ductwork and removed sheetrock barriers above the ceiling tiles at another PSP. This created two gaps that consisted of two rectangles approximately 24 inches by 36 inches that were separated by a metal bar approximately 2 inch wide. The gaps were located above the dropped ceiling and were not easily visible. Approximately a month later, SERC_URE2 performed a final PSP walk-down as part of a project to expand the PSP and discovered the two gaps. Upon discovery SERC_URE2 deployed continuous visual monitoring of the gaps. The next day following the discovery, SERC_URE2 corrected the gaps. | CIP-006-3c | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The gaps were located high above dropped-ceilings, were not easily accessible, and were located in a secured area staffed 24/7 with security guards only accessible to SERC_URE2 personnel through the use of corporate badge readers. The gaps did not border exterior walls and the badge readers continued controlling and logging access at both PSP access points along with security cameras that monitored both ingress and egress of personnel. | when the first gap was created | when the last gaps were corrected | $0 (for SERC2013012977 and SERC2014013393) | Self-Report | To mitigate this violation, SERC_URE2: 1) implemented alternative measures to ensure the area was continuously monitored until the gap was corrected; 2) issued a lessons learned communication to include interim guidance when construction or maintenance is to be performed in the facility at issue; 3) defined roles and responsibilities regarding maintenance and construction work made to, or adjacent to, PSPs in the facility at issue and updated the physical security plan accordingly. This update included details which require that alternative measures are utilized during any maintenance and construction effort which may impact the ability to maintain a six-wall border; and 4) developed and provided training on the updated procedure to key facility management and IT personnel responsible for supervising construction and maintenance work to PSPs. | 6/18/2014 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE2 conducted other activities in addition to the mitigating activities previously described to help prevent recurrence of the CIP-006-3c R1 violation, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE2 developed a training presentation for PSP construction personnel that covered notifying appropriate personnel prior to any construction work, the importance of alternative security measures during construction, explanation of the "six-wall" border or PSP as part of the CIP Standards, acceptable gap dimensions in a PSP, manual key reconciliation if utilized during construction and mandatory final PSP walkdowns and inspections prior to PSP commissioning. This training presentation will be distributed going forward upon notification that any PSP construction or maintenance will begin. SERC_URE2 has also centralized its CIP compliance efforts, which SERC considered to be a mitigating factor in the penalty determination. The compliance personnel report directly to SERC_URE2's chief operating officer through the vice president, NERC/CIP Compliance. Key centralization activities have included developing NERC/CIP compliance business goals, performance metrics, and leading indicators; consolidating multiple internal NERC-related websites into a single NERC repository; centralizing SERC_URE2's review of compliance-related condition reports in SERC_URE2's corrective action system; consolidating all internal assessments; rewriting policies and procedures to ensure consistency and efficiency; centralizing SERC_URE2's review of and response to NERC alerts and advisories; and integrating NERC CIP into SERC_URE2's enterprise-wide business continuity exercise and program. SERC considered SERC_URE's compliance history to be an aggravating factor in the penalty determination.
2014-09-30 | FERC | NP14-50-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012540 | Settlement Agreement | TRE_URE1 submitted a Self-Report that it was in violation of CIP-007-1 R5. Texas RE determined TRE_URE1 to be in violation in several instances. TRE_URE1 did not review annually seven group/role permissions for verification of user account access privileges per R5.1.3. Second, TRE_URE1 failed to change passwords for 89 shared accounts prior to putting systems into service per R5.2.1. TRE_URE1 has since either changed the passwords or disabled or deleted all 89 accounts. Third, TRE_URE1 did not annually change passwords for the 89 shared accounts per R5.3.3. TRE_URE1 has since either changed the passwords or disabled or deleted all 89 accounts. Fourth, there were 755 instances of unidentified individuals with access to 132 shared accounts per R5.2.2. TRE_URE1 has since identified all personnel with access or removed access. Lastly, there were 132 instances of failing to limit access to only those with authorization and 132 instances of failing to secure accounts in the event of personnel changes per R5.2.3. TRE_URE1 has since identified all personnel with access or removed access. The cause of this violation is attributed to the inconsistent application of procedures among the eleven departments that share ownership and accountability for access management. | CIP-007-1 | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, TRE_URE1’s failure to implement its policies could result in the misuse of account types and leave them unprotected in a manner that could lead to internal or external compromise. TRE_URE1’s failure to use proper account management could lead to the introduction of unnecessary new accounts and the activation of old accounts that could allow an attacker to access or compromise a system. In addition, TRE_URE1’s failure to change passwords annually could leave passwords susceptible to internal and external attacks that could allow an attacker to access or compromise a system. Furthermore, TRE_URE1’s failure to remove default accounts on the affected Cyber Assets located in an Electric Security Perimeter could allow an attacker to access or compromise a system. The risk to the BPS is mitigated because TRE_URE1 had defense-in-depth that consisted of: personnel risk assessments, cyber security training, logical network access control, physical access control, automated security event monitoring, account audit trails, and intrusion detection and prevention systems. No harm is known to have occurred. | when the Standard became mandatory and enforceable | when TRE_URE1 completed the last of its actions to become compliant with all requirements it self-reported | 28000 | Self-Report | To mitigate this violation, TRE_URE1 will: 1) Review its relevant policy and update it as needed; 2) Identify tools currently available to perform detective activities and determine implementation plan, if applicable; 3) Review account provisioning processes for necessary improvements; 4) Identify impact to periodic access review process; 5) Revise periodic access review process; and 6) Conduct training for applicable subject matter experts for revised processes. 7) Will clearly assign accountability for all accounts and training to help ensure that ownership responsibilities are understood and acted upon; 8) Will leverage existing tools to provide additional monitoring and escalation of issues before they become a violation of a Reliability Standard; and 9) Will processes to incorporate monitoring activities and tools to develop repeatable processes through the use of workflow solution. | 12/31/2014 (approved completion date) | TBD | Neither Admits or Denies | Texas RE reviewed TRE_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE determined that TRE_URE1’s compliance history should not serve as a basis for aggravating the penalty as TRE_URE1 does not have any prior similar violations.
2014-09-30 | FERC | NP14-50-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013150 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-1 R2. WECC determined WECC_URE1 failed to ensure that only those ports and services necessary for the operations and for monitoring of Cyber Assets within an Electronic Security Perimeter (ESP) were enabled on four access points to an ESP. WECC determined WECC_URE1 had enabled certain ports and services that were not found on the baseline report of appropriate ports and services. WECC_URE1's position was that all of the services involved communications initiated "from" the outside interface of the firewall and outward. By design, no information from these ports and services goes into the ESP. As a result, WECC_URE1 misunderstood that these are not "to and through" types of ports and services covered by CIP-005 R2.2. The root cause of this violation was WECC_URE1's misunderstanding of CIP-005 R2.2 and what services were required to be documented or accounted for on the baseline reports. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1's failure to enable only those ports and services required for operations and for monitoring Cyber Assets within an ESP created a variety of vulnerabilities within WECC_URE1's system. This in turn could have led to devices being used without authorization and could have exposed WECC_URE1's internal system to potentially harmful programs. Due to the number of access points involved, and the various ports and services that were enabled, WECC_URE1 may have missed opportunities to prevent malicious attacks. Although WECC_URE1 failed to ensure that only ports and services necessary for the operation and monitoring of Cyber Assets location within the ESPs were enabled, WECC_URE1 did employ a defense-in-depth architecture designed to prevent malicious cyber attacks. Specifically, WECC_URE1 employs physical and logical cyber security controls. These controls include physical security mechanisms such as special locks, closed circuit television, and a logical perimeter. Furthermore, the devices involved had additional cyber security controls offering additional protections to the access points, including firewalls, vulnerability scanning tools, and a security information events management system. No harm is known to have occurred. | when the Standard became mandatory and enforceable on WECC_URE1 | when WECC_URE1 updated the baselines to include the ports and services that were necessary for the operations and for monitoring of Cyber Assets within an ESP | $0 | Compliance Audit | To mitigate this violation, WECC_URE1 updated the baseline to include the ports and services required for operations and for monitoring Cyber Assets within the ESP. | 2014-06-26 | 8/12/2014 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE1 has existing strong internal controls, including preventative, detective and corrective controls. WECC determined that in this instance a $0 penalty was appropriate. During a previous Compliance Audit, WECC_URE1 had the same CIP-005 R2.2 security controls that WECC_URE1 used during the period of this violation. WECC did not find a violation of CIP-005 R2.2 at that time.
2014-09-30 | FERC | NP14-50-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012311 | Settlement Agreement | During a Compliance Audit WECC determined that WECC_URE was in violation of CIP-002-3 R1. WECC determined that WECC_URE2 implemented a Critical Asset identification methodology that did not include a risk-based assessment. The binary model used by WECC_URE2 to identify Critical Assets did not consider bulk power system (BPS) risks specific to WECC_URE2's BPS operations in its capacity as a Responsible Entity. The root cause of this violation was a misunderstanding of the transition guidance for implementing a Version 4 Critical Asset methodology. | CIP-002-3 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. WECC_URE2's failure to implement a risk-based assessment, resulted in the declassification of numerous facilities as Critical Assets. Consequently, Critical Cyber Assets (CCAs) associated with these facilities were no longer afforded CIP protections. WECC_URE2 implemented physical and electronic security measures. Further, during the course of the audit, the Audit Team performed site visits at WECC_URE2's noted WECC_URE2 observes best practices for both physical and electronic security. These practices helped reduce the risk to the CCAs. Furthermore, while WECC_URE2 did not implement a risk-based assessment methodology associated with CIP version 3, it did rely on the bright-line criteria established in CIP version 4. | when WECC_URE2 implemented its Critical Asset identification methodology that was not risk based | the effective date of NERC's guidance allowing entities to declare and use a Version 4 Bright Line Criteria for identifying Critical Assets | $25,000 (for WECC2013012311 and WECC2012011326) | Compliance Audit | To mitigate this violation, WECC_URE2 relied on NERC's guidance allowing entities to declare and use a Version 4 Bright Line Criteria for identifying Critical Assets. | 9/5/2013 | 7/10/2014 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance.
2014-09-30 | FERC | NP14-50-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012011326 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-004-1 R3. WECC determined WECC_URE2 allowed two contractors to have access to Critical Cyber Assets (CCAs). Enforcement determined these two contractors were allowed unescorted access to the CCAs prior to the contractors' completion of a personnel risk assessment (PRA). The root cause of this violation was human error. | CIP-004-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to ensure two contractors with access to CCAs completed a PRA prior to gaining unescorted access to the CCAs. The first contractor had physical access to WECC_URE2. The Physical Security Perimeter (PSP) in scope contained servers, workstations, and networking equipment essential to the operation. The second contractor had logical access to WECC_URE2's control center Electronic Security Perimeter. Failure to conduct PRAs could lead to improperly vetting the identity and criminal history of personnel managing CCAs. This could result in malicious access to these assets. Such access may then be used to cause harm to CCAs essential to the operation of the BPS which could negatively impact the BPS. However, in this instance the contractor in question was in good standing and had no logical access to any devices within the PSP. In addition, WECC_URE2's system operators manned the PSP in scope 24 hours a day, seven days a week. Card readers and video actively monitored and protected all access points. Finally, the devices within the PSP had antivirus and malware prevention tools installed which would reduce the risk of malicious software being introduced onto the CCAs. | when WECC_URE2 first allowed a contractor to have access to CCAs prior to the contractor's completion of a PRA | when PAC performed PRAs for both contractors | $25,000 (for WECC2013012311 and WECC2012011326) | Self-Report | To mitigate this violation, WECC_URE2: 1) conducted PRAs for the two contractors at issue; 2) completed a review to confirm that identity verification and seven-year criminal background checks have been completed and documented for all contractor/vendor personnel who currently require unescorted physical access to any of WECC_URE2's designated CCA areas, or cyber access to any of WECC_URE2's designated CCA systems; 3) completed internal process redesign and finalized a revised PRA process; 4) completed implementation of the new PRA process; 5) completed validation of the new PRA process and corrected deficiencies as necessary; and 6) gathered required compliance documentation and submitted completed mitigation plan. | 2012-10-19 | 2013-09-04 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined WECC_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-09-30 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011035 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO stating that it was in violation of CIP-005-2 R1. MRO_URE1 failed to protect Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP). Specifically, MRO_URE1 failed to apply security updates for an electronic access control and monitoring device, an authentication server, which relied on Windows Server 2003. The authentication server (a non-Critical Cyber Asset (CCA), located outside the ESP, was used for multi-factor authentication for support personnel for access to the ESP. Critical security patches were not evaluated or applied for nearly 34 months. MRO_URE1 discovered the violation while performing a Cyber Vulnerability Assessment. The root cause of the violation was failure by MRO_URE1 to evaluate and apply Windows security patches for the Windows Server 2003 authentication server at issue. MRO_URE1 failed to evaluate the security patches due to the misconfiguration of the server and it also determined that the authentication server at issue was running a different operating system than all of the other devices. Therefore, the other devices that were running Windows Server 2008 received the updates. The violation began when the authentication server stopped receiving security updates and ended when the server and antivirus programs were replaced and the firewall was modified to allow updates to the server. | CIP-005-2 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO determined that the violation posed a moderate risk because the authentication server at issue was responsible for authentication of remote ESP access. The potential harm was compromised access to MRO_URE1's ESP containing Critical Assets. Although multiple critical security patches were not applied to this server, all antivirus and anti-malware definitions were updated and all third-party software received security patch updates. Further, activity on this authentication server was logged and these logs were transmitted to a central logging server that is configured to generate alerts for unusual activity. Additionally, the host server was isolated and protected by a firewall from the electronic monitoring system local area network and corporate network and unable to access the control center. These protections mitigated risk to the BPS. No harm is known to have occurred. | when the authentication server stopped receiving security updates | Mitigation Plan completion | $30,000 (for MRO2012011035 and MRO2012011040) | Self-Report | To mitigate this violation, MRO_URE1: 1) installed Windows Server 2008 on the authentication server which resulted in the device receiving security patches like all of the other devices; 2) replaced the antivirus program with the same program installed on other workstations and/or servers; and 3) modified the firewall to allow updates on the server at issue. | 2013-03-05 | 2013-04-08 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-09-30 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011040 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO stating that it was in violation of CIP-006-3a R2. MRO_URE1 failed to protect its Physical Access Control Systems (PACS) that authorize and/or log access to the Physical Security Perimeter (PSP). Specifically, MRO_URE1 failed to apply security updates on a Windows XP host server that was used as the operating system for the electronic card reader. The host server is responsible for controlling all access to the PSP. Due to the frequency of critical security patches released by Microsoft, it is likely multiple critical security patches were not evaluated or applied for more than 26 months. MRO_URE1 discovered the violation while performing a Cyber Vulnerability Assessment. The root cause of the violation was failure by MRO_URE1 to evaluate and apply Windows security patches for the Windows XP host server at issue. All other Energy Management System (EMS) workstations were using Windows 7 and were receiving the updates automatically. The host server relied on updates to download and apply patches, but the system was configured for manual updates instead of automatic updates. However, other software on the host server was up to date. The violation began when the host server stopped receiving security updates and ended when a new key card access system was installed. | CIP-006-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO determined that the violation posed a minimal risk because the host server for MRO_URE1's PACS was a non-critical Cyber Asset used to control access to the PSP. The potential harm was compromised access to MRO_URE1's PSP through its card key access system because its host server did not receive security updates. The host server was isolated and protected by a firewall from the electronic monitoring system local area network and corporate network. The firewall allowed all outbound connections, but limited inbound connections from a small number of servers. Activity on the host server and firewall was logged and these logs were transmitted to a central logging server that is configured to generate alerts for unusual activity. All antivirus and anti-malware definitions were updated and all third-party software received security patch updates. In addition, access points to the PSP were monitored via an alarm system and observation by the system operators. No harm is known to have occurred. | when the host server stopped receiving security updates | when a new key card access system was installed | $30,000 (for MRO2012011035 and MRO2012011040) | Self-Report | To mitigate this violation, MRO_URE1: 1) installed a new key card access system to protect its PSPs; 2) updated documentation to reflect changes to the card key access system; 3) replaced the device at issue with a new Windows 7 machine and a new PACS; and 4) provided security patch updates for the new software to the corporate information technology group. | 2013-07-30 | 2013-08-30 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
2014-09-30 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011292 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-003-1 R5. Specifically, MRO_URE2 failed to review at least annually the access privileges to protected information to confirm that access privileges correspond with appropriate personnel roles and responsibilities, as required by CIP-003-1 R5.2. MRO_URE2 had a documented program for managing access to protected Critical Cyber Asset (CCA) information. However, MRO_URE2 failed to provide evidence that it reviewed personnel roles and responsibilities annually. The program provided access to all individuals with access to any CCA, regardless of the individual's personnel role and responsibility. MRO_URE2 limited access to security sensitive information to personnel that had successfully completed a personnel risk assessment and had received CIP cyber security training. However, MRO_URE2 did not keep the records of specific information for each individual. | CIP-003-1 | R5; R5.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE2 had a fully implemented and documented access control program. The deficiency was limited to MRO_URE2's lack of annual review to confirm that access privileges correspond with appropriate personnel roles and responsibilities. Additionally, although MRO_URE2 did not define access privileges based on roles and responsibilities, MRO_URE2 limited access to protected CCA information to individuals with cyber security training and personnel risk assessments. Therefore, MRO_URE2 had security controls in place prior to granting access to any protected information. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 created a new storage location for "Security Sensitive" information and documented who has access | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) updated the CIP protected information procedure to have one classification for protected information which will be “Security Sensitive,” and removed the “Company Confidential” classification from the procedure; 2) updated the action items for the annual assessment to include a review of the newly created report and a review of the access to the information storage repository; 3) created a secured repository for security sensitive documents and restricted access to its location; 4) created a new report that identifies who has access to the secured repository and their roles and responsibilities; 5) performed training on the updated information protection and access control program and procedures; and 6) performed an annual assessment which included the new report and a review of the information protection program. | 2013-12-17 | 2014-03-19 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-09-30 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011293 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-003-3 R6. Specifically, MRO_URE2 did not establish supporting configuration management activities to identify, control and document all entity or vendor related changes to hardware and software components of Critical Cyber Assets (CCAs) pursuant to the change control process, as required by CIP-003-3 R6. During the Compliance Audit, MRO asked for change control process documentation for software changes on a supervisory control and data acquisition (SCADA) CCA. MRO discovered that the software change was installed on the CCA, but it was not tested because the change was only supposed to be installed on four domain controllers. MRO_URE2 staff performed the software installs on the four windows domain controller servers. The software was not assigned to any other Cyber Assets (including CCA’s) in the configuration management data model beyond the domain controller servers. MRO_URE2 did not know that the domain controllers pushed the software changes to each asset within the domain. Therefore, the change ticket for the upgrade that occurred did not identify the SCADA server as part of the change, and consequently there was no evidence of CIP-007-3 R1 cyber security testing or CIP-007-3 R3 security patch management for the particular software on the SCADA CCA. MRO_URE2 performed a comprehensive review of the configuration management data model. The review identified 14 software package installations that were not represented in the configuration management data model. Additionally, the review determined that the configuration management data model built into the system manager was set up to support the configuration of processes and services that are allowed to run on each Cyber Asset rather than documenting each installed software package on each Cyber Asset. Therefore, the daily scans of enabled services, the cyber security control testing of changes, and the security patch management process focused on the Windows processes and services modeled on MRO_URE2’s Cyber Assets rather than the installed software packages. The violation was caused by MRO_URE2's failure to maintain its data management tool. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE2 failed to ensure that all software changes to CCAs were properly identified. This resulted in a failure to identify software changes as they were deployed. Changes were deployed to CCAs without requiring validation of security controls. No harm is known to have occurred. | when MRO_URE2 did not establish supporting configuration management activities to identify, control, and document all entity or vendor related changes to hardware and software components of CCAs pursuant to the change control process | Mitigation Plan completion | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) performed a review of the configuration management data model to determine how it reflects the software installed on NERC CIP assets; 2) uninstalled Adobe Reader 7 from the nine servers it was discovered on; 3) designed the database table structure and coding necessary to support the enhancements for software packages in the system manager; 4) allowed system manager to model the names of installed software packages exactly as they appear in the control panel; 5) updated system manager to support automatic software package scans similar to the existing port and service scanning feature; 6) modeled the additional software packages with appropriate naming information in the updated system manager configuration management data model so that each asset in the model contains the exact list of installed software packages; 7) modified the system manager documentation and configuration management procedure to reflect the additional support and requirements for data modeling software packages; and 8) trained staff on the system manager and configuration management procedure changes. | 2013-12-11 | 2014-04-25 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-09-30 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011301 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-005-1 R1. MRO_URE2 failed to ensure that every Critical Cyber Asset (CCA) resides within an Electronic Security Perimeter (ESP), as required by CIP-005-1 R1, and failed to afford the protective measures of CIP-003, CIP-004 R3, CIP-005 R2 and R3, CIP-006 R2 and R3, CIP-007 R1 and R3 through R9, CIP-008, and CIP-009, for Cyber Assets responsible for electronic access control and monitoring, as required by CIP-005-1 R1.5, and failed to maintain documentation of all interconnected CCA and non-critical Cyber Assets within the ESP, as required by CIP-005-1 R1.6. MRO_URE2's network switches were physically connected to multiple networks with ESP and non-ESP traffic, and were not identified as ESP access points. MRO_URE2 did not properly identify network equipment with mixed trust and communication equipment. Therefore, MRO_URE2 failed to ensure that every CCA resided within the ESP, as required by CIP-005-1 R1. MRO_URE2 also had two servers responsible for authenticating users for external ESP access, but they were not identified as electronic access control and/or monitoring (EACM) devices. As such, these devices were not managed under the CIP program and were not afforded the protective measures of CIP-003, CIP-004 R3, CIP-005 R2 and R3, CIP-006 R2 and R3, CIP-007 R1 and R3 through R9, CIP-008, and CIP-009, as required by CIP-005-1 R1.5. The two cyber assets that are used in access monitoring of the ESP were subject to domain-level access reviews, but not local, device-level reviews, as required by CIP-007 R5.1.3. Additionally, two sampled Cyber Assets that were used in the access monitoring of the ESP were not configured to systematically enforce password length or complexity requirements and were not associated with a technical feasibility exception (TFE), as required by CIP-007 R5.3. MRO_URE2 also failed to document the SONET switches connecting the primary and backup control centers as either CCAs or non-critical Cyber Assets in an ESP, despite being located in the ESP's communication path between sites. Therefore, MRO_URE2 failed to maintain documentation of all interconnected CCA and non-critical Cyber Assets within the ESP, as required by CIP-005-1 R1.6. | CIP-005-1 | R1; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). One ESP for two physically separated control centers is not a recommended configuration, making it difficult to afford the protective measures specified in the CIP Reliability Standards. At MRO_URE2, four network switches shared ESP and non-ESP traffic and were not identified and treated as access points. Additionally, this ESP configuration required the communication infrastructure, synchronous optical networking (SONET), to be identified as Cyber Assets within the ESP. However, MRO_URE2 did not include it, and therefore, it was not part of the MRO_URE2 CIP program. As a result, there were a large number of issues associated with the protective measures specified by CIP-005 R1. This also resulted in an increased opportunity for unauthorized access to Cyber Assets. As it is not practical to include this type of equipment in the CIP program, the mitigating activities involved the addition of access points to allow the SONET equipment to remain excluded. Mitigating factors which reduced the risk of this violation include the fact that the ESP and non-ESP traffic reside on separate virtual local area networks (VLANs) and that the SONET communication infrastructure was privately owned and managed internally by MRO_URE2. Additionally, although the authentication servers were not identified as electronic access control and monitoring (EACM) devices and did not have the protections of CIP-005 R1.5, the risk to the BPS was reduced by the servers being protected using an effective firewall implementation. The other issues (password complexity and device level reviews) were mitigated as part of other violations and corrected by the issuance of TFEs. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 ensured that every CCA resided within an ESP | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) determined where to deploy the switches in network topology to serve as access points to the electronic storage networks and created network diagrams depicting their location; 2) selected and ordered switches for use in the project; 3) upgraded switch firmware and configured switches for initial deployment; 4) coordinated outage times; 5) repeated the procedure (outage, deployment, test, burn in time) for equipment; 6) defined new switches as assets in the system manager; 7) updated network diagrams to show the new switches in topology; 8) configured switches as access points to the electronic storage networks; 9) configured alerting and verified proper operation; and 10) identified the network switches as access points in system manager and updated network diagrams to show the switches as ESP access points. | 2014-06-05 | 2014-06-18 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE2 divided its single ESP into two separate ESPs to achieve a more robust design and improve security. This required installation and configuration of four CISCO network switches. MRO considered this investment as a mitigating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011302 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-005-1 R4. MRO_URE2 failed to perform a cyber vulnerability assessment (CVA) of the electronic access points to the Electronic Security Perimeter (ESP) that included the following: (1) a review to verify that only ports and services required for operations are enabled, as required by CIP-005-1 R4.2; (2) discovery of all access points to the ESP, as required by CIP-005-1 R4.3; and (3) a review of controls for default accounts, as required by CIP-005-1 R4.4. During the Compliance Audit, MRO discovered that the MRO_URE2 CVA only documented a review of services, but not ports. Therefore, MRO determined that MRO_URE2 failed to perform a review to verify that only ports required for operations are enabled, as required by CIP-005-1 R4.2. Additionally, MRO_URE2 only performed an network mapper (NMAP) scan to discover all undocumented electronic access points. This process did not discover all access points to the ESP, such as modems, multi-homed hosts, or other external connections, as required by CIP-005-1 R4.3. Finally, for the CVA, MRO_URE2 provided evidence that it reviewed controls for passwords and network management community strings, but it did not provide evidence that it reviewed controls for default accounts on firewalls, which act as electronic access points, as required by CIP-005-1 R4.4. | CIP-005-1 | R4; R4.2; R4.3; R4.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review and verify ports may result in undetected access points. However, the risk was mitigated by the nature of the device in use for the firewall. In this case, it was an appliance-based solution which reduced the opportunity for an inconsistency between services and ports. Additionally, MRO_URE2's failure to perform a review to discover all access points to the ESP could have resulted in undocumented modems or serial connections. However, upon performing the review, MRO_URE2 did not detect any such devices. Finally, MRO_URE2 performed a comprehensive review of the ESP default accounts and did not discover any issues. The risk was reduced for MRO_URE2 as the vulnerability assessment is a secondary control for detecting these exposures. The documented processes and procedures are designed to minimize the potential for violations. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 performed a CVA of the electronic access points to the ESP that included a review to verify that only ports and services required for operations are enabled, as required by CIP-005-1 R4.2, discovery of all access points to the ESP, as required by CIP-005-1 R4.3, and a review of controls for default accounts, as required by CIP-005-1 R4.4. | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) performed an electronic and physical review of access points to the ESP; 2) submitted evidence of the CVA with the physical access review to the MRO; and 3) revised procedures associated with the CVA process to reflect the need to perform an electronic and physical review of access points to the ESP. | 2013-09-27 | 2014-06-06 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011300 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-006-1 R1. MRO_URE2 failed to afford the protective measures specified in CIP-007-1 R2 and CIP-007-1 R5 to Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP), as required by CIP-006-1 R1.8. During the Compliance Audit, MRO discovered that MRO_URE2 failed to protect Cyber Assets that authorize and/or log access to the PSPs. Four physical access control system (PACS) Cyber Assets did not have electronic access logs generated for activity performed at the local device level, as required by CIP-007-1 R5.1.2. Additionally, four sampled PACS Cyber Assets did not have an audit trail used for monitoring shared account activity at the local device level, as required by CIP-007-1 R5.2.3. This issue was a documentation deficiency and was mitigated as part of the CIP-007-1 R2 violation (MRO2012011296) which also posed a minimal risk to the bulk power system (BPS). Furthermore, two sampled PACS Cyber Assets had open ports and services that could not be tied to approved lists, as required by CIP-007-1 R2. These same devices were not enforcing the required password complexities and were not associated with an approved technical feasibility exception (TFE), as required by CIP-007-1 R5.3. These issues were identified because MRO_URE2 focused its attention on the network accounts which were maintained on the Windows domain controller, which had no findings and was the location of the majority of accounts. However, MRO_URE2 neglected to protect the local and root level accounts which existed on these assets, as required by CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, the risk was mitigated because the majority of user accounts associated with the operation of this device were maintained on a central domain controller. These accounts were found to have no issues. There are a total of four devices which are part of this finding. The issue identified concerning the ports and services was related to not identifying which specific assets were allowed to use common services. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 submitted TFEs | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) submitted TFEs where necessary; 2) configured all Windows Event Collector and Event Log Forwarding on PACS; 3) created new identifications and changed passwords to comply with password complexity requirements; and 4) corrected the ports and services baseline documentation. | 2013-09-19 | 2014-04-25 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011295 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-007-1 R1. Specifically, MRO_URE2 did not create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation, as required by CIP-007-1 R1.1, and did not document the test results, as required by CIP-007-1 R1.3. MRO discovered that MRO_URE2 failed to ensure that significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. MRO_URE2 did not provide evidence of testing to ensure changes to existing Cyber Assets within the ESP do not adversely affect existing cyber security controls. The testing evidence within each change ticket included several questions that contain high-level subjective responses related to testing cyber security controls rather than actual evidence of tests conducted after the change has been implemented. Additionally, MRO_URE2's domain controller pushed changes to the supervisory control and data acquisition (SCADA) device and changed one file, and changed an extension of Windows Active Directory for password complexity rules. MRO_URE2 did not have testing evidence that it performed this change in accordance with testing procedures set up for the SCADA device. MRO_URE2 implemented a new process, and proper documentation was created for a change to the SCADA device. | CIP-007-1 | R1; R1.1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE2 did not provide evidence that it performed testing for security controls for significant changes to Cyber Assets. Additionally, the risk was aggravated by the related CIP-003-1 R6 (MRO2012011293) violation in which MRO_URE2 did not identify all changes to Critical Cyber Assets. As a result, MRO_URE2 did not test security controls prior to placing the devices in operation. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 implemented a new procedure to minimize adverse effects on the production system or its operation and documented test results | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) performed a review of the configuration management data model to determine the accuracy of the software installed on NERC CIP assets; 2) uninstalled Adobe Reader 7 from the nine servers it was discovered on; 3) designed the database table structure and coding necessary to support the enhancements for Software Packages in the System Manager; 4) allowed the System Manager to model the names of installed software packages exactly as they appear in the Control Panel - Programs feature of Windows-based assets; 5) updated the System Manager to support automatic software package scans similar to the existing port and service scanning feature; and 6) implemented a new procedure to minimize adverse effects on the production system or its operation and documented test results. | 2014-01-15 | 2014-06-18 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011296 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-007-1 R2. MRO_URE2 failed to establish and document a process to ensure that only ports and services required for normal and emergency operations are enabled, as required by CIP-007-1 R2. During the Compliance Audit, MRO staff asked for a list of ports assigned for a sample of Microsoft Windows-based Cyber Assets. MRO_URE2 provided a spreadsheet containing extracts from its configuration management database of the approved ports for normal and emergency operations and for monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). The spreadsheet submitted had a tab for each asset along with a tab called "Programs-Any Port." The individual asset tabs listed the explicitly-allowed ports for each asset. Some processes use a dynamic port range. The "Programs-Any Port" tab listed the processes that are configured in allowing any port on any server. It also included a short description of the nature of the “Allow Any Port” flag. This “Programs-Any Port” tab was not asset-specific. MRO staff also asked for a system-generated list of all active ports for a sample of specific assets. MRO_URE2 provided a spreadsheet with a tab for each requested asset. Each tab listed the open ports and enabled services. Five of six sampled critical and non-Critical Cyber Assets within the ESP were identified as having open ports and services that could not be tied to approved lists. The ports and services were approved for all of the critical and non-Critical Cyber Assets within the ESP, but they were not documented as approved for specific critical and non-Critical Cyber Assets within the ESP. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk associated with vague documentation is that it hindered the ability for the cyber vulnerability assessment to ensure that applications and services running on Cyber Assets were limited to those required for normal and emergency operations. However, the ports and services that were not documented for specific critical and non-Critical Cyber Assets were approved for all critical and non-Critical Cyber Assets within the ESP. Therefore, they were approved for devices within the ESP, but they were not properly documented for specific critical and non-Critical Cyber Assets within the ESP. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion when MRO_URE2 completed mitigation | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2 modified the System Manager port scanning functionality to do the following: 1) save the asset's allowed ports configuration at the time of the scan; 2) save the NETSTAT results with the scan request; 3) save the results of the port scan for both TCP and UDP ports; and 4) modify port scanning process for "Allow Any Port" so that the process names must match configuration and the program must be assigned to the specific asset. | 2013-10-07 | 2014-06-11 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011297 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-007-1 R5. During the Audit, MRO discovered five critical and non-critical Cyber Assets within the Electronic Security Perimeter (ESP) that did not have electronic access logs generated at the device level. Therefore, MRO_URE2 failed to establish methods that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days, as required by CIP-007-1 R5.1.2. MRO also discovered six Cyber Assets within the ESP that were subject to domain level access reviews, but not device level access reviews. Therefore, MRO_URE2 failed to review, at least annually, user accounts to verify that access privileges were in accordance with CIP-003 R5, as required by CIP-007-1 R5.1.3. During the Audit, MRO also discovered that five critical and non-critical Cyber Assets within the ESP did not have an audit trail capturing shared accounts user activity at the device level. Therefore, MRO_URE2 failed to have an audit trail of the account use (automated or manual), as required by CIP-007-1 R5.2.3. MRO also discovered that MRO_URE2 failed to change the shared password for two devices. Therefore, MRO_URE2 failed to change the passwords, at least annually, or more frequently based on risk, as required by CIP-007-1 R5.3.3. Furthermore, MRO discovered that six critical and non-critical Cyber Assets within the ESP were not configured to systematically enforce password length or complexity for local accounts, as required by CIP-007-1 R5.3.1 and R5.3.2. MRO_URE2's energy management system utilizes domain accounts for application and network security. MRO_URE2 focused on domain accounts for electronic access logs, account reviews, audit trails, and password complexity. However, MRO_URE2 did not apply those measures to default accounts at the device level, and therefore, failed to apply the protective measures required in CIP-007-1 R5. | CIP-007-1 | R5; R5.1.2; R5.1.3; R5.2.3; R5.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although MRO_URE2 had a logging and access review process, it was limited to domain level accounts. This left local and administrative accounts without any logging and access review protection. Five out of six Cyber Assets within the ESP were not properly configured for logging or account review. Additionally, since logging was not implemented on local accounts, no user activity trail was available for those accounts. Furthermore, MRO_URE2 failed to change the password for two years on two of the six devices. These were special accounts where MRO_URE2 had an insufficient procedure for changing passwords for personnel changes. However, MRO_URE2 restricted access to these accounts to individuals with current personnel risk assessments and cyber security training. Additionally, no harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 completed mitigation | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) implemented Windows Event Collector and Event Log Forwarding on all Microsoft Server 2008 and Windows 7 assets. MRO_URE2 will maintain all security logs for a minimum of 90 calendar days. Certain security events will generate a system manager system event and will be handled via the EMMS security status monitoring procedure; 2) reviewed local accounts on all assets as part of the annual Cyber Vulnerability Assessment; and, 3) changed passwords, where technically feasible, at least annually and submitted technical feasibility exceptions. | 2014-09-19 | 2014-06-06 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011298 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-007-3a R3. MRO_URE2 failed to establish, document, and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for Cyber Assets within the Electronic Security Perimeter (ESP), as required by CIP-007-3a R3. MRO_URE2 performed software installations on four Windows domain controller servers. Software was not assigned to any other Cyber Assets in the configuration management data model beyond the domain controller servers. It was not evident at the time that the domain controllers pushed the software via a DLL file to each asset within the domain. Therefore, the change ticket for the software upgrade that occurred did not identify one supervisory control and data acquisition (SCADA) server as part of the change, and consequently, there was no evidence of security patch management as required by CIP-007-3a R3.2. Upon discovering the issue, MRO_URE2 performed a comprehensive review to ensure that there were no additional data errors and ensure that all change tickets to Cyber Assets followed the correct patch process. The review identified 14 software package installations that were not accurately represented in the configuration management data model. | CIP-007-3a | R3; R3.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE2 failed to document the implementation of the security patches, MRO_URE2 documented the assessment of each patch prior to installation. Additionally, the patches were properly implemented. The security patches applied to the Critical Cyber Assets (CCAs) were not documented as CCA-related due to configuration errors in the change control management system. Therefore, this issue was limited to a documentation deficiency. No harm is known to have occurred. | when the database error occurred which resulted in an improper change ticket | when MRO_URE2 established, documented, and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for Cyber Assets within the ESP | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) enhanced the system manager so it allows better support for modeling the names of installed software packages exactly as they appear in the control panel - programs feature of Windows-based assets; 2) uninstalled Adobe Reader from the nine servers it was discovered on; 3) enhanced system manager to support automatic software package scans similar to the existing port and service scanning feature; and 4) modeled the additional software packages and software package naming information in the updated system manager configuration management data model so that each asset in the model contains the exact list of installed software packages. | 2013-12-11 | 2014-04-25 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011299 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE2 was in violation of CIP-007-1 R8. MRO_URE2 failed to perform a cyber vulnerability assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter (ESP) that reviewed controls for default accounts, as required by CIP-007-1 R8.3, and failed to document the action plan to remediate or mitigate vulnerabilities identified in the assessment, as required by CIP-007-1 R8.4. During the Compliance Audit, MRO requested documentation associated with a review of controls for default accounts. MRO_URE2 reported that it performed the assessment at the domain level and not the device level. Therefore, MRO_URE2 did not have any documentation to demonstrate that it performed a review for default accounts on devices, as required by CIP-007-1 R8.3. Additionally, MRO_URE2 documented action plans to mitigate issues identified in its CVA, but the plans were not specific and resulted in inconclusive tracking. The action items did not identify specific Critical Cyber Assets, and it was unclear whether the action plan was complete and whether all of the vulnerabilities were properly remediated. | CIP-007-1 | R8; R8.3; R8.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE2 did not perform an annual CVA at the local account level, it did perform an annual CVA at the domain level. Additionally, the risk associated with the action plan was limited to a documentation deficiency. No harm is known to have occurred. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 performed the CVA and included a review of accounts at the domain and local device level | $40,000 (for MRO2012011292; MRO2012011293; MRO2012011295; MRO2012011296; MRO2012011297; MRO2012011298; MRO2012011299; MRO2012011300; MRO2012011301; and MRO2012011302) | Compliance Audit | To mitigate this violation, MRO_URE2: 1) performed a domain and device level review of accounts; 2) reviewed procedures associated with the CVA process to ensure they reflect the need to perform an account review at the domain and local device level; and 3) updated the CVA report to clearly identify dynamic ports in the evidence. | 2013-09-27 | 2014-06-16 | Admits | MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013388 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R5. SERC_URE1 failed to change one non-administrative energy management system (EMS) user account password annually. SERC_URE1 originally self-reported eight non-administrative EMS user account passwords were not changed annually. After reviewing the evidence, SERC determined that, pursuant to CAN-0010, although SERC_URE1 did not change the eight passwords within the timeframe required by its definition of "annual," it did change the passwords in two consecutive calendar years. As a result, SERC determined that SERC_URE1 was not in violation of CIP-007-3a R5.3.3 for these eight passwords. While SERC was assessing this issue, SERC_URE1 discovered a ninth EMS user account that it had previously overlooked. This user account did not have its password changed during the calendar year. Based on this oversight, SERC determined that SERC_URE1 was in violation of CIP-007-3a R5.3.3 for this single user account. | CIP-007-3a | R5; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation involved 1.8% total user accounts. In order to access the user account, a malicious party would have to gain access to the Physical Security Perimeter (PSP), log-on to the Windows domain with valid credentials, and would have to know the password for the user account they were trying to misuse. Remote electronic access to this account is not possible. The PSP is monitored by security twenty-four hours a day, seven days a week, access cards are required for entry into the PSP, and there are alarm contacts for forced entry. The single user account was not a shared account and had no control capabilities or administrative privileges. There were no instances of inappropriate access attempts during this time period. | one day past the last day SERC_URE1 had to change the passwords annually | when SERC_URE1 changed the user account password | $10,000 (for SERC2014013388, SERC2014013389, SERC2014013390, and SERC2014013391) | Self-Report | To mitigate this violation, SERC_URE1: 1) changed passwords for all nine accounts upon discovery; and 2) configured the EMS to force these passwords for the nine accounts to expire 365 days after the last change. | 2014-04-16 | 2014-07-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013389 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R3.2. SERC_URE1 failed to maintain security monitoring and logging processes to detect and alert for attempts at or actual unauthorized accesses to its Electronic Security Perimeters (ESPs). On the same day, SERC_URE1 submitted a second Self-Report to SERC stating that it was in violation of CIP-005-3a R3.2. In this case, the logging service necessary for collecting and storing information related to activities on the network at the back-up control center (BCC) failed as a result of depletion of disk space. SERC determined that the second Self-Report involved the same Standard and Requirement as the first Self-Report and decided to treat the second Self-Report as an expansion of scope. The first instance was discovered when SERC_URE1 determined that the two firewalls serving as access points to the energy control center (ECC) ESP and an operations center ESP were no longer sending the logs from the firewalls to the log aggregation server for review and alerting. After an internal review, SERC_URE1 determined that this condition existed for approximately three weeks. The failure occurred when SERC_URE1 rebooted the log aggregation server which caused the logging service to default to manual and stopped it from accepting logs from the firewalls. Since the firewall memory buffers are limited, no logs were stored locally for SERC_URE1 to review manually. The second instance also was discovered on the same day, when SERC_URE1 determined that the logging service for the one firewall at the BCC failed because the disk space of the log aggregation server filled to capacity. Once filled, the log aggregation server stopped accepting the logs from the firewalls. After an internal review, SERC_URE1 determined that the log aggregation partition for the BCC was down for approximately a month and a half. Since the firewall memory buffers are limited, no logs were stored locally for SERC_URE1 to review manually. While SERC was performing its assessment of this violation, SERC_URE1 notified SERC that it had also discovered that the alerts from the BCC log center were not being received by the appropriate personnel. SERC_URE1 had not configured a rule on the firewall to permit the email message from the log server within the ESP to be sent to the appropriate personnel. The firewall rules for the ECC and the operations center were properly configured to allow email alerts to be sent to appropriate personnel. This issue started when the new SERC_URE1 energy management system (EMS) went into production. | CIP-005-3a | R3; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to review and alert for unauthorized access attempts and the failure to retain the logs for 90 days could have created a situation where unauthorized access attempts or actual unauthorized access to the ESP would not have been recognized or investigated, potentially allowing the function and capability of the Cyber Assets to be degraded or compromised. Also, SERC_URE1's failure to properly configure the firewall rules to allow email alerts to the appropriate personnel for two years could have permitted unauthorized access or access attempts to go without investigation or response. However, all passwords are set to expire after 90-days and after five unsuccessful access attempts, the EMS domain will lock-out the account. Also, all System Operators get alarms for any events on the system. Therefore, an alert would have been sent to all actual the actual System Operators if anyone accessed the EMS software and took any operating actions. SERC_URE1 reviewed the available logs of the Critical Cyber Assets and Cyber Assets within the ESPs, and found no cyber security issues for those devices. The failure to log at the firewalls lasted for a period of no more than two months and the failure to send email alerts only affected the BCC, which was not in continuous operation during the time of the violation. The BCC was only operational and active for two hours during the period of non-compliance. No harm is known to have occurred. | when SERC_URE1 started using the new EMS and the firewall rule to permit communications from the BCC log server was not implemented | when the firewall rule to permit communications from the BCC log server was implemented | $10,000 (for SERC2014013388, SERC2014013389, SERC2014013390, and SERC2014013391) | Self-Report | To mitigate this violation, SERC_URE1: 1) restarted the logging service and made disk space available; 2) changed the logging service startup mode to automatic which will cause the service to start on its own following future server reboots; 3) set the recovery options so that Windows would restart in the event it fails; 4) configured a monitoring service on the EMS to collect the free space for disk partitions used by the log services; 5) enabled alarming when the free space falls below certain thresholds to provide advance warning; and 6) added a firewall incident rule to permit the server to send emails. | 2014-05-30 | 2014-07-30 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013390 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R6. SERC_URE1 failed to have automated or organizational process controls to monitor for events related to cyber security. On the same day, SERC_URE1 submitted a second Self-Report to SERC stating that it was in violation of CIP-007-3a R6. In this case, a logging service necessary for collecting and storing information related to activities on the network at the energy control center (ECC) did not startup when the server was rebooted. The startup configuration for the service was set to “manual.” SERC determined that the second Self-Report involved the same Standard and Requirement as the first Self-Report and decided to treat the second Self-Report as an expansion of scope. The first instance was discovered when SERC_URE1 determined that the log aggregation server stopped accepting logs for review and alerting from the Cyber Assets within the Electronic Service Perimeter (ESP) at the ECC and an operations center. After an internal review, SERC_URE1 determined that this condition existed for approximately three weeks. The failure occurred when SERC_URE1 rebooted the log aggregation server which caused the logging service to default to manual and stopped it from accepting logs from the Cyber Assets within the ESP. This issue affected Windows workstations (all Critical Cyber Assets (CCAs)), Windows servers, Linux servers (all CCAs), switches identified as non-critical Cyber Assets within the ESP, and a Windows server for the Physical Access Control System which was within the ESP. The second instance also was discovered when SERC_URE1 determined that the logging service for the back-up control center (BCC) failed because the disk space of the log aggregation server filled to capacity. Once filled, the log aggregation server stopped accepting the logs from the Cyber Assets within the ESP. After an internal review, SERC_URE1 determined that the log aggregation partition for the BCC was down for approximately a month and a half. This issue affected Windows workstations identified as CCAs in the BCC, Windows servers identified as CCAs in the BCC, Linux servers identified as CCAs in the BCC, and a switch in the BCC that was a non-critical Cyber Asset within the ESP. While SERC was performing its assessment of this issue, SERC_URE1 notified SERC that it had also discovered that the alerts from the BCC log center were not being received by the appropriate personnel. SERC_URE1 had not configured a rule on the firewall to permit the email message from the log server within the ESP to be sent to the appropriate personnel (ECC and the operations center were properly configured). This issue started when the new SERC_URE1 energy management system (EMS) went into production. | CIP-007-3a | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's failure to review and maintain 90 days’ worth of logs for multiple CCAs and non-critical Cyber Assets within the ESP could have permitted a cyber-security incident to go undetected for a prolonged length of time. This failure could have degraded the Cyber Assets’ function and capability. However, all passwords are set to expire after 90-days and after five unsuccessful access attempts, the EMS domain will lock-out the account. Also, all System Operators get alarms for any events on the system. Therefore, an alert would have been sent to all actual the actual System Operators if anyone accessed the EMS software and took any operating actions. Only ten days of logs were not sent for SERC_URE1's review, involving Linux servers (CCAs) and the switches identified as non-critical Cyber Assets. Once the service to the aggregation server was reestablished and the available logs were sent, review showed that no cyber security events needed investigation. The failure to log at the firewalls lasted for no more than two months. The failure to send email alerts only affected the BCC, which was not in continuous operation during the time of the violation. The BCC was only operational and active for two hours during the period of non-compliance. No harm is known to have occurred. | when SERC_URE1 started using the new EMS and the firewall rule to permit communications from the BCC log server was not implemented | when the firewall rule to permit communications from the BCC log server was implemented | $10,000 (for SERC2014013388, SERC2014013389, SERC2014013390, and SERC2014013391) | Self-Report | To mitigate this violation, SERC_URE1: 1) restarted the logging service and made disk space available; 2) changed the logging service startup mode to automatic which will cause the service to start on its own following future server reboots; 3) set the recovery options so that Windows would restart in the event it fails; 4) configured a monitoring service on the EMS to collect the free space for disk partitions used by the log services; 5) enabled alarming when the free space falls below certain thresholds to provide advance warning; 6) retained logs locally for Windows machines for a portion of the outage time and sent them to the servers once they came back up; 7) processed those logs at that time by the service and no alarms for cyber security incidents were generated; 8) manually reviewed all logs that were still available in the Linux and Cisco devices; and 9) added a firewall incident rule to permit the server to send emails. | 2014-05-30 | 2014-07-30 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013391 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R3.2. SERC_URE1 failed to implement security patches that it had assessed were applicable. SERC reviewed SERC_URE1's security patch management program document. This document requires that SERC_URE1 assess security patches for applicability within 30 days of availability, and requires the logging of the assessment that was conducted. It also guides the user in documenting/logging the status and implementation of the security patches. SERC also reviewed the log of the assessed security patches and confirmed that all patches were reviewed within 30 days of availability, that all security patches determined to be applicable were documented and tested, and that a priority for deployment was established. SERC_URE1 deployed its new energy management system (EMS) and for approximately a year and a half, SERC_URE1 determined that 26.9% of the assessed security patches were applicable. SERC learned that although SERC_URE1 documented that it planned to apply the assessed security patches during its regular patching cycle, SERC_URE1 failed to define and document the patching cycle in its security patch management program; therefore, the patches that SERC_URE1 determined were required were not deployed. SERC_URE1 ultimately installed the security patches at the end of the year. At that point, 16.4% patches went more than 350 days after SERC_URE1 assessed they were applicable without being installed, 49.2% patches went between 100 and 350 days after SERC_URE1 assessed they were applicable without being installed and 34.4% patches went less than 100 days after SERC_URE1 assessed they were applicable without being installed. SERC_URE1 did not document any compensating measures for the patches it did not install. | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC_URE1 assessed security patches within 30 days of availability and documented the results. Although SERC_URE1 did not define its patch cycle in its program, it documented that the applicable security patches should be installed during the regular patching cycle. None of the assessed security patches were for known vulnerabilities with active exploits circulating, so they did not require immediate application. The lack of a defined 'regular patching schedule' did not preclude SERC_URE1 from applying any patches that would have been deemed critical just after the assessment would have been completed. Also, the devices in question were protected by an Electronic Service Perimeter (ESP) and Physical Security Perimeter. | when SERC_URE1 started using the new EMS, and did not have patching cycle defined in its compliance documentation | when all security patches were applied | $10,000 (for SERC2014013388, SERC2014013389, SERC2014013390, and SERC2014013391) | Self-Report | To mitigate this violation, SERC_URE1: 1) installed applicable security patches from last patch installation; 2) defined SERC_URE1's security patch implementation cycle; 3) added the security patch implementation cycle definition to its systems management policy document; 4) added the reference to the security patch implementation cycle timeframe the review, assess, and schedule security patches document; 5) trained personnel responsible for security patch assessment and installation on the changes to ensure they understood what the security patch implementation cycle is; 6) created and maintained an organizational chart that shows each of these cross-business relationships. This chart forms the basis for communicating the expectations for performance to all members of leadership with parties shown in the chart; 7) developed a training module to be delivered to applicable standard owners and subject matter experts, to highlight the seriousness of the role they play in the SERC_URE1 compliance program and in upholding the reliability of the BPS. | 2014-06-30 | 2014-07-29 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013153 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-3c R2.2. WECC_URE1's energy management system (EMS) initiated a password change for the departure of an employee who resigned. A workplan to invoke a change of a shared administrative account password was initiated and subject matter experts (SMEs) were assigned to different asset groups to change the password. During the changing of shared account passwords, WECC_URE1 identified that it failed to identify a physical access control systems (PACS) panel as a PACS device, and failed to timely change the default account password. In addition, WECC_URE1 failed to afford the protective measures specified in CIP-007-3 R5.2.1 for one PACS asset, and failed to afford the protective measures specified in CIP-007-3 R2, CIP-007-3 R4, and CIP-007-3 R8, for the PACS panel. | CIP-006-3c | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to identify and subsequently provide protections for a device that provides, monitors and logs access to a Physical Security Perimeter (PSP) could result in the compromise of Critical Cyber Assets (CCAs) critical to the reliability of the BPS. In addition, failing to ensure that Cyber Assets used in the access control and monitoring of the PSPs are afforded protected measures puts such assets at risk to be manipulated. Such manipulation could allow unauthorized access to the PSP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets contained in the PSP. Such access may then be used to cause harm to CCAs essential to the operation of the BPS, thereby potentially negatively impacting the BPS. As a compensating measure, WECC_URE1 installed the panel and server inside a PSP and ESP, affording all physical and logical protections required by CIP-006 and CIP-005 to the devices. Due to the serial connection to the PACS server and the panel’s location inside a PSP, it is unlikely that an external adversary would be able to surreptitiously access the panel and damage the PACS. This violation caused no actual harm. | the first day after WECC determined Mitigation Plan completion for WECC_URE1's first violation of the Standard | Mitigation Plan completion | $22,000 (for WECC2013013248 and WECC2013013153) | Self-Report | To mitigate this violation, WECC_URE1 immediately changed the default password for the device in question. In addition, WECC_URE1: 1) updated its existing CIP-007 R5 shared account management procedure, password management procedure and factory default accounts procedure to incorporate a quality assurance process to ensure that one SME performs the password change and another SME verifies the completion of the task; and 2) performed SME training on the updated procedure. | 2014-05-07 | TBD | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1’s compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013248 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1, was in violation of CIP-005-3a R2. WECC Enforcement determined WECC_URE1 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) at two access points (four physical devices acting as two logical access points in failover mode), and failed to implement strong procedural or technical controls to ensure authenticity of the accessing party where external interactive access into the ESP has been enabled. | CIP-005-3a | R2; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party where external interactive access into the ESP has been enabled, including access to WECC_URE1’s Critical Cyber Assets inside the ESP. WECC_URE1 allowed interactive access from an internal network. As compensating measures, WECC_URE1 has implemented a defense-in-depth architecture of physical and logical cyber security controls, including physical security mechanisms, special locks, closed-circuit television, and logical perimeter and internal cyber security controls, including firewalls. In addition, the devices are located within a Physical Security Perimeter. This violation caused no actual harm. | the first day after WECC determined Mitigation Plan completion for WECC_URE1's first violation of the Standard | present | $22,000 (for WECC2013013248 and WECC2013013153) | Compliance Audit | To mitigate this violation, WECC_URE1 will: 1) check current firewall licensing; 2) develop secure connection solution, host-based identification with multi-factor authentication to secure access; 3) implement third-party security assessment; 4) procure network equipment and applications; and 5) implement secure connection solution. | 11/19/2014 (approved completion date) | TBD | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1’s compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009818 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R1. WECC enforcement reviewed the Self-Report, Audit Report, numerous data requests and transcripts of telephone interviews, and determined that WECC_URE2 failed to ensure that every Critical Cyber Asset (CCA) resided within an ESP; and failed to document the Electronic Security Perimeter (ESP) and all access points to the ESP. Specifically, WECC_URE2 failed to identify and protect one human machine interface (HMI), two servers, and a personal computer within a defined ESP. In addition, WECC_URE2 identified two unsecured access point ports connected to CCAs and failed to comply with the 90-day access log review requirement specified in CIP-005-3 R3.2, as incorporated in CIP-005-3 R1.5. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 failed to define and document the respective ESP for one CCA (an HMI) at a substation; two servers and one personal computer, and therefore could not ensure that these devices had all the protections of an ESP and Physical Security Perimeter (PSP), such as logging and monitoring of electronic access, ports and service restrictions, and an access control model that denies access by default. As compensating measures, WECC_URE2 stated the HMI was password-protected and located in a secure facility restricted by card readers. Only a small number of technicians and employees had physical access only, and the vendor of the device also had dial-up access. For the servers and the personal computer, WECC_URE2 stated the de-listing was an administrative error only; each asset continued to receive the protections and updates afforded assets within the PSP and ESP. Failure to identify and secure access points used in the access control and monitoring of CCAs puts such assets at risk to be manipulated, and may permit unauthorized internal and or external access, which could allow for successful cyber-attacks against CCAs. Unsecured access points may allow unauthorized access to the ESP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets within the ESP. As compensating measures, the dial-up phone numbers were only known by personnel with access to WECC_URE2's secured system, thus reducing the possibility of malicious use as individuals outside the organization would not know the correct number to dial to access the devices. Additionally, the devices require special software installed on the client accessing them in order to be able to interact with the devices. Further, WECC_URE2 implemented some detective controls in that any changes made to relays would have triggered alerts, notifying response personnel of the change, and some preventive controls, in that the device was configured to deny by default unless access was requested from an approved phone number belonging to a similar device. Similar devices required access to be granted from the WECC_URE2 secure system to use. WECC determined that for one dial-up access point, WECC_URE2 failed to follow its change control procedures when upgrading one substation. WECC_URE2 failure to follow its change control and configuration management process could potentially allow adding or modifying hardware and software changes that could be harmful to CCAs by introducing or exposing potential security vulnerabilities. Failure to set local security controls could permit anyone with the appropriate number to compromise the device. As a compensating measure, WECC_URE2 stated anyone seeking access would need to know the exact phone number to get access. WECC_URE2's failure to comply with the 90-day access log review requirement exposes its Cyber Assets used in the access control and monitoring of the ESP to possible malicious access attempts, and delays in discovering those attempts. However, as a compensating measure, both instances of WECC_URE2's failure to comply were limited to events in 2011, and WECC_URE2 reported no instances of late log reviews in 2012. For these combined issues, WECC determined this violation posed a moderate risk to the reliability of the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $50,000 (for WECC2012009818 WECC2012010700 WECC2013011896 WECC2013011897 and WECC2012010880) | Self-Report | To mitigate this violation, WECC_URE2: 1) disconnected dial-up access to the devices; 2) updated its hardware inventory to reflect the changes; and 3) performed physical verification of all similar sites. | 2013-10-10 | 2014-05-15 | Agrees | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's voluntary corrective action to remediate this violation to be a mitigating factor. WECC determined WECC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010700 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-005-1 R2. The Audit team determined WECC_URE2 failed to comply with R2.2 of the Standard. WECC_URE2 failed to enable only ports and services required for operations and monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). WECC_URE2 allowed electronic access in error by defining firewall permission rules for one Cyber Asset that had been reportedly removed from service in 2009. The Audit team also determined that WECC_URE2 failed to comply with R2.4 of the Standard, because it failed to apply strong procedural or technical controls to one of its access points to ensure authenticity of the accessing party. Testing demonstrated that authorized users could interactively connect through the ESP access point to a router inside the ESP using a secure shell network protocol (SSH), and then connect from the router back to the firewall using SSH. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The firewall was configured to permit traffic to a device that was removed from service, it does not pose a risk to the BPS. The firewall configuration would only pose a risk if a Cyber Asset is subsequently placed into service with the same internet protocol (IP) address: then traffic could be permitted through the firewall, thus the requirement to implement a deny-by-default access control model, as well as violating the requirement to enable only the ports and services required for operations and for monitoring Cyber Assets within the ESP. The company has implemented adaptive security appliances as electronic access points to the defined ESP for each of its registered entities that compensated for the risk. In addition to an implicit deny by default, the company generally applies highly restrictive access control permissions to enable traffic entering the ESP from outside. There are a few instances where “permit any any” commands are coded, however the Audit Team determined that these are for outbound traffic only and are used for determining required traffic prior to tightening down the rules. The company prohibits dial-up access in the control center environment, including dial-up access to the servers and the physical access control systems. The company utilizes two-factor authentication methods for strong authentication of interactive access into the ESP. Maintenance of the access points is normally performed by connecting to the device from within the ESP, which does not require strong authentication. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $50,000 (for WECC2012009818 WECC2012010700 WECC2013011896 WECC2013011897 and WECC2012010880) | Compliance Audit | To mitigate this violation, WECC_URE2: 1) updated its firewall rule to prevent SSH authentication from taking place behind firewall; and 2) updated firewall rule sets and removed the extra IP addresses in scope. | 2012-10-26 | 2014-01-27 | Agrees | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's voluntary corrective action to remediate this violation to be a mitigating factor. WECC determined WECC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011896 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-005-3 R4. WECC determined that WECC_URE2, under its company's cyber security program, failed to perform Cyber Vulnerability Assessments (CVAs) for electronic access points to the Electronic Security Perimeter (ESP), at least annually. Specifically in this case, WECC_URE2 failed to include two associated access point devices in the CVA. | CIP-005-3a | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The device is a dial-up access point used to restrict access and provide two-factor authentication for external interactive access to the ESP. In this instance, WECC_URE2 failed to conduct a CVA for one access point to an ESP. Specifically, the company hired a third-party vendor to conduct the CVA for WECC_URE2, but did not send the vendor the device number for the devices in question. Thus the vendor did not include the devices as part of its annual CVA. WECC_URE2 stated all Cyber Assets behind the device in scope were monitored and logged where technically feasible and required user name/password to access. Additionally, only a select number of individuals knew the dial-in number to the device and only someone with the number would be able to access it. However, WECC_URE2's failure to conduct a CVA could allow cyber vulnerabilities in such assets to go unchecked and undetected. Subsequently, such vulnerabilities could be exploited by malicious access to the Critical Cyber Assets (CCAs), providing an opportunity for unauthorized internal and/or external access, allowing successful cyber-attacks against CCAs essential to the operation of the BPS and disrupting the operation of the BPS. | when WECC_URE2 failed to conduct a CVA for the access point | Mitigation Plan completion | $50,000 (for WECC2012009818 WECC2012010700 WECC2013011896 WECC2013011897 and WECC2012010880) | Self-Certification | To mitigate this violation, WECC_URE2: 1) manually tested logical secure ports; 2) developed and instituted ongoing bimonthly dial-up testing process to ensure reporting of unauthorized access attempts; 3) conducted initial training and awareness regarding compliance instances to affected employees; 4) reviewed and updated CVA process; and 5) conducted annual CVA to test new process. | 2013-01-24 | 2014-01-24 | Agrees | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's voluntary corrective action to remediate this violation to be a mitigating factor. WECC determined WECC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011897 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP 005-3 R4. WECC determined that WECC_URE2, under its company's cyber security program, failed to review, update, and maintain documentation for dial-up access point devices. WECC_URE2 did not update the documentation to reflect the modification of the network or controls within ninety calendar days of the change, and did not retain electronic access logs for the devices because the devices were not included in the configurations and processes. | CIP-005-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 failed to review and maintain documentation to reflect the current configuration for one Critical Asset, an access point device to an ESP at a substation. Additionally, the device’s security controls were not included in the current configuration, and WECC_URE2 was not maintaining 90 days of logs that included the device. The device was intended to be used within WECC_URE2's secure network, but the configuration error could have allowed anyone with the number for the dial-up device to access the device itself, and the devices within the Electronic Security Perimeter (ESP). All devices behind the access point device were monitored and logged where technically feasible, and required a user name and password to access. Additionally, only a select number of individuals knew the dial-in number to the device and only someone with the number would be able to access it. | when WECC_URE2 failed to maintain logs | Mitigation Plan completion | $50,000 (for WECC2012009818 WECC2012010700 WECC2013011896 WECC2013011897 and WECC2012010880) | Self-Certification | To mitigate this violation, WECC_URE2 disconnected the remote access and ensured logging and authentication was enabled on the DG devices in scope. | 2013-07-16 | 2013-11-13 | Agrees | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's voluntary corrective action to remediate this violation to be a mitigating factor. WECC determined WECC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010880 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. WECC determined WECC_URE2 failed to establish, document, and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for numerous Cyber Assets within its Electronic Security Perimeters (ESPs). In addition, WECC_URE2 failed to evaluate a security patch for a Cyber Asset used to provide two-factor authentication for all interactive access into the ESP, within 30 days. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to implement its program for tracking, evaluating, testing, and installing cyber security software patches for numerous devices residing within ESPs. The devices are comprised of personal computers, printers, and servers of which 2 are Critical Cyber Assets (CCAs) and the others are non-CCAs that were residing within an ESP. The devices are used for hosting traffic monitoring software, 2-factor authentication on remote log-ins, CFE databases, general workstations, and printers. WECC_URE2's failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. WECC_URE2 stated all devices were logically behind restrictive boundary devices that monitored and logged all traffic into the network that helped minimize the risk. Additionally, all devices resided within PSPs where access was restricted to only those individuals with authorization, training, and PRAs. The devices in scope had all auto run/play capability disabled, anti-malware and virus prevention where technically feasible, and lastly no email accounts resided on the devices. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $50,000 (for WECC2012009818 WECC2012010700 WECC2013011896 WECC2013011897 and WECC2012010880) | Self-Report | To mitigate this violation, WECC_URE2: 1) issued device removal work orders for the majority of the devices; 2) submitted a technical feasibility exception for devices where patches cannot be applied; 3) finalized, released, and implemented a new procedure for all patches to monitor for the three remaining EMS Cyber Assets within the ESP in scope; and 4) renewed contract for available of security patches. | 2013-10-16 | 2014-04-11 | Agrees | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's voluntary corrective action to remediate this violation to be a mitigating factor. WECC determined WECC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012041 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-005-3a R3. WECC Enforcement determined WECC_URE3 was in violation of CIP-005-3a R3 because WECC_URE3 failed to log access for 80 network switches for 82 days and because WECC_URE3 failed to log access for 4 firewalls for 6 days. WECC Enforcement determined that the 84 access points were located across 26 Electronic Security Perimeters (ESPs) and 19 Physical Security Perimeters (PSPs). The root cause of the violation was WECC_URE3's reconfiguration of the network switches and firewalls during the transition from WECC_URE3's old network log servers to WECC_URE3's new network log servers and a change to the file names where the log messages were being stored. | CIP-005-3a | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, this failure exposed 17 Critical Assets to possible unauthorized access attempts for a period of 82 days. Although WECC_URE3 failed to log access at 84 access points, each of the devices were physically located within an identified PSP and were protected from unauthorized access through the use of Physical Access Control System (PACS). WECC_URE3's PACS only allow access to personnel who are trained, vetted, and authorized for such access. Further, the firewalls (which filter data transmission between ESPs) and switches (which provide data communication) in scope do not perform a monitoring function; they are configured to send data to the syslog servers where the monitoring is performed. WECC_URE3's intrusion detection system was monitoring all internal traffic during the 82 days that logging was not occurring, and no abnormal or suspicious activity was detected. | the first day WECC_URE3 failed to log access for the network switches | the first day WECC_URE3 logged access for the network switches | $40,000 (for WECC2013012041 and WECC2013012103) | Self-Certification | To mitigate this violation, WECC_URE3: 1) revised the security test plan form to include a log testing option that serves as a check to ensure verification of successful logging for future firmware/software upgrades, device configuration changes, or changes that might affect logging, any issues identified with logging will be flagged and corrected prior to the change being put into production (declared in service); 2) revised the NERC CIP implementation checklist to add a post-production logging verification which confirms that logging is functional; 3) revised the configuration change control quality assurance log to add a control for the independent reviewers to verify that the security test results include logging evidence; and 4) required training for subject matter experts on the new process and revised forms. | 9/30/2013 | 10/8/2013 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program and considered it to be a mitigating factor in the penalty determination. In addition to monetary penalties, to settle this matter, WECC_URE3 submitted to WECC, a summary of actions taken and improvements made to its change control program checklist that ensures WECC_URE3 follows all actions associated with the CIP Standards impacted by the change. The objective of implementing a change control checklist is to reduce human and technical errors associated with NERC CIP Reliability Standards.
2014-08-27 | FERC | NP14-49-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012103 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-005-3a R5. WECC Enforcement determined WECC_URE3 was in violation of CIP-005-3a R5.2 for failing to update its documentation to reflect the addition of energy management system (EMS) refresh equipment located at two locations within 90 calendar days of the change. The root cause of this violation was human error that led to a documentation mistake. | CIP-005-3a | R5; R5.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to update the addition of the EMS refresh equipment could have resulted in a failure to afford all the necessary CIP protections due to a detrimental reliance upon incomplete electronic access point availability data, increasing the vulnerability risk to harmful intrusions and malicious attacks into the ESP. Although WECC_URE3 failed to timely update its Electronic Security Perimeter (ESP) network documentation, it did update the documentation shortly after the 90-day period. Specifically, the documentation was updated 52 days beyond the 90-day requirement. The remaining configuration change control documentation was accurate. In addition, WECC_URE3's network has a host intrusion detection system and an access control process that restricts physical and logical access to only individuals with approved NERC CIP qualifications. Finally, all traffic to and from ESPs must pass through firewalls, which are configured to restrict, monitor, and alert upon suspected malicious activity. | 91 calendar days after the modification | the date WECC_URE3 updated its documentation to reflect the modification of the network or controls | $40,000 (for WECC2013012041 and WECC2013012103) | Compliance Audit | To mitigate this violation, WECC_URE3 updated its documentation to reflect the modification of the network or controls. | 9/27/2012 | 10/5/2012 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program and considered it to be a mitigating factor in the penalty determination. In addition to monetary penalties, to settle this matter, WECC_URE3 submitted to WECC, a summary of actions taken and improvements made to its change control program checklist that ensures WECC_URE3 follows all actions associated with the CIP Standards impacted by the change. The objective of implementing a change control checklist is to reduce human and technical errors associated with NERC CIP Reliability Standards.
2014-08-27 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011747 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R2. Specifically, RF determined that RFC_URE1 failed to implement strong procedural or technical controls at certain access points. RFC_URE1 previously interpreted the phrase in CIP-005 R2.4, “where external interactive access into the Electronic Security Perimeter [(ESP)] has been enabled,” such that the word “where” referred to an object or Cyber Asset, rather than the condition of enabling access. As a result of this interpretation, which RFC_URE1 believed was reasonable at that time, RFC_URE1 implemented CIP-005 R2.4 controls only for direct interactive access to the ESP access points. More specifically, RFC_URE1 enabled external interactive access into its ESPs by making modifications to the controls on its ESP access points. However, RFC_URE1 did not implement strong procedural and technical controls for all individuals who had external interactive access to a Cyber Asset within the ESP. As a result of RFC_URE1's revised interpretation of CIP-005-1 R2, which came as a result of industry and NERC guidance on the meaning of CIP-005-1 R2, RFC_URE1 discovered a total of 33 instances where RFC_URE1 enabled external interactive access into an ESP without implementing strong technical or procedural controls at the access points to ensure authenticity of the accessing party. RFC_URE1 determined that 32% of the indirect access hosts were at risk, which included access to the ESP from non-traditional environments and from administrative servers. | CIP-005-1 | R2; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, without implementing adequately strong technical or procedural controls to ensure authenticity of personnel accessing CCAs within an ESP through the ESP access point, the likelihood of unauthorized access to these CCAs was increased. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 considered it a security best practice to have controls for any individual who had external interactive access to a Cyber Asset within the ESP and, as such, implemented strong procedural or technical controls for several instances where external interactive access was allowed through the ESP access points. RFC_URE1 also had all other required controls relevant to CIP standards, including, for example, proper background checks, security awareness and training, patch management, security event monitoring, access control, recovery plans, and Cyber Vulnerability Assessments. RFC_URE1 monitors logs from cyber assets within ESPs and uses rules to trigger alerts related to unauthorized access attempts. RFC_URE1 stated there were no instances of unauthorized access to cyber assets within ESPs. No harm is known to have occurred. | when the Standard became mandatory and enforceable on RFC_URE1 | present | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Self-Report | To mitigate this violation, RFC_URE1 will: 1) determine the extent of the issue by analyzing each of the ESP access points to determine if external interactive access has been enabled into the ESP; 2) examine the technical or procedural controls where external interactive access has been enabled and determine whether strong technical or procedural controls have been implemented to ensure authenticity of the accessing party; 3) develop a strategy for implementing required technical and procedural controls at ESP access points, implement a process for new requests for external interactive access, implement proof of concept for technical and procedural controls, adjust technical and procedural controls as necessary based on lessons learned from the proof of concept, and complete implementation of strong technical and procedural controls for all instances of external interactive access through ESP access points; and 4) analyze intermediate servers and confirm a remediation plan, remove access from non-production servers, remediate remaining direct access and administrative servers, improve controls for the SSH keys used to strongly authenticate users, and remediate all remaining Cyber Assets. | 6/9/2015 (approved completion date) | TBD | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-08-27 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011720 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that t was in violation of CIP-005-3 R4. Specifically, RFC_URE1 failed to include all required components in its Cyber Vulnerability Assessments (CVA) of the electronic access points to the Electronic Security Perimeter (ESP). RFC_URE1 engaged a third party to conduct a review of CIP-005 R4. As a result of the third-party review, RFC_URE1 discovered two issues with CIP-005-3. First, while RFC_URE1 conducted ports and services scans at the management interface of the access points, RFC_URE1 did not scan the ports and services through the ESP access points. As a result, RFC_URE1 did not conduct a complete ports and services scan as required by CIP-005-3 R4.2. Second, RFC_URE1's review of default accounts, passwords, and network management community strings was based on a tool that uses a variety of plug-ins to identify default account use. Based on the limited effectiveness of the network port scan of the ESP access points discussed above, RFC_URE1 discovered that the plug-ins intended to review default accounts did not allow for the complete review of default account controls. As a result, RFC_URE1's review of controls for default accounts, passwords, and network management community strings was not comprehensive, as required by CIP-005-3 R4.4. | CIP-005-3 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically the deficiencies in RFC_URE1's CVAs increased the likelihood that unidentified vulnerabilities may have existed and could have been exploited. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, each ESP access point was protected within its own ESP, so RFC_URE1's ports and services scan was limited in its effectiveness. However, RFC_URE1 did conduct a review of these ports and services. Second, RFC_URE1's review of controls for default accounts, passwords, and network management community strings was not comprehensive, but RFC_URE1 did conduct a review of controls for default accounts, passwords, and network management community strings. Third, RFC_URE1 had in place technical controls such as network segmentation, security monitoring, and training and awareness that reduced the likelihood of the potential impact occurring. Fourth, RFC_URE1 monitors the log events from the ESP access points and has intrusion detection sensors deployed at most ESP access points and RFC_URE1 generates alarms from these systems. RFC_URE1 did not receive any alarms during the violation period indicating that a vulnerability was exploited related to ESP access points. No harm is known to have occurred. | the date RFC_URE1 was required to conduct the CVA | Mitigation Plan completion | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Self-Report | To mitigate this violation, RFC_URE1: 1) expanded the review of ports and services for CIP-005 R4 to include ports and services through the firewall; 2) expanded the review of default accounts, passwords, and network community strings for CIP-005 R4; 3) implemented technical device discovery to identify all Cyber Assets within ESPs; 4) reviewed all ports and services enabled on Cyber Assets with ESPs; 5) ensured that action plans and execution statuses are complete for the CVA; and 6) ensured that all individuals responsible for conducting the CVA worked on revising the CVA procedure. | 2012-12-31 | 2014-05-08 | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-08-27 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011718 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R8. Specifically, RFC_URE1 failed to include all required components in its Cyber Vulnerability Assessments (CVAs) for all Cyber Assets within the Electronic Security Perimeter (ESP). RFC_URE1 engaged a third party to conduct a review of CIP-007 R8. As a result of the third-party review, RFC_URE1 discovered three issues with CIP-007-3a R8. First, for the two prior year CVAs, RFC_URE1 relied on its list of Cyber Assets within the ESPs generated from its asset management system. RFC_URE1 did not perform a technical discovery of Cyber Assets within the ESP until the next CVA. At that time, RFC_URE1 discovered 12 Cyber Assets within ESPs that were not recorded on its list of Cyber Assets within the ESPs. Therefore, the Cyber Assets may not have been subject to the prior CVAs. Second, RFC_URE1 conducted a ports and services scan for all of the Cyber Assets within the ESP that support credentialed scans (66% of all Cyber Assets), but RFC_URE1 was only able to scan a portion of those Cyber Assets that did not support credentialed scans (34% of all Cyber Assets) because of technical limitations of the protocol on those devices. In addition, RFC_URE1 did not compare the ports and services identified to a baseline standard to determine what was authorized, but instead relied upon analyst judgment. As a result, RFC_URE1 did not conduct complete ports and services scans, as required by CIP-007-3a R8.2. Third, prior to the specific year, RFC_URE1 did not document action plans and track statuses for Cyber Assets with Windows and Unix/Linux systems as required by CIP-007-3a R8.4. | CIP-007-3a | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the deficiencies in RFC_URE1's CVAs increased the likelihood that unidentified vulnerabilities may have existed and could have been exploited. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 did conduct a review of these ports and services. Second, each ESP access point was protected within its own ESP, so RFC_URE1's ports and services scan was limited in its effectiveness. However, other ports that were enabled on the ESP access points were protected by the ESP access points’ own access control lists, which provided a high level of security. Second, RFC_URE1's review of controls for default accounts, passwords, and network management community strings was not comprehensive, but RFC_URE1 did conduct a review of controls for default accounts, passwords, and network management community strings. Third, RFC_URE1 had in place technical controls such as network segmentation, security monitoring, and training and awareness that reduced the likelihood of the potential impact occurring. Fourth, for its cyber assets within ESPs, RFC_URE1 uses two types of antivirus software, and intrusion detection systems to generate alarms. During this time, there were no alarms related to any vulnerabilities that were not identified in the CVA. No harm is known to have occurred. | the date RFC_URE1 was required to conduct the CVA | Mitigation Plan completion | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented technical device discovery to identify all Cyber Assets within ESPs; 2) reviewed all ports and services enabled on Cyber Assets with ESPs; 3) ensured that action plans and execution statuses are complete for the assessment; and 4) revised its CVA procedure. | 2012-12-31 | 2014-05-08 | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF considered RF_URE'1 compliance history to be an aggravating factor in the penalty determination.
2014-08-27 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012418 | Settlement Agreement | During a Compliance Audit, RF determined that RFC_URE1 was in violation of CIP-006-1 R1.8. Specifically, RFC_URE1 failed to afford protective measures to certain Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP). RFC_URE1 did not properly identify and protect certain physical access control systems (PACS), including 14 workstations and 11 door controllers, in accordance with CIP-006-1 R1.8 because RFC_URE1 previously did not consider the workstations and controllers as being subject to the standard. Specifically, the 14 workstations and 11 door controllers were not considered by RFC_URE1 to be Critical Cyber Assets (CCAs) and, therefore were not included on this CCA list at the time of the audit; however these devices were afforded security protections similar to those afforded RFC_URE1's Cyber Assets. However, the controllers perform the authentication functions of access control and log access in the event of server failure, and therefore require CIP-006-1 R1.8 protective measures. RFC_URE1 failed to afford the following protective measures to those assets: CIP-003, CIP-004 R3, CIP-005 R2, CIP-005 R3, CIP-006 R4, CIP-006 R5, CIP-007, CIP-008 and CIP-009. Additionally, access rights can be assigned and revoked from the workstations, therefore the workstations perform the authorization function of access control and require CIP-006-1 R1.8 protective measures. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the risk is moderate as the Cyber Assets could be compromised, allowing unauthorized physical access to RFC_URE1's PSPs and Critical Cyber Assets (CCAs). The risk posed by the foregoing facts and circumstances was mitigated by the fact that RFC_URE1 implemented the following physical and electronic controls. First, RFC_URE1 has 24-hour closed-circuit television monitoring of the RFC_URE1 campus and PSP locations, including 90 days of recording capabilities, and investigations of physical security events by security personnel. Second, RFC_URE1 campus security officers regularly perform physical inspections of the RFC_URE1 campus and PSP locations. Third, the PACS Cyber Assets, including workstations and controllers, are protected from unauthorized physical access pursuant to CIP-006-3c R2.1. Fourth, RFC_URE1 has visitor and escorted personnel tracking in place, including maintaining and reviewing visitor log books and video surveillance of the entire campus and PSP areas. Fifth, to ensure that only authorized personnel access PSP areas, RFC_URE1 utilizes fingerprint readers in addition to keycard readers. At two locations, RFC_URE1 has implemented two-factor physical access control at all PSP access points. Sixth, data traffic is passed between the host PACS server and the controllers using symmetric encryption. Seventh, to prevent damage and any unauthorized access, the controllers are located within protected areas and further protected by alarmed key locks that send alarm signals to the central monitoring station when opened. Eighth, the PACS Cyber Assets, including workstations and controllers, are on segmented virtual local area networks, which limit electronic access. Finally, RFC_URE1 would periodically log inadvertent failed access attempts into the PSP area; however, none of these attempts were ever categorized by RFC_URE1 as being “malicious” or being done with what would be considered “bad intentions.” No harm is known to have occurred. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Compliance Audit | To mitigate this violation, RFC_URE1: 1) deployed new Windows servers in two Electronic Security Perimeters and installed C*Cure client on those servers; 2) configured the server access for authorized individuals, ensuring strong authentication, and provided CIP-006-3c R2.2 protective measures for the workstations; 3) implemented security measures to address protections specified in CIP-006-3c R2.2 requirements for three workstations; 4) submitted Technical Feasibility Exceptions as required; and 5) deleted or uninstalled the requisite software from the workstations and laptops. | 2014-04-22 | TBD | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-08-27 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011748 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R1. Specifically, RFC_URE1 failed to implement its cyber security test procedures. RFC_URE1 has in place documented test procedures for Cyber Assets which state that RFC_URE1 must perform test procedures on a comparable Cyber Asset (an asset which resides outside the Electronic Security Perimeter (ESP) and reflects the configuration of the Cyber Asset within the ESP) prior to the implementation of a significant change to a Cyber Asset within the ESP. RFC_URE1 failed to follow its documented test procedures for four instances of significant changes within an ESP. First, RFC_URE1 implemented a change on a non-critical Cyber Asset within an ESP to resolve an operational issue with security scanning software that was installed on that Cyber Asset. A technician attempting to remediate an issue with the existing software version installed a prior version of that software without conducting test procedures on a comparable Cyber Asset. Upon learning of this change, RFC_URE1 conducted test procedures on the Cyber Asset and verified that no degradation of cyber security controls occurred. Second, for nine separate Critical Cyber Asset (CCA) workstations, the software provisioning process detected the absence of third-party software and subsequently installed the software automatically. As a result, RFC_URE1 did not conduct test procedures on a comparable Cyber Asset. Upon learning of the change, RFC_URE1 conducted test procedures and verified that no degradation of cyber security controls occurred. Third, RFC_URE1 implemented a change on a non-critical Cyber Asset within an ESP to complete the implementation of a service pack for an existing operating system installed on the Cyber Asset. The system administrator handling the change did not conduct test procedures on a comparable Cyber Asset. RFC_URE1 immediately realized the error, and within a few hours of installation, RFC_URE1 conducted test procedures on the Cyber Asset and verified that there were no adverse effects on the existing cyber security controls. Fourth, RFC_URE1 implemented a change on a CCA to install two security patches which did not take effect until three days after the change was implemented. The system administrator handling the change did not conduct test procedures on a comparable Cyber Asset because the system administrator inadvertently included the CCA in a collection of non-CIP assets. Within 24 hours of RFC_URE1 installing the security patches, RFC_URE1's change detection and reconciliation process identified the issue. RFC_URE1 conducted test procedures on the CCA and verified that no degradation of cybersecurity controls occurred. | CIP-007-3a | R1; R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the risk is moderate as a system administrator may inadvertently make a significant change without following the required test procedures. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, in all cases, RFC_URE1 conducted test procedures within a short time period after discovering the issue. Second, RFC_URE1 implemented detective controls such as daily compliance scans, which were in place prior to the violation, which run the installation of Windows, AIX and Linux operating systems. The daily compliance scans were used to verify the state of cyber security controls on Cyber Assets. These scans help identify any degradation of cybersecurity controls within 24 hours. Third, RFC_URE1 completed the test procedures on all the Cyber Asset where a significant change was inadvertently deployed. The test procedures showed that the no security controls were degraded as result of the inadvertent changes. No harm is known to have occurred. | when the first instance of noncompliance occurred | Mitigation Plan completion | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Self-Report | To mitigate this violation, RFC_URE1: 1) completed and documented cyber security test procedures on the affected Cyber Assets, prevented automated software provisioning, and verified that no degradation of cyber security controls had occurred; 2) established and documented procedural controls to address instances where inadvertent significant changes are made on assets that were subject to compliance with the Standard; 3) required team members from platform operations and reliability services team of client computing services department to attest to the reading and understanding of RFC_URE1's cyber security test procedures relevant to the technologies they support; 4) implemented a technical control which prevents the automated provisioning of software to Cyber Assets in the ESP that run Windows Vista; and 5) required team members from the reliability services team of client computing services department to attest to reading and understanding RFC_URE1's desktop imaging procedure for dispatch. | 2013-05-08 | 2014-05-07 | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF considered RF_URE'1 compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011724 | Settlement Agreement | RFC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R4. Specifically, RFC_URE1 failed on two instances to use anti-virus and other malicious software prevention tools on certain Cyber Assets within the Electronic Security Perimeter (ESP). First, RFC_URE1 discovered operational issues with the use of the anti-virus software installed on 16.7% Cyber Assets within an ESP that diminished RFC_URE1's ability to detect, prevent, deter, or mitigate the introduction, exposure, and propagation of malware on these Cyber Assets. The operational issues, which occurred for approximately ten months, were related to the configuration of a service account upon which the anti-virus software relies to communicate with the affected Cyber Assets. In addition, there were eight Cyber Assets that were affected by different operational issues with the same anti-virus software that were unrelated to the configuration of the service account. RFC_URE1 uses a detective control to help ensure the reliable operation of the anti-virus software. This detective control consists of third-party software to monitor the configuration of the anti-virus software on each Cyber Asset. Upon identifying the operational issues with the anti-virus software, RFC_URE1 investigated why the detective control failed and determined that the control was not accurately reporting the anti-virus software status due to a flaw in the logic used to validate the anti-virus software configuration. Once RFC_URE1 discovered this issue, it analyzed the Cyber Assets and determined that no malware existed on these Cyber Assets. Second, RFC_URE1 discovered that anti-virus software was inadvertently uninstalled from two Critical Cyber Assets (CCAs) within RFC_URE1's identified ESP. A system administrator had queried RFC_URE1's CCA list by only one of the CCAs’ two alias names. The two CCAs were represented on the list by another alias name. As a result, RFC_URE1 did not conduct anti-virus and malware prevention for these two CCAs. | CIP-007-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the availability, integrity, or confidentiality of one or more Cyber Assets could have been affected if malicious software was introduced during the relatively lengthy duration of this violation. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Malicious software prevention serves two purposes: the protection of individual Cyber Assets and the prevention of malicious software propagation to other Cyber Assets. The likelihood of a Cyber Asset being compromised was lower due to the type of operating system installed and the absence of general purpose computing functionality on the affected Cyber Assets. Either AIX or Linux operating systems were installed on each of the affected Cyber Assets. Both of these operating systems have a lower number of known malware items compared to other operating systems, including, for example, Microsoft Windows. While not entirely immune from malicious software, these operating system platforms more frequently serve as propagation mechanisms rather than targets for malicious software attacks. The affected Cyber Assets were not configured or utilized as mail servers or general purpose file or print servers. These types of general purpose computing functions would increase the risk of propagation of malicious software. Therefore, the likelihood of the affected Cyber Assets being used to propagate malicious software to other appropriately configured Cyber Assets was decreased. No harm is known to have occurred. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2013011747, RFC2013011720, RFC2013011718, RFC2013012418, RFC2013011748, and RFC2013011724) | Self-Report | To mitigate this violation, RFC_URE1: 1) reinstalled anti-virus software on the two CCAs at issue, and reviewed and updated its compliance reporting system to ensure the accuracy of anti-virus software information being reported for Cyber Assets with AIX or Linux operating systems; 2) implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality; and 3) ensured the operational effectiveness of anti-virus software, and updated its approved TFE. | 2013-01-31 | 2014-02-10 | Admits | RF determined that a monetary penalty is not warranted for the violations. RF based this determination on the factors set forth below. RF’s penalty determination was in part based on RFC_URE1's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RF is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1's discovery of the Self-Reported violations and response to the Compliance Audit finding is behavior that RF seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. RF also considered the nature of the violations. As a mitigating factor in the penalty determination, RF considered that the violations do not represent a systemic compliance performance failure. Although there are six violations at issue in this Agreement, the causes are not the same for all of the violations, and the violations are not necessarily related to one another. For example, certain of the violations resulted from a failure to implement RFC_URE1's documented procedures (CIP-007 R1 and R5), and certain of the violations resulted from an incorrect interpretation of the Requirement (CIP-005 R2), or software issues (CIP-007 R4). Accordingly, the violations do not appear to be related to one another and are not indicative of a systemic compliance performance failure by RFC_URE1. Instead, the violations largely indicate sporadic deficiencies caught by RFC_URE1's robust internal controls. Where RFC_URE1's internal controls did not result in its swift discovery of the violation, RFC_URE1 has committed to strengthen those internal controls through its mitigating actions. RFC_URE1 implemented technical and procedural controls and control enhancements targeted toward preventing reoccurrence of the circumstances that caused the violations. RFC_URE1 also revised certain governing procedures and processes. For example, with respect to CIP-005-3 R2, RFC_URE1 updated its existing process to ensure that strong procedural and technical controls are implemented prior to enabling any new interactive access to the ESP. With respect to CIP-005 R4 and CIP-007-3 R8 issues, RFC_URE1 committed to update its Cyber Vulnerability Assessment Procedure to ensure that annual vulnerability assessments consistently achieve the assessment objectives. Also, with respect to CIP-007 R4, RFC_URE1 committed to revise its compliance reporting system to ensure accuracy of anti-virus software information being reported for certain Cyber Assets and also implemented a request process to resolve operational issues identified with the implementation of anti-virus software functionality. RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF considered RF_URE'1 compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013345 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R1.6. SERC_URE1 failed to follow its visitor control program in three separate instances, and left unauthorized personnel inside the Physical Security Perimeter (PSP) unescorted. In the first instance SERC_URE1 security personnel discovered that a security guard had escorted two contract employees into a PSP and then left them unattended within the PSP for approximately 50 minutes. The security guard incorrectly believed that one of the contract employees had authorized unescorted access rights but that the individual’s badge was inoperable. In the second instance a visiting SERC_URE1 employee was escorted into a PSP for a meeting. At the end of the meeting, SERC_URE1 employees forgot to escort the visiting employee out of the PSP. The then unescorted visiting employee attempted to leave the PSP by swiping his badge at the PSP exit door card reader. However, the visiting employee did not have authorized unescorted access rights, and the badge reader failed to operate the door lock to allow the visiting employee to exit. The visiting employee then pressed the exit bar on the PSP door to leave the PSP, generating a "forced open" alarm. This alarm led SERC_URE1 to discover this instance of the violation. The employee was left unescorted for approximately five minutes, the time it took to get from the conference room to the exit door of the PSP. While investigating the second instance, SERC_URE1 discovered a third instance where a visitor was unescorted. A contract employee was escorted into a PSP for a meeting and then left the meeting unescorted. An SERC_URE1 employee with authorized unescorted access rights discovered the contract employee and escorted the contract employee back to his original escort. After the meeting ended, the escort escorted the contract employee out of the PSP. The original escort left the contract employee unescorted for approximately 28 minutes. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In all three instances, the Critical Cyber Assets (CCAs) within the PSPs require user names and passwords in order to gain access and have alarms to alert security personnel in the event of multiple failed login attempts. SERC_URE1 did not receive any alarms for failed login attempts to the affected Cyber Assets during the violation. Additionally, in the first instance, the video log review showed that the contract employees did not access or approach any of the protected Cyber Assets within the PSP. The one contractor left unattended had a current personnel risk assessment and cyber security training, but had not been approved for access at the time of this occurrence. This particular PSP contained Electronic Access Control and Monitoring and Physical Access Control Systems devices, but no CCAs were within this established PSP. SERC_URE1 personnel also monitor the PSP with security cameras 24 hours a day, 7 days a week. | when the SERC_URE1 contract employee who was unauthorized for unescorted access left a meeting inside a PSP without being escorted when two contract employees were left unescorted within a PSP by an SERC_URE1 security guard when the SERC_URE1 employee who was unauthorized for unescorted access was left unescorted inside the PSP | when the SERC_URE1 contract employee who was unauthorized for unescorted access was returned to his assigned escort when the two contract employees were escorted out of the PSP by SERC_URE1 security personnel when the SERC_URE1 employee who was unauthorized for unescorted access left the PSP | $0 | Self-Report | To mitigate this violation, SERC_URE1: 1) removed the contracted security officer involved in this violation from SERC_URE1’s account; 2) sent a NERC protected areas unescorted access advisory to all vice presidents, directors, and supervisors with direct reports with unescorted access to PSPs, reminding them of their escorting responsibilities in PSPs; 3) reviewed the procedure for escorting personnel into a PSP with all security officers with escorting responsibility in PSPs and had them sign a confirmation that they understood the procedure. | 1/7/2014 | 2014-05-02 | Admits | SERC reviewed SERC_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE1 completed or will complete the following above and beyond action, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE1 has agreed to not hold meetings with more than three individuals who require escorted access within its PSPs that contain conference rooms. Escorted tours of the PSPs in question will still be permitted. SERC considered SERC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013013041 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3c R8. SERC_URE2 improperly replaced a Physical Security Perimeter (PSP) access point key core and failed to properly maintain documentation of the change in accordance with its physical security plan. SERC determined that this violation was more appropriately addressed as a CIP-006-3c R4 violation for failure to implement the operational and procedural controls to manage physical access at all access points to the PSP. SERC_URE2 discovered that the standard restricted key core for an access point to a PSP had been replaced with a less restricted key core despite control requirements for the more restrictive core. SERC_URE2 determined that the key core had been changed during repair work on the door. There were 31 keys that could open the new restricted key core, 27 of which were assigned to individual employees and contractors, and four of which were held by corporate security in workplace violence kits and secured in locked safes monitored by an intrusion detection system. While the new restricted key core was installed on the PSP door, none of the four workplace violence keys were accessed or removed from the locked safes. Of the 27 individual key holders, 12 had been authorized for access to the PSP in question, had current personnel risk assessments (PRAs), and had received their annual cyber security training. For the remaining 15 key holders, eight had current PRAs and annual cyber security training but were not authorized for access to the PSP in question for the entire duration of the violation, while seven did not have both a current PRA and annual cyber security training and were not authorized to access to PSP in question. SERC_URE2 had inspected the PSP door in question in 2011 and 2012 after the key core had been changed but did not discover the less restricted key core. During a site inspection, SERC_URE2 discovered the wrong key core and took immediate actions to remediate the issue. SERC_URE2 did not discover the changed key core earlier because its testing in 2011 and 2012 involved bypassing the key core using a plastic barrier in the lock housing and then pulling the door open without proper badge presentation. This action generated a forced entry alarm as desired, but SERC_URE2 did not also test whether opening the door using the standard key worked and if it generated a forced entry alarm as would be expected. Upon discovery, SERC_URE2 posted a security guard at the door, and the door remained under constant human observation until the less restricted key core was replaced with the proper restricted key core. | CIP-006-3c | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The affected door would issue an alarm to on-site security personnel if an override key was used to access the PSP. None of the individuals with keys for the new restricted key core knew that the keys would give them access to the control center PSP and none of the individuals used the keys to gain access to the PSP. The PSP protected a control center that was staffed 24 hours a day, seven days a week and had on-site security that made regular patrols. | when SERC_URE2 replaced the existing restricted key core with a less restricted key core | when the inappropriate key core was discovered and the access point was secured by a security officer | 10000 | Self-Report | To mitigate this violation, SERC_URE2: 1) conducted retraining that addressed the process for maintaining documentation of changes of any physical security system redesign or reconfiguration for all personnel performing maintenance on doors at PSPs; 2) disseminated an awareness message regarding this issue to all operating company facility operations personnel to reinforce security and compliance regarding this issue; and 3) verified that all PSP access points equipped with controlled physical key locks are configured to only allow use of the proper controlled physical key. | 2013-11-15 | 2014-03-20 | Admits | SERC reviewed SERC_URE2 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC determined that SERC_URE2's compliance history should not serve as a basis for aggravating the penalty.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012524 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it was in violation of CIP-007-3a R3. Specifically, non-critical Cyber Assets that reside within SPPRE_URE1’s Electronic Security Perimeters (ESPs) were not included in its security patch management program. SPPRE_URE1 did not consider the switches to be Cyber Assets because they were originally non-programmable, however when SPPRE_URE1 installed an upgrade, the switches became programmable to routable switches. After the upgrade, SPPRE_URE1 failed to include them in its security patch management program. Therefore, patches had not been assessed and implemented. In addition, SPPRE_URE1 was unable to locate documentation of implementation of its patch management program for a period of time; therefore, it could not demonstrate its patch management program was properly implemented during this time frame. In the same Self-Report, SPPRE_URE1 reported a possible violation of CIP-007-3a R3.1 because it identified instances where a security patch or security upgrade for its Supervisory Control and Data Acquisition (SCADA) system may not have been assessed for applicability with thirty calendar days of availability because SPPRE_URE1 relied on its SCADA vendor to perform patch assessments. | CIP-007-3a | R3; R3.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 immediately upon discovery of the issue assessed and applied security patches and security upgrades to the devices. Furthermore, electronic access to the devices layer-2 switches is relegated to IT system administrators, and SPPRE_URE1 utilizes security monitoring analysis and response systems and system performance software to continuously monitor and alert for malicious activity. Additionally, SPPRE_URE1’s change management program has robust internal controls. Management has to approve changes prior to implementation and the CIP senior manager monitors all significant changes in real-time throughout the change management process. The potential harm to the SPPRE_URE1 system would be minimal because the devices were not critical to SPPRE_URE1's operations. | when SPPRE_URE1 did not have documentation of implementing its patch management program | present | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report | To mitigate this violation, SPPRE_URE1: 1) assessed and implemented patches on the devices; and 2) began performing all patch assessments for its SCADA system rather than relying on its vendor. In addition, SPPRE_URE1 will: 2) incorporate the patch management process into its automated change management tool; and, 3) train affected SPPRE_URE1 personnel on the revised change management process and the automated change management tool. | 10/22/2014 (approved completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012526 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had a violation of CIP-007-3 R5 (R5.1.2, R5.2.3, R5.3.1, R5.3.2). SPPRE_URE1 did not have documentation of all user activity for devices located within its Electronic Security Perimeters (ESPs). Specifically, user activity was not logged with sufficient detail as required by R5.1.2, and the shared account activity did not have an audit trail of account use as required by R5.2.3. Additionally, the devices were unable to enforce complex passwords per R5.3.1 and R5.3.2, and a Technical Feasibility Exception (TFE) had not been requested. Subsequently, during a Compliance Audit SPP RE determined that SPPRE_URE1 was in violation of CIP-007-3 R5.3.3. Specifically, five Cyber Asset account passwords had not been changed on an annual basis. | CIP-007-3 | R5; R5.1.2; R5.2.3; R5.3.1; R5.3.2; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the devices, the lack of sufficient detail in the audit trail logs reduces SPPRE_URE1’s ability to maintain awareness of and accountability for the use of accounts, which might inhibit SPPRE_URE1’s ability to respond to the misuse of these accounts. Because the passwords for the devices do not meet the CIP complexity requirements, there is a chance that the accounts could be compromised. However, the passwords were changed immediately upon discovery, and access is relegated only to energy management system (EMS) and Supervisory Control and Data Acquisition administrators. By not changing the five Cyber Asset account passwords annually, there is a risk that a compromise of the Cyber Assets could occur. However, the Cyber Assets are electronically protected by a network firewall and up-to-date anti-virus software. Furthermore, SPPRE_URE1 changed the passwords immediately following the review of its Cyber Vulnerability Assessment (CVA). The five devices and the Cyber Assets are located inside SPPRE_URE1 ESPs and Physical Security Perimeters. Access to the devices and the Cyber Assets is limited to individuals with authorized electronic and/or physical access rights. Additionally, SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity. | when the password for the EMS switches should have been changed | Mitigation Plan completion | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) immediately changed the five Cyber Asset passwords; 2) applied for a TFE for the device passwords because they cannot meet the CIP complexity requirements; 3) implemented tools for maintaining electronic audit trails for the devices shared account; 4) implemented tools for maintaining electronic records of account activities that enable tracking and notification of password aging; and, 5) implemented revised procedures for account management for the devices and annual password changes for the five Cyber Assets. | 2014-04-25 | 2014-06-02 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SSPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013028 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had a violation of CIP-005-3 R1.5. Specifically, Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeters (ESPs) were not afforded the protective measures as specified in CIP-007-3 R5. Specifically, SPPRE_URE1’s security event and incident manager (SEIM) server, used to monitor and log access at electronic access points to the ESPs, did not have an up to date user account list. The list did not include system accounts. Also, shared accounts were not documented properly. Subsequently, during a Compliance Audit SPP RE determined that SPPRE_URE1 could not demonstrate that all Cyber Assets that perform electronic access control and monitoring (EACM) of the ESPs were compliant with CIP-007-3 R1.1 because SPPRE_URE1 did not have documented cyber security test procedures to ensure new or significant changes to existing EACM Cyber Assets did not adversely affect cyber security controls; CIP-007-3 R5.3.3 because SPPRE_URE1 did not have evidence that the EACM devices’ passwords were changed on an annual basis; and CIP-007-3 R6 because, for two firewalls that serve as ESP access points, SPPRE_URE1 did not implement automated tools or organizational process controls to monitor system events during the times that the logs are not captured. | CIP-005-3 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. By not having a complete user account list that included system accounts (R5), and not changing the five passwords annually (R5.3.3), SPPRE_URE1 creates the risk that compromise of the user and system accounts might occur; thereby, a compromise of the SEIM server. However, SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity; therefore, the risk is minimal. Additionally, where technically feasible, SPPRE_URE1 exceeds the complex password minimum that is required by the Standard. Although SPPRE_URE1 did not have documented cyber security test procedures (CIP-007-3 R1.1), SPPRE_URE1 stated how it performed functional security testing and gave detailed examples of how cyber security testing was performed. SPPRE_URE1’s assertion was consistent with its change control and configuration management program for performing security testing prior to the deployment of a Cyber Asset or changes to its production environment. This indicates that SPPRE_URE1 performed cyber security testing, albeit not properly documented, and performed cyber security testing in a manner that minimized adverse effects on the production system or its operation. Regarding CIP-007-3 R6, the violation only occurred during a brief period of time when the device was not in service or during SPPRE_URE1’s cyber security incident annual testing. SPPRE_URE1 had implemented automated tools and organizational processes to monitor cyber security system events for all its other Cyber Assets. Access to SPPRE_URE1’s Physical Security Perimeters (PSPs) is restricted to personnel with approved personnel risk assessments and cyber security training and is monitored 24 hours a day, seven days a week by security cameras. Additionally, SPPRE_URE1’s change management program has robust internal controls. Management has to approve changes prior to implementation and the CIP senior manager monitors all significant changes in real-time throughout the change management process. | when the Mitigation Plan was completed for the prior CIP-007-1 R6 violation | present | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) trained affected personnel on the controls and tools to document and verify event security monitoring for all Cyber Assets within the ESPs; 2) created formal cyber security test procedures and trained affected personnel on the new procedures; 3) immediately changed the five EACM passwords; and 4) implemented a new password policy and trained affected personnel on the new policy. In addition, SPPRE_URE1 will: 1) conduct a review of the SIEM accounts and ensure the users with those accounts are consistent with roles and responsibilities; 2) update the SEIM master access list; 3) train employees who maintain the SEIM master access list to ensure that the list is properly maintained; 4) implement system event monitoring for all Cyber Assets within the ESPs and verify the controls are logging properly; and 5) implement tools for reviewing and maintaining system event logs related to cyber security. | 1/15/2015 (approved completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013040 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had a violation of CIP-005-3 R3.2. Specifically, SPPRE_URE1’s firewall security monitoring processes were not configured to capture all Electronic Security Perimeter (ESP) access activity. Specifically, the logging configuration set for the firewalls was not adequate to provide sufficient detail to create an alert. Subsequently, during a Compliance Audit SPP RE determined that SPPRE_URE1’s logging and monitoring security process for electronic access control and monitoring (EACM) access points to its ESPs was not operational 24 hours a day, seven days a week. Specifically, SPPRE_URE1 did not implement automated tools or organizational process controls to monitor all system events related to two firewalls on its backup system that serve as access points to the ESP, nor did it implement a manual process to review the system logs. | CIP-005-3 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to monitor and log electronic access in both CIP-005-3 R3.2 instances could have decreased SPPRE_URE1’s ability to prevent and/or detect a compromise of Cyber Assets within its ESPs. However, the firewalls are located on SPPRE_URE1’s ICCP links and only talk over one corporate network port. All other ports are closed. Logical access to the firewalls must be made from within SPPRE_URE1’s Physical Security Perimeters (PSPs). For the two firewalls that serve as EACM devices, the violation occurred during a brief period of time, when the backup server was running and the server was not in service or during SPPRE_URE1’s annual cyber security incident testing. SPPRE_URE1 had implemented automated tools and organizational processes to monitor cyber security system events for all other SPPRE_URE1 Cyber Assets. Additionally, during the brief period of time SPPRE_URE1 failed to review the logs, the systems within SPPRE_URE1’s ESPs are completely disconnected from other network sources and once the connection is restored, software agents on most of the affected devices will restore missing logs, so the only lost data is from a limited set of devices. Lastly, access is restricted to personnel with approved personnel risk assessments and cyber security training, and SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity. | when the Mitigation Plan was completed for the prior CIP-005-1 R3 violation | present | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1 will: 1) correct logging configurations on the firewalls; 2) implement security logging processes of successful and unsuccessful attempts to all access points of the ESPs or apply for a Technical Feasibility Exception; 3) implement monitoring of unauthorized access attempts; and, 4) implement technology and procedural methods to provide redundancy to the security event and incident monitoring server and two firewalls to capture logs when the server is down and during the annual cyber security incident testing. | 10/22/2014 (approved completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013042 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPPRE_URE1 was in violation of CIP-005-3 R2, inclusive of R2.2 and R2.4. SPPRE_URE1 was found in violation of CIP-005-3 R2.2 because at access points to its Electronic Security Perimeters (ESPs), SPPRE_URE1 had enabled ports and services not required for operations and/or monitoring of Cyber Assets within the ESPs. Specifically, SPPRE_URE1 enabled ports and services not required for operations and/or monitoring on two access points; one access point controlled access to SPPRE_URE1’s primary ESP, and the other controlled access to SPPRE_URE1’s secondary ESP. SPPRE_URE1 did not have the open ports and services identified in its baseline, and it attested that the ports were enabled for future use. Additionally, SPP RE determined that SPPRE_URE1 had a violation of CIP-005-3 R2.4 because where external (i.e. inter-zone) interactive access between a non-ESP zone and an ESP zone within the SPPRE_URE1 system had been enabled, SPPRE_URE1 had not implemented strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. SPPRE_URE1 attested it does not allow external interactive access between its non-ESP and ESP zones; however, SPPRE_URE1 had enabled rules, i.e. permissions, which allowed access between the two zones via encrypted telecommunications. The two zones are not accessible outside of the SPPRE_URE1 corporate network. | CIP-005-3a | R2; R2.2; R2.4 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Regarding the CIP-005-3 R2.2 violation, the unnecessary ports and services enabled at two access points to the ESPs could have been compromised from the outside. However, the devices inside SPPRE_URE1’s ESPs were protected by up to date antivirus software and malware. Additionally, SPPRE_URE1’s ESPs are monitored by an intrusion prevention system that has the ability to alert SPPRE_URE1 staff of malicious traffic. SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity. Regarding the CIP-005-3 R2.4 violation, by allowing interactive access between the non-ESP and ESP zones, SPPRE_URE1 made its system more vulnerable to compromise by an intruder with malicious intent. However, the access between the two zones is minimal and utilizes strong, cryptographic methods to protect the traffic integrity and confidentiality. Both zones are under the complete control and exclusive use of approved SPPRE_URE1 personnel and no other access is permitted. Lastly, both zones are located within SPPRE_URE1’s Physical Security Perimeters (PSPs) that are monitored 24 hours a day, seven days a week by security cameras, and PSP access is restricted to personnel with approved personnel risk assessments and cyber security training. | when the Mitigation Plan for the prior CIP-005-1 R2 violation was completed | present | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Compliance Audit | To mitigate this violation, SPPRE_URE1 will: 1) eliminate the use of ports and services not required for operations and monitoring of Cyber Assets; 2) identify requirement for remote interactive access into SPPRE_URE1’s ESPs and changing rules to deny access if necessary; and 3) define and document the procedures for implementing controls for inter-zone access. | 10/22/2014 (approved completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013044 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had a violation of CIP-006-1 R1.8 because its Physical Access Control System (PACS) was not reviewed in the Cyber Vulnerability Assessments (CVAs) as required in CIP-007-2 R8. Additionally, the PACS server did not have an up to date user account list as specified in CIP-007-3 R5. Specifically, the PACS server user account list did not include all system accounts. Subsequently, during a Compliance Audit SPP RE determined that SPPRE_URE1 did not identify its Physical Security Perimeter (PSP) door control panels as PACS Cyber Assets. Specifically, SPPRE_URE1 could not demonstrate that the PACS door panels were compliant with CIP-007-3 R1.1 because SPPRE_URE1 did not have documented cyber security test procedures to ensure new or significant changes to existing PACS devices did not adversely affect cyber security controls; CIP-007-3 R2 because SPPRE_URE1 did not provide evidence that its documented process included an assessment of services not associated with a logical port for PACS devices; and CIP-007-3 R5.3.3 because SPPRE_URE1 did not have evidence that the PACS devices’ passwords were changed on an annual basis. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1’s failure to afford several of the required protective measures to its Cyber Assets that monitor its PSPs could have led to a decrease in SPPRE_URE1’s ability to prevent and/or detect a compromise of its PSPs access points. However, SPPRE_URE1 had protective measures implemented during the violation period that mitigated the risk. Regarding CIP-007-3 R8 SPPRE_URE1 properly identified vulnerabilities and created corrective action plans for vulnerabilities that were identified. In addition, the PACS server resides within SPPRE_URE1’s PSPs, has up to date antivirus software, and electronic access to the server and the PACS application is controlled via assigned user-names and passwords. Also, access to the PACS server is limited to IT administrators with authorized electronic and physical access rights. Regarding CIP-007-3 R5, not having a complete user account list creates the risk that a compromise of the system accounts might occur; thereby, a compromise of the PACS server. However, SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity; therefore, the risk is minimal. Additionally, where technically feasible, SPPRE_URE1 exceeds the complex password minimum that is required by the standard. Regarding the PACS door control panels that were not identified as Cyber Assets, each of the panels resides in a locked cabinet within a PSP. Also, access to the PACS panels is limited to individuals with authorized electronic and physical access rights. The PACS panels also have tamper alarms that alert SPPRE_URE1 personnel of any unauthorized access attempts to the panels. SPPRE_URE1 has additional internal controls in place to mitigate the risk as discussed in the following: Regarding CIP-007-3 R1.1, SPPRE_URE1’s lack of formal cyber security test procedures to ensure new or significant changes to the PACS server decreases SPPRE_URE1’s ability to ensure that its cyber security test procedures are being conducted in accordance with procedural requirements. SPPRE_URE1 stated how it performed functional security testing to the SPP RE Audit Team and gave detailed examples of how cyber security testing was performed. SPPRE_URE1’s statements and examples demonstrate that SPPRE_URE1 performed proper cyber security testing, albeit not completely documented, in a manner that minimized adverse effects on the production system or its operation; and that SPPRE_URE1 followed its change control and configuration management process when performing its security testing prior to the deployment of a Cyber Asset or a change to its production environment. Regarding CIP-007-3 R2, SPPRE_URE1’s lack of evidence demonstrating that its documented process included an assessment of local services for the PACS servers creates a risk that one or more of the local services might be compromised. However, the risk was mitigated because access to the PACS system is limited to individuals with authorized electronic and/or physical access rights. Additionally, SPPRE_URE1 utilizes security monitoring analysis and response systems and system performance software to continuously monitor and alert for malicious activity. Regarding CIP-007-3 R5.3.3, the failure to change the PACS server passwords annually increases the risk that the PACS system might be compromised. However, SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity. In addition, where technically feasible, SPPRE_URE1 exceeds the complex password minimum that is required by the standard. Additionally, SPPRE_URE1’s PACS is electronically protected by a network firewall and up to date anti-virus software. Moreover, SPPRE_URE1’s change management program has robust internal controls. Management has to approve changes prior to implementation and the CIP senior manager monitors all significant changes in real-time throughout the change management process. | when the standard became mandatory and enforceable on SPPRE_URE1 | present | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1 will: 1) perform an analysis to investigate the PACS panel capabilities to meet compliance with CIP-006-2 R2.2; 2) apply for a TFE if the PACS panels do not have the capability to meet compliance with any of the requirements; 3) complete any network redesign to place PACS panels behind an ESP-like environment; 4) implement security event monitoring for all PACS server Cyber Assets and verify that the security monitoring controls are logging properly; 5) implement tools for maintaining and reviewing logs of system events related to cyber security; and, 6) train affected personnel on the controls and tools to document and verify event security monitoring for the PACS server and PACS panels. | approved completion date | TBD | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013045 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it was in violation of CIP-007-3 R1.3. Specifically, SPPRE_URE1’s change management process was not consistently followed; therefore, all required test result documentation could not be located for a period of time when SPPRE_URE1 converted to an automated change management process. Subsequently, during a Compliance Audit SPP RE determined that for a period of time, SPPRE_URE1 did not have formal, documented cyber security test procedures to ensure new or significant changes to existing Cyber Assets within its Electronic Security Perimeters (ESPs) did not adversely affect cyber security controls. | CIP-007-1 | R1; R1.1; R1.3 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the CIP-007-3 R1.3 and CIP-007-1 R1.1 violations, SPPRE_URE1 stated how it performed cyber security testing. SPPRE_URE1’s statements and examples demonstrate that it performed cyber security testing in a manner that minimized adverse effects on its production system prior to deployment of a Cyber Asset. Additionally, SPPRE_URE1’s change management program has robust internal controls. SPPRE_URE1 management has to approve changes prior to implementation and the CIP senior manager monitors significant changes in real-time throughout the change management process. Lastly, SPPRE_URE1 utilizes security monitoring analysis and response systems, and system performance software to continuously monitor and alert for malicious activity; therefore, minimizing the risk of cyber security events on the SPPRE_URE1 system. | when the standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) created and implemented formal cyber security testing procedures; 2) incorporated cyber security testing procedures into the change management tool to include a check of cyber security controls; 3) documented test results; and, 4) trained all affected SPPRE_URE1 personnel on the new procedures. | 2013-11-15 | 2014-01-03 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013048 | Settlement Agreement | On June 19, 2013, SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had a violation of CIP-007-3 R6, R6.1, et.al. For non-critical Cyber Assets that reside within SPPRE_URE1’s Electronic Security Perimeters (ESPs), system events related to cyber security were not being logged and monitored. Subsequently, during a Compliance Audit conducted SPP RE determined that three Cyber Assets were not afforded the protections of CIP-007-3 R6, et.al. SPPRE_URE1 was found in violation of R6.1 and R6.2 because it did not implement automated tools or organizational process controls to monitor all system events that are related to cyber security incidents for three Cyber Assets. SPPRE_URE1 was found in violation of R6.3 and R.6.4 because while the SEIM server is rebooted, logs from the three Cyber Assets are not captured. Additionally, the monitoring and access logs of the three Cyber Assets are not captured during cyber security incident testing. Lastly, because these security event logs were lost, SPPRE_URE1 did not review them as required by R6.5. | CIP-007-3 | R6 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1’s failure to implement logging and monitoring for the non-critical Cyber Assets, and its non-continuous monitoring of the three Cyber Assets during the brief time the SEIM server is unavailable, could have allowed unauthorized access to those devices to go unnoticed and created the potential for malicious access. However, SPPRE_URE1 utilizes security monitoring analysis and response systems and system performance software to continuously monitor and alert for malicious activity within the ESPs and at the ESP access points. Additionally, access to SPPRE_URE1’s Cyber Assets is limited to those individuals with authorized electronic and/or physical access rights. Regarding the three Cyber Assets, the violation occurred during a brief period of time, when the backup server was running and the SEIM server was not in service or during SPPRE_URE1’s annual cyber security incident testing. SPPRE_URE1 had implemented automated tools and organizational processes to monitor cyber security system events for all other SPPRE_URE1 Cyber Assets. Regarding SPPRE_URE1’s failure to review the logs for the eight Cyber Assets, the systems within the ESPs are completely disconnected from other network sources and once the connection is restored, software agents on most of the affected devices will restore missing logs, so the only lost data is from a limited set of devices. Additionally, access to SPPRE_URE1’s Physical Security Perimeters, monitored 24 hours a day, seven days a week by security cameras, and is restricted to personnel with approved personnel risk assessments and cyber security training. | violation end date for the prior CIP-007-1 R6 violation | Mitigation Plan completion | $68,000 (for SPP2013012524, SPP2013012526, SPP2013013028, SPP2013013040, SPP2013013042, SPP2013013044, SPP2013013045, and SPP2013013048) | Self-Report/ Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) implemented security monitoring controls on the five non-critical Cyber Assets; 2) implemented security event monitoring for all Cyber Assets within the SPPRE_URE1 ESPs and verified that the security monitoring controls were logging properly; 3) implemented tools for maintaining and reviewing logs of system events related to cyber security; and, 4) trained affected personnel on the controls and tools to document and verify cyber security event monitoring for all Cyber Assets within the ESPs. | 2014-04-25 | 2014-06-05 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE determined that SPPRE_URE1's compliance history constitutes as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012930 | Settlement Agreement | TRE_URE1 submitted a Self-Report during the Self-Certification period stating that it was in violation of CIP-003-3 R6. Specifically, TRE_URE1 failed to follow its change control and configuration management process. TRE_URE1 installed a firewall at one of its substations without adherence to its change control and configuration management process that made a previously installed communications processor, to which it was connected, a Critical Cyber Asset (CCA). This resulted in the inadvertent installation of a CCA into TRE_URE1's Electronic Security Perimeter (ESP). Instead of utilizing its change control and configuration management process when installing the firewall, TRE_URE1 used other company processes in order to schedule and track its installation work. TRE_URE1 identified the root cause of this violation to be human error based on the TRE_URE1 installation group’s lack of CIP compliance training. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, adding CCAs to the ESP without following the change control and configuration management processes could have resulted in the network being compromised, harmful intrusions, malicious attacks, the misoperation of existing CCAs due to software glitches, and Cyber Assets not being afforded all the required CIP protections. The risk to the reliability of the BPS was mitigated by the following factors. The CCA hosting network was isolated from TRE_URE1's corporate network. In addition, the Energy Management System (EMS) communicates directly to the remote terminal unit (RTU) using a different serial path than the RTU to CCA communication path. Moreover, no configuration settings were implemented before, during, or after the violation period on the EMS or RTU to facilitate routable protocol communication. Further, the firewall connected to the communications processer required a complex alpha, numeric, and special character combination password to access, required specific rules to open any port or service, did not utilize default accounts or passwords, and ran a reduced hardware kernel that minimized malware exploitation. Additionally, both the firewall and communications processor resided within a Physical Security Perimeter (PSP). Lastly, TRE_URE1 had an implemented and documented procedure that has been in place since the Standard’s enforceable date that addressed the expectation of the CCA asset owners to adhere to the change control and configuration processes when a CCA is added or modified. Regarding actual impact, no adverse consequences were noted. | when the communications processor was declared a CCA and installed in the ESP | when the CCA was disconnected | $10,000 (for TRE2013012930, TRE201403577, and TRE201403578) | Self-Report | To mitigate this violation, TRE_URE1: 1) disconnected and disabled the Ethernet ports on the communications processor, removing the CCA classification; and 2) discussed with its applicable asset managers regarding Cyber Assets and the impacts of their roles on CIP compliance. TRE_URE1 expects these actions to address the root cause (i.e. asset managers not being trained on the impact to CIP compliance when they make modifications to the network without following the change control and configuration management processes). | 2013-04-11 | 2014-04-15 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. TRE_URE1 did not receive credit for self-reporting TRE2013012930 because the Self-Report was submitted during the Self-Certification period.
2014-07-31 | FERC | NP14-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013577 | Settlement Agreement | TRE_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1.7. Specifically, TRE_URE1 failed to update its documented physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration. TRE_URE1 failed to reflect the new Physical Security Perimeter (PSP) of its substation hosting a Critical Cyber Asset (CCA) in an Electronic Security Perimeter (ESP) that was created when a firewall was prematurely installed. Despite TRE_URE1's implementation of physical controls to protect the ESP hosting the subject CCA, it failed to update its documented physical security plan to reflect the subject substation configurations before the firewall was disconnected from the communications processor. The CIP-006-3c R1.7 violation is a consequence of TRE_URE1's failure to follow its CIP-003 R6 change control and configuration management processes when the firewall was prematurely installed resulting in the newly created PSP hosting the subject CCA not being documented. | CIP-006-3c | R1; R1.7 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A failure to update the physical security plan with the new PSPs at the subject substation could have resulted in personnel detrimentally relying upon incomplete physical access information to make security protection decisions, increasing the risk of harmful and unauthorized access to Cyber Assets and the ESP. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE1 utilizes physical security controls, like physical security monitoring, key locked doors, and card readers that monitor and control access to the control house where the subject Cyber Assets resided. Additionally, this is a documentation issue and not a failure to protect the Cyber Assets in the PSP. The control house devices were programmed to meet NERC requirements and those seeking access had to first establish an OP net user account. Further, the network hosting the subject Cyber Assets was isolated from the corporate network, ensuring another layer of security. TRE_URE1 has always maintained a physical security plan and the subject Cyber Assets resided within a six-wall border. Physical access to the Cyber Assets required a badge with NERC certified credentials and a key to enter the control house, which resides in a locked substation that also requires approved authorization to enter. During the four-month violation period, the access logs showed two access attempts to the control house. One successful access attempt was made by security and another access attempt made by a TRE_URE1 employee was rejected confirming that the protections worked appropriately. Regarding actual impact, no adverse consequences were noted. | 31 days after the communications processor was declared a CCA and the PSP was modified | when the CCA was disconnected and PSP modification was negated | $10,000 (for TRE2013012930, TRE201403577, and TRE201403578) | Self-Report | To mitigate this violation, TRE_URE1: 1) disconnected and disabled the Ethernet ports on the communications processor, removing the CCA classification. No change to the physical security plan was required; and 2) discussed with its applicable asset managers regarding Cyber Assets and the impacts of their roles on CIP compliance. TRE_URE1 expects these actions to address the root cause (i.e. asset managers not being trained on the impact to CIP Compliance when they make modifications to the network without following the change control and configuration management processes). | 2013-04-11 | 2014-04-15 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013578 | Settlement Agreement | TRE_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R5.2. Specifically, TRE_URE1 failed to update its documentation to reflect the addition of an electronic access point/firewall within 90 calendar days of its installation. The CIP-005-3a R5.2 violation is a consequence of TRE_URE1's failure to follow its CIP-003 R6 change control and configuration management processes when the subject firewall was prematurely installed, resulting in the establishment of an electronic access point that facilitated the remote collection of user activity reports and system logs from the field. The ability of the firewall to communicate outside the Electronic Security Perimeter (ESP) via a routable protocol allowed the communications processor to become a Critical Cyber Asset (CCA). The addition of an electronic access point represents a modification to the network. Therefore, the applicable CIP-005 documentation was required to be updated within 90 days. TRE_URE1 did not document the new electronic access point created by the premature installation of the firewall. | CIP-005-3a | R5; R5.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to document the electronic access point could have resulted in a failure to afford all the necessary CIP protections due to a detrimental reliance upon incomplete electronic access point availability data, increasing the vulnerability risk to harmful intrusions and malicious attacks into the ESP. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE1 utilizes an application of firewall security controls despite its failure to document the electronic access point. The security controls were evidenced by the firewall rules denying all connections by default and the implementation of connections to only allow traffic from authorized Local Area Network addresses. Only those ports and services needed for normal operations were active on the firewall. TRE_URE1 implemented strong procedural and technical controls to ensure the authenticity of the accessing party. Further, the subject firewall required a complex alpha, numeric, and special character combination password to access, specific rules to open any port or service, did not utilize default accounts or passwords, and ran a reduced hardware kernel that minimizes malware exploitation. Additionally, the firewall/access point resided within an ESP and a Physical Security Perimeter (PSP). In the event of any unauthorized access attempts an alert via an email is sent to the network support distribution listserv. Lastly, TRE_URE1 had an implemented and documented CIP-005 procedure that has been in place since the Standard’s enforceable date that addressed the requirement to document modifications to the network. Regarding actual impact, no adverse consequences were noted. | 91 days after the firewall was installed | when the firewall was disconnected from the communications processor and the CCA was disconnected | $10,000 (for TRE2013012930, TRE201403577, and TRE201403578) | Self-Report | To mitigate this violation, TRE_URE1: 1) disconnected and disabled the Ethernet ports on the communications processor, removing the CCA classification; and 2) discussed with its applicable asset managers regarding Cyber Assets and the impacts of their roles on CIP compliance. TRE_URE1 expects these actions to address the root cause (i.e. asset managers not being trained on the impact to CIP Compliance when they make modifications to the network without following the change control and configuration management processes). | 2013-04-11 | 2014-04-15 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012539 | Settlement Agreement | WECC_URE1 submitted a Self-Report for CIP-005-3 R2.4. However, after discussions with WECC, it was determined that the violation was for CIP-005 R1 not R2.4. Therefore, WECC dismissed the CIP-005 R2.4 violation and had WECC_URE1 submit a new Self-Report under the correct Requirement. WECC notified WECC_URE1 that it would be conducting an on-site Compliance Audit. Prior to the Compliance Audit, WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-2 R1 (R1.5). WECC_URE1 stated that due to an incorrect interpretation of the Standard it had improperly classified six devices and therefore failed to afford the devices the protection of CIP-003 R3, R4, and R6, CIP-005 R2 and R3, CIP-007 R1, R5, R6, R8, and R9, and CIP-009 R1 through R5. Specifically, WECC_URE1 reported that it had active directory domain controllers that facilitated the authentication for interactive access to its energy management center and backup control center Electronic Security Perimeters (ESPs), which was not classified as an Electronic Access Control and Monitoring (EACM) device. WECC determined WECC_URE1 failed to afford the protections of CIP-003 R3, R4, and R6, CIP-005 R2 and R3, CIP-007 R1, R5, R6, R8, and R9, and CIP-009 R1 through R5 to multiple EACM devices used to monitor two of its ESPs. | CIP-005-2 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to provide a number of protections required by CIP-005-2 R1.5 to certain EACM devices, WECC_URE1 did maintain the devices within a Physical Security Perimeter (PSP). The PSP is actively monitored 24 hours a day, seven days a week. Additionally, only authorized individuals who have undergone cyber security training are granted access to the PSP. Further, the devices in scope were limited in connectivity and two-factor authentication was required for any external interactive access into the demilitarized zone. Furthermore, to gain access to the EACM devices, WECC_URE1 requires multi-factor authentication including a biometric scan, and administrators must present an additional username and password combination. Finally, WECC_URE1's security event and incident management system records and alerts WECC_URE1 personnel of all failed log-in attempts. No harm is known to have occurred. | when the Standard became mandatory and enforceable on WECC_URE1 | present | $20,000 (for WECC2013012539, WECC2013012739, WECC2013012740, and WECC2013012255) | Self-Report | To mitigate this violation, WECC_URE1 will remove the six corporate active directory servers from performing authentication for external interactive access into the ESPs. | 10/15/2014 (approved completion date) | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Although WECC_URE1 submitted the Self-Report for CIP-005 R1.5 following a Notice of Compliance Audit, WECC_URE1 had initially disclosed its noncompliance in a Self-Report of CIP-005 R2.4 prior to the notice of the upcoming Compliance Audit; thus, WECC applied self-reporting credit for this violation. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012739 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE1 was in violation of CIP-005-3a R2 (R2.2). Specifically, WECC determined that at two access points to two Electronic Security Perimeters (ESPs), WECC_URE1 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the ESP. The scope of the violation included four physical hardware devices and a total of 27 open ports enabled through the firewall, which were not required for operations or monitoring Cyber Assets within the ESP. | CIP-005-3a | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 employed a defense-in-depth architecture designed to prevent malicious cyber attacks. Specifically, WECC_URE1 utilized various physical and logical cyber security controls. WECC_URE1 used physical security mechanisms with guards, special locks, closed circuit television, additional firewalls, vulnerability scanning tools, and a security incident and events management system. Furthermore, the ports associated with the issue are only accessible from ESP to ESP; thus, one would have to physically be in one of the ESPs to access the ports. WECC_URE1 determined that there were no attempted or unauthorized access attempts that occurred during this time. None of the devices within the ESPs had open ports. No harm is known to have occurred. | when WECC_URE1 implemented the access points for configuration | when WECC_URE1 removed the 27 ports and services not required for operations and monitoring Cyber Assets within the ESP | $20,000 (for WECC2013012539, WECC2013012739, WECC2013012740, and WECC2013012255) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) reviewed the access lists and promptly removed the 27 unnecessary ports and services; 2) reviewed the access point access lists to ensure that only ports and services required for operations and monitoring Cyber Assets within the ESP were enabled; and 3) conducted a meeting with subject matter experts to review the updated procedures. | 2013-09-05 | 2013-12-18 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012740 | Settlement Agreement | During a Compliance Audit WECC determined that WECC_URE1 was in violation of CIP-005-3a R4 (R4.2). Specifically, WECC determined that WECC_URE1's Cyber Vulnerability Assessment (CVA) failed to verify that only ports and services required for operations at electronic access points to its Electronic Security Perimeters (ESPs) were enabled. WECC_URE1 is required to perform an annual CVA, in part, to verify that only ports and services required for operations at access points to ESPs were enabled. WECC determined that in calendar year, WECC_URE1's CVA failed to verify that only ports and services required for operations at access points to ESPs were enabled. | CIP-005-3a | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to enable only those ports and services necessary for operation and for monitoring Cyber Assets within an ESP, WECC_URE1 did employ a defense-in-depth architecture designed to prevent malicious cyber attacks. Specifically, WECC_URE1 utilized various physical and logical cyber security controls. WECC_URE1 also used physical security mechanisms with guards, special locks, and closed circuit television, additional firewalls, vulnerability scanning tools, and a security incident and events management system. No harm is known to have occurred. | when WECC_URE1 conducted its CVA | when WECC_URE1 completed the CVA | $20,000 (for WECC2013012539, WECC2013012739, WECC2013012740, and WECC2013012255) | Compliance Audit | To mitigate this violation, WECC_URE1 : 1) updated its annual CVA procedure methodology to include a manual review of the ESP access points to the ports and services list and provided training to relevant personnel; 2) conducted a meeting with subject matter experts to review the updated procedures; 3) implemented the procedure update for the CVA by manually reviewing the enabled ports and services of the WECC_URE1 access points to the ports and services list; and 4) created a written memo documenting that there were no ports and services not required for operations identified during the assessment. | 2013-09-30 | 2014-06-11 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012255 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1 (R1.8). WECC_URE1 reported that it failed to identify three of its Physical Access Control System (PACS) door badge reader control panels as Cyber Assets that authorize and/or log access to a Physical Security Perimeter (PSP). WECC_URE1 improperly classified the devices as electronic lock control mechanisms and therefore failed to apply the protections required by CIP-006-1 R1.8 to the PACS devices. Specifically, WECC_URE1 failed to afford CIP-003 R6, CIP-007, and CIP-009 R1 through R4 protections to the three PACS control panels. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to identify and properly protect three PACS devices as Cyber Assets involved in the access control and monitoring of a PSP, WECC_URE1 did ensure that the devices were located within an identified PSP that was monitored 24 hours a day, seven days a week. Additionally, the three PACS devices were each located within a locked cabinet equipped with tamper alarms. Furthermore, the devices did not have default accounts and WECC_URE1 routinely changed the passwords on the devices. Finally, the devices were on a segmented network, not on or accessible by WECC_URE1's corporate network. No harm is known to have occurred. | when the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $20,000 (for WECC2013012539, WECC2013012739, WECC2013012740, and WECC2013012255) | Self-Report | To mitigate this violation, WECC_URE1: 1) added the three PACS network controller panels to its Cyber Asset list; 2) assigned a single senior manager with overall responsibility and authority for leading and managing the implementation of, and adherence to, Standards CIP-002 through CIP-009; 3) filed one Technical Feasibility Exception (TFE) related to the inability to disable a service; 4) documented and implemented an information protection program in WECC_URE1 policy; 5) documented and implemented a program for managing access to protected information in WECC_URE1's information protection program policy; 6) documented the baseline configuration of the PACS network controller panels in the configuration management baseline spreadsheet; 7) documented a personnel risk assessment (PRA) program and updated its automated compliance tool provisioning tool to ensure personnel with access to the PACS network controller panels have been properly vetted through the PRA process; 8) implemented and documented the organizational processes and technical mechanisms for control of electronic access at the access points to the protected network of the PACS; 9) documented the processes for monitoring and logging of electronic access in the Electronic Access Control and Monitoring procedure; 10) documented and implemented the operational and procedural controls to manage physical access at the access points to the PSPs; 11) documented and implemented the technical and procedural controls for monitoring physical access at the access points to the PSPs; 12) documented a procedure to ensure that new Cyber Assets and significant changes to existing Cyber Assets of the PACS do not adversely affect existing cyber security controls; 13) established, documented, and implemented a process to ensure that only the ports and services required for normal and emergency operations are enabled; 14) established, documented, and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches; 15) filed a TFE for the PACS network controller panels related to malicious software prevention; 16) established, documented, and implemented technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access; 17) worked closely with vendors and determined that it is not technically feasible to monitor system events that are related to cyber security on the PACS network controller panels; 18) established and implemented formal methods, processes, and procedures for disposal or redeployment of the PACS network controller panels; 19) performed a Cyber Vulnerability Assessment of the PACS network controller panels which identified one vulnerability, and worked with the vendor to review the vulnerability with the conclusion that it is not technically feasible to disable the service with the latest firmware of the device; 20) reviewed and updated documentation related to CIP-007; 21) established the requirement to maintain and create a cyber security incident response plan; and 22) documented and implemented recovery plans for its PACS network controller panels in the procedure for PACS devices. | 2013-07-09 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012020 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-3c R2. WECC_URE2 failed to protect its Physical Access Control Systems (PACS) that authorize and/or log access to the Physical Security Perimeters (PSPs). WECC_URE2 failed to afford these devices the protective measures specified in CIP-005-3 R3; CIP-007-3 R1, R2, R3, R4, R5, R6, and R8; and CIP-009-3 R4 and R5, as required by CIP-006-3c R2.2. WECC_URE2 failed to provide devices the protective measures required by the Standard. The root cause of the violation was WECC_URE2's failure to define the devices as PACS devices, due to lack of knowledge and the absence of a cross-departmental review. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2's failure to protect its PACS from unauthorized physical access at all access points to its PSPs could allow unauthorized and malicious access to its Cyber Assets in the PSP. Failing to ensure that Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) are afforded protected measures puts such assets at risk to be manipulated. If the ports and services required for normal operation of these access control and monitoring assets are unknown, ports and services could be utilized to gain unauthorized access to the PSP, and the unauthorized access may go unnoticed and unchecked, potentially allowing malicious access to cyber assets contained in the PSP. Such access may then be used to cause harm to Critical Cyber Assets essential to the operation of the BPS. As compensating measures, each of the device is located within a PSP. Also, WECC_URE2's corporate intrusion detection system alerts if it detects malicious network behavior. WECC_URE2's network is protected by two sets of clustered firewalls that only allow explicit traffic into and out of the network. WECC_URE2 has a corporate security incident event manager that is configured to detect anomalous network activity. In addition, the devices are locked in secure cabinets within the PSP, with controlled access to the cabinet keys. | when WECC_URE2 first failed to protect its PACS | present | 35000 | Self-Certification | To mitigate this violation WECC_URE2 will: 1) clarify and improve WECC_URE2's methodology to identify PACS devices; 2) identify specific PACS devices required to comply with CIP-006-3c R2: 3) perform a gap assessment to determine which protective measures of CIP-006-3 R2 have been met; 4) create a detailed list of actions needed to address the gap assessment; 5) define a roadmap to determine the technical requirements and solutions needed for CIP-006-3 R2 compliance; and 6) implement the identified solutions according to the roadmap to ensure WECC_URE2 compliance with CIP-006-3 R2. | 12/1/2014 (approved completion date) | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013012774 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R5.2.1. FRCC_URE1 failed to rename six default administrator accounts prior to putting Cyber Assets into service. FRCC_URE1 discovered the violation during a mock audit. FRCC_URE1 had an operational concern with renaming the accounts because the control system was configured to vendor specifications. FRCC_URE1 requested that the vendor provide an impact analysis for changing the name of the domain administrator account and it has been determined that there is minimal operational risk to changing the account name. The underlying cause of the violation was a perception of operational impact to the facility that was not verified with the vendor. | CIP-007-1 | R5; R5.2; R5.2.1 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because all the default accounts are protected by passwords that had been changed to meet the CIP-007-1 R5.3 password criterion. Furthermore, all of the Cyber Assets reside in an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). | when the Standard became mandatory and enforceable on FRCC_URE1 | when the six default accounts were corrected | $56,000 (for FRCC2013012774, FRCC2013013034, FRCC2013013036, FRCC2013013037, and FRCC2013013038) | Self-Report | To mitigate this violation, FRCC_URE1: 1) obtained an impact analysis from the control system vendor for changing the name of the domain administrator account; 2) performed a complete review of all Cyber Assets at the facility at issue to ensure no additional default accounts were in use that had not been renamed; 3) implemented changes to default accounts and recorded the changes with the change management process; and 4) conducted a lessons learned session with CIP administration team. | 2014-01-07 | 2014-02-18 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC determined that FRCC_URE1's compliance history should serve as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013034 | Settlement Agreement | During a Compliance Audit, FRCC determined that FRCC_URE1 was in violation of CIP-005-3a R4.4. FRCC_URE1 failed to perform the required review of controls for network management community strings during its annual Cyber Vulnerability Assessment (CVA). Both FRCC_URE1's documentation and subject matter expert interview failed to provide sufficient evidence to demonstrate that it had reviewed its controls for network management community strings when FRCC_URE1 performed its CVA of the electronic access points to the Electronic Security Perimeter(s). FRCC_URE1's process documentation for the CVA included steps to review the controls for network management community strings, however, FRCC_URE1's evidence did not demonstrate that the automated review of the controls for network management community strings took place during the annual CVA process. | CIP-005-3a | R4; R4.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because all network management community strings had been changed from the vendor supplied defaults to one that uses upper and lower case alphabetic and numeric values. No actual harm is known to have occurred. | when FRCC_URE1 failed to review the network management community string as part of its CVA | when FRCC_URE1 updated its CVA procedure | $56,000 (for FRCC2013012774, FRCC2013013034, FRCC2013013036, FRCC2013013037, and FRCC2013013038) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) reviewed all electronic access points to ensure the condition did not exist elsewhere on FRCC_URE1's footprint; 2) updated the router to ensure that network management community strings were removed where not needed; and 3) updated its CVA automated procedures to include the network management community string review. | 2014-03-26 | 2014-05-29 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013036 | Settlement Agreement | During a Compliance Audit, FRCC determined that FRCC_URE1 was in violation of CIP-007-1 R2.2. FRCC_URE1 failed to provide sufficient evidence to demonstrate that it had enabled only those ports and services required for normal and emergency operations. Also FRCC_URE1 failed to provide sufficient evidence that it disabled other ports and services, including those used for testing purposes. There were 16.98% Cyber Assets sampled and 22.2% were found to be non-compliant. | CIP-007-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to disable ports and services not required for normal and emergency operations leaves Cyber Assets vulnerable to potential cyber attacks and exploitation. The risk was reduced because all Cyber Assets were located in an Electronic Security Perimeter and within a Physical Security Perimeter. Further, all devices had antivirus installed, password protections and are being logged and monitored. | when the Standard became mandatory and enforceable on FRCC_URE1 | present | $56,000 (for FRCC2013012774, FRCC2013013034, FRCC2013013036, FRCC2013013037, and FRCC2013013038) | Compliance Audit | To mitigate this violation, FRCC_URE1 will: 1) change the authorized list of ports and services to match the vendor documentation to determine if ports are being outside of the recommended range; 2) perform an analysis on any ports discovered outside the documented range; 3) contact the vendor to determine if ports discovered outside of documented range are acceptable; 4) receive vendor response to determine if any further action is required; and 5) implement any vendor provided solution to turn off ports outside range. | 7/31/2014 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC determined that FRCC_URE1's compliance history should serve as an aggravating factor in the penalty determination.
2014-07-31 | FERC | NP14-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013037 | Settlement Agreement | During a Compliance Audit, FRCC determined that FRCC_URE1 was in violation of CIP-007-1 R3.1 and R3.2. FRCC_URE1 failed to provide sufficient evidence to demonstrate that it assessed and implemented security patches and upgrades for programs installed on four Critical Cyber Assets (CCAs) within an Electronic Security Perimeter (ESP) at a facility. In addition, FRCC_URE1 failed to provide sufficient evidence to demonstrate that it applied compensating measures to mitigate any risk exposure for not installing the patches on the CCAs. FRCC_URE1 has a program for tracking security patches and upgrades, however, not all applications found on the systems were on in its tracking list. Also, FRCC_URE1 does not maintain a time line for the implementation of any patch they have deemed necessary to install. FRCC_URE1 bases the installation of patches on outage windows which are not on a scheduled or known basis. Furthermore, FRCC_URE1 does not implement any compensating measures while waiting for an outage window, nor has it filed any Technical Feasibility Exceptions (TFEs) in cases where the patch is not installed. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because the lack of assessment and installation of security patches and upgrades can leave the Cyber Assets vulnerable to an attack; FRCC_URE1 does not maintain a timeline for the implementation of any security patch or upgrade they have deemed necessary to install; FRCC_URE1 bases their installation of security patches and upgrades on outage windows which are not on a scheduled or known basis; FRCC_URE1 does not implement any compensating measures while waiting for an outage window; and FRCC_URE1 has not filed any TFEs when they cannot meet strict compliance with the standards and requirements. The risk was reduced because the Cyber Assets were all found inside an ESP and a Physical Security Perimeter as required. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | $56,000 (for FRCC2013012774, FRCC2013013034, FRCC2013013036, FRCC2013013037, and FRCC2013013038) | Compliance Audit | To mitigate this violation, FRCC_URE1 will: 1) reviewed all Cyber Assets at the site at issue and removed all software not required for daily operations; 2) installed all assessed security patches; 3) updated the legacy progress operations patch evaluation form to include steps to document the compensating and mitigating measures if security patches are not able to be applied within the next 30 days; and 4) updated the legacy progress security patch management procedure to include steps to document the compensating and mitigating measures if security patches are not able to be applied within the next 30 days. | 2014-04-30 | 2014-05-29 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-07-31 | FERC | NP14-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013038 | Settlement Agreement | During a Compliance Audit, FRCC determined that FRCC_URE1 it was in violation of CIP-009-1 R5. FRCC_URE1 failed to provide sufficient evidence to demonstrate that it tested at least annually information essential to recovery that is stored on backup media. Specifically, FRCC_URE1's evidence did not demonstrate that it exercised a media test program annually to ensure that information essential to recovery was available. FRCC_URE1 performed testing on backup media but only to the extent to ensure that backups were completed and files created. The backup media was not fully loaded on a production system or replicated test system to ensure data integrity. | CIP-009-1 | R5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the lack of testing of the backup media, which has information essential to recovery of Critical Cyber Assets, can leave the Cyber Assets vulnerable to unsuccessful recovery and subsequent inability to control the Critical Asset. The risk was reduced because, although limited, there was some testing performed to ensure backups were being created. | when the Standard became mandatory and enforceable on FRCC_URE1 | present | $56,000 (for FRCC2013012774, FRCC2013013034, FRCC2013013036, FRCC2013013037, and FRCC2013013038) | Compliance Audit | To mitigate this violation, FRCC_URE1 will: 1) review and identify systems in scope that utilize backup media; 2) review current backup media testing processes or technology enhancements and determine process revisions or technology enhancements that will allow for full testing of backup media; and 3) implement enhanced backup media testing processes/technologies to allow for full testing of backup media integrity. | 10/17/2014 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-06-26 | FERC | NP14-44-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013176 | Settlement Agreement | During a Compliance Audit SERC determined that SERC_URE1 was in violation of CIP-005-3a R4. SERC_URE1's cyber vulnerability assessment (CVA) did not include the reviews and documentation required by CIP-005-3a R4.2, R4.3, R4.4, and R4.5. SERC later determined that the violation extended back to Version 1 of the Standard. SERC learned that SERC_URE1 had two electronic access points requiring an annual CVA. These two access points consisted of three firewalls. SERC_URE1 failed to provide adequate documentation that it performed a review to verify only ports and services required for operations at the access points were enabled, as required by CIP-005 R4.2. SERC_URE1 did not have baseline documentation to use to verify that only necessary ports and services were enabled. SERC_URE1 also failed to discover all access points to an Electronic Security Perimeter (ESP) as required by CIP-005 R4.3. Also, SERC_URE1 failed to provide adequate documentation that it performed a review of controls for default accounts, passwords, and network management community strings as part of the CVA process, as required by CIP-005 R4.4. Finally, SERC_URE1 failed to provide documentation of an action plan to remediate or mitigate vulnerabilities, the execution of the action plan, and the results of the CVA, as required by CIP-005 R4.5. The document identifying the vulnerability assessment process did not address each sub-requirement of CIP-005 in detail and failed to provide a conclusion of the results for any step in the assessment. | CIP-005-1 | R4; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1's failure to complete a full CVA and document the results increased SERC_URE1's vulnerability to unauthorized access into the ESP. However, SERC_URE1 had compensating measures in place including an intrusion prevention system, two-factor authentication for external access, and encryption. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | 0 | Compliance Audit | To mitigate this violation, SERC_URE1: 1) refined its access point CVA process document to include more detail and include ability to indicate progress, present results, and document supervisory review; 2) performed a new CVA and documented it according to the new process document and assessed the results; and 3) informed technicians and reviewers of the methodologies to be used in the CVA process. | 3/21/2014 | TBD | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011886 | Settlement Agreement | TRE_URE1 submitted a Self-Report stating that, it was in violation of CIP-006-3c R1. Texas RE determined that while TRE_URE1's physical security program addressed unescorted access per R1.6, it was not properly implemented in this case. A visitor without authorized access to a Data Center Physical Security Perimeter (PSP) was left unescorted for a total of seven minutes. The first occurrence was for one minute beginning at 15:36. The second occurrence was for two minutes beginning at 19:22. The third occurrence was for four minutes beginning at 19:31. TRE_URE1 attributes the cause of the violation to the escort not fully understanding its responsibilities as well as the visitor not understanding visitor responsibilities. | CIP-006-3c | R1; R1.6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated because although not continuously escorted, the visitor was being monitored by closed-circuit television. No Critical Cyber Asset systems or devices were threatened or compromised. The escort had properly logged the visitor and the duration without escort was seven minutes total. | date visitor was allowed unescorted access | the day the unescorted access ended | 0 | Self-Report | To mitigate this violation, TRE_URE1: 1) Developed awareness on escorting best practices and procedures for prototype of lanyard use; 2) Developed a prototype use of lanyards for visitors and escorts which included escort and visitor responsibilities; and 3) Trained staff regarding escorting best practices and procedures for prototype of lanyard use. Utilizing the lanyards will increase continuous awareness and reduce the likelihood of future recurrence by providing a more visible means of identification of escorts and visitors to the escort, visitors, and any others who may be in the protected area. Additionally, escort and visitor duties will be available on the lanyards which will continuously reinforce the expectations to escorts and visitors. | 2013-08-12 | 2014-05-01 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE reviewed TRE_URE1's compliance history and did not consider it an aggravating factor in the penalty determination.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012873 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-1 R5.2. Specifically, TRE_URE2 discovered that the list of individuals with access to CIP-protected information was not reviewed on an annual basis. TRE_URE2's violation implicated one of its plants made up of a total of three units. Although TRE_URE2 has a documented procedure that states it will review at least annually the access privileges to protected information to confirm that access privileges are correct and that it corresponds with the entity’s needs, appropriate personnel roles and responsibilities, TRE_URE2 failed to review the access privileges list for approximately 40 months. | CIP-003-1 | R5; R5.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the access privileges list had not been reviewed in 40 months compared to the 12-month minimum review period required by CIP-003-1 R5.2. Accordingly, sensitive information related to Critical Cyber Assets (CCAs) could have been compromised, thereby leaving TRE_URE2's CCAs and Critical Assets unprotected and at risk. Furthermore, access control management of the CCAs was important due to its association with the plant (Critical Asset) that represents a significant percentage of TRE_URE2's portfolio. The risk was partially mitigated because persons granted access to CIP protected information during the violation review period had completed a personnel risk assessment and CIP training prior to being granted access. In addition, TRE_URE2 had a documented program addressing CIP-003 R5.2. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the Standard became mandatory and enforceable on TRE_URE2 | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Certification | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-03-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013013281 | Settlement Agreement | TRE_URE2 submitted a Self-Report stating that it was in violation of CIP-004-3a R2. During an internal assessment, TRE_URE2 discovered personnel and contractors had received cyber security training prior to access to restricted areas, however, 5.8% of personnel with authorized access, did not complete the required annual refresher training by the end of the year as outlined in its cyber security training program. TRE_URE2's violation implicated one of its plants made up of a total of three units. | CIP-004-3a | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The annual cyber security program was not fully implemented as evidenced by 5.8% of personnel with authorized access not completing the annual program refresher training. A lack of training could have resulted in the subject personnel using the Critical Cyber Assets (CCAs) or responding to a Cyber Security Incident in a manner that jeopardizes the reliability of the BPS. The risk was mitigated by the fact that the subject personnel received cyber security training prior to being granted initial physical access to CCAs and all 5.8% of personnel had the required personnel risk assessments. Further, TRE_URE2 maintained ongoing security awareness training as evidenced by posted security training posters. Lastly, TRE_URE2 had an established, documented, and maintained annual cyber security training program. Texas RE is not aware of any Cyber Security Incidents arising during the period of the violation and there was no evidence that suggested the personnel at issue misused CCAs. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | the day after the required annual refresher training was due to be completed | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Report | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-03-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012874 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-004-1 R4. Specifically, TRE_URE2 failed to include specific physical access rights on its list(s) of personnel with authorized access to Critical Cyber Assets (CCAs). TRE_URE2's violation implicated one of its plants made up of a total of three units. A review of TRE_URE2's Critical Infrastructure Protection procedure and physical security plan during the violation duration period addresses the expectation of the subject Standard to include the specific electronic and physical access rights on the list(s) of personnel with authorized cyber or authorized unescorted physical access to CCAs. However, a review of TRE_URE2's CCA access list, representing personnel with authorized cyber and/or authorized unescorted physical access to CCAs, failed to include the specific electronic and physical access rights for each individual, a violation of CIP-004-1 R4. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated by TRE_URE2 having established controls related to recordkeeping, cyber access privileges, and unescorted physical access privileges. For example, when physical access was authorized for an employee or contractor, the signed authorization request form designated the specific physical access to be granted. Upon implementation of actual access, TRE_URE2's Physical Access Control System (PACS) maintained and controlled access to specific individual Physical Security Perimeters (PSPs). Next, the PACS provided real-time monitoring and alerts for unauthorized physical access attempts to the individual PSPs. TRE_URE2 determined that there were no unauthorized physical access attempts to the individual PSPs. Further, the TRE_URE2 network security system provided real-time monitoring and alerting for unauthorized logical access attempts to the protected Cyber Assets. Lastly, TRE_URE2 had an implemented CIP-004 R4 program. The noted observations of non-compliance suggest more of a documentation issue due to human error than a failure by TRE_URE2 to control and manage Cyber Asset privileges. TRE_URE2 documented the specific logical and physical access privileges, but the data was not included in the designated list referenced in the subject Standard. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the Standard became mandatory and enforceable on TRE_URE2 | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Certification | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-03-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013013148 | Settlement Agreement | TRE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R3. Specifically, TRE_URE2 failed to monitor an Electronic Security Perimeter (ESP) access point (firewall) 24 hours a day, seven days a week, a violation of CIP-005-3a R3. TRE_URE2's violation implicated one of its plants made up of a total of three units. | CIP-005-3a | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, the subject access point was not monitored for 19 months compared to the required continuously monitored standard. During an internal review, TRE_URE2 discovered that one access point was not configured to be monitored by the TRE_URE2 network security system. The TRE_URE2 network security system provided alerts and daily monitoring of logical access to protected Cyber Assets 24 hours a day, seven days a week. During the violation period, one of the two ESP firewall's activity was not being logged or monitored which increased the ESP’s vulnerability to harmful intrusions and malicious attacks, jeopardizing the reliability of the BPS. Further, this access point monitoring omission represents 50% of the total ESP access points. Lastly, ESP access control and monitoring was important to the security of the Critical Cyber Assets (CCAs) due to their association with the plant (Critical Asset) that represents a significant percentage of TRE_URE2's portfolio. The moderate risk was partially mitigated because the subject unmonitored access point/firewall was configured to allow one-way read-only access to environmental status information. Additionally, this access point/firewall did not provide access to unit controls information and did not allow remote interactive control communications. Further, TRE_URE2 had a documented and partially implemented procedure that addressed the manual and automated cyber security logging, event collection, monitoring, and alerting. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the unmonitored firewall was installed | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Report | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-03-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013013098 | Settlement Agreement | TRE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R4.3. TRE_URE2 discovered that a firewall added to the Electronic Security Perimeter (ESP) was not identified as an access point during both that year's and next year's Cyber Vulnerability Assessments (CVAs) as required by CIP-005-3a R4.3. TRE_URE2's violation implicated one of its plants made up of a total of three units. | CIP-005-3a | R4; R4.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated because the subject access point was used to provide only outbound data for environmental monitoring purposes. The outbound user datagram protocol (UDP) data packets sent were related to precipitator voltage control and rapper control status data such as in/out of service, volts, amps, phase angle, opacity, and spark rate. Further, there was no remote interactive two-way communication to Critical Cyber Assets (CCAs) enabled through this access point/firewall. The firewall was behind a Physical Security Perimeter. The information transmitted had no immediate or automatic impact to generation. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the CVA was completed but excluded the subject access point that was added earlier that year | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Report | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-02-19 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012875 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-1 R1.1. TRE_URE2 discovered that it failed to follow its procedures to test and verify ports and services during the testing of security patches, signatures, and upgrades, resulting in the documented CIP-007 procedures not being implemented in a manner that minimizes adverse effects on the production system or its operation. TRE_URE2's violation implicated one of its plants made up of a total of three units. Specifically, TRE_URE2 maintained a test bed for the generation unit control system at the plant. The plant instrument and control technicians tested changes on the test bed to verify functionality of the control system assets after applying such changes (e.g. security patches and upgrades). TRE_URE2 determined that the testing performed was focused on functionality and did not address potential adverse effects to existing cyber security controls and, as such, potentially did not fully satisfy CIP-007-3a R.1.1. | CIP-007-1 | R1; R1.1 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the subject Critical Cyber Assets (CCAs) are associated with the plant (Critical Asset) that represents a significant percentage of TRE_URE2's portfolio. Additionally, the likelihood of system misoperations, harmful intrusions, and unexpected disruptions to the CCA communication configuration was higher because of TRE_URE2's failure to test ports and services response to Cyber Asset software changes before they were applied in live production. The moderate risk was partially mitigated by the network security system that provided alerts and daily monitoring of logical access to protected Cyber Assets to ensure system protection during the violation duration period. In addition, TRE_URE2 had an implemented and documented procedure that addressed the testing of Cyber Assets within the Electronic Security Perimeter. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the Standard became mandatory and enforceable on TRE_URE2 | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Certification | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-03-10 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013013099 | Settlement Agreement | TRE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R8. Specifically, TRE_URE2 discovered that not all Cyber Assets within the Electronic Security Perimeter (ESP) were assessed in the Cyber Vulnerability Assessments (CVAs) conducted during three years. TRE_URE2's violation implicated one of its plants made up of a total of three units. TRE_URE2 hired a contractor to conduct a CVA on all its Critical Assets. However, the contractor used a sampling approach resulting in only 20.9% of assets being evaluated instead of 100% as required by CIP-007-1 R8. For the following two year's CVAs, the majority of non-critical Critical Assets in the ESP were not assessed due to human error in execution of the CVAs. In the one year, only 34.5% of assets were evaluated and in the following year, only 35% of assets were evaluated. | CIP-007-1 | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the subject CCAs are associated with the plant (Critical Asset) that represents a significant percentage of TRE_URE2's portfolio. Additionally, the likelihood of harmful intrusions and malicious attacks were higher because the complete vulnerability risks were unknown for approximately 31 months. The moderate risk was partially mitigated by the double redundant firewall, continuous alerting and monitoring of both the electronic and physical access to Cyber Assets, and the consistent review of the access activity logs. In addition, continuous security monitoring was in place to detect and to alert for attempts at or actual unauthorized accesses, providing for the appropriate notification to the designated response personnel. TRE_URE2 determined that there were no unauthorized physical access attempts to the individual PSPs. Lastly, TRE_URE2 had an implemented and documented procedure that addressed CVAs and the manual and automated cyber security logging, event collection, monitoring, and alerting. Finally, when TRE_URE2 performed its risk-based assessment methodology (RBAM), TRE_URE2 determined that the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | when the first CVA was conducted that should have included all the subject Cyber Assets | Mitigation Plan completion | $40,000 (for TRE2013012873, TRE2013012874, TRE2013012875, TRE2013013098, TRE2013013099, TRE2013013148, and TRE2013013281) | Self-Report | To mitigate this violation, TRE_URE2: 1) segregated Unit 2 from Units 1 and 3 at the plant to segregate the compressed air systems and unit control systems that were commonly linked across all three units at the plant; 2) performed an annual application of its RBAM that declared the plant was no longer a Critical Asset and that its remaining five Critical Assets had no related CCAs. | 2013-05-13 | 2014-02-19 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Texas RE also took into consideration that within the past two years, TRE_URE2 and its affiliates have substantially invested funds to improve the cyber security and reliability of its facility assets and have added additional personnel to the cyber security and reliability program.
2014-06-26 | FERC | NP14-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013238 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-003-1 R5. During an internal review, WECC_URE1 discovered that when the compliance group and document resources network file shares were created, the administrators group was given, by default, full control of these network file shares as well as CIP restricted SharePoint sites. Due to this oversight, the individuals with administrator access had not received proper approval. WECC_URE1 failed to implement access controls on two file shares that contained Critical Cyber Asset (CCA) information. The information included in the file shares included CIP operational procedures, asset lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain CCAs, equipment layouts of CCAs, disaster recovery plans, incident response plans, and security configuration information. WECC_URE1 is required to document and implement a program for managing access to protected CCA information. Although WECC_URE1 does have a process in place associated with provisioning access for users with access to CIP restricted information, that provisioning process was not clearly defined with respect to administration and support of electronic devices and networks that information resides upon. In this case, WECC determined that WECC_URE1 failed to document and implement a program for managing access to protected CCA information, resulting in a violation of CIP-003-1 R5. | CIP-003-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's failure to manage access to CCA information could allow an unauthorized individual to misuse the information to potentially gain logical or physical access to CCAs. As compensating measures, there were 35 administrators who had access (but no approval), to 8 servers, on which resided 13 SharePoint sites and 2 file shares that contained CCA information. Of these 35 individuals, all had personnel risk assessments (PRAs). Although these individuals did not receive all of the necessary training for proper approval, each of the individuals had some training. Of the 35 administrators, 16 had CIP access training which includes CCA information protection program training, 11 had Critical Energy Infrastructure Information (CEII) training and 9 had approved authorized unescorted physical access. Furthermore, there were 10 individuals who had partial approvals and had access to some file shares and some SharePoint sites. All 10 of these individuals had CIP access training which includes CCA information protection program training, 9 out of 10 had authorized unescorted physical access, 6 out of 10 had CEII training, and all individuals had PRAs. All of the individuals with administrator access to the CIP information have administrator access because of their required job function as IT support. | when the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | 24000 | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented a secure, physically and electronically isolated environment to store CIP restricted information as well as associated processes and procedures, which WECC_URE1 will use to maintain and manage access to WECC_URE1's CIP restricted information; 2) created and designated a specific active directory security group that will allow WECC_URE1 to track administrator support personnel; 3) trained support personnel responsible for granting and/or revoking access to these active directory groups to ensure these individuals understand the access provisioning process; 4) required that all personnel with authorized access to the administrator active directory security group and administrator accounts complete WECC_URE1's CIP access training or CCA information protection program training; 5) removed the new CIP server environment from the widespread application of group policies, meaning that any policies that are pushed across WECC_URE1's corporate network to all servers will not affect the security posture of the new CIP server environment; 6) stored the passwords for the approved administrator accounts and service accounts in a password vault, with select individuals from corporate security being the data custodians of the password vault; 7) developed internal procedures to address changes to the corporate security data custodian who manages the password vault; and 8) required all individuals to obtain approval from the corporate security data custodian to gain access to these administrator and service account passwords in order to prevent individuals from inadvertently bypassing the access provisioning process. | 2014-03-17 | TBD | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-06-26 | FERC | NP14-43-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013128 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R1. Specifically, WECC_URE1 failed to provide continuous escort to a visitor within a Physical Security Perimeter (PSP) for a period of three minutes on a single day. Both the visitor and his authorized escort were contract workers, and the PSP contained over 30 Critical Cyber Assets (CCAs). | CIP-006-3c | R1; R1.6.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 implemented multiple security controls to reduce the risk that an individual could tamper with the CCAs, affecting its energy management system. These controls included disabling USB drives on all devices within the PSP, implementing alarms on CCA workstations that would trigger upon tampering, and stationing security personnel onsite to respond to any alarms associated with tampering. Unauthorized electronic access attempts would also trigger alerts. Further, WECC_URE1 IT staff would be notified in the event of any configuration changes to the CCAs. The entity discovered the noncompliance quickly and began implementing corrective actions within 48 hours. No harm is known to have occurred. | when WECC_URE1 failed to continuously escort a visitor while within a PSP | when continuous escort of the visitor resumed | 12000 | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked CIP access for three contract workers employed by the contractor in question and who had authorized unescorted physical access to WECC_URE1 PSPs; 2) required all employees of the contractor to take (or retake) CIP access training and attend a meeting in which CIP obligations and responsibilities were discussed; 3) sent emails to employees in the affected PSP as well as employees and contractors with access to the affected PSP, reminding recipients of visitor procedures and access control procedures; and 4) restored CIP access to the three contract workers whose access had been revoked. | 2013-10-10 | 2014-01-24 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-06-26 | FERC | NP14-40-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013012564 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-003-3 R6. FRCC_URE1 failed, on two instances, to follow its established change control and configuration management processes when commissioning Cyber Assets within the Electronic Security Perimeter (ESP). For the first instance, FRCC_URE1 discovered that two Cyber Assets were placed in an ESP without going through the change control procedures ensuring antivirus signatures were current and would be updated. For the second instance, FRCC_URE1 discovered that a third Cyber Asset, that had previously resided outside of an ESP, was repurposed for use within the ESP without changing the default password of the administrative account. The Cyber Asset was commissioned in the ESP; however, the FRCC_URE1 analyst failed to verify that the default password had been changed at that time. Both instances resulted from personnel failing to follow the change and configuration management process. | CIP-003-3 | R6 | Lower | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to follow established change control and configuration management processes can let potential cyber security vulnerabilities enter the ESP, and leave both new and existing Cyber Assets vulnerable to a cyber threat. In the first instance, the Cyber Assets' antivirus signatures were not applied to the devices for approximately one and half months. These Cyber Assets could have been subjected to malware during this period. The first Cyber Asset performs scans and sends automated e-mails with reports of available patches on a weekly basis to the team responsible for patching administration. The reports are used in a weekly patching reconciliation and if the report was not generated, the patching administrator would be aware upon initiating the reconciliation process. The Cyber Asset is monitored and an alert is sent to a network team if it goes offline. If the Cyber Asset was infected with malware, the reports might not be sent, potentially delaying the notification of available patches. The second Cyber Asset is a virtual server that provides Terminal Server licenses for users connecting via two factor authentication. Both of the Cyber Assets commissioned are non-Critical Cyber Assets with no control functionality of the Bulk Electric System (BES). Once antivirus signatures were updated, virus scans were performed on the two Cyber Assets and it was confirmed that neither had virus infections. These Cyber Assets do not have e-mail capability and access to the Internet is blocked by the firewall. Additional mitigating measures include host firewalls and current antivirus and anti-malware on other Cyber Assets within the ESP. All Cyber Assets are located within a Physical Security Perimeter (PSP) and an ESP and cannot be accessed remotely. In the second instance, the third Cyber Asset is a device profiler that evaluates the configuration baselines for Cyber Assets residing in the authentication ESP. If this Cyber Asset was compromised, the potential risk would be the possible failure to report changes to Cyber Asset configurations as well as the addition of new Cyber Assets within the authentication environment. The Cyber Asset commissioned is a non-Critical Cyber Asset with no control functionality of the BES. The Cyber Asset is located within a PSP and an ESP and cannot be accessed remotely. Furthermore, in both instances, an intrusion detection system monitors all network traffic at the ESP perimeter and alerts for malicious activity, viruses, spyware, and other nefarious activity. Any suspicious activity is reported to appropriate personnel. | when FRCC_URE1 failed to apply antivirus signatures to the devices | date of milestone when FRCC_URE1 updated its change and configuration management process | $20,000 (for FRCC2013012564, FRCC2013012546, FRCC2012010851, and FRCC2012011635) | Self-Report | To mitigate this violation, FRCC_URE1: 1) opened change request in accordance with the change and configuration management process devices installed; 2) performed awareness training of CIP-003 R6 change and configuration management process; 3) updated change and configuration management process to address equipment that is being repurposed, and communicate to relevant staff; 4) reviewed other devices installed on or after FRCC_URE1 failed to apply antivirus signatures to the devices to ensure proper change control process was followed; 5) reviewed and updated training materials; 6) configured ticketing system to include task for information security review of NERC changes; 7) performed individual coaching of change control and configuration management personnel; and 8) performed second review of all NERC significant changes opened on or after FRCC_URE1 failed to apply antivirus signatures to the devices to ensure changes were consistent with change control procedures. To mitigate this violation, FRCC_URE1 will: 1) review existing CIP-007 R1 procedures with information security staff and implement manual check of completed changes subject to R1 testing; 2) assess existing procedure used to perform CIP-007 R1 testing for potential enhancements; and 3) perform review of all NERC significant change tickets opened to determine if changes were consistent with change control procedures. | 9/12/2014 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-06-26 | FERC | NP14-40-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013012546 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3 R4, R4.1, and R4.2. FRCC_URE1 failed to properly maintain the required access list, failed to remove access within the required timeframe, and incorrectly granted access. There were four instances of noncompliance involving seven personnel: 1) in the first instance, the user's cyber access was not removed when no longer needed; 2) in the second instance, the user's physical card access was not removed from the card access system within the seven days required when access was no longer needed, and the access list had not been updated within seven days required; 3) in the third instance, the user was inappropriately granted physical access to the Physical Security Perimeter (PSP); and 4) in the fourth instance, access was removed timely and was also granted appropriately for users; however, the access list was not updated when required. | CIP-004-3 | R4; R4.1; R4.2 | Lower | High | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to grant and revoke access in a timely fashion, as well as failure to maintain the accuracy of the access list is critical to protection of the Critical Cyber Assets (CCAs) and could leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk to the reliability of the BPS was reduced because: 1) in the first instance, the termination was not for cause, the user was out of the country at the time of termination and did not have remote access to the network, and access was removed only one day late with the access list being updated an additional day later; 2) in the second instance, the employee’s card key required to grant physical access had been collected on his last day worked, and he was a long-term, trusted employee who did not have any Cyber Asset access; 3) in the third instance, another user was not granted any Cyber Asset access and was not aware that he was given PSP access. There was also no attempt to gain access to the PSP; and 4) in the fourth instance, access was removed within the seven days required for two users and was also granted appropriately for two other users after verification of required personnel risk assessment and cyber training. The access list; however, was not updated within the required seven days. | when FRCC_URE1 failed to remove access rights to CCAs for an employee | when FRCC_URE1 removed access rights to CCAs | $20,000 (for FRCC2013012564, FRCC2013012546, FRCC2012010851, and FRCC2012011635) | Self-Report | To mitigate this violation, FRCC_URE1: 1) removed inappropriate access; 2) corrected reporting issues for access report; 3) updated termination procedure to include a checklist of actions to take and to use a standard ticket status; 4) updated procedures for modifying the ticketing system configuration for an access administration analyst to ensure all access requests were viewable by the analyst; 5) held human error prevention training; 6) created access administrator's procedure to ensure searches were only performed using employee identification; 7) communicated use of service desk number for security related requests company-wide; 8) documented corporate security process for destroying cardkey and subsequent actions for access removal. Trained and communicated this process to relevant staff; and 9) identified and reported any additional occurrences throughout the implementation of the Mitigation Plan. | 2013-11-13 | 2014-01-15 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-06-26 | FERC | NP14-40-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010851 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R6, R6.2, R6.4, and R6.5. FRCC_URE1 failed to: 1) ensure on two instances that three Cyber Assets within the Electronic Security Perimeter (ESP), when technically feasible, implemented automated tools or organizational process controls to monitor systems events that are related to cyber security; 2) issue automated or manual alerts for detected Cyber Security Incidents; 3) retain all logs as specified in R6 for 90 calendar days; and 4) review logs of system events related to cyber security. For the first instance, while troubleshooting an unrelated issue, a senior system security architect discovered that the power station firewall was blocking syslog communications from a vendor firewall Cyber Asset, preventing security event logs from being sent to the log consolidation system. The vendor firewall is a Cyber Asset within an ESP and is used to allow the vendor remote access for remote tuning. During a six month period, manual log retention was stopped and logs were not retained electronically. The senior system security architect modified the firewall rules to allow syslog traffic between the log consolidation tool and the vendor firewall device. For the second instance, a senior information security operations analyst reviewed the alerts generated by the log consolidation tool and discovered two virtual servers at the data center, that support the Physical Access Control System (PACS) were missing logs. The analyst discovered the logs were missing for approximately three weeks due to an upgrade that set certain configuration files back to default settings causing logs to no longer be sent to the log consolidation tool. The logs were successfully restarted and confirmed with a review on the following day. | CIP-007-3a | R6; R6.2: R6.4; R6.5 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because the devices were within the ESP and all access point logs were effectively maintained. In addition, FRCC_URE1 also employed an intrusion detection system (IDS) to monitor the network on which these devices reside. Furthermore, one of the subject device did maintain logs but the logs were blocked by the access point and hence were not stored on the security event and incident monitoring (SEIM) system. For the first instance, the risk to the reliability of the BPS is reduced because the vendor firewall is not a Critical Cyber Asset (CCA). This firewall resides behind a FRCC_URE1 managed plant ESP access point firewall and is dedicated to providing remote access for scheduled vendor support. Access through the vendor firewall is disabled by default and no remote support sessions occurred during the time that logs were not being captured. Although the lack of logs would reduce the ability to conduct forensic analysis, the likelihood of an unauthorized person exercising the opportunity to gain access without detection was reduced substantially because the firewall is located in a secure ESP and Physical Security Perimeter (PSP). Suspicious activity within the ESP is further reduced because administrative access is controlled by the information technology security group. The vendor firewall device is used to support remote generator tuning and no tuning was performed during this period so there was no use made of the device. The firewall rules were set to deny by default, so no inadvertent access would have been allowed. For the second instance, the risk is reduced because the virtual servers and the servers they host are not CCAs. Although the lack of logs would reduce the ability to conduct forensic analysis, the likelihood of an unauthorized person exercising the opportunity to gain access without detection was reduced substantially because of virtual servers are located in PSP. The virtual servers host the PACS system; however, they do not authorize and/or log access to the PSP. No logs within the PACS were lost. | when FRCC_URE1 first failed to retain logs | when FRCC_URE1 restarted retaining the logs | $20,000 (for FRCC2013012564, FRCC2013012546, FRCC2012010851, and FRCC2012011635) | Self-Report | To mitigate this violation, FRCC_URE1: 1) enhanced existing test procedures to ensure log availability; and 2) conducted training and review sessions on log verification and identifying significant changes to Cyber Assets. | 2012-08-31 | 2013-04-01 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history to be an aggravating factor in the penalty determination.
2014-06-26 | FERC | NP14-40-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011635 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R4 and R4.2. FRCC_URE1 failed to follow the documented process for updating antivirus and malware prevention signatures as required for six Cyber Assets. An information security analyst discovered that six Cyber Assets did not have up-to-date antivirus signatures within the monthly timeframe identified in the process. The analyst checked to ensure that Cyber Assets were in compliance and noticed that these Cyber Assets were not receiving antivirus updates. Five Cyber Assets, located in a data center, were using a manual process that allows for weekly signature updates to be approved. After the manual approval occurs, the updates are automatically downloaded and installed. The Cyber Assets continued to download the updates; however, the application of the updates was not functioning. All signatures for the five Cyber Assets were updated approximately three weeks after the last install update. The sixth Cyber Asset is located in a control center. This device uses an automated process to update antivirus signatures. A second information security analyst attempted to manually apply the update. The Cyber Asset returned a “No Disk Space Available” error message. Signatures were updated for the Cyber Asset approximately three months after the last signature update. | CIP-007-3a | R4; R4.2 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was reduced because all Cyber Assets subject to this issue had antivirus and malware software installed and enabled. Furthermore, five of the Cyber Assets provided Electronic Access Control and Monitoring of Physical Security Perimeters (PSPs) and did not have any control functionality of the energy control center Critical Cyber Assets (CCA). The remaining Cyber Asset was a non-CCA with no control functionality of the control center CCAs. This Cyber Asset was being used to store the configuration information for other Cyber Assets. All Cyber Assets were located inside the Electronic Security Perimeter (ESP) and PSP. | when the antivirus and malware prevention signatures were last updated | when the antivirus and malware prevention signatures were updated | $20,000 (for FRCC2013012564, FRCC2013012546, FRCC2012010851, and FRCC2012011635) | Self-Report | To mitigate this violation, FRCC_URE1: 1) updated the antivirus signatures on six devices to correct outdated signatures; 2) performed a manual review of antivirus signature ages across all Cyber Assets; 3) updated the malware and antivirus tools and process to incorporate the manual review; 4) conducted final reconciliation of Cyber Asset antivirus status; 5) communicated manual procedures for updating antivirus signatures to responsible personnel; and 6) reported additional occurrences to FRCC. | 2013-09-09 | 2014-01-15 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-05-29 | FERC | NP14-40-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011715 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3a R2. Specifically, MRO_URE1 failed to provide the protective measures required by CIP-006-3a R2. MRO_URE1's Physical Access Control System (PACS) used to manage physical access to Cyber Assets located in a control center for generation dispatch was not protected by intrusion detection system (IDS) configuration. The IDS was originally implemented for this device, but the verification of on-going inclusion in the IDS configuration was not verified after an authorized and documented change that occurred. The discovery was made while performing an in-depth system maintenance on the IDS sensor. MRO_URE1 discovered that a panel used in the access control and monitoring for a Physical Security Perimeter (PSP) was not protected by the IDS configuration. | CIP-006-3a | R2 | Medium | Severe | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The PACS was subjected to security protections even though it was not protected by the IDS because: 1) PACS resided in a non-public physical space with physical access limited to CIP authorized personnel; 2) PACS resided on a non-public network with electronic access limited to internal corporate computing equipment with a firewall controlling remote access to the corporate network; 3) the PACS at issue remained functional and no unauthorized access of PSPs occurred based on devices inside the Electronic Security Perimeters within the affected PSPs that were protected by the IDS; and 4) individuals had to use login credentials for the panel at a MRO_URE1 control center. | when MRO_URE1 failed to have the correct IDS protections on the panels | when MRO_URE1 corrected the IDS protections for the panels | 5000 | Self-Report | To mitigate this violation, MRO_URE1: 1) confirmed devices were physically connected and functioning with the correct integrated network services (INS) devices and ports; 2) during mitigation, panels were protected by a PSP and connected to a non-public network; 3) documented a formal process for validating IDS functionality and that the IDS is physically connected to the correct INS devices and configured for monitoring the correct ports on the INS devices; 4) conducted training on the updated IDS validation process and updated procedures for IT security and INS subject matter experts; and 5) created a baseline diagram of the IDS physical configuration to be used as a reference for annual validation tasks. | 2013-04-05 | 2013-05-09 | Admits | The same event caused a violation for an affiliated entity. MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013011781 | Notice of Confirmed Violation | MRO_URE2 submitted a Self-Report stating that it was in violation of CIP-006-1 R1. Specifically, MRO_URE2 failed to provide the protective measures required by CIP-006-1 R1.8. MRO_URE2's Physical Access Control System (PACS) used to manage physical access to Cyber Assets located in a control center and generating station for dispatch was not protected by intrusion detection system (IDS) configuration. While performing an in-depth system maintenance on the IDS sensor at an MRO_URE2 control center, discovered that a panel used in the access control and monitoring for a Physical Security Perimeter (PSP) was not protected by the IDS configuration. The IDS was originally implemented for this device but the verification of on-going inclusion in the IDS solution was not verified after an authorized and documented change. As a result, MRO_URE2 conducted a comprehensive verification of the IDS configuration for all other panels. MRO_URE2 discovered that a panel at a generating station was not protected by the IDS configuration. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The PACS was subjected to security protections even though it was not protected by the IDS because: 1) PACS resided in a non-public physical space with physical access limited to CIP authorized personnel; 2) PACS resided on a non-public network with electronic access limited to internal corporate computing equipment with a firewall controlling remote access to the corporate network; 3) the PACS at issue remained functional and no unauthorized access of PSPs occurred based on devices inside the Electronic Security Perimeters within the affected PSPs that were protected by the IDS; and 4) individuals had to use login credentials for the panels at an MRO_URE2 control center and generating facility. | when the Standard became mandatory and enforceable on MRO_URE2 | when MRO_URE2 corrected the IDS protections for the panels | 5000 | Self-Report | To mitigate this violation, MRO_URE2: 1) confirmed devices were physically connected and functioning with the correct integrated network services (INS) devices and ports; 2) during mitigation, panels were protected by a PSP and connected to a non-public network; 3) documented a formal process for validating IDS functionality and that the IDS is physically connected to the correct INS devices and configured for monitoring the correct ports on the INS devices; 4) conducted training on the updated IDS validation process and updated procedures for IT security and INS subject matter experts; and 5) created a baseline diagram of the IDS physical configuration to be used as a reference for annual validation tasks. | 2013-04-05 | 2013-05-09 | Admits | The same event caused a violation for an affiliated entity. MRO reviewed MRO_URE2's internal compliance program and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012011038 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. Specifically, NPCC_URE1 failed to afford the protective measures in CIP-007 R3 and CIP-007 R5.3 for Cyber Assets used in the access control and monitoring of its Electronic Security Perimeters (ESPs). NPCC_URE1 determined that ten accounts did not have passwords changed at least annually as required by CIP-007 R5.3.3. The affected accounts consisted of the following: one shared administrator account on two Cyber Assets (firewall servers used to configure firewall rule sets on electronic access points); three shared administrator accounts on two Cyber Assets (RSA appliance servers used to support two-factor authentication to Cyber Assets used in the access control and/or monitoring of an ESP); and six accounts (consisting of two shared, administrator accounts, three user accounts with administrative privileges, and one shared account with non-elevated privileges) on two Cyber Assets (network domain controllers that are used in conjunction with RSA to support two-factor authentication to Cyber Assets used in the access control and/or monitoring of an ESP). These Cyber Assets are used by NPCC_URE1 to manage access to Critical Cyber Assets (CCAs) and non-critical Cyber Assets within defined ESPs. NPCC_URE1 also determined that it did not perform its assessment of security patches and security upgrades for applicability on four Cyber Assets used to perform centralized logging and alerting within thirty calendar days of availability as required by CIP-007 R3. The assessments of security patches and security upgrades were not completed within 30 calendar days as required because of unclear and undefined roles and responsibilities. | CIP-005-3a | R1; R1.5 | Medium | Severe | The issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE1's failure to afford several of the required protective measures to its Cyber Assets used in ESP access control and/or monitoring rendered its system more vulnerable to attack. The risk to the BPS was reduced because NPCC_URE1 provided password protection to all Cyber Assets that monitor its ESP, and the Cyber Assets are protected with a firewall that can only be accessed by authorized personnel using two-factor authentication. Additionally, all Cyber Assets are within a Physical Security Perimeter (PSP), and electronic and physical access to PSPs is controlled, monitored, and logged. All personnel and contractors that had access to Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with antivirus software and malware prevention tools. | when the Standard became mandatory and enforceable on NPCC_URE1 | when NPCC_URE1 completed its Mitigation Plan | $0 (for NPCC2012011037 and NPCC2012011038) | Self-Report | To mitigate this issue, NPCC_URE1: 1) filed Technical Feasibility Exceptions (TFEs) for the Cyber Assets identified in the Self-Report as they relate to CIP-007 R5.3 requirements; 2) performed a review of CIP-007 R3 controls for Cyber Assets used in the access control and/or monitoring of the ESPs and established a corrective action plan to address any issues or improvements identified during the reviews; 3) performed a review of account management controls for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs pursuant to CIP-007 R5 (including the need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews; and 4) implemented corrective actions as identified in action plans created in milestones 1-3 for applicable Cyber Assets used in the access control and/or monitoring of the ESPs. | 2013-07-11 | 2014-02-25 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012011037 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3a R2.2. Specifically, NPCC_URE1 failed to afford the protective measures in CIP-007 R3.1 and CIP-007 R5.3.3 for Cyber Assets that authorize and/or log access to the Physical Security Perimeters (PSPs). For CIP-007-3 R3.1, NPCC_URE1 self-identified 14 security patches applicable to two access control intrusion detection servers that were not assessed within 30 days of availability. NPCC_URE1 determined that this lapse was due to unclear and undefined roles and responsibilities within the company. The security patches related to the operating system were assessed approximately 120 days after they became available. For CIP-007 R5.3.3, NPCC_URE1 failed to change passwords annually for 2 servers and 39 accounts used for physical access control. NPCC_URE1 determined that this was due to a software bug within its system. Specifically, the date field was incorrectly changing during any update to a user account rather than strictly during a password change. | CIP-006-3a | R2; R2.2 | Medium | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to apply patches and password controls properly can leave Cyber Assets vulnerable to cyber threats. The patches were properly assessed within 120 days rather than the required 30 days. The two servers are behind a firewall which requires two-factor authentication and are within a defined PSP. The servers reside at secure data centers which contain card readers and locks on the individual doors. An audible alarm sounds and an alarm is sent to the security operations center if there are any attempts to circumvent a door or cabinet that contains a card reader. The security operations center is staffed at all times. Camera footage may be utilized remotely by the security operations center for resolution purposes. | when the Standard became mandatory and enforceable on NPCC_URE1 | when NPCC_URE1 completed its Mitigation Plan | $0 (for NPCC2012011037 and NPCC2012011038) | Self-Report | To mitigate this issue, NPCC_URE1: 1) collaborated with its manufacturer to confirm the operator table and password history table were in sync and that NPCC_URE1's results can be replicated in manufacturer’s lab to ensure it was not specific to NPCC_URE1's environment; 2) created a script that automatically notifies a users via email if his or her password has not been changed in 305 days (60 days before 365 days limit), 335 days (30 days before 365 days limit) and 358 days (7 days before the 365 days limit); 3) created a script that automatically notifies via email the access control intrusion detection system application administrators if any account password has not been changed in 359 days or more and requests that the administrator terminate and/or disable the account; 4) updated corporate security document to reflect the notifications outlined in milestones 2 and 3; 5) trained corporate security personnel responsible for the updates made to corporate security document; 6) communicated the requirement to change passwords annually and that a failure to change passwords annually will result in termination of the account; 7) conducted an extent of condition analysis on all the physical access control devices in regards to the protective measures required by CIP-006-3a R2.2. As part of the analysis, a review of corporate security’s CIP-007 procedures and test plans was conducted and a determination made if any gaps existed in relation to specified protective measures in CIP-007-3. The analysis included a review of security patch management controls under CIP-007 R3 and a review of account management devices and their associated technical and procedural controls under CIP-007 R5. The results were reviewed, and a corrective action plan was developed and completed to address identified gaps; 8) communicated and trained affected personnel on the changes from the corrective action plan; 9) performed an extent of condition review for the affected servers to evaluate the CIP-007 R3 controls for Cyber Assets used access control and monitoring of the PSP and established a corrective action plan to address any issues or improvements identified during the review; 10) performed an extent of condition review of account management controls for the affected servers in relation to Cyber Assets used in the access control and/or monitoring of the PSPs (including the need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews; and 11) implemented corrective actions as identified in action plans for applicable Cyber Assets used in the access control and/or monitoring of the PSPs. | 2013-06-20 | 2014-02-14 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012345 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-004-3 R4.1. SPPRE_URE1 did not maintain an accurate list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. One employee was listed as having “user” level access to CCAs when the employee’s actual access rights were “administrative” level. Furthermore, the noted discrepancy was not identified despite multiple quarterly CCA access reviews. | CIP-004-3 | R4; R4.1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1's failure was due to a documentation error on the access list and not an actual mistake in the level of access granted. A review of the employee’s access indicated that “administrative” level access was appropriate, and the employee had the necessary credentials for such access. | the date an account audit identified the employee's account as requiring “administrative” level access instead of the "user" access it was recorded on the list of access rights | the date the access list was updated to indicate “administrative” level access was held by the employee | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1 : 1) implemented a new system for tracking and managing user access requests, authorizations, revocations, and reviews; 2) updated its access control program to detail workflow of the new access control system; 3) tested the new system in a test environment; 4) entered all user records into the new system and implemented the new system into the production environment; and 5) performed a quarterly review of all access rights utilizing the new system. | 2013-08-30 | 2013-09-10 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered SPPRE_URE1's compliance history to be an aggravating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012347 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-005-3a R4 (R4.2, R4.5). SPP RE determined that SPPRE_URE1's Cyber Vulnerability Assessment (CVA) for the access points to its Electronic Security Perimeters did not include: 1) evidence of a review to verify that only ports and services required for operations at the access points were enabled; or 2) a documented action plan to remediate or mitigate vulnerabilities identified in the CVA. With regard to R4.2, SPPRE_URE1 did not retain the output files that were used to confirm that the ports and services enabled on SPPRE_URE1's access points adhered to SPPRE_URE1's ports and services baseline. With regard to R4.5, SPPRE_URE1 indicated that it ensured a remediation “action plan” was in place to remediate any identified vulnerabilities by verifying that an open change control ticket existed for all identified vulnerabilities. However, SPPRE_URE1 did not provide evidence that linked the identified vulnerabilities to open SPPRE_URE1 change control tickets. Therefore, SPP RE could not verify that all vulnerabilities had been remediated during its review of the CVA evidence. | CIP-005-3a | R4; R4.2; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A lack of evidence to confirm that only the operationally required ports and services were enabled presents the risk that non-required ports or services may have remained enabled on the access points, thereby increasing the vulnerability of the access points to malicious exploitation of the non-required ports and services. Nevertheless, SPPRE_URE1 did attest that it had conducted a review of ports and services despite the failure to retain the associated output files, and SPPRE_URE1's CVA did not identify any non-required ports or services as being enabled. Regarding R4.5, SPPRE_URE1 utilized its work order system to confirm that existing work orders existed to correct all identified CVA vulnerabilities. Therefore, SPPRE_URE1 did have documented actions in place to remediate the vulnerabilities, despite its lack of a documented “action plan” as required by R4.5 and SPPRE_URE1's CVA procedure. | the last date in the year all CVA actions could have been completed | Mitigation Plan completion | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) updated its CVA procedure to include a requirement that SPPRE_URE1 retain all baseline output evidence; 2) updated its CVA procedure to require that change control tickets being utilized as “action plans” be referenced in its vulnerability assessment section of the CVA; and 3) supplied output file evidence to demonstrate its review and confirmation that only operationally required ports and services are enabled. | 2013-11-21 | 2014-01-13 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012348 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-006-3c R1 (R1.6.1, R1.6.2). Regarding R1.6.1, SPPRE_URE1 did not document the entry and exit to the Physical Security Perimeter (PSP) of renovation contractors on five occasions in its visitor log. Regarding R1.6.2, SPPRE_URE1's log book did not contain an identified escort for janitorial staff (not having authorized unescorted access) on five occasions. Furthermore, on one occasion, a SPPRE_URE1 employee listed his name only as "Dispatcher" in the log book, thereby preventing the employee's identification as authorized to escort visitors. | CIP-006-3c | R1; R1.6.1; R1.6.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to adequately log visitors at the PSP access points created a risk that personnel were not properly supervised in the vicinity of Critical Cyber Assets, which increased the risk of misuse or sabotage. Nevertheless, the personnel in question were employed by SPPRE_URE1 to perform tasks within the control centers, and SPPRE_URE1 asserted that the personnel in question were escorted at all times while inside the PSPs, despite the failure to adequately log each instance. | the date of the first failure to adequately log | the date of the last instance of the last failure to adequately log | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) created a new tracking form, better aligned with its logging requirements; 2) updated its physical security plan to require escorts fill out the new tracking form on behalf of their visitors; 3) emailed all possible PSP escorts to inform them of the new tracking form and logging expectations; 4) placed instructions at each PSP visitor log book to clearly identify escort duties; and 5) trained all personnel on what information must be captured for each visitor. | 2013-08-12 | 2013-09-05 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012349 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-3a R8 (R8.2, R8.4). SPPRE_URE1's Cyber Vulnerability Assessment (CVA) for the Cyber Assets within its Electronic Security Perimeter (ESP) did not include: 1) evidence of a review to verify that only ports and services required for operations at the access points were enabled (R8.2); or 2) a documented action plan to remediate or mitigate vulnerabilities identified in the CVA (R8.4). Regarding R8.2, SPPRE_URE1 did not retain the output files that were used to confirm that the ports and services enabled on SPPRE_URE1's Cyber Assets within its ESP adhered to SPPRE_URE1's ports and services baseline. Regarding R8.4, SPPRE_URE1 indicated that it ensured a remediation “action plan” was in place to remediate any identified vulnerabilities by verifying that an open change control ticket existed for all identified vulnerabilities. However, SPPRE_URE1 did not provide evidence that linked the identified vulnerabilities to open SPPRE_URE1 change control tickets. Therefore, SPP RE could not verify that all vulnerabilities had been remediated during its review of the CVA evidence. | CIP-007-3a | R8; R8.2; R8.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A lack of evidence to confirm that only the operationally required ports and services were enabled presents the risk that non-required ports or services may have remained enabled on the Cyber Assets, thereby increasing the vulnerability of the Cyber Assets to malicious exploitation of the unidentified ports and services. Nevertheless, SPPRE_URE1 did attest that it had conducted a review of ports and services despite the failure to retain the associated output files, and SPPRE_URE1's CVA did not identify any non-required ports or services as being enabled. Regarding R8.4, SPPRE_URE1 utilized its work order system to confirm that existing work orders existed to correct all identified CVA vulnerabilities. Therefore, SPPRE_URE1 did have documented actions in place to remediate the vulnerabilities, despite its lack of a documented “action plan” as required by R8.4 and SPPRE_URE1's CVA procedure. | the last date in the year all CVA actions could have been completed | Mitigation Plan completion | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) updated its CVA procedure to include a requirement that SPPRE_URE1 retain all baseline output evidence; 2) updated its CVA procedure to require that change control tickets being utilized as “action plans” be referenced in its vulnerability assessment section of the CVA; and 3) supplied output evidence to demonstrate its review and confirmation that only operationally required ports and services are enabled. | 2013-11-21 | 2014-01-13 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012351 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-3a R3 (R3.1, R3.2). SPPRE_URE1 did not document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. SPPRE_URE1 supplied a date range for its assessment period. For 38.7% of the patches or upgrades reviewed, the date range spanned more than 30 days. Additionally, SPP RE identified one instance in which SPPRE_URE1 had a patch change ticket pending for more than a year, but had not applied the patch or applied compensating measures to mitigate risk exposure. | CIP-007-3a | R3; R3.1; R3.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A lack of timely security patch or upgrade assessments and installations unnecessarily exposes SPPRE_URE1's systems to vulnerabilities that could have been lessened through timely patch or upgrade assessments and installations. However, in 91.7% of the assessments periods surpassing 30 days, all assessments were completed in 44 days or less, and the remaining assessment was completed in 66 days. Regarding the one patch for which compensating measures were not documented and applied, the patch presented only one specific database vulnerability, and any attempt to exploit the vulnerability would have required a malicious actor to traverse the hardened Electronic Security Perimeter (ESP). SPPRE_URE1's ESP environment was protected by firewalls (employing deny by default rules) and monitored by a security information and event management server. Additionally, SPPRE_URE1's host devices were outfitted with up-to-date anti-malware. | the first instance in which SPPRE_URE1 exceeded the required assessment timeframe | Mitigation Plan completion | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) tested and implemented the one pending patch identified in the violation description; 2) updated the patch management system to require the application and documentation of mitigating measures if a security patch is not implemented within 365 days of the release; 3) developed and implemented an alert system to ensure that patch/upgrade assessments are conducted within the required 30-day timeframe; 4) developed and implemented training to ensure the proper completion of change control tickets; and 5) required that administrators sign an attestation detailing their understanding of the SPPRE_URE1 patch management process. | 2013-08-02 | 2013-09-05 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012354 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 was in violation of CIP-006-1 R1 (R1.8). Specifically, regarding CIP-007 R8 (R8.2, R8.4), as made applicable by CIP-006-1 R1 (R1.8), SPPRE_URE1's Cyber Vulnerability Assessment (CVA) for the Physical Access Control Systems within its Electronic Security Perimeter did not include: 1) evidence of a review to verify that only ports and services required for operations were enabled; or 2) a documented action plan to remediate or mitigate vulnerabilities identified in the CVA. Additionally, regarding CIP-007 R6 et seq., as made applicable by CIP-006-1 R1 (R1.8), SPPRE_URE1's log server was not collecting Cyber Asset logs during reboot, and therefore, logs originating during the reboot timeframe were not subject to the controls outlined in CIP-007 R6.1 through R6.5. It was determined that when systems hosting a security information and event management (SIEM) log collection agent were rebooted, logs from SPPRE_URE1's networking equipment would be lost for the brief period of time until the log collection agent came back online. Downtime was estimated at five minutes per system restart, so these reboots resulted in approximately 15 minutes of missed logs from switches over a 90-day period. Therefore, SPPRE_URE1 was capturing and analyzing logs over 99.9% of the time and missing an average of 10 seconds per day. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding CIP-007 R8.2, a lack of evidence to confirm that only the operationally required ports and services are enabled presents the risk that non-required ports or services may have remained enabled on the devices, thereby increasing the vulnerability of the devices to malicious exploitation of the non-required ports and services. Nevertheless, SPPRE_URE1 did attest that it had conducted a review of ports and services despite the failure to retain the associated output files, and a subsequent CVA did not identify any non-required ports or services as being enabled. Regarding CIP-007 R8.4, SPPRE_URE1 utilized its work order system to confirm that work orders existed to correct all identified CVA vulnerabilities. Therefore, SPPRE_URE1 did have documented actions in place to remediate the vulnerabilities, despite its lack of a documented “action plan” as required by R8.4 and SPPRE_URE1's CVA procedure. Regarding the CIP-007 R6 logging failure, SPPRE_URE1 was monitoring and logging electronic access to the devices controlling access to the Physical Security Perimeter 99.9% of the time. | the date the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $19,000 (for SPP2013012345, SPP2013012347, SPP2013012348, SPP2013012349, SPP2013012351, and SPP2013012354) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) configured local logging at its switches; 2) implemented and documented a manual log review process to be followed anytime its log review server is offline; 3) updated its CVA procedure to include a step for retaining baseline evidence to confirm that only the operationally required ports and services are enabled; and 4) added language to its CVA procedure specifying that any vulnerability identified will be linked to a change control ticket number. | 2013-07-26 | 2013-08-27 | Neither Admits nor Denies | SPP RE reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPPRE_URE1 was cooperative throughout the processing of the violation, resulting in a reduction to the overall penalty.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009925 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-1 R1 (1.4, 1.5, 1.6). Regarding R1, SPP RE_URE2 did not ensure every Critical Cyber Asset (CCA) resided within an Electronic Security Perimeter (ESP). Specifically, SPP RE_URE2 did not place one CCA inside an identified ESP. Regarding R1.4, SPP RE_URE2 did not identify two devices as non-critical Cyber Assets (or access points) within a defined ESP, and therefore, SPP RE_URE2 could not demonstrate that the devices had been subjected to the applicable CIP requirements. Regarding R1.5, SPP RE_URE2 could not demonstrate that Cyber Assets used in the access control and monitoring of the SPP RE_URE2 ESP were afforded the protective measures specified in CIP-005-3 R2.4, CIP-005-3 R2 (2.5, 2.5.2), CIP-005-3 R2.6, CIP-007-3 R1 (1.2, 1.3), CIP-007-3 R3 (3.1), CIP-007-3 R5.1.3, CIP-007-3 R5.2.2, CIP-007-3 R5.3.2, CIP-007-3 R5.3.3, CIP-007-3 R7 (7.1, 7.2, 7.3), and CIP-009-3 R5. Regarding R1.6, SPP RE_URE2 did not document a Cyber Asset deployed for access control and monitoring of the electronic access points, and therefore, SPP RE_URE2 could not demonstrate that the server was afforded the protective measures referenced in CIP-005-3 R1.5. | CIP-005-1 | R1; R1.4; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding R1, SPP RE_URE2's implementation method created a vulnerability vector into the ESP. However, the device involved was protected by a SPP RE_URE2 corporate firewall; the implicated ESP network was monitored and protected in real-time by an intrusion prevention system; and the device and CCAs inside the ESP were outfitted with up-to-date antivirus protection. Regarding R1.4, although SPP RE_URE2 failed to identify the devices as non-critical Cyber Assets (or access points) within a defined ESP, the devices were serially connected and reside within the SPP RE_URE2 Physical Security Perimeter. Moreover, the technical design and function of the devices limits their susceptibility to cyber attack. Regarding R1.5, the vendor did provide SPP RE_URE2 with a copy of an independent auditor’s Statement on Auditing Standards No. 70 (SAS 70) audit of the vendor’s internal control processes as they related to the deployment and monitoring of the vendor’s devices. The SAS 70 report identified “no relevant exceptions” to the vendor’s identified control descriptions, and the identified controls included background checks for monitoring personnel and authentication requirements for accessing vendor equipment at customer locations. Regarding R1.6, despite the failure to identify the authentication server as a Cyber Asset deployed for access control and monitoring of the electronic access points, SPP RE_URE2 had: 1) installed antivirus software on the device ; 2) placed the device in a physically secure location; 3) protected electronic access via a hardened firewall; 4) and limited access to the firewall to individuals with criminal background checks and appropriate cyber security training. | when the Standard became mandatory and enforceable on SPP RE_URE2 | present | $10,000 (for SPP2012009925, SPP2012009926, and SPP2012009930) | Compliance Audit | To mitigate this violation, SPP RE_URE2 : 1) removed device access; 2) removed the devices from the ESP; 3)_implemented multi-factor authentication at the ESP access points; and 4) replaced a system, which will allow for the production of evidence to demonstrate compliance with CIP-005-3a R1.5. | TBD | TBD | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009926 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-3 R2 (2.1, 2.2, 2.4, and 2.5.3). Regarding R2.1, SPP RE_URE2 had not deployed an access control model that denies access by default at two of its Electronic Security Perimeter (ESP) electronic access points (EAP)s. Regarding R2.2, SPP RE_URE2 did not have documentation (baselines) to demonstrate that only ports and services required for operations and for monitoring Cyber Assets within the ESP were enabled on its ESP access point firewalls. Regarding R2.4, SPP RE_URE2 did not provide evidence to demonstrate that it had implemented strong procedural or technical controls at its access points to ensure the authenticity of its service. While SPP RE_URE2 was able to demonstrate that authentication was occurring, SPP RE_URE2 could not demonstrate that the authentication was multi-factor. Regarding R2.5.3, SPP RE_URE2 did not follow the quarterly review process for electronic access rights per CIP-004-3 R4.1 as made applicable by CIP-005-3 R2.5.3. Only annual reviews were being conducted. | CIP-005-1 | R2; R2.1; R2.2; R2.4; R2.5.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding R2.1, 2.2, and 2.4, while the identified instances of noncompliance created the potential for malicious access or malware injection, the SPP RE_URE2 ESP was monitored by a robust intrusion prevention system that had the ability to alert SPP RE_URE2 staff of malicious traffic and stop it once detected. Additionally, the devices residing inside the ESP were protected by passwords meeting the CIP requirements and up-to-date anti-virus protection. Regarding R2.5.3 SPP RE_URE2 did appropriately grant and revoke access in accordance with CIP-004-3 R4.2, despite the lack of quarterly reviews of electronic access permissions. | when the Standard became mandatory and enforceable on SPP RE_URE2 | present | $10,000 (for SPP2012009925, SPP2012009926, and SPP2012009930) | Compliance Audit | To mitigate this violation, SPP RE_URE2 completed a network redesign | TBD | TBD | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009930 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-006-1 R1.8. SPP RE_URE2 could not demonstrate that Cyber Assets used to authorize and/or log access to its Physical Security Perimeters (PSPs) were afforded all of the protective measures specified in CIP-007 as made applicable by CIP-006-1 R1.8. Specifically, SPP RE_URE2 was unable to demonstrate that devices were subjected to the CIP-007 protective measures. Also, SPP RE_URE2 devices were technically incapable of the anti-malware installation required by CIP-007-3 R4, and SPP RE_URE2 had not requested a Technical Feasibility Exception (TFE). | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Nevertheless, the devices are deployed with hardened firmware that prevents malicious modification, and associated devices were protected in accordance with the CIP-007 requirements. For other devices, access to such devices was limited to only those individuals with authorized physical access rights. Additionally, the devices had passwords meeting the CIP complexity requirements, and electronic access was restricted to those individuals requiring access. Lastly, loss of the devices would not have limited SPP RE_URE2 ability to perform its BPS monitoring and control duties because the devices’ only task is to support physical security control. Such control can be performed by a redundant system, or manually, in the event of a device failure, per the SPP RE_URE2 Emergency Restoration Plan and Cyber Security Incident Response Plan. | when the Standard became mandatory and enforceable on SPP RE_URE2 | present | $10,000 (for SPP2012009925, SPP2012009926, and SPP2012009930) | Compliance Audit | To mitigate this violation, SPP RE_URE2 : 1) requested a TFE; 2) deactivated a device and implemented a remote Virtual Private Network connection through the ESP access point; 3) removed another device from the ESP; and 4) restricted the consoles access to monitor the PSPs. | TBD | TBD | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SPP RE considered SPP RE_URE2's compliance history to be an aggravating factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011837 | Settlement Agreement | During a Compliance Audit Texas RE determined that TRE_URE1 was in violation of CIP-002-1 R1, R1.1, and R1.2. Specifically, TRE_URE1 failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets, as required by CIP-002-1 R1. TRE_URE1 failed to provide any documented evidence that it identified and documented a RBAM. Additionally, TRE_URE1 did not consider all assets listed in R1.2 when developing its RBAM. | CIP-002-1 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to identify, protect, and secure Critical Cyber Assets (CCAs) and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE1 did not have any CCAs. Consequently, TRE_URE1 did not own or operate any CCAs during the violation period. Therefore, Texas RE concluded that there had been no actual harm to the BPS. | when the Standard became mandatory and enforceable on TRE_URE1 | when the entity signed its revised RBAM that included the application of the evaluation criteria | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Compliance Audit | To mitigate this violation, TRE_URE1: 1) created an RBAM and revised it to include evaluation criteria that examined the risk to the BPS; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-29 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011838 | Settlement Agreement | During a Compliance Audit Texas RE determined that TRE_URE1 was in violation of CIP-002-1 R2. Specifically, TRE_URE1 failed to develop a list of its identified Critical Assets through the annual application of the risk-based assessment methodology (RBAM) required in CIP-002-1 R1. | CIP-002-1 | R2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to identify, protect, and secure Critical Cyber Assets (CCAs) and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE1 did not have any CCAs. Consequently, TRE_URE1 did not own or operate any CCAs during the violation period. Therefore, Texas RE concluded that there had been no actual harm to the BPS. | when the Standard became mandatory and enforceable on TRE_URE1 | when the entity documented an application of the RBAM to develop a list of identified Critical Assets | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Compliance Audit | To mitigate this violation, TRE_URE1: 1) developed a list of Critical Assets based on the application of its RBAM; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-29 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011839 | Settlement Agreement | During a Compliance Audit Texas RE determined that TRE_URE1 was in violation of CIP-002-1 R3. Specifically, TRE_URE1 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of the Critical Asset. | CIP-002-1 | R3 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to identify, protect, and secure Critical Cyber Assets (CCAs) and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE1 did not have any CCAs. Consequently, TRE_URE1 did not own or operate any CCAs during the violation period. Therefore, Texas RE concluded that there had been no actual harm to the BPS. | when the Standard became mandatory and enforceable on TRE_URE1 | when the entity documented an annual review and application of the RBAM establishing TRE_URE1 no longer had CCAs | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Compliance Audit | To mitigate this violation, TRE_URE1: 1) determined through a risk-based assessment methodology (RBAM) that it does not have CCAs; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-29 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012901 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R1, R1.1, and R1.2. Specifically, TRE_URE2 failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets that includes the application of the evaluation criteria, as required by R1.1. Additionally, TRE_URE2 did not consider all assets listed in R1.2 when developing its RBAM. | CIP-002-3 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2's noncompliance resulted in misidentified or unidentified Critical Assets and over-reporting, under-reporting, or misreporting of associated Critical Cyber Assets (CCAs). Furthermore, given the cross-cutting nature of networked technology, malicious attack or intentional or unintentional misuse may impact multiple assets at once. Therefore, failure to identify, protect, and secure CCAs and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE2 did not have any CCAs. Therefore, Texas RE concluded that there had been no actual impact to the BPS. | when the Standard became mandatory and enforceable on TRE_URE2 | when the entity signed its revised RBAM that included the application of the evaluation criteria | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Self-Certification | To mitigate this violation, TRE_URE2: 1) created an RBAM and revised it to include evaluation criteria that examined the risk to the BPS; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-29 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012902 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R2. Specifically, TRE_URE2 failed to develop a list of its identified Critical Assets through the annual application of the risk-based assessment methodology (RBAM) as required in CIP-002-3 R1. | CIP-002-3 | R2 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2's noncompliance resulted in misidentified or unidentified Critical Assets and over-reporting, under-reporting, or misreporting of associated Critical Cyber Assets (CCAs). Furthermore, given the cross-cutting nature of networked technology, malicious attack or intentional or unintentional misuse may impact multiple assets at once. Therefore, failure to identify, protect, and secure CCAs and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE2 did not have any CCAs. Therefore, Texas RE concluded that there had been no actual impact to the BPS. | when the Standard became mandatory and enforceable on TRE_URE2 | when the entity documented an application of the RBAM to develop a list of identified Critical Assets | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Self-Certification | To mitigate this violation, TRE_URE2: 1) developed a list of Critical Assets based on the application of its RBAM; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-29 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-40-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012903 | Settlement Agreement | TRE_URE2 submitted a Self-Certification stating that it was in violation of CIP-002-3 R3. Specifically, TRE_URE2 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of the Critical Asset. | CIP-002-3 | R3 | High | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2's noncompliance resulted in misidentified or unidentified Critical Assets and over-reporting, under-reporting, or misreporting of associated Critical Cyber Assets (CCAs). Furthermore, given the cross-cutting nature of networked technology, malicious attack or intentional or unintentional misuse may impact multiple assets at once. Therefore, failure to identify, protect, and secure CCAs and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, after further review and proper execution of the RBAM it became evident that TRE_URE2 did not have any CCAs. Therefore, Texas RE concluded that there had been no actual impact to the BPS. | when the Standard became mandatory and enforceable on TRE_URE2 | when the entity documented an annual review and application of the RBAM establishing TRE_URE2 no longer had CCAs | $25,000 (for TRE2013011837, TRE2013011838, TRE2013011839, TRE2013012901, TRE2013012902, and TRE2013012903) | Self-Certification | To mitigate this violation, TRE_URE2: 1) determined through a risk-based assessment that it does not have CCAs; 2) updated the RBAM to describe in detail how to apply the evaluation criteria to identify its Critical Assets and CCAs; and 3) created a compliance management plan that details its RBAM, Critical Assets, and CCA annual review process. | 2014-01-27 | 2014-01-31 | Neither Admits nor Denies | Texas RE reviewed TRE_URE2's internal compliance program documentation and considered it to be a neutral factor in the penalty determination.
2014-04-30 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010534 | Notice of Confirmed Violation | During a Compliance Audi, MRO determined that MRO_URE1 was in violation of CIP-004-1 R3. Specifically, MRO discovered that MRO_URE1 failed to ensure that each personnel risk assessment (PRA) included an identity verification, as required by CIP-004-1 R3.1, and failed to document the results of PRAs of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as required by CIP-004-1 R3.3. Upon discovering the issues during the Compliance Audit, MRO_URE1 performed a comprehensive review of its PRA records. MRO_URE1 discovered it had also failed to document one identity verification for one employee, and failed to perform PRAs for five contractors within 30 days of granting authorized cyber access. | CIP-004-1 | R3; R3.1; R3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five contractors identified were long-term third-party employees used to support the energy management system and had access to the system prior to the CIP-004-1 R3 mandatory compliance date. Additionally, MRO_URE1 performed a PRA on each of the contractors within six months of the Standard's mandatory compliance date. MRO_URE1 also provided an attestation stating that it performed an identity verification on the employee, but failed to retain the proper documentation demonstrating the verification. Upon performing a comprehensive review, MRO_URE1 determined that the documentation issue was limited to the single occurrence. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1 revised its Cyber Security personnel and training program, and adopted a policy so that all new hires will receive an identity verification and seven-year criminal check from a private investigation firm. | 2013-06-28 | 2013-07-31 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-04-30 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010536 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE was in violation of CIP-004-3 R4. Specifically, MRO discovered that MRO_URE1 failed to update a list of personnel with authorized cyber access for five contractors within seven days of a change in access rights, as required by CIP-004-3 R4.1. Five contractors did not require access to Critical Cyber Assets (CCAs), however, their access to accounts was not removed until approximately a month after access was no longer required to the CCAs. Therefore, the contractors remained on the access list 21 days longer then the seven days permitted by CIP-004-3 R4.1. | CIP-004-3 | R4; R4.1 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1 failed to remove CCA access for five contractors access for 21 days due to a failure to follow its procedures. These contractors had administrative level access to the energy management system. However, MRO determined that this violation did not pose a serious or substantial risk to the BPS because the contractors were long-term third-party employees which were re-assigned to other projects and were not terminated for cause. Furthermore, although MRO_URE1 failed to remove access to the accounts locally, the third-party removed remote access for the contractors within seven days. Additionally, MRO_URE1 has a policy that requires escorted access to Critical Assets for contractors, so the contractors would have been unable to have physical access to the assets. Further, the duration of the violation was 21 days. | when MRO_URE1 failed to change the access rights within seven days | when MRO_URE1 updated its list of personnel with authorized cyber access | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) reviewed policies in place that account for CIP-004 R4; 2) reviewed processes for MRO_URE1 employee access approval, job changes and revocation; 3) reviewed processes for contractor access approval, job changes, and revocation; 4) reviewed the contractor procedures for access and revocation; and 5) developed an automated workflow for tracking access changes. | 2013-07-18 | 2013-08-27 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-04-30 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010537 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 failed to protect Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP) as required by CIP-005-1 R1.5. Specifically, MRO_URE1 failed to document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades as required by CIP-007-1 R3.1. Upon discovering the issue, MRO_URE1 performed a comprehensive review of its patches and security upgrades. MRO_URE1 failed to document the assessment of nine patches within thirty days of availability. | CIP-005-1 | R1; R1.5 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document the assessment of nine patches within thirty days of availability, MRO_URE1 monitored and applied the appropriate security patches on its ESP access points. Additionally, MRO_URE1 demonstrated that it received email alerts from a third-party contractor when patches and vulnerabilities existed for the device, and provided evidence that it appropriately and promptly installed the proper patches. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1 reviewed the third-party patch management services and reviewed its agreements with the third party to ensure that patches will be assessed on a timely basis. | 2012-12-19 | 2013-06-11 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-04-30 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010539 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-006-1 R1. Specifically, MRO discovered that MRO_URE1 failed to identify all access points through each Physical Security Perimeter (PSP) and failed to implement measures to control entry at those access points, as required by CIP-006-1 R1.2. MRO_URE1 failed to identify and implement measures to control entry at a door with access to a computer room, and a door to the inverter room. Additionally, MRO discovered that MRO_URE1 failed to afford the protective measures specified in Standards CIP-003, CIP-004 R3, CIP-005 R2 and R3, CIP-006 R2 and R3, CIP-007, CIP-008, and CIP-009, for one Cyber Asset used in controlling the physical access card readers to the energy management system (EMS), as required by CIP-006-1 R1.8. | CIP-006-1 | R1; R1.2; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to identify and control entry to access points may result in easier access for unauthorized individuals. However, MRO determined that this violation did not pose a serious or substantial risk to the BPS because the undocumented doors were either controlled by a steel bar and padlock when not used for moving equipment or locked and blocked shut by a handrail. Additionally, MRO_URE1's physical access card reader controller utilizes a custom operating system. This custom system reduced the risk of malware and well-known vulnerabilities. Furthermore, the physical access card reader controller was located within the PSP which limits physical access to the device. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) installed a new card door reader on double doors located in MRO_URE1's equipment room; 2) removed and filled in the oversized door in MRO_URE1's inverter room; 3) drafted and implemented a compliance plan to address topics related to compliance with CIP requirements; and 4) added a secondary monitoring system to the security of the PSP, which will be tied into MRO_URE1's EMS. | 2013-10-28 | 2013-11-05 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-04-30 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010541 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-006-1 R3. Specifically, MRO discovered that MRO_URE1 failed to implement technical controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. MRO discovered that the double doors with access to the energy management system computer room were not documented and did not have controls for monitoring physical access. Upon discovering the issue, MRO requested that MRO_URE1 perform a comprehensive review of its PSP access points. MRO_URE1 reported that a second door into the inverter room was also not documented and also did not have controls for monitoring physical access. Both access points did not have either an alarm system or human observation to monitor access, as required by CIP-006-1 R3. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to identify and monitor entry to access points may result in easier access for unauthorized individuals. However, MRO determined that this violation did not pose a serious or substantial risk to the BPS because the undocumented doors were either controlled by a steel bar and padlock when not used for moving equipment, or locked and blocked shut by a handrail. Therefore, access through the doors was impaired via physical barriers. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) installed a card door reader to provide monitoring and logging of the PSP; and 2) removed and filled the other door in order to eliminate the access point. | 2013-06-12 | 2013-07-31 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-03-31 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010542 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-007-1 R2. MRO_URE1 failed to document a process for identifying which ports and services are required for normal and emergency operations, as required by CIP-007-1 R2. Additionally, MRO_URE1 identified several ports in the dynamic range in a network mapper port scan, but those ports were not identified in any of the approved baseline documents. Therefore, MRO_URE1 also failed to enable only ports and services required for normal and emergency operations, as required by CIP-007-1 R2.1. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document a process for identifying ports and services, MRO_URE1 did perform the process to identify ports and services for normal and emergency operations and provided baseline reports. However, MRO_URE1 failed to document several dynamic ports. Upon completing a comprehensive review of its ports and services, MRO_URE1 confirmed that no unauthorized applications were discovered, and the lack of documentation was limited to dynamic ports. Additionally, MRO_URE1 upgraded its energy management system (EMS) since the Compliance Audit, and developed new baselines. MRO_URE1 also performed a comprehensive review of ports and services on its new EMS and did not discover any errors in the documentation. | when the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) developed verification procedures that detail the process for assessing ports and services including the creation and verification of baselines; 2) prepared a capital project for acquiring a tool-based technical solution that will provide advanced protections to Critical Cyber Assets within MRO_URE1's Electronic Security Perimeters, access points, and monitoring systems; and 3) will alternate between third-party Cyber Vulnerability Assessments (CVAs) and in-house CVAs. This will address concerns with checks and balances within MRO_URE1 where the same personnel that completed the work are the only ones equipped to execute the CVA in order to assess the work. | 2013-08-14 | 2013-12-16 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-03-31 | FERC | NP14-35-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010545 | Notice of Confirmed Violation | During a Compliance Audit, MRO determined that MRO_URE1 was in violation of CIP-007-1 R5. Specifically, MRO_URE1 failed to ensure that user accounts were implemented as approved by designated personnel for six accounts, as required by CIP-007-1 R5.1.1, and failed to require and use passwords that consist of a combination of alpha, numeric, and "special" characters for four accounts, as required by CIP-007-1 R5.3.2. | CIP-007-1 | R5; R5.1.1; R5.3.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 did not have a combination of alpha, numeric, and "special" characters on four accounts, each of the accounts had passwords that were at least six characters, the passwords were changed annually, and the devices with the accounts were not capable of passwords with a combination of special characters. Therefore, MRO_URE1 submitted a Technical Feasibility Exception (TFE) for several devices. Additionally, although MRO_URE1 failed to provide evidence of designated personnel approval for six user accounts, MRO_URE1 was able to demonstrate the user accounts were appropriate for each user. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 ensured that user accounts were implemented as approved by designated personnel and that passwords met complexity requirements where technically feasible | $20,000 (for MRO2012010534, MRO2012010536, MRO2012010537, MRO2012010539, MRO2012010541, MRO2012010542, and MRO2012010545) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) upgraded its energy management system (EMS) to verify the system for CIP compliance prior to implementation; 2) performed factory acceptance testing on the new EMS and worked with the EMS vendor to inventory accounts and password complexity requirements; 3) updated the account list spreadsheet to account for electronic access and inventory all user accounts; 4) removed the term “grandfathered” from all electronic and account access dates to provide accurate access approval dates; 5) reviewed user and account authentication for the upgrade to ensure all accounts comply as technically feasible for password complexity, and in the event it is not technically feasible, submitted a TFE; 6) reviewed the MRO_URE1 Cyber Security account management policy; 7) purchased a change control and configuration management solution to help automate and track compliance with CIP-007 R5, and provide one centralized platform to automated security and compliance for the EMS; 8) created a personnel authorizing access document which provides a list of designated personnel that are responsible for authorizing access to protected information; and 9) reviewed a list of individuals who have access to protected information to determine if the access they have correlates with their current responsibilities. | 2013-07-01 | 2013-08-27 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO_URE1 invested approximately $140,000 in a compliance software program to address compliance with CIP Reliability Standards. MRO considered this investment and commitment to compliance as a factor that reduced the penalty.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012979 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3 R2. During a periodic review, WECC_URE1 discovered that an individual who had access to Critical Cyber Assets (CCAs) did not receive NERC CIP cyber training in calendar year 2012. After discovering this instance, WECC_URE1 conducted further examination of its training records and discovered that a total of 11 individuals who had authorized logical and unescorted physical access to CCAs had no training records for 2012. WECC determined that WECC_URE1 could not provide documentation demonstrating that 11 individuals with authorized logical and unescorted physical access to CCAs received appropriate cyber security training in 2012. WECC determined the cause of the violation was that WECC_URE1's training program improperly duplicated its code system and indicated the individuals had received training, when in fact they had not. | CIP-004-3 | R2; R2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 11 individuals had received initial cyber security training, and were also trained during calendar year 2011. WECC_URE1 ensured all personnel had current personnel risk assessments, thus reducing the chance of intentional mishandling of CCAs. In addition, WECC_URE1 continuously staffs and monitors its access points to its Physical Security Perimeters. | when WECC_URE1 failed to provide cyber security training to the 11 individuals | when WECC_URE1 revoked access to CCAs for the 11 individuals | 8000 | Self-Report | To mitigate this violation, WECC_URE1: 1) completed a full review of all physical and cyber access provisioning; 2) revoked access for each of the 11 individuals; 3) provided cyber security training to those individuals still requiring access; and 4) instituted a new training procedure to prevent similar duplication errors in the future. The new procedure includes that: a) a new program title for training will be created each year; b) a new learning objective will be created each year; and c) a new activity code will be created each year. | 2013-09-23 | 2013-11-01 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered compliance history to be an aggravating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012011543 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.8. WECC_URE2 failed to perform a Cyber Vulnerability Assessment (CVA) on all devices used in the access control and monitoring of the Physical Security Perimeter (PSP). WECC_URE2 also failed to identify and protect devices as Cyber Assets used in physical access control and monitoring (PACM). | CIP-006-1 | R1;1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by WECC_URE2's failure renders WECC_URE2 Critical Cyber Assets and Cyber Assets within PSPs vulnerable to physical as well as cyber attack or misuse. WECC_URE2 failed to ensure the efficacy of protections for devices when it failed to perform CVAs. WECC determined, however, that the risk posed by WECC_URE2 noncompliance is offset given compensating measures in place during the pendency of the violation period. All the devices at issue are located in secure corporate networks where logical access is controlled and monitored by firewalls. Additionally, all devices were located in secure facilities where all physical access is controlled and monitored. | when WECC_URE2 failed to ensure CIP-006-1 R1.8 protections for the devices | Mitigation Plan completion | $40,000 (for WECC2012011543 and WECC2013012332) | Self-Report | To mitigate this violation, WECC_URE2: 1) relocated the devices to an Electronic Security Perimeter-like protected network and integrated them into existing processes and controls to ensure their full compliance with CIP-006 R1.8. This includes adding them to WECC_URE2's CIP-related asset database so future activities, such as change management, will follow procedures; 2) conducted a CVA for all in-scope workstations and included devices in future scheduled CVAs; 3) updated CIP-005 R2 and R3 and CIP-007 document and process applicability to include in-scope WECC_URE2 devices; 4) updated and resubmitted CIP-007 R4 and R6 Technical Feasibility Exceptions; and 5) implemented CIP-007 processes to devices that are technically feasible. The CIP-007 R5 processes will also facilitate compliance with CIP-004 R3. | 2013-08-13 | 2013-08-15 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012332 | Settlement Agreement | During a Compliance Audi WECC determined that WECC_URE2,was in violation of CIP-007-3a R7. WECC_URE2 failed to implement its disposal and redeployment process for Critical Cyber Assets and Cyber Assets within an Electronic Security Perimeter. | CIP-007-3a | R7 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to establish controls to dispose of Cyber Assets could allow malicious access to sensitive information related to cyber security or reliability. Such information could then be used to get access to Critical Cyber Assets essential to the operation of BPS and potentially disrupt the operation of the BPS. The devices contained limited sensitive cyber security and reliability data. WECC determined that the violation posed a moderate risk given the number of devices in scope, and increased access to data stored on the devices. The risk posed by WECC_URE2 noncompliance is mitigated by the compensating measures in place during the pendency of the violation. The devices, remained in the WECC_URE2 corporate environment. None of the devices were sent out to third parties before information had been erased/removed per WECC_URE2's process. | when WECC_URE2 failed to follow its disposal and redeployment process for devices identified as a Critical Cyber Asset or Critical Asset | Mitigation Plan completion | $40,000 (for WECC2012011543 and WECC2013012332) | Compliance Audit | To mitigate risk of this violation, WECC_URE2: 1) updated the system security management document and disposal and redeployment overview document; 2) updated the process flow for CIP-007 R7, appearing in the system security management document to reflect these changes; 3) updated the Cyber Asset decommissioning process to include review for declassification items and their redeployment treatment; 4) reviewed the Cyber Assets for WECC_URE2's critical infrastructure information program, ensuring protection of any critical infrastructure information according to the CIP requirements; and 5) documented completion of the review. | 2014-01-17 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010274 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-002-1 R3. The WECC Audit team identified three Critical Cyber Assets (CCAs) that were not listed in the current or prior version of the signed and dated lists of CCAs. Specifically, three assets were visually verified by the Audit team as being contained within the Electronic Security Perimeter (ESP) and the Physical Security Perimeter (PSP) at the control center, but were not identified or included on the signed and dated record of the current list of CCAs. The assets consisted of two energy management system (EMS) operator consoles and one EMS operator thin-client computer that are used to provide EMS support staff with access to the EMS. The assets are connected by ethernet cabling and by a routable protocol to the EMS. The Audit team determined that the three assets at issue should have been identified as CCAs because they are essential to the operation of the control center (a CCA) and use a routable protocol within the control center. Therefore, WECC_URE3 failed to appropriately identify or document components of the EMS as CCAs, resulting in a violation of CIP-002-3 R3. | CIP-002-1 | R3; R3.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE3 did not identify these assets as CCAs, the three assets are contained and protected with the primary control center's ESP and PSP. Additionally, at the time the violation was discovered, the thin-client computer had only been installed for two weeks. Further, all employees that had access to the assets had personnel risk assessments and cyber security training. | when WECC_URE3 failed to include the devices to its CCA list | Mitigation Plan completion | $45,000 (WECC2012010274, WECC2012010364, WECC2012010275, WECC2012010390, and WECC2012010308) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) added the three assets to the CCA list and afforded the required protections of the CIP Reliability Standards; 2) enhanced the process for classifying CCAs in order to prevent future violations of the same Standard; 3) reviewed the process to ensure that all Cyber Assets have been assessed according to WECC_URE3's CCA criteria; and 4) implemented the enhanced process for classifying CCAs to verify that all Cyber Assets have been evaluated and identified correctly. | 2012-09-27 | 2013-07-18 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010364 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-003-1 R5. The WECC Audit team determined that WECC_URE3 has an information access control program, but failed to provide evidence of managing and reviewing access to protected Critical Cyber Asset (CCA) information. Specifically, WECC_URE3 failed to maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information (R5.1); failed to identify personnel by name, title, and the information for which they are responsible for authorizing access (R5.1.1); failed to provide a list of personnel responsible for authorizing access to protected information annually (R5.1.2); failed to review at least annually the access privileges to protected information (R5.2); and failed to document at least annually the processes for controlling access privileges to protected information (R5.3). Therefore, WECC determined WECC_URE3's failure to provide evidence of its performance related to managing and reviewing access to protected CCAs at WECC_URE3's control center and backup control center for approximately two years is a violation of CIP-003-1 R5, specifically R5.1, R5.1.1, R5.1.2, R5.2 and R5.3. | CIP-003-1 | R5; R5.1; R5.1.2; R5.2; R5.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE3 failed to provide documentation or evidence of the performance related to managing and reviewing access to CCAs, WECC_URE3 did have a program and was informally managing access to the protected CCA information by quarterly reviews of staff access to this information. Additionally, WECC_URE3's annual review process and the authority to grant access to Cyber Assets were granted to WECC_URE3's energy management system management members to formalize responsibilities. Further, during the violation period, all personnel who had access to protected CCA information had personnel risk assessments and current CIP cyber security training and all the CCAs were protected within an Electronic Security Perimeter and Physical Security Perimeter. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $45,000 (WECC2012010274, WECC2012010364, WECC2012010275, WECC2012010390, and WECC2012010308) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) implemented a revised information access control program; 2) maintained a list of designated personnel who are responsible for authorizing logical and physical access to protected information; 3) identified personnel by name, title, and the information for which they are responsible for authorizing access; 4) verified annually the list of personnel responsible for authorizing access to protected information; 5) reviewed at least annually the access privileges to protected information; and 6) assessed annually the processes for controlling access privileges to protected information. | 2012-09-21 | 2012-09-25 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010275 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-005-3 R4. The WECC Audit team reviewed documentation from a third-party vendor that WECC_URE3 uses to perform its vulnerability assessments and determined that WECC_URE3 conducted two Cyber Vulnerability Assessments (CVAs) on Electronic Security Perimeter (ESP) access points. The second CVA did not include documented results of the assessment, the action plan, and the execution of the action plan. Specifically, the vendor's report did not provide any procedures, analysis of evidence, or results of the assessment. | CIP-005-3 | R4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, without the full documentation of the CVA result and action plan, it was unclear whether the six access points that encompassed the two Critical Assets (the primary and backup control centers) were exposed to vulnerabilities. Thus, failing to have detailed evidence of the performance of the CVA could result in unchecked assets, and undetected cyber vulnerabilities. Although WECC_URE3 did not have detailed evidence of performance of the assessment, it did have a vendor report indicating the CVA had been completed and the access points in scope were contained and protected within the Physical Security Perimeters of the primary and backup control centers. | when WECC_URE3 failed to perform a valid CVA | Mitigation Plan completion | $45,000 (WECC2012010274, WECC2012010364, WECC2012010275, WECC2012010390, and WECC2012010308) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) enhanced its CCA documentation to clearly identify all access points to the ESPs; 2) updated the scope of work to be performed when using an outside vendor for CVAs; 3) had the vendor assess all access points to the ESPs; and 4) performed an additional level of review after the CVA has been completed by the vendor to ensure a gap analysis of the CVA was performed to verify that it met the requirements of CIP-005 R4. | 2013-03-19 | 2013-08-29 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010390 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-006-1 R1. The WECC Audit team determined that WECC_URE3 failed to afford CIP-005 R2 and R3, and CIP-007 R1 through R9 protections to Cyber Assets used in the physical access control and monitoring of its Physical Security Perimeters (PSPs). Specifically, WECC_URE3 failed to implement electronic access controls (CIP-005 R2); failed to monitor electronic access (CIP-005 R3); and failed to ensure systems security management (CIP-007 R1 through R9) to nine workstations, four access control management (ACM) firewalls, one host, one application server, and one card access server. WECC further determined that a WECC_URE3 affiliate submitted a Self-Report because it failed to afford the same protective measures used in the physical access control and monitoring of its PSPs. The scope of WECC_URE3's noncompliance is the same reported by the affiliate because the two entities share the same corporate-wide Physical Access Control System (PACS) and the devices in scope were used at both WECC_URE3's and the affiliate's facilities. WECC_URE3 and the affiliate share the same PACS, thus, failing to provide protections resulted in a violation of CIP-006 R1.8 for both entities. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE3 failed to provide PACS the protections provided by CIP-005 R2 and R3 and CIP-007, WECC_URE3 does have several physical security controls in place. Specifically, WECC_URE3's PACS is protected by armed security officers at all times, and the PSPs are monitored by cameras. Additionally, WECC_URE3 requires an escort and security logs to be completed by persons visiting the site. Further, WECC_URE3 has personnel risk assessments for all persons that have access to the PSP that houses the PAC server. WECC_URE3 implemented a cyber security awareness policy which allows employees to identify, classify, respond to, and report cyber security incidents. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $45,000 (WECC2012010274, WECC2012010364, WECC2012010275, WECC2012010390, and WECC2012010308) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) deployed electronic access controls for the Cyber Assets that authorize and/or log access to PSPs; 2) documented the organizational process and technical procedural mechanisms for electronic access control; 3) deployed electronic access monitoring for the Cyber Assets that authorize and/or log access to PSPs; 4) documented the electronic or manual processes for monitoring and logging access twenty-four hours a day, seven days a week; 5) documented and implemented the testing of Cyber Assets and significant changes to existing Cyber Assets that authorize and/or log access to the PSPs; 6) documented and implemented a procedure and process to ensure that only those ports and servers required for normal operations are enabled for Cyber Assets that authorize and/or log access to the PSPs; 7) documented and implemented a security patch management program for Cyber Assets that authorize and/or log access to the PSPs; 8) documented and used the antivirus software and malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets that authorize and/or log access to the PSPs; 9) created alerts that would be sent to the cyber security team for any attempted use of unauthorized software and ensured the logs would be reviewed every 90 days; 10) documented and implemented procedural controls to authorize and enforce access authentication of, and accountability for, all user activity that would minimize the risk of unauthorized system access for Cyber Assets that authorize and/or log access to the PSPs; 11) captured and stored in the security events manager all event logs generated by Windows hosts; 12) captured and stored in the security events manager all sys logs generated by layer firewalls for login activity and configuration changes; 13) documented and implemented security status monitoring by using the WECC_URE3 security information and events management system for Cyber Assets that would monitor/alert system/security logs access to the PSPs; 14) documented and implemented formal methods, processes, and procedures for disposal or deployment of Cyber Assets that authorize and/or log access to the PSPs; 15) documented and implemented a Cyber Vulnerability Assessment program with annual testing for Cyber Assets using vulnerability penetration testing to verify that only ports and services required are enabled and control for accounts verified; 16) documented the results of the assessment and ensured that the results would be reviewed and identify all vulnerabilities; and 17) documented and implemented procedures to review and update all such documentation annually and whenever changes resulted from modifications to the systems or controls within thirty days for Cyber Assets that authorize and/or log access to the PSPs. | 2013-01-04 | 2013-01-15 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-35-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010308 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 was in violation of CIP-007-3a R8. The WECC Audit team reviewed documentation from a third-party vendor that WECC_URE3 uses to perform its vulnerability assessments. The vendor statement of work file, along with the vendor Cyber Vulnerability Assessment (CVA) process demonstrates that WECC_URE3 has a documented process identifying its vulnerability assessment process. However, WECC_URE3 did not provide to the WECC Audit team specific documentation that the CVA verified that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter (ESP) were enabled (R8.2); it did not document the controls for default accounts (R8.3); and the results of the final CVA were not documented nor was an action plan identified or executed (R8.4). WECC determined WECC_URE3 was in violation of CIP-007-3a R8 because WECC_URE3 could not provide specific documentation that confirms the vendor reviewed the open ports for one Cyber Asset, and all other Critical Cyber Assets (CCAs) and non-critical CCAs in the ESP during the CVA process. | CIP-007-3a | R8; R8.2; R8.3; R8.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE3 failing to perform a CVA on all Cyber Assets within an ESP could result in inaccurate and deficient CVA results. Because WECC_URE3's CVA failed to assess vulnerabilities on seven Cyber Assets, cyber vulnerabilities in these assets could go unchecked and undetected. Although WECC_URE3 did not have adequate CVA documentation on the seven Cyber Assets, it did perform an assessment on most of its Cyber Assets, and the assets in scope are all contained and protected within the ESPs and Physical Security Perimeters of the primary and backup control centers. Further, personnel with access to the assets had the required personnel risk assessment and CIP cyber security training. | when WECC_URE3 failed to perform a valid CVA | Mitigation Plan completion | $45,000 (WECC2012010274, WECC2012010364, WECC2012010275, WECC2012010390, and WECC2012010308) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) updated its CCA documentation to clearly identify all CCAs and non-critical Cyber Assets that reside within the ESP; 2) updated the scope of work to be performed when using an outside vendor for vulnerability assessments; and 3) performed an additional level of review which will include assessing the report and executing a gap analysis of the CVA to verify it meets the requirements of the Standard. | 2012-11-01 | 2013-03-22 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-03-31 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009525 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-004-3 R4. A contractor employee working for NPCC_URE1 was terminated by his employer. The termination was the result of a workforce reduction and was not for cause. The contractor employee had authorized unescorted physical access to Critical Cyber Assets (CCAs) at one NPCC_URE1 substation. The employer failed to timely notify NPCC_URE1 of the termination. The contractor employee’s physical access rights were revoked. This violation was discovered during an internal review of CIP training records. NPCC determined that NPCC_URE1 had a violation of CIP-004-1 R4.2 for failing to revoke the terminated contractor's access to CCAs within 24 hours of termination and within seven calendar days of when the contractor no longer required such access to CCAs. | CIP-004-3 | R4; R4.2 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, the delayed revocation of the contractor’s access to the CCAs could have resulted in unauthorized access to NPCC_URE1’s CCAs by the contractor who could have taken actions, after his termination, that could negatively affect the reliability of the BPS. The risk to the reliability of the BPS was mitigated by the following factors. The termination was not for cause. A personnel risk assessment was conducted for the affected contractor with no adverse findings. The card reader access records confirm that the contractor did not attempt to access the substation after his termination. In addition, there are the following security measures are in place to protect the CCAs. The CCAs are inside a control house, which is a physical security perimeter, at the substation. Physical access to the CCAs is controlled by a card key and card lock system which has continuous monitoring and logging. The substation has video cameras. Electronic access to CCA’s is monitored. The CCA’s are protected by malicious software prevention tools. | when the contractor employee's authorized unescorted access was required to be revoked | when the contractor employee's authorized unescorted access was revoked | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE1: 1) administered CIP awareness training to appropriate personnel; 2) issued an internal communication to NPCC_URE1's parent company managers/supervisors who currently have and/or previously employed NERC CIP contractors, highlighting: a) CIP vendor sourcing; CIP contractor on-boarding prerequisites; CIP access grants; and CIP access revocation; 3) issued an employee communication regarding the CIP compliance requirements and existing processes in context of contractors; 4) performed an internal assessment to verify that all vendors providing CIP contractors to NPCC_URE1 have prescriptive NERC CIP compliance requirements language contained in their Procurement Agreement or have executed the NERC CIP Contract Amendment; 5) reviewed all contractor resources for a specific group who have unescorted physical access to critical substations for accuracy and appropriateness; and 6) administered CIP awareness training to the affected contractor. | 2012-02-10 | 2013-08-09 | Neither Admits nor Denies | NPCC reviewed NPCC_URE1, internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE1's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE1 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE1 provided appropriate authorized management to assure full cooperation throughout the settlement process. NPCC considered NPCC_URE1's compliance history to be a aggravating factor in penalty determination.
2014-03-31 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010254 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-004-3 R3. A senior supervisor was granted unescorted physical access rights to enter the Physical Security Perimeter (PSP) at substations containing Critical Cyber Assets (CCAs) before a personnel risk assessment (PRA) was complete. At the time of the incident, the senior supervisor had completed his annual CIP training and had taken NPCC_URE2's NERC CIP training, a module that was part of a multiple-day annual expert training (AET). The senior supervisor mistakenly believed that the PRA requirement was fulfilled by completing the multiple-day AET training program. The senior supervisor mistakenly entered the date he completed this multiple-day training as the PRA date on his access request form. When reviewing the access request form for final approval, the senior supervisor’s manager did not notice the error and approved access based on the incorrect PRA date that was noted on the form. | CIP-004-3 | R3 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to perform a PRA prior to granting unescorted access can potentially lead to breaches of security and the employee did access various locations that contained CCAs. The risk to the BPS was mitigated by the following factors. The senior supervisor has been a long-time employee with NPCC_URE2 for 26 years and did not have electronic access rights to the CCAs. When NPCC_URE2 discovered the violation, it revoked the senior supervisor’s unescorted physical access rights to CCAs. In addition, a PRA was completed for the affected employee with no adverse findings. Furthermore, the following security measures were in place. Physical access to the PSP is controlled by a card key and card lock system which has continuous monitoring and logging. The substations also have video cameras. Electronic access to the CCAs is monitored and the CCAs are protected by malicious software prevention tools. | when unescorted access to the CCAs was granted to the senior supervisor prior to a PRA being conducted | when unescorted access to the CCAs was revoked | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) incorporated a process requiring its security group perform a secondary verification that PRAs and annual CIP training are complete prior to granting employees unescorted physical access to CCAs; 2) issued a communication to authorized access approvers that reconfirms the requirement to verify that PRAs and annual CIP training is complete prior to granting employees unescorted physical access to CCAs; 3) issued a broad employee communication regarding NERC CIP access prerequisites; 4) provided additional training to the project management group regarding NERC CIP access prerequisites and process requirements; 5) updated the NERC CIP physical access request form to provide more explicit instructions to managers responsible for verifying PRAs and CIP Training dates; and 6) initiated a requirement that a verification of completion of PRAs, for all active employees and contractors, who have authorized unescorted physical access to CCAs be performed. | 2012-06-14 | 2013-10-04 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process. The instant violation occurred concurrently with violation NPCC2012010426, which is also being concurrently filed. Based on the NERC Sanction Guidelines, NPCC determined these two violations CIP-004-3 R3 were “related to a single act or common incidence of non-compliance” for which NPCC would assess “a single aggregate penalty.” NPCC considered NPCC_URE2's compliance history to be a aggravating factor in penalty determination.
2014-03-31 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010255 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-006-3c R4. A senior supervisor was asked to escort a locksmith into NPCC_URE2's Physical Security Perimeter (PSP) to perform work at the substation that contained Critical Cyber Assets (CCAs). The senior supervisor mistakenly believed that he had been granted unescorted physical access to the PSP. The supervisor had taken NERC CIP training as a module that was part of a multiple-day annual expert training that covers a broad range of topics. The senior supervisor mistakenly thought that this training qualified him for access to CCAs. Believing that he had access, the senior supervisor attempted to enter the PSP using his electronic card key. The card key reader functioned properly and denied his access. The senior supervisor called the security control center and stated that he should have access rights to the PSP and requested entry. The security control center operator remotely opened the substation control house door and observed, by video surveillance, the senior supervisor, and the locksmith, who the senior supervisor was escorting. In a follow-up to review why the senior supervisor’s badge had not allowed him access the PSP, corporate security realized that the senior supervisor's access rights were not currently active, and he should not have been granted entry. NPCC determined that NPCC_URE2 had a violation of CIP-006-3c R4 for failing to properly implement its operational and procedural controls to manage physical access at all access points to the PSP 24 hours a day, seven days a week. | CIP-006-3c | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to properly implement operational and procedural controls to manage physical access to the PSP could expose the CCAs within the PSP to sabotage. The risk to the reliability of the BPS was mitigated by the following factors. The security control center operator monitored the camera for the entire time that the locksmith and senior supervisor were at the PSP resolving a door lock issue. In addition, the security control center operator properly logged the supervisor and locksmith's entry and departure from the PSP. The supervisor had completed the required CIP training for the previous year. In addition, a personnel risk assessment was completed for the supervisor with no adverse findings. Furthermore, the senior supervisor has been a long-time employee with NPCC_URE2 for three decades. | when the senior supervisor had unescorted physical access to the PSP | when the senior supervisor exited the PSP | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) issued a communication to security control center employees confirming that NERC CIP doors are not to be opened by security control center employees, with exceptions for fire, police, and medical emergencies; 2) provided additional training regarding NPCC_URE2's NERC general and emergency access procedures; and 3) documented the security control center procedure for granting remote access. | 2012-05-24 | 2013-10-03 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process.
2014-03-31 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010256 | Settlement Agreement | During a Spot Check related to NPCC_URE2's Self-Report of CIP-006-3c R4 (NPCC2012010255), NPCC determined that NPCC_URE2 was in violation of CIP-006-3 R1.6. NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-006-3c R4. A senior supervisor was asked to escort a locksmith into NPCC_URE2's physical Security Perimeter (PSP) to perform work at the substation that contained Critical Cyber Assets (CCAs). The senior supervisor mistakenly believed that he had been granted unescorted physical access to the PSP. The supervisor had taken NERC CIP training as a module that was part of a multiple-day annual expert training that covers a broad range of topics. However, this NERC CIP training was not the CIP-004 R2 cyber security training required for personnel having authorized cyber or authorized unescorted physical access to CCAs. The senior supervisor mistakenly thought that this training qualified him for access to CCAs. Believing that he had access, the senior supervisor attempted to enter the PSP using his electronic card key. The card key reader functioned properly and denied his access. The senior supervisor called the security control center and stated that he should have access rights to the PSP and requested entry. The security control center operator remotely opened the substation control house door and observed, by video surveillance, the senior supervisor, and the locksmith. In a follow-up to review why the senior supervisor’s badge had not allowed him access the PSP, corporate security realized that the senior supervisor's access rights were not currently active, and he should not have been granted entry. Because the senior supervisor did not have authorized unescorted access to the PSP, the locksmith was not provided appropriate continuous escorted access within the PSP resulting in a violation of CIP-006-3c R1.6.2 | CIP-006-3c | R1; R1.6.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to properly implement operational and procedural controls to manage physical access to the PSP could expose the CCAs within the PSP to sabotage. The risk to the reliability of the BPS was mitigated by the following factors. The security control center operator monitored the camera for the entire time that the locksmith and senior supervisor were at the PSP resolving a door lock issue. In addition, the security control center operator properly logged the supervisor and locksmith's entry and departure from the PSP. The supervisor had completed the required CIP training for the previous year on July 28, 2011. In addition, a personnel risk assessment was completed for the supervisor with no adverse findings. Furthermore, the senior supervisor has been a long-time employee with NPCC_URE2 for three decades. | when the locksmith accessed the PSP without an authorized escort | when the locksmith exited the PSP | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Spot Check | To mitigate the violation, NPCC_URE2: 1) issued a communication to security control center employees confirming that NERC CIP doors are not to be opened by security control center employees, with exceptions for fire, police, and medical emergencies; 2) provided additional training regarding NPCC_URE2's NERC General and Emergency Access Procedures; and 3) documented the Security Control Center Procedure for granting remote access. | 2012-05-24 | 2013-10-03 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process.
2014-03-31 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010426 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating it was in violation of CIP-004-3 R3. On June 20, 2011, an employee was mistakenly granted unescorted physical access rights to enter Physical Security Perimeters (PSPs) at substations containing Critical Cyber Assets (CCAs) before a personnel risk assessment (PRA) was completed. Upon discovery that the PRA was not complete, the employee’s unescorted physical access rights to CCAs at substations were revoked. This missing PRA was discovered as part of a mitigation action for another occurrence of a missing PRA that was self-reported (NPCC2012010254). | CIP-004-3 | R3 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to perform a PRA prior to granting unescorted access can potentially lead to breaches of security. The risk to the reliability of the BPS was mitigated by the following factors. For the duration of the violation, the employee did not attempt to access the CCAs. In addition, a PRA was completed for the affected employee with no adverse findings. In addition, the following security measures are in place to protect the CCAs. The CCAs are inside a control house, which is a physical security perimeter, at the substation. Physical access to the CCAs is controlled by a card key and card lock system which has continuous monitoring and logging. The substation has video cameras. Electronic access to CCA’s is monitored. The CCA’s are protected by malicious software prevention tools. Furthermore, the affected employee had completed the required CIP-004 R2 training. | when unescorted access to the CCAs was granted to the employee prior to a PRA being conducted | when unescorted access to the CCAs was revoked for the employee | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) incorporated a process requiring its security group to perform a secondary verification that PRAs and annual CIP training are complete prior to granting employees unescorted physical access to CCAs; 2) issued a communication to authorized access approvers that reconfirms the requirement to verify that PRAs and annual CIP training is complete prior to granting employees unescorted physical access to CCAs; 3) issued a broad employee communication regarding NERC CIP access prerequisites; 4) provided additional training to the project management group regarding NERC CIP access prerequisites and process requirements; 5) updated the NERC CIP physical access request form to provide more explicit instructions to managers responsible for verifying PRAs and CIP Training dates; and 6) initiated a requirement that a verification of completion of PRAs, for all active employees and contractors, who have authorized unescorted physical access to CCAs, be performed. | 2012-06-14 | 2013-10-04 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process. The instant violation occurred concurrently with violation NPCC2012010254, which is also being concurrently filed. Based on the NERC Sanction Guidelines, NPCC determined these two violations CIP-004-3 R3 were “related to a single act or common incidence of non-compliance” for which NPCC would assess “a single aggregate penalty.” NPCC considered NPCC_URE2's compliance history to be a aggravating factor in penalty determination.
2014-02-27 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011629 | Settlement Agreement | During an on-site Compliance Audit, NPCC determined that NPCC_URE2 was in violation of CIP-007-3a R2. NPCC_URE2's Cyber Vulnerability Assessment (CVA) from a particular year identified open logical ports on switches that were not part of the baseline documentation. The ports were opened when NPCC_URE2 updated the firmware and loaded their baseline configuration to the switches and the firmware opened these ports by default. The violation involved specific switches at substations. The CVA identified two ports/IP services on specific devices that were enabled and were not part of the baseline documentation. | CIP-007-3a | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected devices are located behind a Physical Security Perimeter and an Electronic Security Perimeter. Also, NPCC_URE2 deploys a defense in-depth CIP strategy, through the use of access control lists, firewalls, and a network-based intrusion detection system. Furthermore, the substation's firewalls are continuously monitored. | when the ports were left open | when NPCC_URE2 ensured that only the ports and services required for normal and emergency operations were enabled | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Compliance Audit | To mitigate the violation, NPCC_URE2: 1) revised related testing procedures; 2) confirmed updates were made to ensure that only ports and services required for normal and emergency operations are enabled; 3) provided awareness training to telecom operations regarding the process to make changes on Critical Cyber Assets within the substation environment; 4) revised related procedures to better define applicability and roles and responsibilities; 5) finalized related operating procedures; and 6) developed a substation control and integration quality review procedure. | 2013-12-18 | 2014-01-08 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process.
2014-02-27 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011633 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-004-3 R3. An employee was granted unescorted physical access rights to enter the Physical Security Perimeter (PSP) containing Critical Cyber Assets (CCAs) at a control center before a personnel risk assessment (PRA) was complete. An incorrect PRA completion date was entered on a physical access request form by the employee’s supervisor. The date entered was the date the PRA was requested. The authorized access approver did not detect the error. The access request form was sent to corporate security for processing. Corporate security detected that the PRA was not complete but the access request was processed in error. The error was detected during NPCC_URE2's annual review of PRA and CIP training records. Access was revoked and the PRA was completed that same day. | CIP-004-3 | R3 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failure to perform a PRA prior to granting unescorted access can potentially lead to breaches of security. The risk to the BPS was mitigated by the following factors. A PRA was completed for the affected employee with no adverse findings. The employee completed CIP-004 R2 training, In addition, the following security measures are in place for the PSP. Physical access is controlled by a card key and card lock system which has continuous monitoring and logging. Furthermore, electronic access to CCAs are monitored and the CCAs are protected by malicious software prevention tools. | when unescorted access to the CCAs was granted to the employee prior to a PRA being conducted | when unescorted access to the CCAs was revoked for the employee | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) issued a communication to existing CIP access requestors and authorized access approvers that reconfirms the requirement to verify PRAs and annual CIP training is complete prior to granting employees unescorted physical access to CCAs; 2) verified, as part of the annual review of CIP training records, completion of PRAs for all active employees and contractors, who have authorized unescorted physical access and cyber access to CCAs; and 3) revised global security procedure to clarify PRA validation. | 2012-12-24 | 2013-10-17 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process. NPCC considered NPCC_URE2's compliance history to be a aggravating factor in penalty determination. Concurrently being filed are two prior violations of CIP-004 R3 (NPCC2012010254 and NPCC2012010426). NPCC considered these prior violations of CIP-004 R3 as an aggravating factor in the penalty determination.
2014-02-27 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013011743 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating, that it was in violation of CIP-004-3 R4.2. An employee of a telecommunications contractor working for NPCC_URE2 was terminated by the telecommunications contractor. The termination was the result of an organizational restructuring and was not for cause. Before the termination, the telecommunications contractor’s employee had authorized unescorted physical access to Critical Cyber Assets at the affected energy management system (EMS) server room. The telecommunications contractor failed to timely notify NPCC_URE2 of the termination. The telecommunications contractor employee’s physical access rights were revoked past the seven calendar days after NPCC_URE2 should have revoked the telecommunications contractor employee's access, as required by R4.2. | CIP-004-3 | R4; R4.2 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, delayed access revocation may increase the risk to the BPS by the actions of the contractor employee following his termination. The risk to the BPS was mitigated by the following factors. A review of physical access records confirmed that the telecommunications contractor employee did not access the affected EMS server room after the termination date. The employee of the telecommunications contractor also did not have cyber access to Critical Cyber Assets (CCAs). In addition, security measures were in place for the Physical Security Perimeter. Physical access is controlled by a card key and card lock system which has continuous monitoring and logging. The doors to the server rooms have video cameras. In addition, the facility has multiple video cameras and layers of protection. Card key and card lock readers are at the facility gate and at the entry doors to the facility. The server rooms also have card key and card lock readers to further control access. The contractor’s employee did not have access to the EMS computer room or control rooms. | when the contracted employee's authorized unescorted access was required to be revoked | when the contracted employee's authorized unescorted access was revoked | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) administered CIP awareness training to the telecommunications contractor involved in the event; and 2) re-verified the applicable list of contractor personnel who have physical access rights to CCAs at the affected EMS server room to ensure that the contractor personnel are still employees of the contractors. | 2013-01-23 | 2013-10-15 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2, internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process. NPCC considered NPCC_URE2's compliance history to be a aggravating factor in penalty determination.
2014-02-27 | FERC | NP14-34-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013012747 | Settlement Agreement | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-003-3 R6. A firmware update rollout was performed on Local Area Network (LAN) Ethernet switches at substations. NPCC_URE2's change control and configuration management process uses a form to document changes to Critical Cyber Assets (CCAs). In this instance, the form was not used. This violation was discovered during a review of mitigation involving a violation of CIP-007-3a R2 (NPCC2012011629). The firmware updates were performed but specific ports and services were not closed at the time of the firmware updates. | CIP-003-3 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The affected devices are located behind a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). Also, NPCC_URE2 deploys a defense in-depth CIP strategy, through the use of access control lists, firewalls, and a network-based intrusion detection system. Furthermore, the substations firewalls are continuously monitored. | when NPCC_URE2 failed to use the form per its change control and management process to document a change to its CCAs | Mitigation Plan completion | $86,000 for NPCC2012010254, NPCC2012010255, NPCC2012010256, NPCC2012010426, NPCC2012011633, NPCC2013011743, NPCC2012011629, NPCC2013012747, and NPCC2012009525 | Self-Report | To mitigate the violation, NPCC_URE2: 1) provided awareness training to telecommunications operations regarding the process to make changes on CCAs within the substation environment; 2) revised its change control and configuration management procedure to better define applicability, roles, and responsibilities; and 3) developed substation control and integration quality review procedure. | 2013-12-31 | 2014-01-08 | Neither Admits nor Denies | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC also considered NPCC_URE2's cooperation during the processing of the violation as an above and beyond mitigating factor in the penalty determination. During the process, NPCC_URE2 addressed the non-compliance and provided, in detail, the facts pertaining to the violation. In addition, NPCC_URE2 provided appropriate authorized management to assure full cooperation throughout the settlement process.
2014-02-27 | FERC | NP14-34-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011160 | Settlement Agreement | TRE_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R4. TRE_URE1's violation occurred in three instances. First, TRE_URE1 did not have a documented process for updating anti-malware on the date the Standard became mandatory and enforceable on TRE_URE1. The procedure was completed and effective approximately three months later. Second, TRE_URE1 failed to install malware prevention tools on nine Cyber Assets within an Electronic Security Perimeter (ESP) as of the date the Standard became mandatory and enforceable date on TRE_URE1. TRE_URE1 remedied the issue by installing malware prevention tools on the nine Cyber Assets. Installation on the last of the Cyber Assets was completed approximately eleven months later. Third, although TRE_URE1 contends it installed anti-virus and associated signature updates on six Cyber Assets (servers) within an ESP, it failed to retain evidence of such prior installations after it upgraded its anti-virus/signature server. TRE_URE1 has evidence of installing signatures beginning on the date when TRE_URE1 upgraded its anti-virus system. Thus, TRE_URE1 does not have evidence of anti-virus and associated signatures being implemented on six Cyber Assets for the period beginning on the date the Standard became mandatory and enforceable on TRE_URE1 until TRE_URE1 upgraded its anti-virus system. | CIP-007-1 | R4; R4.1 | Medium | Severe | This violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). The Cyber Assets at issue were all protected by a firewall; thus, there were additional controls in place to mitigate potential cyber-attacks. In addition, the violation affected less than 10% of TRE_URE1's total Critical Cyber Assets. Further, there was no evidence of exposure to malware for the subject Critical Assets. | when the standard became mandatory and enforceable on TRE_URE1 | when TRE_URE1 began retaining evidence of the implementation of anti-virus and associated signatures | 0 | Self-Certification | To mitigate this violation, TRE_URE1: 1) created a documented procedure requiring the installation of anti-malware software; 2) installed anti-malware software on nine affected Cyber Assets and provided evidence of same; and 3) installed signature files on the six servers and provided evidence of same, demonstrating that the anti-virus software had also been installed. | 2011-11-22 | 2013-07-09 | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it a mitigating factor in the penalty determination.
2014-02-27 | FERC | NP14-34-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012801 | Notice of Confirmed Violation | On August 19, 2013, WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4. WECC_URE1 failed to perform a quarterly review of local administrator user accounts on its equipment for the first quarter of 2013. Specifically, WECC_URE1 failed to review the list of shared accounts and personnel that have access to the devices. | CIP-004-3a | R4 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 has an authentication service running on these devices which prevents the shared accounts in scope from logging in to configure the devices. Also, interactive access to these devices is only allowed through individual user accounts, and user accounts were reviewed quarterly. WECC_URE1 requires two-factor authentication in order to create a proxy session to the Critical Cyber Assets (CCAs). The CCAs then require an additional two-factor authentication. Additionally, the devices in scope are located within a Physical Security Perimeter accessible to only personnel that have been granted access via an authorized identification badge. Finally, WECC_URE1 implemented detective controls. | the first day of the first quarter in which WECC_URE1 failed to perform quarterly log reviews | the last day of the first quarter of which WECC_URE1 failed to perform quarterly log reviews | 15000 | Self-Report | To mitigate this violation, WECC_URE1 : 1) updated the review calendar to ensure that accounts are clearly included in the quarterly access reviews; 2) created, documented, and implemented a more formal process of generating lists and reviewing access to accounts; and 3) trained the team on the updated list generation and access review procedures. | 2014-01-31 | TBD | Agrees | WECC reviewed WECC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-02-27 | FERC | NP14-27-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010252 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R4.1 and R4.2. NPCC_URE1 upgraded its Supervisory Control and Data Acquisition (SCADA) system’s hardware and software and operating system. As part of the upgrade, antivirus and anti-malware prevention tools were installed per Reliability Standard CIP-007 R4.1 and R4.2. At the conclusion of the upgrade, antivirus and anti-malware prevention tools were installed on the nine production servers. The initial install included a 30-day trial copy of an antivirus application on all of the core servers both at the primary control center (PCC) and the backup control center (BCC). NPCC_URE1's intention was to activate a full license before the 30-day trial expired. The antivirus vendor would allow both scanning and signature updates during the initial trial, satisfying Reliability Standard CIP-007 R4. Although NPCC_URE1 did install the antivirus and anti-malware tools as required, it did not activate the applications when the new equipment was placed in service. In addition, NPCC_URE1 did not renew the antivirus application license prior to the expiration of the 30-day trial. Automatic scanning of the equipment or manual scanning was not performed. The lack of a functioning antivirus tool was identified, when NPCC_URE1's automated monitoring identified that the antivirus and anti-malware prevention tools (scanning and signature updates) were not operational and that neither scanning nor signature updates were processed or scheduled. | CIP-007-3a | R4; R4.1; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, an intrusion to the system due to lack of antivirus protection could cause all NPCC_URE1 circuit breakers to be opened, interrupting the transmission paths which would result in a portion of the system's load being disconnected. The risk to the BPS was mitigated by the following factors. The Cyber Assets are located in a Physical Security Perimeter where the network is isolated utilizing firewalls at the access points. These devices do not have direct internet access. A VPN connection to the SCADA vendor for support is normally disconnected and the cable is only connected when support is required. During the time period of this violation, NPCC_URE1 did not experience or cause any emergencies resulting from the operation or misoperation of the SCADA system. | when NPCC_URE1 upgraded its SCADA system | when NPCC_URE1 installed the antivirus tool | $14,000 (for NPCC2012010252 and NPCC2012010253) | Self-Report | To mitigate this violation, NPCC_URE1 installed an antivirus tool. The tool was deployed following the Change Management process. The tool was operated in manual scan mode until approximately three weeks after the antivirus tool was installed. The tool was operated in manual mode to allow the NPCC_URE1 SCADA vendor to measure the performance impact of the tool on the SCADA processes and to tune the antivirus function. The tool was enabled for automatic scanning approximately three weeks after the antivirus tool was installed in manual mode. The SCADA administrator responsible for monitoring the SCADA system, at the time of the violation, is no longer assigned to the SCADA system. | 2012-05-04 | 2012-11-26 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-02-27 | FERC | NP14-27-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010253 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R4.1. NPCC_URE1 installed two devices as a Cyber Asset into service. During the planning stage for deployment of the antivirus and anti-malware tools, the Supervisory Control and Data Acquisition (SCADA) manager determined that deployment of the antivirus/malware detection tools was not feasible due to network issues at the time and was planning to submit a technical feasibility exception (TFE) request. During the deployment phase of the Cyber Asset, the SCADA manager resigned from NPCC_URE1. The present SCADA manager was made aware of the lack of antivirus on these Cyber Assets approximately three months after installation of the two devices. The SCADA manager reviewed the technical details of the interoperability of the antivirus and the Cyber Assets and determined it was feasible to deploy the antivirus tool. | CIP-007-3a | R4; R4.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, these two Cyber Assets are not Critical Cyber Assets. They are located within a Physical Security Perimeter and within an Electronic Security Perimeter on an isolated network. Remote access to the devices is not provided or allowed. During the time period of this violation, NPCC_URE1 did not experience or cause any emergencies resulting from the operation or misoperation of these Cyber Assets. | when NPCC_URE1 installed the two devices | Mitigation Plan completion | $14,000 (for NPCC2012010252 and NPCC2012010253) | Self-Report | To mitigate this violation, NPCC_URE1 successfully installed an antivirus tool for the two devices. | 2012-04-27 | 2012-11-26 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-02-27 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011216 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-3 R4. SERC_URE1 failed to maintain a list of personnel with authorized unescorted physical access to 44 Critical Cyber Assets (CCAs) located at one of SERC_URE1’s Critical Assets, as required by CIP-004-3a R4. The CCAs at issue were breaker control devices, and they were located in a facility identified by SERC_URE1 as a Critical Asset. This facility was typically unmanned. SERC_URE1 remotely managed and operated the devices. Due to the nature of this facility, SERC_URE1 failed to maintain a list of individuals with physical access. Despite not having a documented ability to do so, SERC_URE1’s employees occasionally would physically access the facility. Therefore, SERC_URE1’s failure to maintain a list of personnel with authorized unescorted physical access to the facility resulted in unauthorized individuals gaining physical access. | CIP-004-1 | R4; R4.1 | Lower | Severe | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SERC_URE1’s failure resulted in individuals having unauthorized physical access to 44 CCAs. SERC_URE1 had protected the CCAs at issue using a variety of physical and electronic controls. For instance, the CCAs resided in a control house, located behind a locked perimeter fence with armed guards continuously monitoring and controlling access and only permitting SERC_URE1 personnel to enter the facility. Additionally, to use physical access to issue commands to the breakers, an individual would require both physical access to the breaker control devices and a username and password. Each command would have required a separate login, increasing the time necessary to manipulate the breakers, and, therefore, the likelihood of the unauthorized access being detected. Many of the individuals with undocumented access had undergone an SERC_URE1 corporate personnel risk assessment, which included a seven-year criminal check conducted at national and county levels, social security verification, a national sex offender database check, and a terrorist watch list check. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of personnel who require authorized unescorted physical access to the Critical Asset location; 2) revised the inter-departmental process/procedure to include clarification that the missing list is required; 3) communicated the revised process/procedure to support staff; 4) began managing access using the updated list and process/procedure; and 5) completed a review of procedures and revised/assigned responsibilities appropriately. | 2013-02-28 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-02-27 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011217 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.4. SERC_URE1 failed to include procedures for the appropriate use of physical access controls in its physical security plan and to update the physical security plan within 30 days of a physical security system redesign or reconfiguration. SERC_URE1 implemented its physical security procedure as its physical security plan for its energy control center and secondary control center. The plan did not include language related to responding to the loss of physical access controls or prohibition of inappropriate use of physical access controls (excluding a mention of prohibiting the propping open of doors), as required by CIP-006-1 R1.4. This language did exist in a separate established procedure, delegating all response to loss of physical security control to a law enforcement group. SERC_URE1’s senior manager did not approve the procedure prior to implementation because of the missing language. Additionally, CIP-006-1 R1.7 requires that the physical security plan require updates within 90 days to account for redesign or reconfiguration of physical access controls. Beginning with CIP-006-2 R1.7, such updates were required to occur within 30 days. SERC_URE1, however, failed to revise its physical security plan to require the update of the physical security plan within 30 calendar days of the completion of a physical security system redesign or reconfiguration. | CIP-006-1 | R1; R1.4; R1.7 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While SERC_URE1’s approved physical security plan did not contain the appropriate language addressing the loss of physical access controls and prohibition of inappropriate use of physical access controls, those items were addressed in a separate procedure (SERC_URE1’s system operations procedure), and those items were addressed during SERC_URE1’s annual CIP training. While the plan language incorrectly required a review within 90 calendar days and did not contain information regarding the response to loss of physical security controls, all other remaining requirements of CIP-006 R1 were addressed. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 updated its physical security plan | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) updated its physical security plan to include language regarding appropriate use of physical access controls; 2) updated its physical security plan to reflect the 30 calendar day requirement; and 3) reminded all employees responsible for reviewing and revising documentation of this responsibility. | 2012-09-27 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-02-27 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011218 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted two Self-Reports to SERC stating that it was in violation of CIP-004-3 R4.2. SERC_URE1 failed to timely revoke access to Critical Cyber Assets (CCAs). In total, SERC_URE1 reported three occasions on which it failed to revoke access to CCAs within seven calendar days for individuals no longer requiring such access. SERC ultimately determined that only two of these occasions constituted a violation of CIP-004-3 R4.2. SERC_URE1 promoted an employee but did not revoke physical access to CCAs at the employee’s primary location, and at the employee’s secondary location. Additionally, SERC_URE1 did not revoke the employee’s electronic access to CCAs. SERC_URE1’s internal access revocation procedure required SERC_URE1 to revoke a promoted employee’s access within seven calendar days of the effective date of the promotion and reinstate that employee if necessary and approved. SERC_URE1 reinstated the employee’s physical access at the employee’s primary location immediately following the revocation. SERC_URE1 determined that the employee no longer required physical or electronic access to CCAs at the employee’s secondary location. SERC_URE1 terminated an employee’s temporary status, when permanent status was effective. SERC_URE1’s internal access revocation policy required it to revoke the employee’s access to CCAs prior to reinstating them, if necessary. SERC_URE1 failed to revoke the employee’s access privileges within seven days of the termination of the employee’s temporary status. | CIP-004-3 | R4; R4.2 | Medium | Moderate | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both of the employees at issue had undergone personnel risk assessments and cyber security training in accordance with the CIP Reliability Standards. The temporary employee had no electronic access to CCAs and had physical access only to CCAs residing within the primary control center. Additionally, while the employee receiving the promotion did have electronic access, that access was non-administrative access with very limited functionality. Furthermore, both employees remained employed by SERC_URE1 in different capacities following their status changes, and both employees retained physical access to CCAs as required by their new positions. | seven days after the first employee was promoted and no longer required access to certain CCAs the date the access revocation in the second instance should have occurred | the date all required access revocations had taken place the date the employee was reinstated in a permanent position, requiring the same access levels, and therefore eliminating the need to revoke access | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of personnel who require authorized unescorted physical access to the Critical Asset location; 2) revised the inter-departmental process/procedure to include clarification that the missing list is required; 3) communicated revised process/procedure to support staff; 4) began managing access using the updated list and process/procedure; and 5) reviewed procedures and added additional layers of notifications to prevent oversights of this nature in the future. | 2013-02-28 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011219 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R4. SERC_URE1 failed to implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter (PSP) 24 hours a day, seven days a week. An SERC_URE1 employee was performing assigned tasks within an established PSP to which the employee had authorized unescorted physical access. Logging data shows that the employee entered the PSP. To complete these tasks, the employee propped open a door that was an access point to that PSP. After completing the assigned tasks, the employee exited the PSP but left the door propped open. The next day, SERC_URE1 discovered the propped-open door by reviewing video recordings and immediately dispatched an employee to secure the access point. The door did trigger an alarm when initially propped open. SERC_URE1’s operations staff acknowledged the alarm and suspended further alarming after recognizing the employee that was sent into the PSP. SERC_URE1’s operations staff is responsible for clearing alarms and ensuring appropriate responses to them as necessary. | CIP-006-3c | R4 | Medium | Severe | The violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to maintain proper physical access control during a time period when alarming is suspended for site work could render Cyber Assets and Critical Cyber Assets within the PSP vulnerable to both physical and electronic sabotage. In this case, however, the PSP and the access point were located within a secure facility, the door was subject to video monitoring throughout the violation period, and a review of the video logs showed that no unauthorized individuals had entered the PSP during the violation period. The facility was constructed of concrete, was surrounded by an eight-foot barbed-wire perimeter fence, and could only be accessed via two badge-controlled access points. | when the PSP access door was propped open | when SERC_URE1 discovered and closed the PSP access door | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) included a reminder regarding the handling of open doors in its quarterly CIP Awareness email distribution. Additionally, this reminder is now included in every quarterly awareness notification and the CIP technical portion (verbal discussion) of its internal CIP training program reinforces the door policy; and 2) briefed responsible personnel on this issue and made them aware of the implications violations of this nature have to security and compliance. | 2012-10-04 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011220 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-3a R4. SERC_URE1’s Cyber Vulnerability Assessment (CVA) for an Electronic Security Perimeter (ESP) access point associated with one Critical Asset, was deficient. The access point at issue is a dial-up access point coupled with an encryption device for added security. The Critical Cyber Assets (CCAs) secured by this access point are located in a locked facility. SERC_URE1 manages these CCAs by remotely accessing them through the dial-up access point. The CVA was deficient in the following ways: 1) it failed to include a review to verify that only ports and services required for operations at these access points were enabled; and 2) it failed to review the established controls for default accounts, passwords, and network management security strings. Four years of SERC_URE1’s CVAs addressed the access point to the SERC_URE1 ESP, including a review of the services running on the access point device. These CVAs, however, did not include a scan of all ports, including listening ports. SERC_URE1 also failed to compare the open ports and services to a list of those ports and services required for operations. Additionally, while the SERC_URE1 CVA procedures required SERC_URE1 to perform a review of controls for default accounts, passwords, and network community strings pursuant to CIP-005-3a R4.4, SERC_URE1 did not perform this review for this one access point. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The electronic access point at issue allowed remote access to 44 relay control devices classified as CCAs. The risk posed by SERC_URE1’s failure to complete a full CVA on this access point was mitigated due to the communication methods utilized to communicate with the access device. The access device used a dial-up connection and was not connected to any Internet Protocol- (IP-) based networks, neutralizing any IP-based vulnerability. Additionally, because remote administrative access to the access control device was disabled, no configuration changes could be made to the device via the remote connection. Furthermore, all remote access sessions are encrypted and require both a username and password at the access control device for initiation of communication, and an additional username and password are required to connect to the CCAs across the access point. Inside the control house, the access device could only be accessed locally by directly plugging in a device, and by using an administrative account and password. The control house is a locked facility, which resides behind a locked gate and within a yard with additional physical security measures. Further, local electronic access at the CCAs residing behind the access device requires a username and password be entered prior to issuing commands to the associated breakers, and only one associated breaker can be controlled during a login session. Lastly, SERC_URE1 stated that there were no default accounts or passwords in place, and the lack of a connecting IP-based network would have prevented the remote exploitation of any network management community strings. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of the CVA process/procedure to ensure all required elements are identified; 2) revised the CVA process/procedure to include all required elements; 3) communicated the revised process/procedure to support staff; and 4) performed a CVA using the updated process/procedure. | 2013-01-31 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011221 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. SERC_URE1 stated that none of the devices within the Electronic Security Perimeter (ESP) at one Cyber Asset were technically capable of monitoring system events related to cyber security and SERC_URE1 did not have Technical Feasibility Exceptions (TFEs) filed for those devices. SERC determined that: 1) SERC_URE1 did not implement automated tools or organizational process controls to monitor system events that are related to cyber security for 44 Critical Cyber Assets (CCAs) (control devices) residing within the ESP of one SERC_URE1 Critical Asset; 2) SERC_URE1 did not implement and document organizational processes and technical and procedural mechanisms for monitoring for security events on the 44 CCAs within the specified ESP; 3) SERC_URE1’s 44 CCAs were not configured for, nor technically capable of, providing automated or manual alerts for detected Cyber Security Incidents; 4) SERC_URE1 was not maintaining logs of system events related to cyber security to support incident response, and therefore was not maintaining said logs for 90 days; and 5) SERC_URE1 had no ability to review logs for Cyber Security Incidents because no logs were maintained. | CIP-007-1 | R6; R6.1; R6.2; R6.3; R6.4; R6.5 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had both electronic and physical protections in place to guard against compromise of the 44 CCAs, which included physical access controls and monitoring of the Critical Asset. Additionally, remote electronic access to the CCAs can only be obtained through a communication device utilizing dial-up communication via a non-routable protocol, hence isolating the 44 CCAs residing across the access point from any network originating vulnerabilities. Furthermore, remote access to the communication device requires the possession of an encryption token, and a different shared password is required first to access the communication device, and next, an additional password is required to access the serially connected Cyber Assets. Lastly, the communications device (electronic access point) is configured for alarming upon multiple failed login attempts, with such alarms sent to dispatch personnel for response. Regarding local electronic access and physical access controls, the devices in question can only be accessed from inside the control house, by directly plugging in a computer device, and by using an administrative account and password. The control house is a locked facility and resides behind a locked gate. Additionally, the Critical Asset resides within a yard, which has a 24 hour a day, seven day a week-staffed security checkpoint controlling ingress and egress and monitoring the facilities. Further, local electronic access at the CCAs residing behind the access device requires a username and password be entered prior to issuing commands to the associated breakers, and only one associated breaker can be controlled during a login session. | when the Standard became mandatory and enforceable on SERC_URE1 | the date by which SERC_URE1 had implemented and documented revised automated tools or organizational process controls to monitor system events that are related to cyber security | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete investigation of technically feasible means of ensuring that all Cyber Assets within the ESP at one Critical Asset implement automated tools or organizational process controls to monitor system events that are related to cyber security. The result of this investigation was to replace the electronic access control and monitoring device with another device that provides the required capabilities; 2) revised the automated tools or organizational process controls to include the missing required elements; 3) communicated revised technical and automated tools or organizational process controls to support staff; and 4) implemented and documented revised automated tools or organizational process controls to monitor system events that are related to cyber security. | 2013-03-28 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011222 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. SERC_URE1 failed to establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. This violation involved 44 Critical Cyber Assets (CCAs) residing within a single Electronic Security Perimeter (ESP) and associated with a single Cyber Asset. The 44 CCAs are breaker control devices. The CCAs are serially connected to a network. SERC_URE1 typically accesses these CCAs remotely, using dial-up access. SERC determined SERC_URE1 violated the Standard because it failed to generate logs of sufficient detail to provide audit trails of individual user account access activity on the 44 CCAs, as required by CIP-007-1 R5.1.2. Further, SERC_URE1 failed to review the CCA user accounts to verify that access privileges were in accordance with Standard CIP-003 R5 and Standard CIP-004 R4, as required by CIP-007-1 R5.1.3. Additionally, SERC_URE1 did not identify all individuals with access to CCA shared passwords on the SERC_URE1 access list, as required by CIP-007-1 R5.2.2. Furthermore, SERC_URE1 did not have a policy for the use of shared accounts that limited access to only those with authorization, an audit trail of the shared account use, or steps for securing the account in the event of personnel changes, as required by CIP-007-1 R5.2.3. Finally, the CCAs could not technically enforce the password requirements, SERC_URE1 failed to change the CCA passwords on an annual basis, and SERC_URE1 did not have Technical Feasibility Exceptions (TFEs) where such enforcement was infeasible, as required by CIP-007-1 R5.3. | CIP-007-1 | R5 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had physical protections in place to guard against compromise of the 44 CCAs, including monitoring of the assets. Regarding shared access and physical access controls, the devices in question can only be accessed via personal computer through the entry of a shared password, after entering the control house. The control house is a locked facility, and the control house resides behind a locked gate. Furthermore, the Critical Asset resides within a yard, which has a 24 hour a day, seven day a week-staffed security checkpoint controlling ingress and egress and monitoring the facilities. Additionally, electronic access at the CCAs requires a username and password be entered prior to issuing commands to the associated breakers, and only one associated breaker can be controlled during a login. Therefore, the issuance of multiple commands to the breakers would require multiple login sessions and increase the opportunity for operations staff to observe the entry of malicious commands targeting the breakers. Lastly, the redundant design of SERC_URE1’s facility would allow operations to continue despite the initial compromise of a breaker via the subject CCAs. | when the Standard became mandatory and enforceable on SERC_URE1 | the date by which SERC_URE1 had implemented and documented revised automated tools and procedures | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of CCA account management technical and procedural controls to ensure all requirements are identified; 2) revised the CCA account management technical and procedural controls to include all required elements; 3) communicated revised technical and procedural controls to support staff; and 4) implemented and documented CCA account management using the updated technical and procedural controls. | 2013-03-28 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011223 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-008-3 R1. The SERC_URE1 Cyber Security Incident response plan did not include specific procedures to classify events as reportable Cyber Security Incidents. SERC_URE1 also reported that it did not: 1) define all response actions; 2) include roles and responsibilities for the incident response team; and 3) explicitly specify the communications plans. SERC determined that SERC_URE1’s Cyber Security Incident response plan failed to address the requirements of CIP-008-1 R1 fully. Specifically, the portion of the plan addressing CIP-008-1 R1.1 defined terms and severity levels to be utilized in assessing an event, but did not characterize when those events would qualify as reportable. The portion of the plan addressing CIP-008-1 R1.2 provides additional severity level descriptions that expand upon and sometimes conflict with the severity level descriptions contained in other sections of the plan. SERC determined that the Cyber Security Incident response plan was also unclear regarding roles and responsibilities of incident response teams during its implementation. The plan failed to identify clearly a communication plan because it did not state the internal personnel to whom an incident should be reported. The plan did, however, address events that may classify as possible Cyber Security Incidents and provided instructions on how to respond to such events. | CIP-008-1 | R1; R1.1; R1.2 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Despite the noted deficiencies, SERC_URE1 did have a Cyber Security Incident response plan in place. The Cyber Security Incident response plan provided a broad-based approach to assessing Cyber Security Incidents, including the use of various hypothetical incident descriptions to aid personnel in determining conduct that represented reportable events. Additionally, the various scenarios were provided with reporting time requirements based on the perceived threat level of each scenario. Furthermore, SERC_URE1, while not clearly defining roles and expectations in all cases, did frequently reference staff by title throughout the document, and outlined SERC_URE1 expectations of those staff members in the event of a Cyber Security Incident. | when the Standard became mandatory and enforceable on SERC_URE1 | the date SERC_URE1 implemented a procedure that fully addressed the requirements of CIP-008-3 R1 | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of the Cyber Security Incident response plan to ensure all required elements are identified; 2) revised the Cyber Security Incident response plan to include all required elements; 3) communicated the revised plan to support staff; and 4) implemented and documented the revised Cyber Security Incident response plan. | 2013-02-15 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011224 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R8.2. SERC_URE1 reported it had failed to retain testing and maintenance records for its physical security systems for the determined time. SERC determined that SERC_URE1’s Physical Security Plan did require testing and maintenance on regular intervals of less than three years, as required by CIP-006-1 R6. However, the procedure did not designate a retention period for testing and maintaining records for the determined cycle, as required. As a result, SERC_URE1 could not produce maintenance and testing evidence for the designated maintenance and testing interval. | CIP-006-1 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s procedures did require maintenance and testing. However, SERC_URE1 failed to provide evidence that maintenance and testing occurred for the designated maintenance and testing interval. Furthermore, SERC_URE1 has physical access controls that would activate in the event of a physical security system’s failure, including locking systems that default to physical keyed access, 24-hour monitoring by SERC_URE1 security and energy management system personnel, and a card access restoration plan. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) developed and implemented physical access procedures; 2) disabled the card access system; and 3) established testing and maintenance records. | 2012-10-31 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011225 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R8. The Cyber Vulnerability Assessments (CVAs) performed by SERC_URE1 at the Electronic Security Perimeter (ESP) residing within one Critical Asset were deficient. The ESP at issue in this violation is identified by SERC_URE1 as a Critical Asset. This Critical Asset was typically unmanned, but SERC_URE1 managed and operated the devices remotely using dial-up access. According to SERC_URE1’s Self-Report, the CVAs for this ESP were deficient for the following reasons: 1) they failed to establish a baseline of open ports and running services or compare this baseline to the vendor-required ports and services; 2) they failed to scan for open ports on the implicated Critical Cyber Assets (CCAs); and 3) they failed to review the established controls for default accounts. SERC_URE1’s CVAs focused on the access point to this SERC_URE1 ESP and did not consider the 44 CCAs residing within the ESP. Additionally, SERC_URE1 failed to review the ports and services on the CCAs and failed to review accounts and passwords used to access the CCAs. SERC_URE1 did document the results of the assessment as outlined in its CVA documents. | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The 44 CCAs at issue resided within a locked facility. The risk posed by SERC_URE1’s failure to complete a full CVA on these devices was lessened due to the communication methods utilized by the device and the access point to the devices. The CCAs were breaker control devices residing on isolated, non-routable, serial connections, and the only remote access to the devices was dial-up access at the access control device, which had no routable connection to an Internet Protocol- (IP-) based network. The access point device used a dial-up connection and was not connected to any IP-based networks, limiting exposure to any IP-based vulnerabilities. Furthermore, all remote access sessions are encrypted and require both a user name and password at the access control device for initiation of communication, and an additional username and password are required to connect to the CCAs across the access point. Inside the control house, the CCAs could only be accessed locally by directly plugging in a device, and by using an administrative account and password. The control house is a locked facility, which resides behind a locked gate, and within a yard with additional physical security measures. Further, local electronic access at the CCAs residing behind the access device requires a username and password to be entered prior to issuing commands to the associated breakers, and only one associated breaker can be controlled during a login session. SERC_URE1 stated that there were no default accounts or passwords in place. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) performed a complete review of CVA process/procedure to ensure all required elements are identified; 2) revised the CVA process/procedure to include all required elements and ensure the review is done for all devices; 3) created a baseline for ports and services to compare to vendor-required ports and services; 4) communicated revised process/procedure to support staff; and 5) performed a CVA using the updated process/procedure. | 2013-01-31 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011226 | Settlement Agreement | SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. SERC determined that SERC_URE1 did not correctly identify an access control unit (ACU) that authorizes and logs access to one SERC_URE1 Physical Security Perimeter (PSP) as a Cyber Asset. The ACU was used to authorize and log access to one PSP and was in service prior to the date on which SERC_URE1 was required to comply with the CIP Reliability Standards. SERC determined SERC_URE1 failed to provide it the protections described in CIP-006-1 R1.8. The device was located inside an established PSP and inside a locked mechanical room. SERC_URE1, however, failed to identify the ACU in its Physical Security Plan as a device used to monitor or log access to a PSP. As a result, SERC_URE1 had no evidence that it provided the ACU the protections required by CIP-006-1 R1.8. | CIP-006-1 | R1.8 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Despite SERC_URE1’s failure to afford the single ACU the requirements enumerated in CIP-006-1 R1.8, the ACU was a proprietary device and was afforded some physical and electronic protections. For example, the ACU was located in a PSP and was protected from unauthorized physical access. Furthermore, the ACU was located in an isolated system with no external connections, and physical access to the ACU was required for electronic interaction. Additionally, due to the ACU’s location inside the PSP, and the inability of SERC_URE1 to connect electronically to the ACU remotely, any staff members having access to the system were subject to the personnel risk assessment requirements of CIP-004-3. At each door for which the ACU was authorizing access, video cameras recorded ingress and egress to the PSP in which the ACU resided, and the referenced Critical Asset in which the ACU resides is manned by security personnel 24 hours a day, seven days a week. Finally, should the ACU have failed, armed security guards would have controlled access to the facility pursuant to SERC_URE1’s procedures. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) developed and implemented physical access procedures; 2) disabled the card access system; and 3) established testing and maintenance records. | 2012-10-31 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011440 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R6. SERC_URE1 failed to monitor and log physical access 24 hours a day, seven days a week as required. SERC_URE1’s card access system at its primary control center malfunctioned and failed on several occasions to record sufficient information to identify individuals and their time of access uniquely. Specifically, certain logs were not retrievable for the period of 19 days. SERC_URE1 utilized a card access, magnetic lock system to control physical access at its primary control center. In one instance the system suffered a non-recoverable failure which required SERC_URE1 to restore the system in order to regain functionality. The failure and subsequent system restoration resulted in the loss of 10 days of logs. In another instance, a synchronization issue between the primary and secondary physical access control servers resulted in the loss of five days of logs. Finally, during the aforementioned Compliance Audit, SERC discovered that a malfunction of SERC_URE1’s card access system at its standby control center caused SERC_URE1 to fail to log evidence sufficient to identify individuals and their time of access uniquely on two separate dates. SERC_URE1 determined that its stand-alone device used to control access into the standby control center could not provide the required data. This device is not connected to a central logging system, requiring logs to be stored locally. | CIP-006-3c | R6 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Despite the logging malfunctions, the card access and magnetic locking systems continued to function properly, ensuring the physical security of the primary and standby control centers. Additionally, cameras were deployed at both facilities to record access, and access to both facilities is initially restricted by perimeter fencing and locked gates. Furthermore, at the primary control center, security guards were present on a continuous basis during the violation. | the first date of an identified logging failure | the last date of an identified logging failure | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Self-Report | To mitigate this violation, SERC_URE1: 1) developed and implemented physical access procedures; 2) disabled the card access system; 3) created paper logs for access to the Physical Security Perimeter; and 4) revised the process in which the logs are retrieved from the stand-alone locks located at this Critical Asset. | 2012-12-31 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. SERC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011585 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-005-1 R1.5. SERC_URE1 failed to afford an Electronic Access Control and Monitoring (EACM) device used to control access to the Electronic Security Perimeter (ESP) all the listed protections. SERC_URE1 used the EACM device at issue for authenticating and logging access into breaker control devices (Critical Cyber Assets). SERC_URE1 failed to identify all individuals with access to the EACM device’s shared administrator account, as required by CIP-007 R5.2.2 and listed in CIP-005 R1.5. SERC_URE1 also failed to require passwords at least six characters long and containing a combination of alpha, numeric, and “special” characters, as required by CIP-007, R5.3.1 and R5.3.2, respectively and listed in CIP-005 R1.5. The EACM device at issue was technically incapable of establishing these password controls, but SERC_URE1 failed to file a Technical Feasibility Exception. | CIP-005-1 | R1; R1.5 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because. Despite the technical inability to enforce the CIP password requirements, SERC_URE1 claimed that the passwords were maintained in accordance with CIP requirements. Furthermore, the EACM device could only be accessed at its physical location inside a control house. SERC_URE1 had physical protections in place to guard against physical access, including monitoring of the assets, and no remote administrative access to the access control device. The control house is a locked facility, and resides behind a locked gate, and the Critical Asset, has 24 hour a day, seven day a week-staffed security checkpoint controlling ingress and egress and monitoring the facilities. Additionally, electronic access at the CCAs requires a username and password be entered at both the access control device and the associated CCAs prior to commands being issued to the connected breakers. Finally, only one associated breaker could be controlled during each remote login session. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012011216, SERC2012011217, SERC2012011218, SERC2012011219, SERC2012011220, SERC2012011221, SERC2012011222, SERC2012011223, SERC2012011224, SERC2012011225, SERC2012011226, SERC2012011440, and SERC2012011585) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) performed a complete review of CCA and associated access point device account management technical and procedural controls to ensure all requirements are identified; 2) recommended a plan to correct deficiencies. The plan was to replace the access point device with another device that will enforce password requirements and start documenting all individuals that have access to the administrator account on that access point device; 3) revised the CCA and associated access point device account management technical and procedural controls to include all required elements; 4) communicated the revised technical and procedural controls to support staff; and 5) implemented and documented CCA and associated access point device account management using the updated technical and procedural controls. | 2013-03-28 | TBD | Neither Admits nor Denies | SERC considered SERC_URE1’s internal compliance program (ICP) as a mitigating factor when determining the penalty for these violations. In determining an appropriate penalty for the violations addressed herein, SERC considered that SERC2012011216, SERC2012011585, SERC2012011220, SERC2012011225, SERC2012011221, and SERC2012011222 related to the same facility.
2014-01-30 | FERC | NP14-27-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011015 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report during the Self-Certification period, stating that it was in violation of CIP-006-1 R1.8. Specifically, Texas RE_URE1 failed to afford the protective measures in CIP-007 R3.1 and CIP-007 R5.3.3 to Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s) (PSPs). For CIP-007-3 R3.1, Texas RE_URE1 self-identified security patches applicable to two access control intrusion detection servers that were not assessed within 30 days of availability. Instead, the 14 security patches related to the operating system were assessed approximately 120 days after they became available. While the assessment was not completed or documented within the 30 calendar day requirement, the patches in question were assessed and implemented where adequate compensating measures to mitigate risk exposure were not in place. The patches were not assessed in a timely manner due to unclear and undefined roles and responsibilities within Texas RE_URE1. For CIP-007 R5.3.3, Texas RE_URE1 failed to change passwords annually for two servers and 39 accounts used for physical access control. Upon further investigation and testing, it was discovered that the operator table fields "pwd_chang_date" and “pwd_chang_time” were updated every time the user record was modified. Therefore, any time an administrator updated a user name with the current position title or any other field in the operator table through the application's graphical user interface (GUI), the "pwd_chang_date" and "pwd_chang_time" fields would reflect the date and time of the change. The operator table fields "pwd_chang_date" and "pwd_chang_time" should only change when the password has been changed. Upon the discovery of this problem, Texas RE_URE1 placed an emergency service call to the manufacturer of the access control intrusion detection system application. The manufacturer replicated the password change date synchronization failure between the operator table and the password history table in its test lab. The manufacturer's technical support team confirmed the software bug, and presented it to its engineering department for correction. | CIP-006-1 | R1; R1.8 | Medium | Lower | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A failure to properly apply patches and password controls can leave Cyber Assets vulnerable to cyber threats. The patches were properly assessed within 120 days rather than the required 30 days. The risk was reduced because the Cyber Assets were located within an ESP which required authentication for external interactive access. The Cyber Assets were located within a PSP. Access points protecting Cyber Assets have card access and alarm points for monitoring, which report into an access control/intrusion detection system. This system runs 24 hours a day, seven days a week. The PSP also had multiple physical access control layers within a non-public controlled space and logical control measures, such as data encryption and circuit monitoring to detect unauthorized access or physical tampering. Manual visitor logging was also in place to keep track of all visitors that request access. Individuals requiring access through access points into a restricted area must sign the log and provide required information and authorization. | when the Standard became mandatory and enforceable on Texas RE_URE1 | Mitigation Plan completion | $0 (for TRE2012011015, TRE2012011016, TRE2012011382, and TRE2012011387) | Self-Report | To mitigate this violation, Texas RE_URE1: 1) collaborated with the manufacturer to confirm the issue is not specific to Texas RE_URE1's environment; 2) created a script that will automatically notify users via email if their password has not been changed within the required time frames; 3) created a script that will automatically notify via email the access control intrusion detection system application administrators if any account password has not been properly changed and request the administrator to terminate and/or disable the account; 4) updated the corporate security document to reflect the notifications outlined in previous two milestones. The on-call administrator will delete the account and record it in a service ticket upon receipt of the notification of account passwords exceeding the required interval; 5) trained corporate security personnel responsible for the updates made to corporate security systems security management document; 6) communicated to users in the access control intrusion detection system the requirement to change their passwords and that failure to change their passwords would result in their accounts being terminated; 7) conducted an extent of condition analysis on all the physical access control devices to determine whether there were any gaps that needed to be addressed within the outlined protective measures; 8) conducted an extent of condition analysis on all the physical access control devices in regards to CIP-006-3 R2.2 (the effective version equivalent CIP-006-1 R1.8), protective measures in CIP-003-3 R6 in relation to the change management procedure/change ticket process, and CIP-004-3 R3 personnel risk assessment process and determined if there were any gaps that needed to be addressed in the outlined protective measures; 9) conducted an extent of condition analysis of the physical access control devices in regards to CIP-006-3 R 2.2 specified protective measures in CIP-007-3 and determined if there were any gaps that needed to be addressed with the outlined protective measures; 10) reviewed the results of the extent of condition analysis in the three previous milestones to develop a corrective action plan to address any identified gaps; 11) completed the corrective action plan developed in previous milestone; 12) communicated to and trained affected personnel on the changes from the corrective action plans completed in the previous milestone; 13) performed an extent of condition review for the physical access control devices in relation to CIP-007 R3 controls, and established a corrective action plan to address any issues or improvements identified during the reviews; 14) performed an extent of condition review of account management controls for the devices in regards to CIP-007 R5 (including need to file additional Technical Feasibility Exceptions), and established a corrective action plan to address any issues or improvements identified during the reviews; and 15) implemented corrective actions as identified in action plans created in previous two milestones for Cyber Assets across business units. | 2013-06-20 | 2013-10-31 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011016 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report during the Self-Certification period, stating that it was in violation of CIP-005-1 R1.5. Specifically, Texas RE_URE1 failed to afford the protective measures in CIP-005 R3.2, CIP-007 R3, CIP-007 R5.1.3, and CIP-007 R5.3.3 to Cyber Assets used in the access control and monitoring of its Electronic Security Perimeter(s) (ESPs). For CIP-007 R5.3.3, Texas RE_URE1 determined that one account (shared, administrator account) on two Cyber Assets (firewall servers used to configure firewall rule sets on electronic access points), three accounts (shared, administrator accounts) on two Cyber Assets (RSA appliance servers used to support two-factor authentication to Cyber Assets used in the access control and/or monitoring of an ESP), and six accounts (two shared, administrator accounts, three user accounts with administrative privileges, and one shared account with non-elevated privileges) on two Cyber Assets (network Domain Controllers that are used in conjunction with RSA to support two-factor authentication to Cyber Assets used in the access control and/or monitoring of an ESP) did not have passwords changed at least annually, as required by CIP-007 R5.3.3. These Cyber Assets are used by Texas RE_URE1 to manage access to Critical Cyber Assets (CCAs) and non-critical Cyber Assets within defined ESPs. These instances of noncompliance began when the Standard became mandatory to Texas RE_URE1, and passwords for 7 of the 10 accounts have now been changed. The passwords for the remaining three accounts have not been changed because the vendor will not provide support for issues that arise from making these changes and will not, and cannot, guarantee the stability of the system if they are made. Texas RE_URE1 filed the Technical Feasibility Exceptions (TFEs) for the inability to change the passwords on these three accounts on an annual basis as required in CIP-007 R5.3.3. Texas RE_URE1 did not change the passwords for accounts, and did not initially file TFEs where applicable, because there was no defined process establishing ownership and responsibility for monitoring and implementing account password changes. For CIP-007 R3, Texas RE_URE1 determined the assessment of security patches and security upgrades for applicability on four Cyber Assets used by Texas RE_URE1 to perform centralized logging and alerting as required by CIP-005 R3.2 was not performed within thirty calendar days of availability. The assessments of security patches and security upgrades were not completed within the 30 calendar day requirement because of unclear and undefined roles and responsibilities within Texas RE_URE1. For CIP-005 R3.2, Texas RE_URE1 determined that at one Critical Asset, the access points were not afforded the protective measures of CIP-005 R3.2, as required in CIP-005 R1.5 (two routers). The security monitoring process(es), though technically feasible, did not detect and alert for all attempts at or actual unauthorized accesses to the access points. Additionally, personnel did not assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. This issue was the result of an oversight when configuring automated alerting processes. For CIP-007 R5.1.3, Texas RE_URE1 did not review user accounts on a quarterly basis to verify that access privileges were in accordance with standard CIP-004 R4 as a sub-requirement of standard CIP-007 R5.1.3. However, the user accounts were reviewed on an annual basis. There were 24 Cyber Assets that were impacted. The reviews of user accounts were not completed quarterly due to a lack of understanding by personnel required to apply the protective measures of CIP-005 R1.5. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1's failure to afford several of the required protective measures to its Cyber Assets used in ESP access control and/or monitoring and its failure to provide protection to its CCAs within its ESP rendered its system more vulnerable to attack. The risk to the BPS was reduced because Texas RE_URE1 provided password protection to all Cyber Assets that monitor its ESP. Additionally, all Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. Furthermore, electronic and physical access to PSPs is controlled, monitored, and logged. All personnel and contractors that had access to Cyber Assets and CCAs had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with antivirus software and malware prevention tools. | when the Standard became mandatory and enforceable on Texas RE_URE1 | Mitigation Plan completion | $0 (for TRE2012011015, TRE2012011016, TRE2012011382, and TRE2012011387) | Self-Report | To mitigate this violation Texas RE_URE1: 1) performed an assessment and extent of condition review of asset type classification for Cyber Assets in scope of CIP-005 R1.5; 2) filed TFEs for the Cyber Assets identified in the Self-Report as they relate to CIP-007 R5.3 requirements; 3) performed a cyber vulnerability assessment (CVA); 4) performed a review of personnel with access to the Cyber Asset. Texas RE_URE1 then removed access to applicable Cyber Assets, where necessary; 5) assessed the PRA program as per CIP-004 R3 to identify possible improvements for validating PRAs prior to granting access to Cyber Assets used in the access control and/or monitoring of the ESPs. Also, Texas RE_URE1 assessed the controls defined for updating PRAs pursuant to CIP-004 R3.2. Texas RE_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 6) performed training and education on the applicability of standards and requirements associated with Cyber Assets used in the access control and/or monitoring of the ESPs as per CIP-005 R1.5; 7) performed an assessment of compliance to CIP-005 R1.5 for Cyber Assets subject to NERC CIP requirements identified as Cyber Assets used in electronic access control and/or monitoring of the ESPs but not properly classified in a previous milestone; 8) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R2. Additionally, Texas RE_URE1 performed an extent of condition review of CIP-005 R2 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs. Texas RE_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 9) performed an extent of condition review of CIP-007 R3 controls for Cyber Assets used in the access control and/or monitoring of the ESPs. Texas RE_URE1 established a corrective action plan to address any issues or improvements identified during the reviews; 10) performed an extent of condition review of account management controls for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs pursuant to CIP-007 R5 (including the need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews; 11) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R3. Additionally, Texas RE_URE1 performed an extent of condition review of CIP-005 R3 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs, and established a corrective action plan to address any issues or improvements identified during the reviews; and 12) implemented corrective actions as identified in action plans created in the Mitigation Plan milestones for applicable Cyber Assets used in the access control and/or monitoring of the ESPs across business units. | 2013-07-11 | 2013-10-31 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011382 | Settlement Agreement | During a Compliance Audit, Texas RE determined that Texas RE_URE1 was in violation of CIP-005-1 R4.2, R4.3, R4.4, and R4.5. Specifically, Texas RE_URE1 did not identify all access points to its Electronic Security Perimeters (ESPs). Through the review of the network diagram provided by Texas RE_URE1, Texas RE determined that Texas RE_URE1 labeled routers in operation at the ESP as electronic access points. However, these routers were not identified and assessed as electronic access points on the inventory list of Cyber Assets during the annual cyber vulnerability assessment (CVA). As a result, Texas RE determined that Texas RE_URE1 did not perform a CVA of the electronic access points to the ESP at least annually as required by CIP-005-1 R4.2, R4.3, R4.4, and R4.5. | CIP-005-1 | R4; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Texas RE_URE1 did not perform a CVA to the routers depicted on its network diagram and only performed a CVA on the firewalls, Texas RE_URE1 provided a defense-in-depth architecture, including electronic access controls for authentication and encryption at the ESP. In addition, the risk was reduced because Texas RE_URE1 had physical security controls in place at the Physical Security Perimeter (key card readers, locked doors and cameras), thus reducing the likelihood of a successful cyber-attack. | when the Standard became mandatory and enforceable on Texas RE_URE1 | date CVA was completed | $0 (for TRE2012011015, TRE2012011016, TRE2012011382, and TRE2012011387) | Compliance Audit | To mitigate this issue, Texas RE_URE1: 1) performed a CVA on identified Cyber Assets as required by CIP-005 R4; 2) reviewed and updated the Cyber Asset identification methodology and process flow to ensure that there is a process for identifying and labeling Cyber Assets used as electronic access points to an ESP; 3) performed a review of the annual CVA to identify areas of improvement, including a review of the processes for discovering all access points to the ESP as required by CIP-005 R4.3; 4) performed an extent of condition review of all Critical Assets to ensure that Cyber Assets used as electronic access points have been properly classified as such and that there has been a CVA performed on the electronic access points in accordance with CIP-005 R4. Additionally, Texas RE_URE1 updated its procedure by incorporating a new asset identification methodology into the CVA process. Texas RE_URE1 also conducted electronic discovery scans, and CCA lists and ESP diagrams were analyzed to confirm proper classification of the CIP assets. The CVAs were reviewed and no discrepancies were identified; 5) completed implementation of activities on actions plans established as part of the reviews performed in the previous two milestones; and 6) trained impacted individuals on updated policies, procedures, and/or process flows resulting from implementation of action plan items in previous milestone. | 2013-07-31 | 2013-08-07 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011387 | Settlement Agreement | During a Compliance Audit, Texas RE determined that Texas RE_URE1 was in violation of CIP-007-1 R1.1 and R1.2. Specifically, Texas RE_URE1 failed to document its Cyber Security test procedures in a manner that minimizes adverse effects on the production system or its operation, as required by CIP-007-1 R1.1; and failed to document that testing is performed in a manner that reflects the production environment, as required by CIP-007-1 R1.2. Texas RE determined that Texas RE_URE1's Cyber Security Policy (Policy) describes how the entity will test implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware for Cyber Assets pertaining to two specific departments. However, the Policy did not provide specifics on how the entity would ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls. Through the review of the implementation of Texas RE_URE1's test procedures, Texas RE determined that Texas RE_URE1 had an agreement with vendors to test security updates and patches at the vendor's production environment; however, Texas RE_URE1 installed these security updates and patches from the vendor on Cyber Assets within the ESP without testing in an environment that reflected the entity's production environment. Specifically, Texas RE_URE1 did not stipulate that such tests should be performed in a manner that reflects the production environment. Texas RE_URE1 stated only "client services will deploy the vendor patch to a lab environment." | CIP-007-1 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because Texas RE_URE1 did not provide a test environment that reflects production, it was not able to detect any adverse effects a defective update or patch may bring to the real operation. The risk was reduced because Texas RE_URE1 demonstrated that it had protective measures in place during the time of the violation. Texas RE_URE1 and third party contractors must download or receive security patches from trusted sources. As part of testing procedures, security patches must be validated prior to installation on any Texas RE_URE1 assets. | when the Standard became mandatory and enforceable on Texas RE_URE1 | Mitigation Plan completion | $0 (for TRE2012011015, TRE2012011016, TRE2012011382, and TRE2012011387) | Compliance Audit | To mitigate this issue, Texas RE_URE1: 1) reviewed and enhanced the Policy to include the cyber security controls to be considered when testing new Cyber Assets and significant changes to existing Cyber Assets within the ESP, to minimize adverse effects on the production system and existing cyber security controls; 2) established a template for documenting the similarities and differences between environments used for testing and production environments, including description of the measures used to account for any differences when testing cyber security controls; 3) reviewed and updated the NERC CIP Cyber Asset test procedures to include cyber security controls listed in the Policy; 4) updated business unit change management policies and procedures to reflect activities referenced in milestones one and two; and 5) trained impacted individuals on updated policies, procedures, and/or processes. | 2013-11-15 | 2013-11-19 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012656 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R2.1. WECC_URE1 granted unescorted physical access to a Physical Security Perimeter (PSP) to a third-party contractor. Specifically, a security officer signed out a physical key to the contractor. The access was to a control center containing over 100 Critical Cyber Assets (CCAs) related to WECC_URE1's Supervisory Control and Data Acquisition and energy management system systems. WECC_URE1 failed to provide the required cyber security training to the contractor before granting access. WECC_URE1 determined that the contractor used the physical key to access the PSP after the contractor's deactivated access card was rejected twice. The access card rejections triggered an alert to security, which responded to investigate. Based on a review of logs, interviews, and video monitoring, WECC_URE1 determined that the contractor did not access or attempt to access CCAs during the approximately ten minutes the contractor was within the PSP. The physical key was returned to security approximately ten minutes after it was signed out, when the contractor left the facility. | CIP-004-3a | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The violation involved one contractor who was granted access to test WECC_URE1's fire suppression system. The contractor did not access or attempt to access CCAs during the ten minutes the contractor was within the PSP. Further, WECC_URE1 implemented protective controls for the CCAs, including username and password restrictions, to prevent the contractor from logging on to its logical systems. The facility in question was manned at all times, and access points and certain areas within the PSP were monitored live via closed-circuit television. In addition, WECC_URE1 implemented contact alarms set to trigger upon unauthorized access attempts. The contact alarms activated in this case, and security responded to investigate within approximately 10 minutes. | when the contractor gained access to a PSP without having proper training | when WECC_URE1 revoked access for the contractor | $12,000 (for WECC2013012656 and WECC2013012657) | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked access for the contractor in question and confiscated the contractor's key; 2) reviewed the key procedure to ensure documented instruction for issuance of a key to personnel who have authorized access; and 3) re-trained security guards on the proper procedure for issuance of keys. | 2013-07-19 | 2013-12-06 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012657 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R3. WECC_URE1 granted unescorted physical access to a Physical Security Perimeter (PSP) to a third-party contractor. Specifically, a security officer signed out a physical key to the contractor. The access was to a control center containing over 100 Critical Cyber Assets (CCAs) related to WECC_URE1's Supervisory Control and Data Acquisition and energy management system systems. WECC_URE1 failed to conduct a personnel risk assessment (PRA) for this contractor prior to granting access. WECC_URE1 determined that the contractor used the physical key to access the PSP after the contractor's deactivated access card was rejected twice. The access card rejections triggered an alert to security, which responded to investigate. Based on a review of logs, interviews, and video monitoring, WECC_URE1 determined that the contractor did not access or attempt to access CCAs during the approximately ten minutes the contractor was within the PSP. The physical key was returned to security approximately ten minutes after it was signed out, when the contractor left the facility. | CIP-004-3a | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The violation involved one contractor who was granted access to test WECC_URE1's fire suppression system. The contractor did not access or attempt to access CCAs during the ten minutes the contractor was within the PSP. Further, WECC_URE1 implemented protective controls for the CCAs, including username and password restriction, to prevent the contractor from logging on to its logical systems. The facility in question was manned at all times, and access points and certain areas within the PSP were monitored live via closed-circuit television. In addition, WECC_URE1 implemented contact alarms set to trigger upon unauthorized access attempts. The contact alarms activated in this case, and security responded to investigate within approximately 10 minutes. | when the contractor gained access to a PSP without having a valid PRA | when WECC_URE1 revoked access for the contractor | $12,000 (for WECC2013012656 and WECC2013012657) | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked access for the contractor in question and confiscated the contractor's key; 2) reviewed the key procedure to ensure documented instruction for issuance of a key to personnel who have authorized access; and 3) re-trained security guards on the proper procedure for issuance of keys. | 2013-07-19 | 2013-12-06 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013013114 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-005-1 R1. WECC determined WECC_URE2 did not afford the protective measures specified in CIP-005-1 R1.5 to electronic access points (routers) at Electronic Security Perimeters (ESPs), located at five facilities. While WECC_URE2 owns the routers, a different entity has logical access and control over the devices. Because WECC_URE2 does not have control over the devices, it could not provide documentation that the routers were being afforded the protective measures specified in CIP-005-1 R1.5, specifically the technical and procedural controls for control of electronic access specified in CIP-005-1 R2. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, failing to provide Cyber Assets the required protective measures puts such assets and ESPs at risk to be manipulated or compromised. Such information could then be used to get access to Critical Cyber Assets essential to the operation of the BPS and potentially disrupt the operation of the BPS. Although WECC_URE2 failed to afford these access points the protections of CIP-005-1 R2, the routers are located within Physical Security Perimeters and require user authentication to operate. In addition, according to the entity with logical access and control over the devices, only CIP-authorized operators (i.e. operators with a valid personnel risk assessment and cyber security training) have access to the workstations that send signals through the routers. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $30,000 | Self-Certification | To mitigate this violation, WECC_URE2: 1) contacted the entity with logical access and control over the devices to determine what protections it was affording the routers at issue. The entity with logical access and control over the devices informed WECC_URE2 that only CIP-authorized operators (i.e. operators with a valid personnel risk assessment and cyber security training) have access to the workstations that send signals through the routers. It also informed WECC_URE2 which vendor manages the routers; 2) obtained permission from the entity with logical access and control over the devices to terminate the contract with the vendor. WECC_URE2 then contacted the vendor and requested a termination of the contract for managing the routers; and 3) gained control of the routers. Upon gaining control of the routers, WECC_URE2 took the following steps: a) changed the user access by establishing new user IDs and passwords; b) upgraded all patches and security updates; c) established an access control list for the routers; and d) updated all the documentation pertaining to the routers (ESP documentation and Technical Feasibility Exceptions). | 2013-12-04 | TBD | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-14-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009748 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-005-1 R1. Specifically, MRO_URE1 failed to afford Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP) the protective measures as specified in CIP-007-1 R1.3, R8.2, and R8.4. While reviewing MRO_URE1's Cyber Vulnerability Assessment documentation, MRO discovered that an ESP device had an open port, and the port was not listed in the device baseline. MRO_URE1 did not document any action items to correct this discrepancy. Therefore, MRO_URE1 failed to verify that only ports and services required for operation of the Cyber Assets within the ESP were enabled as required by CIP-007-1 R8.2, and failed to document the action plan to mitigate vulnerabilities identified in the assessment as required by CIP-007-1 R8.4. Additionally, MRO_URE1 failed to provide evidence of testing when the a device was commissioned, as required by CIP 007-1 R1.3. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device is a supplemental security protection measure and it is located outside of the ESP within a demilitarized zone. Therefore, a potential unauthorized user could not use the device to access devices within the ESP. Additionally, although the port was not documented properly, the port was properly enabled. Furthermore, MRO_URE1 provided baseline profiles to indicate that at least some level of security control testing was performed. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 updated its cyber baseline profile and completed the testing as required by CIP-007-1 R1.3 | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated its Cyber Asset profile documentation for the device; 2) performed a comprehensive review of all devices used for the access control and monitoring of the ESP to confirm that configurations are correct and to verify that the access points are consistent with documentation; and 3) updated documentation for all devices used for the access control and monitoring of the ESP. | 2013-08-26 | 2013-09-30 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-14-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009749 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-005-1 R2. Specifically, MRO_URE1 failed to document the configuration of one port at an access point required for operation and monitoring Cyber Assets within the Electronic Security Perimeter (ESP) as required by CIP-005-1 R2.2. The port was properly enabled, but the port was not documented in the baseline. During mitigation, MRO_URE1 performed a comprehensive review of its ports and services documentation. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document the configuration of one port at an access point, MRO_URE1's process for determining which ports to enable was not deficient. Additionally, the port at issue was properly enabled and required for operation. MRO_URE1 failed to document the port in the baseline document. Therefore, this violation was limited to a documentation deficiency for one port subject to CIP-005-1 R2.2. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented the configuration of its port | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the Cyber Asset profile documentation for the device; 2) performed a comprehensive review of all ESP access points to confirm that configurations are correct and to verify that the access points are consistent with documentation; and 3) updated documentation for all devices classified as ESP access points. | 2013-08-21 | 2013-09-11 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-14-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009751 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-006-1 R1.8. Specifically, MRO_URE1 failed to afford the protective measures as described in CIP-007-1 R2 for Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP). MRO_URE1 failed to document a process to ensure that only ports and services required for normal and emergency operations were enabled as required by CIP-007-1 R2. MRO_URE1's Cyber Vulnerability Assessment identified open ports that were not identified in the associated baseline documentation. Upon discovering the ports, MRO_URE1 did not update its baseline documentation. During mitigation, MRO_URE1 performed a comprehensive review of its ports and services and did not identify any other discrepancies in its ports and services documentation. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document its ports, MRO_URE1's process for determining which ports to enable was not deficient. All of MRO_URE1's ports and services subject to CIP-006-1 R1.8 were properly enabled for normal and emergency operations. Furthermore, the PACS devices are afforded the protections of being located within the Electronic Security Perimeter. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented ports and services for normal and emergency operation | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the Cyber Asset profile document for the device; 2) performed a comprehensive review of the procedures; and 3) updated its Cyber Asset profile documentation template to include more accurate reporting of port and service status. | 2013-08-21 | 2013-09-16 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
2014-01-30 | FERC | NP14-14-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009752 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-007-1 R4. Specifically, MRO_URE1 failed to have a process for updating antivirus and malware prevention signatures that addressed testing the signatures prior to installation, as required by CIP-007-1 R4.2. MRO_URE1 installed updated antivirus and malware signatures before it installed the same signatures within the Electronic Security Perimeter (ESP). However, this process was not documented. Additionally, MRO_URE1 only applied this process to some devices. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document its testing process for antivirus and malware signatures, MRO_URE1 first tested the signatures on outside of the ESP. Therefore, if a failure would have occurred, MRO_URE1 would have discovered the issue prior to installing the update on the devices within the ESP. Additionally, although the process for testing was not documented for the other device, the manual nature of the updating process provided MRO_URE1 an opportunity to stop the update if problems were discovered prior to installation of the update. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented and implemented a process for updating antivirus and malware signatures | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of the anti-malware environment and procedures to ensure the documents are accurate and an up-to-date reflection of the technology and management processes; 2) updated documentation for antivirus signature updates and testing procedures; 3) evaluated a new signature testing module from an antivirus vendor; and 4) designed and implemented procedures and technology to provide more robust testing of antivirus signatures. | 2013-08-23 | 2013-09-26 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty.
2014-01-30 | FERC | NP14-14-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009753 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-007-1 R8. Specifically, MRO_URE1 failed to document and track the execution status of its action plan for remediation of one vulnerability identified during its Cyber Vulnerability Assessment (CVA), as required by CIP-007-1 R8.4. During the annual CVA, MRO_URE1 discovered that a service and associated port were enabled in two Cyber Assets, but they were not included in the baseline documentation. As a result, an action item was created to disable the service on both Cyber Assets. The status of the action item at the time of the Compliance Audit was closed. However, the ticket provided as evidence of completion only indicated that one of the Cyber Assets was corrected. When MRO_URE1 went to disable the other service, it determined that the service was necessary and did not disable it as specified in the action item. However, MRO_URE1 did not revise the action item to reflect the erroneous inclusion. | CIP-007-1 | R8; R8.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 originally listed disabling the service as an action item, during the execution of the task, MRO_URE1 determined that the service was necessary. Therefore, the service should not have been listed as an action item and the violation is based on erroneous inclusion. Additionally, the Cyber Asset was protected by the Electronic Security Perimeter and the Physical Security Perimeter. | when MRO_URE1 failed to document the execution status of the CVA | when MRO_URE1 documented the status of its action plan for the vulnerability identified in the CVA | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of the CVA program to identify procedural gaps relative to CIP-007-3 R8; 2) revised the 2010 CVA spreadsheet to indicate the actual actions taken; 3) reviewed the action plans for the 2010 and 2011 iterations of the CVA and confirmed that all action items were completed and documented correctly; and 4) added two columns to the CVA findings template to capture additional information for future assessments. | 2013-08-21 | 2013-09-25 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000442 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8 because the physical access control system (PACS) was not afforded all the protective measures required pursuant to CIP-006-1 R1.8. Specifically, SERC_URE1 reported that it had not afforded the PACS the protective measures described in CIP-007-1 R3 related to security patch management. SERC_URE1 discovered that it was not assessing security patches for all the assets comprising the PACS. The subset of PACS assets at issue in this violation consisted of a total of seven Cyber Assets, three servers and four workstations. SERC_URE1 reported that the PACS assets at issue were deployed in an isolated Electronic Security Perimeter (ESP) with no communication paths to SERC_URE1's Critical Cyber Assets (CCAs), corporate assets, or the internet. While analyzing this issue, SERC learned that SERC_URE1 had a procedure requiring it to assess and apply security patches. SERC_URE1 did assess and apply security patches on its deployed CCAs and other non-critical Cyber Assets, as required. SERC_URE1 had classified all its PACS assets as CIP-protected Cyber Assets, thereby bringing them within the scope of this procedure. SERC_URE1 however, had no evidence that assessments were being performed for the seven PACS assets described above. In total, SERC_URE1 failed to document its assessment of 19 security patches released during a five month period for the seven PACS asset at issue. A month and half later, SERC_URE1 applied these 19 security patches on the seven PACS assets. SERC sent SERC_URE1 an initial notice of a Compliance Audit. During this Compliance Audit, SERC found that SERC_URE1's Physical Security Plan, which details SERC_URE1's organizational processes and technical and procedural mechanisms for controlling access at physical access points to Physical Security Perimeters (PSPs), including the protections required for the PACS assets, failed to address the following protective measures as required by CIP-006-1 R1.8: 1) SERC_URE1 failed to document the enabled ports and services required for operations and monitoring of Cyber Assets within the ESP, as described in CIP-005 R2.2; 2) SERC_URE1 permitted external interactive access to the PACS without authentication, thereby failing to demonstrate strong procedural or technical controls to ensure authenticity of the accessing party at access points, as described in CIP-005 R2.4; 3) SERC_URE1 failed to log authorized traffic through its firewall to the PACS, as described in CIP-005 R3; 4) SERC_URE1 failed to document test results for significant changes to the PACS to ensure the changes did not adversely affect existing cybersecurity controls, as described in CIP-007 R1.3; 5) Despite providing evidence that a third-party vendor tested anti-virus and malware prevention signatures for the PACS, SERC_URE1 failed to document a process for such testing, as described in CIP-007 R3.1; and 6) SERC_URE1 failed to document a backup and recovery process for its physical access control panels, as described in CIP-009 R4. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1's failure to afford PACS devices and logging systems the measures listed in CIP-006-1 R1.8, could have made those devices more easily compromised, allowing malicious access to Cyber Assets within the PSP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS. Failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, altering, and possibly weakening, the existing cybersecurity controls and making SERC_URE1 more vulnerable to physical intrusion. SERC_URE1's failure to timely assess 19 security patches on seven different PACS assets left those Cyber Assets vulnerable for extended periods of time, increasing the risk of a successful cyber intrusion. However, SERC_URE1's PACS assets were deployed within a secured ESP and PSP and there was no electronic access to PACS assets from outside their isolated ESP, significantly decreasing the risk of a successful cyber intrusion. Although the PSP access points did not log authorized traffic, as described in CIP-005 R3, the access points would log unauthorized access attempts; however, no unauthorized access attempts occurred during this period. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this violation, SERC_URE1: 1) established an operations security patch coordinator position; 2) modified the existing SERC_URE1 system security plan to reflect the assignment of a security patch coordinator, the increase in internal compliance monitoring, and the modifications to the documentation processes; 3) provided additional guidance and directions to the system administrators by expanding the Security Patch Management section of the SERC_URE1 plan to include step-by-step processes in the following areas: a) obtaining security patches from each vendor; b) assessing patches and documenting the assessment on each system.; c) implementation and documentation of compensating measures if a patch cannot be applied; d) testing and documentation of security patches on each system; e) installing and documenting the application of patches to the production environment on each system; and f) routine internal confirmation that security patches have been assessed and applied to each system; 4) conducted additional security patch process training session with system administrators; 5) validated the improved process through internal auditing; and 6) confirmed compliance with patch management policies, guidelines, and procedures (PGPs) that: a) the operations' security patch coordinator collects evidence on one-third of the systems each month; b) the operations security patch coordinator verifies monthly evidence meets the requirements of SERC_URE1's PGPs and supplies this evidence to Critical Infrastructure Compliance; and c) Critical Infrastructure Compliance conducts an independent confirmation of compliance. | 2012-12-21 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006644 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R2.2 because it failed to ensure that only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. SERC learned that one electronic access control and monitoring system (EACMS), a firewall, serving as an electronic access point to a SERC_URE1 ESP, had undocumented ports and services enabled that were not required for operations or monitoring of Cyber Assets within the ESP. SERC_URE1 acknowledged that two firewall rules allowed unnecessary network traffic. The first rule allowed unrestricted access from SERC_URE1's internal protected network segments to the CIP protected network segment on ports that were not required for operations or for monitoring of Cyber Assets within the ESP. As a result, 66.67% of SERC_URE1's Critical Cyber Assets were potentially accessible. The second rule allowed access from SERC_URE1's CIP protected network segment to unrestricted destinations on ports not required for operations or for monitoring of Cyber Assets within the ESP. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because the failure to restrict ports and services at access points to only those required for operations could increase the attack surface into the ESP and result in access out of the ESP to low-trust assets that could be leveraged or compromised. In addition, SERC_URE1's failure to implement restrictive rules for inbound and outbound traffic could result in internal compromise or vulnerabilities that propagate between the CIP and non-CIP networks without restriction. However, the risk to the BPS was mitigated because SERC_URE1's vendor was monitoring SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts or access to its ESP. The EACMS assets were located within a Physical Security Perimeter and thus afforded physical access controls. Finally, no unauthorized attempts were detected during the violation period. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) documented the authorized ports/services configuration (baseline); 2) closed all ports not currently in use; 3) conducted a new vulnerability assessment; and 4) updated change control training to include assessment of the ports and services, default accounts, and malware instructions for capturing before and after screen shots. | 2012-04-03 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006645 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R2 because it failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. SERC_URE1 reported that it conducted its annual Cyber Vulnerability Assessment (CVA) and discovered that ports and services were enabled on 31 servers that SERC_URE1 could not show were required for operations out of 397 total Cyber Assets. Specifically, SERC_URE1 did not have documentation stating the enabled ports and services were required for normal and/or emergency operations. | CIP-007-1 | R2; R2.1: R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to disable ports and services that were not required for normal or emergency operations could allow unauthorized individuals or malware to exploit these ports and thereby disrupt operations or gain unauthorized access to or control of Critical Cyber Assets (CCAs). However, the servers are protected by two levels of firewalls that prevent the enabled services from being accessed by an outside entity, and services have been disabled where SERC_URE1 could confirm that it was safe to do so. SERC_URE1 made an affirmative decision to allow the ports and services in question to remain open in an effort to ensure the continued functionality of its servers. Where technically feasible, all Cyber Assets within the Electronic Security Perimeter(s) were running malware protection. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) filed a technical feasibility exception for 47 servers; 2) documented an authorized ports/services list (baseline); and 3) completed a vulnerability assessment that included a scan of firewalls and a comparison to the authorized ports and services list (baseline). | 2012-12-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006646 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R8.3 because it failed to perform a review of the controls for default accounts during its annual Cyber Vulnerability Assessment (CVA). Upon reviewing the results from the CVA SERC_URE1 discovered that it failed to perform a review of controls on default accounts and passwords, as required by CIP-007-1 R8.3. SERC reviewed documentation for default accounts and evidence demonstrating that the accounts were quarterly reviewed. SERC_URE1 also provided evidence demonstrating its use of password controls software, as well as change management tickets, illustrating that the default account passwords were required to be changed annually. In addition, SERC_URE1's policy implementing CIP-007 R5.2 required the proper handling, review, and management of default accounts, including the requirements for password controls. Despite the presence of these controls, SERC_URE1 failed to review these controls as part of its annual CVA. SERC learned that this violation involved nine default accounts enabled on SERC_URE1's Cyber Assets. | CIP-007-1 | R8; R8.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 documented its default account controls in established policies. SERC_URE1 performed quarterly reviews of the default accounts themselves, but it failed to include a review of its controls for those accounts as part of its annual CVA. The devices in question are protected by multiple levels of security, including corporate firewalls, intrusion detection systems, and cybersecurity monitoring software with twenty-four hour a day, seven days a week off-site monitoring and alerting. | when the Standard became mandatory and enforceable on SERC_URE1 | when a comprehensive CVA was conducted, which included reviewing controls for default accounts | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) conducted a review of controls for default accounts; 2) conducted a comprehensive CVA; and 3) provided awareness on the CVA process to the appropriate personnel. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006647 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it had a violation of CIP-005-1 R4 because it failed to perform annual Cyber Vulnerability Assessments (CVAs) that discovered all access points to Electronic Security Perimeters (ESPs) and the completed CVAs were otherwise not adequate. SERC_URE1 discovered that its CVA did not meet the requirements of CIP-005-1 R4, while reviewing its firewall access control rules in conjunction with a prior Self-Report. The CVA failed to verify that only ports and services required for operations were enabled, as required by CIP-005-1 R4.2. The CVA also failed to include a comprehensive list of all SERC_URE1 ESP access points, and the CVA was not performed on all access points, as required by CIP-005-1 R4.3. Finally, the CVA failed to document a review of controls for default accounts, passwords, and network management community strings, as required by CIP-005-1 R4.4. SERC learned that the unidentified access points were utilized to isolate SERC_URE1's assets from the substation communication network, and were deployed on a dedicated leased communication circuit with no public accessibility. The CVA report addressed the discovery of access points to the ESP, generally. However, this report failed to include the discovery of the access points in question. | CIP-005-1 | R4; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1's failure to identify and protect open ports and services, access points to its ESPs, and shared passwords, could have made SERC_URE1 more vulnerable to a cyber attack. However, SERC_URE1 utilized a network intrusion detection system to analyze network traffic for known and suspect malicious activity. SERC_URE1's Cyber Assets were located within a Physical Security Perimeter and thus afforded physical access controls. In addition, SERC_URE1's vendor was monitoring electronic access to SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts to access to its ESP during the time of the violation. Finally, SERC_URE1 reported no unauthorized access attempts to the ESP during the time of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) issued detailed request for proposal to include all requirements of the CIP Standards; and 2) performed a new and more comprehensive CVA. To prevent reoccurrence, SERC_URE1 held a meeting to review the vulnerability assessment report in preparation for the next year's vulnerability assessment. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011007279 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1.5 because it failed to afford all the required protective measures to Cyber Assets used in the electronic access control and monitoring (EACM) of the Electronic Security Perimeter (ESP). SERC_URE1 submitted a second Self-Report stating that it was in violation of CIP-005-2 R5.3 because it failed to maintain electronic access logs for one Cyber Asset used as an EACM device, as required. SERC determined that these facts actually constituted a violation of CIP-005-1 R1.5 and, therefore, consolidated the two Self-Reports into a single violation. SERC sent SERC_URE1 an initial notice of a Compliance Audit. During this Compliance Audit, SERC discovered that SERC_URE1 failed to identify and document two EACM devices and their associated access points to SERC_URE1's ESP. As a consequence, the devices were not afforded the protective measures specified in CIP-005-1 R1.5. As to the first issue, the EACM device at issue was a firewall that protected a network segment containing 40 Critical Cyber Assets. While performing an internal review of its access lists, SERC_URE1 discovered an unapproved administrative account on this device. This account was created without adherence to SERC_URE1's change control and configuration management process, as described in CIP-003-1 R6. Therefore, the use and privileges of the account were not managed in accordance with CIP-007-1 R5, despite SERC_URE1's documented procedures requiring such. Additionally, SERC_URE1 assigned a generic password to the administrative account that did not meet the complexity requirements described in CIP-007-1 R5.3. SERC_URE1 also failed to ensure that it changed this password at least annually, also as described in CIP-007-1 R5.3. As to the second issue, SERC_URE1 discovered that the electronic access logs for one EACM device were not retained. SERC_URE1 determined that it misconfigured a Cyber Asset thus preventing the logs from reaching the centralized log server. As a result of this misconfiguration, SERC_URE1 could not provide evidence that its documented processes for monitoring and logging access at the EACM were implemented twenty-four hours a day, seven days a week. Although, SERC_URE1 initially reported this issue as a violation of CIP-005-2 R5.3, SERC determined that it was in fact a violation of CIP-005-1 R1.5 because SERC_URE1 failed to maintain access logs for an EACM device, as described in CIP-007-1 R5.1.2. As to third issue, SERC determined that SERC_URE1 was in violation of CIP-005-1 R1.5 because it failed to identify and document two EACM devices as access points to its ESP and afford the EACM devices the protective measures specified in CIP-005-1 R1.5. Specifically, SERC_URE1 failed to: 1) document test results of significant changes to EACM devices within its ESP, as described in CIP-007-1 R1.3; 2) document assessments of cybersecurity patches for Cyber Assets within its ESP, as described in CIP-007-1 R3.1; 3) ensure that only ports and services required for operations and monitoring of Cyber Assets within the ESP were enabled, as described in CIP-005-1 R2.2; and 4) implement strong procedural or technical controls at the access points to the ESP to ensure authenticity of the accessing party, despite a requirement to do so in its CIP Cyber Security Policy, as described in CIP-005-1 R2.4. SERC_URE1's failure to ensure that only required ports and services were open included a failure to provide documentation detailing the business need for its open source and destination ports and services at access points. SERC_URE1 also allowed traffic from any source to an excessive number of ports on its EACM devices. SERC learned that SERC_URE1 utilized an off-site third-party vendor to monitor logs and provide alerts for the access points. SERC_URE1, however, failed to identify and document the third-party EACM devices. In addition, SERC_URE1 could not produce evidence that the assets were being afforded the protection of CIP-005-1 R1.5, as required. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failing to identify and protect electronic access points associated with EACM devices and the devices themselves presented a risk of unauthorized access to SERC_URE1's ESP. However, the administrative account was known only to a SERC_URE1's maintenance group, consisting of just two individuals. To access the administrative account, a user would have had to have authorized physical access to SERC_URE1's Physical Security Perimeter (PSP). SERC_URE1 used a network intrusion detection system to analyze network traffic for known and suspect malicious activity. All the EACM devices at issue were located within a PSP and thus afforded physical access controls. SERC_URE1's vendor was monitoring SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts or access to its ESP. Finally, SERC_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) changed the password in question; 2) disabled the account; 3) enhanced the change control training to include: a) appropriate security questions are documented including the assessment of the ports and services to be opened, default accounts and malware; and b) instructions for capturing before and after screen shots; 4) documented a new process to properly identify and categorized EACM assets; 5) installed Cyber Assets used in the access control and/or monitoring of the ESP in order to setup authentication at the access points for Cyber Assets within the ESP. 6) set up an in-house solution for monitoring and alerting of its CIP-protected Cyber Assets. All devices related to this solution are properly classified; 7) retired devices identified during the Audit from service due to the cutover of the new energy management system; 8) established a checklist to ensure that only ports and services needed for operations and monitoring are enabled; 9) established technical controls to ensure authenticity of all accessing parties by implementing two factor authentications for external interactive access. 10) corrected the misconfiguration by changing the Secure Shell settings to allow the network device logs to reach the log archiving server and configured an additional log server for redundancy; and 11) established a system in which a confirmation is made on a monthly basis that all CIP-protected Cyber Assets are actively sending logs to the logging server via SERC_URE1's monthly compliance report. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008318 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R5.1 because it failed to implement a user account as approved. SERC_URE1 reported that it created a user account on a Critical Cyber Asset (CCA) for an employee who had not been authorized for electronic access to that CCA. According to SERC_URE1, the individual was authorized for electronic access to a server, classified as a CCA, within an Electronic Security Perimeter (ESP). The ESP at issue contained three CCAs: two servers and a network switch. Despite only being authorized for one of the servers, SERC_URE1 granted the individual access to two both servers. SERC_URE1 determined that the servers at issue are utilized as repositories for CCA information, specifically, Remote Terminal Unit (RTU) configuration information and relay settings and maintenance records. Therefore, SERC_URE1 determined that they were improperly classified as CCAs and subsequently removed them from its list of CCAs. SERC_URE1 discovered this unauthorized user account during a quarterly review of user account access privileges. | CIP-007-3a | R5; R5.1 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual had a completed personnel risk assessment and cybersecurity training. The account was created on the asset but the credentials were never distributed to the individual. The individual was not authorized or granted physical access to the Physical Security Perimeter in which these assets resided. The individual had electronic access to other CCAs within the ESP. | when the user account was added | when the user account was removed from the CCA | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) clarified the existing procedure with more detailed steps on how to properly grant access to CIP-protected Cyber Assets; 2) provided appropriate personnel with additional training; and 3) removed the individual's account from the second CCA after a quarterly review of access rights determined the individual had not been approved for access to that device. | 2012-09-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008319 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report that it was in violation of CIP-005-1 R2.5 because it failed to document all authentication methods used for interactive access into the Electronic Security Perimeter (ESP). SERC_URE1 reported that it utilized three different authentication methods for accessing Critical Cyber Assets (CCAs) through its ESP. SERC_URE1, however, failed to identify and describe two of the methods in the required documentation. SERC_URE1 stated that the documentation addressed only the primary authentication method and omitted the two alternate approaches that were used less frequently. SERC reviewed SERC_URE1's Electronic Security Program documentation and determined that it failed to adequately detail the authentication methods employed at the electronic access points to the ESP. SERC_URE1's program required that at least two authentication methods be used simultaneously when accessing the ESP. However, it did not describe all the authentication methods deployed, as required by CIP-005-1 R2.5. Specifically, SERC learned that SERC_URE1 utilized three methods of authentication for accessing the ESP: 1) A CIP compliant user name and password; 2) two factor authentication utilizing a secure token; and 3) internet protocol (IP) restricted source and destination addressing. SERC_URE1 documented only the first authentication method. SERC also determined that the third authentication method, utilizing IP restricted source and destination addressing, did not sufficiently ensure the authenticity of the individual accessing the ESP. As a result, SERC determined that this method did not constitute a strong procedural or technical control at an access point to the ESP to ensure authenticity of the accessing party, as required by CIP-005-1 R2.4. SERC learned SERC_URE1 used the third authentication method to allow control room operators to update deployed remote terminal units (RTU) from a workstation within the Physical Security Perimeter (PSP), but not an ESP. The operators would authenticate to access the workstation, and then use the workstation to access an identified CCA within an ESP to update the RTUs. The operators, however, did not authenticate at the ESP access point. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SERC_URE1 only described one authentication method in its required documentation, it represented to SERC that it was using multiple methods, thereby restricting access to its ESPs. The workstation used to update RTUs was located within the PSP where only authorized personnel with completed personnel risk assessments and cybersecurity training had access. Although SERC_URE1 was utilizing IP restricted source and destination addresses to restrict access, this authentication method was limited to a single workstation with a static IP address and a firewall that limited its access. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) enhanced documentation to describe all methods used to authenticate users into the ESP and maintain list of methods used for authentication; and 2) created an on-boarding checklist to determine if Cyber Assets being added to the CIP environment introduce a new authentication method. | 2012-12-10 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008320 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3 R4 because it failed to remove physical access to Critical Cyber Assets (CCAs) within seven calendar days of personnel no longer requiring access. While SERC was performing its assessment and determining the scope of the violation, the following additional issues were found: 1) SERC_URE1 self-reported three non-related instances where it failed to follow documented policies and procedures to control physical and electronic access to CCAs. First, an individual was granted access to a Physical Security Perimeter (PSP) prior to being approved for such access. Second, an individual was authorized access to one PSP; however, the individual was granted access to a different PSP which had not been approved. Finally, an individual was granted electronic access to an Electronic Security Perimeter (ESP) prior to approval; 2) the SERC audit team reported that SERC_URE1 was in violation of CIP-004-3 R4.2 because it did not revoke a contractor’s authorized cyber access rights to CCAs within seven calendar days after such access was no longer required. As to the issue disclosed in the first Self-Report, during its second quarter access list review, SERC_URE1 discovered that a temporary employee who was on a leave of absence maintained unescorted physical access to two Physical Security Perimeters (PSPs). The temporary employee's leave of absence was due to the individual returning to coursework and was not for cause. SERC_URE1 revoked the temporary employee' access. The individual returned to work at SERC_URE1 approximately two months later, and SERC_URE1 reauthorized the temporary employee's access privileges and reinstated them two days later. SERC_URE1's access policies in place at the time of the violation did not address leaves of absence or access revocation during leaves of absence. The temporary employee had been granted authorized unescorted physical access to two PSPs, a transmission room and an office area, and was authorized to have unescorted physical access to another two PSPs. The temporary employee' had no electronic access to any CCAs. Although SERC_URE1 discovered this issue, SERC_URE1 did not report it until approximately a year and four months later because the individual who originally discovered it was not aware of the compliance implications of a failure to revoke access within seven calendar days of an individual no longer requiring such access. The three issues disclosed in the second Self-Report, and subsequent investigation, are described below: 1) SERC_URE1 contracted with a temporary employee to serve as a system administrator for the data historian application on non-critical Cyber Assets within the server room PSP. SERC_URE1 required completion and approval of a Bulk Electric System Cyber Authorized (BESCA) request form prior to granting access to PSPs. In this case, SERC_URE1 inadvertently left one server room, related to the energy control and metering systems (ECMS), off the BESCA request form. Knowing that this temporary employee would need access to the ECMS server room, SERC_URE1 granted the individual access to this server room. SERC_URE1 discovered this unauthorized access during a quarterly review of its access lists and revoked it; 2) SERC_URE1 initially granted an individual authorized unescorted physical access to the transmission room PSP. The individual required a badge replacement, which required SERC_URE1 to re-activate the badge for CIP-related access privileges. SERC_URE1 failed to re-activate the individual’s badge, and the individual was denied access to a PSP to which access had previously been authorized. Upon this denial, the individual contacted SERC_URE1's CIP access administrator requesting that access be reinstated. In response to this request, SERC_URE1 inadvertently granted the individual access to a PSP for which the individual lacked authorization. During a quarterly access list review SERC_URE1 discovered the error and revoked the access. SERC_URE1 staff verified through access log review that the individual did not access the unauthorized PSP. The PSP to which the individual was inadvertently granted access contained no CCAs; and 3) SERC_URE1 created an account granting electronic access to one access point to the SERC_URE1 ESP prior to the individual in question being approved for such an account. A SERC_URE1 administrator created the account prior to receiving the necessary approvals, knowing that the account would be needed in the near future. SERC_URE1, however, never shared the account username and password with the user, effectively limiting the possibility of unauthorized access. Upon discovering that the account had been created without the proper authorization, SERC_URE1 disabled the account and verified that it had never been used. SERC_URE1 created the account to allow access to a firewall, thereby enabling access to an ESP but not the CCAs protected by that ESP. The relevant ESP contained two CCAs. SERC_URE1 discovered this issue during a quarterly access list review and disabled the account approximately a month and a half later. As to the issue discovered during the Compliance Audit, SERC_URE1 owns and maintains two servers classified as CCAs which are also utilized by an affiliated entity. SERC_URE1 is the entity responsible for ensuring that the two servers are protected in accordance with the CIP Standards. The affiliated entity contracted with a vendor to provide technical support for an application running on one of these CCAs. One of the vendor’s employees that had provided technical support voluntarily terminated the employment relationship with the vendor. The contractor sent a package to the affiliated entity informing the affiliated entity of the need to revoke this employee’s access, including in the package the virtual private network (VPN) token that enabled remote cyber access to SERC_URE1's CCAs. The affiliated entity received this package six days after the contractor sent the package. The affiliated entity notified SERC_URE1 of the vendor employee’s termination, and SERC_URE1 revoked this individual’s access to the CCA within 24 hours of notification. However, SERC_URE1 failed to revoke the individual’s access within seven calendar days of that individual no longer requiring such access. | CIP-004-3 | R4; R4.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 conducted personnel risk assessments on the individuals in question and ensured that they had received cybersecurity training prior to granting them access to CCAs. The temporary employee described in the first Self-Report was not authorized nor granted electronic access to any CCAs, SERC_URE1 revoked physical access approximately four weeks after the start of the leave of absence, and SERC_URE1 reinstated access privileges upon the individual’s return. As to the first issue from second Self-Report, the individual in question had no access to CCAs. As to the second issue from the second Self-Report, the individual’s unauthorized access granted access to a PSP in a basement hallway that did not contain any CCAs. As to the third issue from the second Self-Report, SERC_URE1 never distributed the improperly created account information, and the account did not grant access to CCAs. As to the issue discovered during the Compliance Audit, the vendor maintained its relationship with SERC_URE1 after the vendor employee terminated employment with the vendor, indicating a trusted relationship between SERC_URE1 and the vendor. SERC_URE1 identified and promptly remedied these issues through its quarterly review of its access lists, indicating the presence and efficacy of SERC_URE1's internal controls. | seven days following the start of the leave of absence for the first instance of non-compliance | when access was revoked | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) clarified the existing procedure with more detailed steps on how to properly grant access to CIP-protected Cyber Assets; 2) provided the revised Security Requirements Certification Agreement to the vendor and contract agencies for their review and signatures; and 3) provided appropriate personnel with additional training. | 2012-11-07 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE1 did not complete the mitigation plan for this violation on time and SERC considered this an aggravating factor when determining the penalty.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009000 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-005-1 R3 because it failed to provide evidence that it implemented security monitoring processes to detect and alert for actual unauthorized access into its Electronic Security Perimeters (ESP). SERC learned that SERC_URE1 failed to implement security monitoring processes to detect and alert for actual unauthorized access into one of its ESP access points. SERC reviewed SERC_URE1's electronic security program policy and found that it detailed the requirement to detect and alert for unauthorized access, or attempts at such access. However, SERC_URE1 failed to implement the policy on the identified electronic access point. As part of this failure, SERC_URE1 failed to log traffic that is permitted through its firewall that would be needed to detect and alert on actual unauthorized accesses. The access logs would have been needed to investigate and identify, through automated or manual reviews, successful unauthorized access into the ESP. | CIP-005-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because a violation of CIP-005-1 R3 presents a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within the ESP. SERC_URE1, however, was logging denied traffic at access points to the ESP during the time of the violation. SERC_URE1 also utilized a network intrusion detection system to analyze network traffic for known and suspected malicious activity. SERC_URE1's vendor was monitoring electronic access to SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts and/or access to its ESP. SERC_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) retired router when the new energy management system was upgraded with replacement of hardware and software; 2) verified logging was configured correctly; and 3) developed an on-boarding checklist to be completed prior to placing an asset into production environment. | 2012-11-29 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009003 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-006-1 R3 because SERC_URE1's documented and implemented technical and procedural controls for monitoring physical access to its Physical Security Perimeters (PSPs) did not require monitoring twenty-four hours a day, seven days a week, and SERC_URE1 was unable to provide evidence to demonstrate that all unauthorized access attempts to the PSPs were reviewed immediately and handled in accordance with CIP-008. SERC_URE1 utilized a physical access control system (PACS) for access control and monitoring at its primary control center (PCC) and backup control center (BCC). The two facilities housed separate PSPs and were subject to the CIP requirements and the SERC_URE1 physical security plan. Pursuant to this plan, from 6:00 a.m. through 6:00 p.m., seven days a week, SERC_URE1 had dedicated security operators who monitored security consoles at workstations at both the PCC and the BCC. Any unauthorized access attempts to either PSP facility would have triggered an audible alarm by the PACS, which was also displayed at the security console within the affected control center. The security operators were then able to provide an immediate response and investigate any unauthorized access attempts to the PSPs. Outside of these hours, however, the security workstations were not continuously manned, and therefore SERC_URE1 system operators relied upon audible alarms to initiate an immediate response to investigate an unauthorized access attempt. SERC learned that the audible alarm was muted when a forced or held open door was closed, meaning that the system operators did not need to immediately investigate the alarm in order to silence it. Consequently, an unauthorized access attempt to a PSP could go undetected by the on-duty system operator. In addition, the logs of alarms occurring outside of 6:00 a.m. through 6:00 p.m. were distributed via email for management review the following day, further preventing SERC_URE1 from investigating unauthorized access attempts immediately. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to continuously monitor all access points to the PSPs twenty-four hours a day, seven days a week, presented a risk of unauthorized access and exploitable vulnerabilities to CCAs. SERC_URE1, however, had implemented exterior and interior access controls to reduce the risk of unauthorized access to its two PSP facilities, including video surveillance, security officers, and electronic badge access controls. Additionally, to access the PCC, all individuals were required to pass through an electronically controlled gate. Furthermore, SERC_URE1 would have monitored for and immediately responded to alarms by its PACS occurring from 6:00 a.m. through 6:00 p.m., seven days a week. Finally, there were no security issues regarding SERC_URE1's PSPs for the duration of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) identified and implemented technical and procedural controls at all access points to the PSP twenty-four hours per day, seven days per week. The action items taken to accomplish this include: a) created a detailed step-by-step procedure to address technical and procedural controls for monitoring physical access at all access points to the PSP twenty-four hours per day, seven days per week; b) prepared a CIP Compliant area; c) hired security personnel; d) trained security personnel; e) established monitoring twenty-four hours per day, seven days per week; and f) assessed evidence to determine if compliance to the standards and procedures have been achieved. | 2012-12-15 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009004 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-006-1 R6 because it failed to implement a maintenance and testing program to ensure that all physical security systems under requirements CIP-006-1 R2, R3, and R4 function properly. The SERC audit team found that SERC_URE1 failed to document or implement a maintenance and testing program on its physical security systems. SERC_URE1 demonstrated evidence that it performed limited testing of select doors, but it failed to provide evidence for all physical security systems. In addition, SERC_URE1 did not provide evidence that it performed testing of the physical security mechanisms on a cycle no longer than three years, as required by CIP-006-1 R6.1. SERC reviewed SERC_URE1's CIP Cyber Security Policy, which required that all physical access controls, monitoring, and logging equipment be tested and maintained at least every three years, and the logs of the testing kept until the next test. SERC also analyzed SERC_URE1's CIP Physical Security Plan, which required that maintenance and testing be performed every three years, and that documentation of maintenance and testing be maintained by the supervisor of CIP compliance, or a designee. SERC_URE1 provided a change management ticket demonstrating that limited testing was completed. Despite SERC_URE1's policies requiring it to maintain documentation of testing, SERC_URE1 failed to maintain this documentation. | CIP-006-1 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because the failure to implement a maintenance and testing program of the physical security systems could allow a degradation of the security mechanisms that provide access control, monitoring, and logging of access points to the Physical Security Perimeter. Failure to identify possible deficiencies in the physical security systems could allow unauthorized or unmonitored access to Critical Cyber Assets which could impact SERC_URE1's ability to monitor and control the BPS. However, SERC_URE1 did show evidence of a limited test of select doors during the audit period that demonstrated some functionality but did not meet the requirements of CIP-006-1 R6. The audit team performed a functional test of physical security mechanisms associated with all access points during its PSP sampling and found that all security mechanisms under requirements CIP-006-1 R2, R3 and R4 were functioning properly. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan Completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) expand its physical security testing plan to include all access control and monitoring devices that collectively control and monitor physical security to SERC_URE1's CIP restricted areas; 2) created an updated checklist to identify the devices, locations, and the functionality of all physical access control and monitoring devices; 3) conducted a comprehensive test according to its physical security testing plan. The test documentation consisted of the following: a) documentation of any defects discovered during the test; b) notification to SERC_URE1's CIP compliance group of test results; and 4) performed a review for completeness is made on a monthly basis | 2012-08-31 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009005 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The audit team reported that SERC_URE1 was in violation of CIP-006-2 R3 because it failed to deploy its electronic access control and monitoring (EACM) devices used for access control and/or monitoring of the Electronic Security Perimeter (ESP) within an identified Physical Security Perimeter (PSP). The SERC audit team found that SERC_URE1 utilized an off-site third party to monitor EACM logs and provide alerts. SERC_URE1 failed to identify the third-party assets used in the monitoring of the SERC_URE1 EACM devices, and failed to present evidence demonstrating that the third-party assets were deployed within an identified PSP. SERC learned that the devices utilized for monitoring were deployed at an off-site location and received forwarded copies of the ESP access point logs. The third-party scanned the logs for possible security intrusions and alerted SERC_URE1. SERC reviewed the SERC_URE1 CIP Physical Security Plan and its details that the manager, energy control and metering systems is responsible for ensuring that all SERC_URE1 CIP-protected Cyber Assets reside within a defined PSP. In addition, the SERC_URE1 Electronic Security Program document states that the log management systems are considered CIP-protected Cyber Assets. | CIP-006-2 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because failure to afford protective measures to EACM devices could result in successful unauthorized access or unauthorized access attempts going undetected by logging and monitoring systems. SERC_URE1 relied on a third-party vendor to provide timely notification of security-related incidents, and provided no evidence that the assets utilized for the monitoring were adequately protected pursuant to the CIP Standards. Failure to adequately monitor ESP access point logs presented a risk that unauthorized intruders could access and possibly compromise SERC_URE1 Critical Cyber Assets (CCAs) undetected. Such access to the CCAs may then be used to cause harm to CCAs essential to the operation of the BPS. SERC, however, found no evidence indicating that SERC_URE1's vendor failed to protect the Cyber Assets at issue, and the vendor was an established vendor with experience providing offsite monitoring. SERC_URE1 identified no known security breaches during the time frame in question. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) installed Cyber Assets used in the access control and/or monitoring of the ESP in order to setup authentication at the access points for cyber assets within the ESP; 2) changed procedures to use an in house solution for monitoring and alerting of its CIP-Protected Cyber Assets and located all monitoring and alerting devices within a PSP; 3) implemented an enhanced on-boarding checklist to ensure that all systems are classified, placed in the appropriate environment, and afforded the appropriate protective measures; and 4) provided formal training for system administrators on the on-boarding checklist. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009006 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R1 because it failed to document cybersecurity test results for significant changes to Critical Cyber Assets (CCAs) and other Cyber Assets within the Electronic Security Perimeter (ESP). The SERC audit team found that SERC_URE1 failed to adequately document the results of the cybersecurity testing performed while implementing significant changes to CCAs and other Cyber Assets within the ESP. SERC_URE1's change control policies and procedures did require testing prior to implementing any additions to, modifications to, replacements of, or removal of CIP-protected Cyber Assets, including significant changes, as described in CIP-007-1 R1. SERC_URE1 provided change tickets generated pursuant to these policies, indicating that it performed testing in accordance with those policies. Finally, the workflow process required the workflow ticket owner to attest that the cybersecurity testing was performed before closing the ticket, and SERC_URE1 provided these attestations. SERC_URE1 failed to document the results of testing as required by CIP-007-1 R1.3. | CIP-007-1 | R1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to document cybersecurity test results could lead to undocumented changes being implemented on Cyber Assets within the ESP, resulting in possible unauthorized access and the introduction of additional unidentified vulnerabilities. However, SERC_URE1 provided attestations from its personnel implementing the changes indicating that testing was completed. SERC_URE1's change process requires cybersecurity testing to be performed and documented prior to implementation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) created an action plan to enhance the existing Request for Change process to correct and prevent this issue from reoccurring; 2) created instructions on what to document within the Request for Change to capture the completion of security testing; 3) captured test results (pre-scan and post-scans) in the change management tool; 4) structured the process so that the change cannot be completed until test results are documented; and 5) trained system administrators upon completion of the process enhancement. | 2012-04-03 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009007 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R4.2 because it failed to document a process for testing antivirus and malware prevention signatures. The SERC audit team discovered that SERC_URE1 did not document a process to test antivirus and malware prevention signatures prior to deploying them on Cyber Assets. SERC_URE1 presented evidence demonstrating that a third-party vendor would test malware prevention signatures in its own systems and certify that the signatures caused no issues. SERC_URE1, however, failed to document its own process for conducting testing on its own resources prior to deployment on production assets. SERC reviewed the SERC_URE1 Critical Infrastructure Cyber Security Policy and found that it did have a requirement for installation of antivirus signatures. The Cyber Security Plan states that SERC_URE1 will utilize approved anti-malware software and that the signatures will be updated from the central servers. The central servers are automatically updated with the certified virus definitions from the third-party vendor. This policy was insufficient because it did not contain procedures for SERC_URE1 to test signatures prior to installation on the production environment. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to have a process to test signatures could result in untested signatures being installed, which could introduce vulnerabilities to the network or adversely affect operational functionality. However, the vendor distributing these antivirus and malware signatures tested and certified that they were tested on all supported security products across all operating systems. SERC_URE1 maintained protective measures, such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) documented test processes that apply to CIP-protected Cyber Assets; 2) reviewed and approved a test process; 3) trained appropriate personnel on the new process; and 4) implemented and configured the new test process. | 2012-08-15 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009008 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R5.2.1 because it failed to change the default password for a generic account on a Critical Cyber Asset (CCA) prior to putting the system into service. The SERC audit team found that SERC_URE1 failed to change the password for one factory default account on a CCA prior to putting the system into service, despite the ability to do so. The generic account was associated with a File Transfer Protocol (FTP) account and provided access to the FTP directory on the server, but the account did not have the permissions to upload, delete, or execute files. SERC analyzed SERC_URE1's Cyber Vulnerability Assessment (CVA) and learned that there were two default accounts with unchanged passwords, associated with an enabled FTP service, and impacting eight Cyber Assets. SERC also reviewed the CVA and found that it included the same issue. The default accounts in question were titled “ftp” and “anonymous,” and both had unchanged default passwords. SERC_URE1 reported that the two accounts were restricted to an FTP directory and had no ability to upload, delete, or execute files. SERC_URE1 deployed these systems without changing the default password for the default accounts. SERC_URE1's energy management system (EMS) vendor would not provide guidance on whether the accounts could be disabled or the passwords modified without losing the systems’ functionality. SERC reviewed the access logs for the systems at issue and discovered no other uses of the “ftp” or “anonymous” user accounts, other than scheduled CVAs and a test during the audit. | CIP-007-1 | R5; R5.2.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because the default password on a generic account had not been changed on a CCA, making it possible that unauthorized access could be obtained by a malicious party. However, access to the FTP directory at issue enabled individuals to view files in the directory, but they could not upload or execute files, limiting the potential impact of unknown persons having access. SERC_URE1 maintained protective measures such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. Finally, FTP logs from the time period of this violation showed no use of the service other than the CVA scans and a test during the Compliance Audit. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) replaced the EMS in production at the time of the audit with new hardware and software; 2) disabled the generic accounts identified as “anonymous" and "ftp,” which were used on the old system; 3) retired all hardware and software on the previous EMS; and 4) developed an on-boarding checklist to be completed prior to placing an asset into production environment. This checklist includes numerous items to ensure strict compliance with CIP Standards. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009009 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-3a R3 because it failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability. SERC_URE1's security patch assessment process in place during the compliance period resulted in third-party patches not being assessed within the required 30 days. According to this process, SERC_URE1 held monthly patch assessment meetings, during which it assessed newly released patches and created change management tickets for patches as applicable. If SERC_URE1 failed to schedule this meeting within 30 calendar days of the last meeting, it would not meet the 30 day assessment requirement for certain patches. SERC reviewed SERC_URE1's Change Control and Configuration Management documentation and found that it detailed that the security patches were classified as significant changes and requires the patches to be tested in an environment that reflects the production environment. In addition, the documentation requires that the changes have testing performed, documented, and confirmed. SERC_URE1 first failed to assess security patches within 30 calendar days. The patch in question was released, but SERC_URE1 did not assess it within the 30 day requirement. In total, SERC_URE1 failed to assess 22 patches within 30 calendar days. Upon assessment, however, SERC_URE1 determined that only two of these patches applied to 12.3% of SERC_URE1's Cyber Assets, the remaining patches were not associated with Cyber Assets. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to assess patches within 30 calendar days creates the potential that patches for Critical Cyber Assets may not be installed in a timely manner, potentially resulting in an increased risk that those Cyber Assets could be compromised or exploited by unauthorized personnel or software. While using monthly meetings to assess security patches resulted in late assessments, SERC_URE1 was able to assess any missed patches at the next scheduled meeting. Only two of the assessed patches applied to 49 deployed SERC_URE1 Cyber Assets. SERC_URE1 maintained protective measures such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. | when SERC_URE1 failed to assess a patch 30 days following the patch release | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) created a step-by-step procedure that instructs system administrators how to: a) track security patches using Patch Tracking Logs; b) assess released patches on an ongoing basis throughout the month; c) test patches prior to installing into the production environment; and d) schedule installation of the patch; 2 collected evidence of patch assessments which was reviewed by the CIP compliance administrator monthly; 3) performed an assessment to determine which patches were missing and from what assets; and 4) determined that two patches were still missed and assessed them as applicable to a total of four assets. The patches were not installed because the cyber system containing these assets was retired. | 2013-01-10 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012823 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-002-3 R3 because it failed to include an asset in its list of Critical Cyber Assets (CCAs). SERC determined that this was a violation of CIP-005-3a R1.4 instead of CIP-002-3 R3. As a result, SERC dismissed the violation of CIP-002-3 R3 and initiated a violation of CIP-005-3a R1.4. The audit team found that during a SERC_URE1 Cyber Vulnerability Assessment (CVA), SERC_URE1 allowed a vendor to connect a laptop to the Electronic Security Perimeter (ESP) to perform the CVA without first providing evidence that it was protected in accordance with the CIP Standards. The laptop was connected to the ESP for various periods of time during a five day period. The audit team identified this issue as a violation of CIP-002-3 R3. SERC subsequently determined that the laptop was not essential to the operation of any Critical Asset, and, therefore, was not required to be identified as a CCA. SERC determined that the laptop should have been identified as a non-critical Cyber Asset within an ESP and protected pursuant to the requirements of Reliability Standard CIP-005-3. SERC learned that there were 79 CCAs accessible from the laptop during the CVA. | CIP-005-3a | R1; R1.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because without proper identification of non-critical Cyber Assets within the ESP, SERC_URE1 may have not provided the appropriate levels of protection to its ESP, potentially leading to malware and other vulnerabilities being introduced inside the ESP. However, in this case, the vendor laptop met SERC_URE1's security requirements which require implementing virus and malicious software protection. The laptop was behind a firewall limiting internet access. The vendor performed the CVA on site and under constant supervision of an authorized SERC_URE1 cyber security engineer. The vendor had a completed personnel risk assessment. The vendor had completed cybersecurity awareness training. The vendor never had unescorted physical access to SERC_URE1's Cyber Assets. The vendor’s electronic access was limited since the vendor was not given any accounts or passwords. SERC_URE1 has an intrusion detection system which alerts of any unauthorized activity. | when the laptop was first connected to the ESP | when the laptop was disconnected from the ESP for the last time | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) contacted the vendor and requested verification that all the information obtained during the CVA has been erased from the laptop in accordance with SERC_URE1's General Services Agreement; 2) procured a laptop to perform security and administration functions on CIP-protected Cyber Assets and enhanced its procedures to require that only these devices be used for the performance of vulnerability assessments; and 3) provided training to remind personnel of the proper protocol for connecting all Cyber Assets within an ESP. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000512 | Settlement Agreement | During a Spot Check the SERC Spot Check team reported that SERC_URE2 was in violation of CIP-002-1 R3. SERC_URE2 failed to identify all Cyber Assets essential to the operation of Critical Assets as Critical Cyber Assets (CCAs). After reviewing the SERC_URE2 risk-based assessment methodology (RBAM) and Critical Asset list, SERC determined that the violation was more appropriately addressed under CIP-002-1 R2 as a failure to identify all Critical Assets. During the Spot Check, SERC_URE2 did not identify the Automatic Generation Control (AGC) as a CCA. AGC is used by the energy management system (EMS) support personnel and possesses the capability of controlling the Bulk Electric System. SERC determined that SERC_URE2 failed to identify a generation facility, where the AGC system is located, as a Critical Asset. The facility was the primary generation control location for SERC_URE2. As such, the facility should have been identified as a Critical Asset. SERC_URE2 had identified a second facility, a control center, as a Critical Asset, but SERC_URE2 should have also identified the first facility where the AGC was located as a Critical Asset. Due to its failure to identify the first facility as a Critical Asset, the Cyber Assets and CCAs associated with it were not afforded all of the protections of the CIP Standards. | CIP-002-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined the violation posed a moderate risk because SERC_URE2's failure to correctly identify all Critical Assets could leave any associated CCAs without the protections specified in the CIP Standards, which could allow an attacker to disrupt SERC_URE2's control of its portion of the BPS. However, although it did not afford the Cyber Assets at the facility with all of the protections of the CIP Standards, SERC_URE2 did protect those Cyber Assets with both physical and cybersecurity measures. The facility had card readers at the entry points to the facility. All users of the Cyber Assets at the facility were required to have personnel risk assessments and cyber security training. In addition, the Cyber Assets at the facility are separated from the control center EMS by a firewall with a single port allowing access. Cyber Assets used at the facility were configured to block functions not needed for the applicable function, including Telnet network protocol, secure shell network protocol, hypertext transfer protocol, and remote desktop protocol. None of the facility's Cyber Assets could perform switching. In addition, the AGC at the facility was afforded protections such as security patch management, antivirus software, and account management controls. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | 15000 | Spot Check | To mitigate this violation, SERC_URE2: 1) updated the Critical Asset list of SERC_URE2's parent company to include the facility as a Critical Asset; 2) enclosed the AGC operations within an identified Physical Security Perimeter; and 3) merged the secure network protecting the AGC into an existing identified Electronic Security Perimeter. | 2012-07-19 | TBD | Neither Admits Nor Denies | SERC considered SERC_URE2's internal compliance program (ICP) a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006608 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-006-2 R3. SERC_URE3 was unable to provide evidence demonstrating that Cyber Assets used in the Electronic Access Control and/or Monitoring (EACM) of the Electronic Security Perimeter (ESP) resided within an identified Physical Security Perimeter (PSP). SERC_URE3 had EACM Cyber Assets that were located within a data center that met the physical design criteria required to be classified as a PSP. However, SERC_URE3 failed to identify a PSP in or around the data center in its physical security plan or any other documentation. Therefore, EACM Cyber Assets within the data center did not reside within an identified PSP. There were no Critical Cyber Assets (CCAs) within the data center. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the EACM devices were not inside of an identified PSP, they resided within a secure facility that contained access control, monitoring, alarming, and video surveillance. There were no CCAs within the data center. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) consolidated its EACM devices located within its data centers into an authentication monitoring zone (AMZ) secure rack PSP; and 2) updated its physical security plan to include the secure rack PSP. | 2011-03-09 | 2013-12-09 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006610 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R5.2.2 because it failed to document the individuals with access to shared accounts. On the same day, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R5.2.1 because it failed to change passwords for some default accounts prior to putting systems into service. SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-004-3 R4. SERC_URE3 discovered that its vendor with access to SERC_URE3 Critical Cyber Assets (CCAs) had a change in personnel with access to CCAs through a shared account. Although the CCA access list was updated within seven days, SERC_URE3 failed to change the password on the shared account within seven days as required by SERC_URE3's procedures. SERC determined that this violation was actually a violation of CIP-007 R5.2.3 and not a violation of CIP-004 R4 as originally indicated in SERC_URE3's Self-Certification. SERC determined that this violation involved the same Standard and Requirement as the two SERC audit team reports and decided to treat the Self-Certification as an expansion of scope. In total, SERC determined that SERC_URE3 had three separate incidents involving CIP-007 R5.2. In the first incident, which involved CIP-007-1 R5.2.2, SERC_URE3 maintained a policy for managing the use of shared accounts that limited the access to individuals with authorized access. SERC_URE3 documented the departments that had access to the shared operator accounts, but failed to document the individuals with access to a single shared operator account. This single shared account was used on 32.1% CCA servers and several non-critical Cyber Asset servers within the Electronic Security Perimeter (ESP). In the second incident, which involved CIP-007-1 R5.2.1, SERC_URE3's Cyber Vulnerability Assessment (CVA) showed that three Cyber Assets (two CCA database servers and one non-critical Cyber Asset server) within the ESP had default accounts and that SERC_URE3 had not renamed, disabled, or changed the passwords on those default accounts prior to putting the Cyber Assets into service. These Cyber Assets were put into service prior to the enforcement date of the CIP Standards. This violation affected two default database accounts on the three servers which had no password set and one anonymous file transfer protocol (FTP) account enabled for the FTP service on all three servers. After a review, SERC_URE3 determined that the anonymous FTP account could be accessed and used by 53.7% of the accounts on the three servers. SERC_URE3 had two approved Technical Feasibility Exceptions (TFEs) pursuant to CIP-007 R5.3.3 for the three servers. The TFEs stated that changing the account passwords on these three servers on an annual basis was not possible because the changes had not been tested and could adversely impact reliable operations. SERC_URE3 was concerned that changing the account passwords could disrupt the operation of the emergency management system (EMS) because the FTP accounts were used by several applications and scripts. However, TFEs are not available for CIP-007 R5.2.1, and SERC_URE3 was required to change the passwords for default accounts prior to putting them into service. In the third incident, which involved CIP-007-1 R5.2.3, SERC_URE3 permitted its EMS vendor authorized cyber access to CCAs within one of its ESPs through the use of a shared account. SERC_URE3 coordinated with the vendor to maintain a list of the authorized vendor personnel who had approved access and had completed the cyber security training, personnel risk assessment (PRA), and received security awareness reinforcement. SERC_URE3 granted electronic access through the ESP to the vendor personnel via a two-factor authentication process. The first factor was a user name and personal identification number that was known by the vendor. The second factor was a passcode from a regularly changing key fob token which was in the possession of SERC_URE3 personnel at all times. Thus, vendor personnel had to obtain the second factor from SERC_URE3 personnel in order to gain access to CCAs. Once inside the ESP, vendor personnel utilized the shared account to electronically access CCAs and non-critical Cyber Assets within the SERC_URE3 ESPs. The vendor had a change in personnel with a need for access to CCAs and notified SERC_URE3. Although SERC_URE3 removed the vendor employee from its CCA access list within seven days, SERC_URE3 failed to change the password known to the vendor on the shared account within seven days of the change as required by its shared account procedures. SERC_URE3 changed the shared account password 22 days after it should have changed the password. The vendor employee would not have been able to access the CCAs or non-critical Cyber Assets within the ESPs because SERC_URE3 personnel would not have provided the passcode from the key fob token that was required to gain access through the ESP after the vendor employee was removed from the CCA access list. | CIP-007-1 | R5; R5.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE3's failure to implement its policy to minimize and manage the scope and acceptable use of shared and default accounts could have allowed malicious individuals to exploit the shared or default accounts in order to disrupt SERC_URE3 operations and the reliability of the BPS. However, the first incident involved one shared accounts. This account was present on 32.1% of CCAs and several non-critical servers within its ESPs. Access was limited to operators with valid PRAs and annual cyber security training. For the second incident, SERC_URE3 did not allow remote login to the affected Cyber Assets and had physical security controls in place including man-traps, key cards, active monitoring of access that would prevent local logins to those Cyber Assets, and restricted access to these servers to administrators with PRAs and cybersecurity training. Additionally, ESP controls included dual-factor authentication, intrusion detection systems, third-party monitoring, and security event alerting. The third incident involved a single EMS vendor whose personnel were in good standing with SERC_URE3. Authorized remote EMS vendor access was made through the use of a two-factor authentication process. The EMS vendor was required to contact SERC_URE3 in order to obtain the key fob token passcode. All EMS vendor personnel with access to the shared account had valid PRAs and annual cybersecurity training. | when the Standard became mandatory and enforceable on SERC_URE3 | present | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) employed an additional step in the vendor shared account access process whereby, on session completion, SERC_URE3 changes the password and locks the shared account until the vendor's authorized personnel again need access to the ESP(s) for support purposes; 2) supplemented its processes for changing shared account passwords by ensuring the vendor's program manager sends update lists to the applicable SERC_URE3 email distribution list so SERC_URE3 personnel receive updates simultaneously and vendor changes are known by relevant SERC_URE3 personnel; and 3) finalized its updated process to address both enabling and disabling access. To mitigate this violation, SERC_URE3 will: 1) update the list of shared accounts and the specific individuals with access to those share accounts, instead of the departments with access; and 2) terminate the TFEs by modifying or upgrading its current database management software, which removes the hardcoded passwords. | 12/31/2013 (approved completion date) | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006612 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R3 because SERC_URE3 did not document compensating measures applied to mitigate risk exposure in cases where applicable security patches were not installed. SERC_URE3 has a documented security patch management program for tracking, evaluating, testing, and installing cyber security patches for Cyber Assets within Electronic Security Perimeters (ESPs). SERC_URE3 system administrators are responsible for the control, coordination, assessment, and implementation of the security patch management program. SERC_URE3 received security patch advisories from two sources in an attempt to keep abreast of any security vulnerabilities and associated patches. SERC_URE3's system administrators monitor advisories received regarding software security patches and determine the applicability of the security patches and track their evaluation, testing, and installation. The SERC audit team reviewed SERC_URE3's Cyber Vulnerability Assessment (CVA) results and identified several operating system security patches that were not installed. Some of these patches were identified as critical security patches and dated before the time when CIP-007-1 became mandatory and enforceable. SERC_URE3 had not submitted any Technical Feasibility Exceptions (TFEs) that documented compensating measures for the vulnerabilities associated with the security patches that it had not installed. The security patches were applicable to 84.9% of the total Critical Cyber Assets (CCAs), and several non-critical Cyber Assets. SERC_URE3 restricted the software installed on all Cyber Assets inside of the ESP so that operating system and primary function software were the only software installed on each device, thereby limiting the possible vulnerabilities and security patches requiring assessment and installation. SERC_URE3 did not maintain an assessment log that tracked each security patch assessment but instead used an assessment ticket for each security patch, which made it difficult to verify how many patch assessments were missed. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to install a significant number of missing security patches on CCAs and non-critical Cyber Assets and to document compensating measures resulted in a increased risk that those Cyber Assets could be compromised or exploited by unauthorized personnel or software. However, SERC_URE3 limited the software that were installed on the devices to operating systems and primary function software. SERC_URE3 restricted electronic and physical access to the affected Cyber Assets to only approved screened and trained personnel, and the affected Cyber Assets were protected within an ESP and Physical Security Perimeter. | when the Standard became mandatory and enforceable on SERC_URE3 | present | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3 will: 1) test and determine whether it will apply the applicable security patches for the first operating system. If SERC_URE3 decides not to apply any of these applicable operating system patches, it will utilize the TFE process to document compensating measures that have been applied to mitigate risk exposure; 2) implement a newer version of the second operating system as part of an upgrade to the energy management system (EMS). As a result of this upgrade, the missing operating system patches will no longer be necessary. Any applicable operating system patches after the upgrade will be installed on the servers. If SERC_URE3 determines that an applicable patch cannot be implemented, it will utilize the TFE process to document the compensating measures that have been applied to mitigate risk exposure; and 3) revise its security patch management process to include a step to file a TFE to document the compensating measures that are applied whenever an applicable security patch is not installed. | 12/31/2013 (approved completion date) | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006613 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to afford its Physical Access Control System (PACS) devices with the protective measures specified in CIP-005 R2 and R3, and CIP-007 R1, R4.2, and R5.3.3. Specifically, the audit team found that SERC_URE3 failed to present evidence showing that there was electronic access control protection to an Electronic Security Perimeter (ESP) from the corporate network (CIP-005 R2 and R3); cybersecurity controls testing after significant changes (CIP-007 R1); testing of antivirus signatures prior to deployment (CIP-007 R4.2); and shared passwords were being changed at least annually (CIP-007 R5.3.3). The SERC audit team identified PACS devices that were not afforded the protective measures listed in CIP-006-1 R1.8. SERC_URE3 subsequently completed an annual internal assessment of compliance to verify that the scope of the violation was limited to the four PACS devices. SERC later determined that the violation also included additional PACS devices, thereby impacting all the PACS devices that SERC_URE3 had. SERC_URE3 provided no evidence to demonstrate that there was access control protection from an untrusted network to the PACS devices. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-005 R2 and R3. SERC_URE3's maintenance and testing procedures did not address the testing of PACS devices after significant changes to ensure that no degradation of cyber security controls occurred. SERC_URE3 only tested significant changes to the PACS devices at a functional level to ensure that the changes did not stop the PACS devices from working. SERC_URE3 did not test a total of 49 significant changes to 77.8% of its PACS devices made during a five month period to ensure that those changes did not adversely affect the existing cyber security controls. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R1. SERC_URE3's corporate security patch management policy and malicious software tools procedure called for the application of virus definition files immediately upon receipt, but neither addressed the testing of those signatures. SERC_URE3 provided no evidence that it tested the antivirus or malware prevention signatures. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R4.2. SERC_URE3's account management documentation addressed the annual changing of passwords as well as logging and monitoring. SERC_URE3's corporate password standards policy required annual password changes on all company Cyber Assets. Lastly, SERC_URE3's default active directory domain account policies for all Windows devices had controls in place that required the changing of account passwords associated with the PACS devices in question every 60 days. SERC_URE3 did not provide evidence of password controls in place. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R5.3.3. SERC_URE3 completed a system upgrade that addressed the cyber security controls testing of the PACS devices in question. This system upgrade ended SERC_URE3's failure to afford its PACS devices the protective measures specified in CIP-05 R2 and R3 and CIP-007 R1, R4.2, and R5.3.3. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to protect its PACS devices adequately could lead to the disabling or degradation of physical security protections, which could allow unauthorized physical access to Critical Cyber Assets (CCAs) inside Physical Security Perimeters (PSPs). However, 44.4% of the PACS devices in question were located inside of PSPs, and all personnel with physical access to the PACS devices had valid personnel risk assessments and current cyber security training. Live video feed would allow identification of individuals physically accessing the PACS devices. In addition, access controls and access rules limited electronic access to the PACS devices and denied access by default. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring to ensure that all network activity was monitored for security risks and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented its PACS devices into an authentication monitoring zone (AMZ) environment within a secure rack PSP; 2) evaluated, identified, and selected automated security control tools that can be employed to conduct security control testing to verify whether any modifications to the existing cyber security controls are made following significant changes to PACS devices; 3) implemented and developed testing procedures for testing against existing security controls on PACS devices after the selection of automated security control tools; and 4) updated its physical security plan to document the addition of the secure rack PSP. | 2012-06-28 | 2013-12-10 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006614 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R2.2. SERC_URE3 failed to enable only the ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP). SERC reviewed the firewall rules in place at the time of the audit and learned that SERC_URE3 had two Electronic Access Control and Monitoring (EACM) firewalls in place with eight firewall rules that allowed any port or service from the main energy management system (EMS) ESP to communicate with the backup EMS ESP for nine server hosts. SERC_URE3 claimed that these rules allowed the two EMS systems to communicate and replicate each other, providing complete redundancy and fail over capability. SERC_URE3 did not restrict the ports and services at the time because it was concerned that doing so could cause negative operational impacts. As a result, SERC_URE3 was unable to provide documented justification for the firewall rules at the time of the Compliance Audit. Outside of the eight firewall rules in question, SERC_URE3 used an access control model that denied access by default. SERC_URE3 was also unable to provide documentation, individually or by specified grouping, of the configuration of the enabled ports and services. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to restrict ports and services on access control devices could allow the exploitation of vulnerabilities and result in unauthorized access to Critical Cyber Assets (CCAs) inside of the ESP. However, outside of the eight firewall rules in question, SERC_URE3 used an access control model that denied access by default and did not allow traffic from external networks, including the SERC_URE3 corporate network. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring, to ensure that all network activity was monitored for security risk and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented additional firewall rules to allow only acceptable network traffic that it required for normal business activities; 2) evaluated current traffic through vital firewall interfaces to ensure that the allowed traffic is that which is only required and justified based on business needs; 3) reconfigured access control lists to restrict inbound and outbound traffic to only the justified business traffic; and 4) updated firewall policies with justification of enabled access control lists. | 2011-09-29 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006615 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R2, specifically R2.4 and R2.5. SERC_URE3 did not implement organizational and technical processes and/or procedural mechanisms for control of electronic access at electronic access points to the Electronic Security Perimeter (ESP) for some user groups. SERC_URE3 allows personnel from a customer to have read-only access to a man-machine interface (MMI) which was classified as a Critical Cyber Asset (CCA). The connection to the ESP is established through a dedicated communication line owned by SERC_URE3. Access to the ESP is granted using a shared account via a secure virtual private network (VPN) connection. Eight individuals at the customer used the shared account. SERC_URE3 logged access to the MMI at the firewall, but SERC_URE3 could not ensure the authenticity of each individual using that shared account. SERC_URE3 also failed to have organizational documentation that described and identified the process for the customer’s access requests and authorization, authentication methods, and the review process for authorization rights associated with the allowed customer access. | CIP-005-1 | R2; R2.4, R2.5 | Medium | Severe | This violation posed a minimal and did not pose a serious or substantial risk to the reliability of the bulk power system. The customer allowed only eight individuals to use the shared account and managed a list of individuals that used the shared account. The shared account had read-only electronic access and the customer did not have physical access to CCAs. ESP firewalls were logging access. SERC_URE3 subsequently reviewed the logs and found no Cyber Security Incidents or attempts to breach security during the violation. The connection was a dedicated connection owned by SERC_URE3 and only provided access to one ESP access point. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) reviewed the firewall rules and restricted the allowed network addresses from the large customer's site; 2) implemented an authentication scheme that enforces individual, two-factor authentication upon login; 3) implemented a corporate appropriate use banner that will be displayed upon login; 4) reviewed the ports and services on the firewall and disabled any ports and services that were not required for normal or emergency operations; 5) documented each port and service that is necessary to allow the large customer to view its required real-time distribution system information; 6) created individual user accounts for the large customer's personnel to be used in conjunction with two-factor authentication to allow authorized users cyber access through the firewall. In addition, SERC_URE3 employed a time-out feature that suspends user access after a fixed number of hours; and 7) worked with the large customer to complete personnel risk assessments for its employees with cyber access through the SERC_URE3 firewall. | 2012-09-21 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006616 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R1.5. SERC_URE3 did not afford the protective measures specified in CIP-004 R3, CIP-005 R2 and R3, CIP-006 R3, and CIP-007 R1 to its Electronic Access Control and Monitoring (EACM) devices. SERC later determined that SERC_URE3 had also failed to address the testing of virus definition files on EACM devices (CIP-007 R4.2). SERC determined that 52.2% of EACM devices currently in place were in production prior to when the Standard became mandatory and enforceable for SERC_URE3. SERC_URE3 did not provide evidence to show that all personnel with physical access to the data center containing its EACM devices, which was not a defined Physical Security Perimeter (PSP) at the time, had valid personnel risk assessments (PRAs) completed successfully (CIP-004 R3); that there was access control protection from an untrusted network to EACMs (CIP-005 R2); that electronic security monitoring was being conducted (CIP-005 R3); and did not identify the PSP in which the EACM devices resided (CIP-006-2 R3, addressed in NERC Violation ID SERC2011006608). SERC_URE3 addressed the failure to provide its EACM devices with the protective measures specified in CIP-004 R3, CIP-005 R2 and R3, and CIP-006-2 R3 when it installed an authentication monitoring zone (AMZ) within a secure rack PSP that contained all of SERC_URE3's EACM devices. In addition, SERC_URE3 only tested significant changes to the EACM devices at a functional level to ensure that the changes did not stop the EACM devices from working. SERC_URE3 did not test a total of 21 significant changes to 13.0% of its EACM devices made over a five month period to ensure that those changes did not adversely affect the existing cyber security controls. SERC determined that SERC_URE3 was in violation of CIP-005-1 R1.5 because it failed to provide its EACM devices with the protective measures specified in CIP-007-1 R1. SERC_URE3's corporate patch management policy and malicious software tools procedure called for the application of virus definition files immediately upon receipt, but neither addressed the testing of those signatures. SERC_URE3 provided no evidence that it tested antivirus or malware prevention signatures. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its EACM devices with the protective measures specified in CIP-007-1 R4.2. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to protect its EACM devices adequately could lead to the disabling or degradation of electronic security protections, which could allow unauthorized electronic access to Critical Cyber Assets (CCAs) inside Electronic Security Perimeters (ESPs). However, of the employees with access to the EACM devices, 36.8% had valid PRAs and training, and the remaining employees had been subject to corporate pre-employment background checks. SERC_URE3 segmented the associated network and added additional controls to protect the EACM devices therein by isolating them physically and logically from the rest of the corporate network. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring to ensure that all network activity was monitored for security risks and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented an authentication monitoring zone (AMZ) within a secure rack PSP; 2) evaluated, identified, and selected automated security control tools that can be employed to conduct security control testing to verify whether any modifications to the existing cyber security controls are made following significant changes to EACM devices; 3) implemented and developed testing procedures for testing against existing security controls on EACM devices after the selection of automated security control tools; and 4) updated its physical security plan to document the addition of the secure rack PSP. | 2012-06-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006617 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R1.1. SERC_URE3 did not identify an externally connected communication end point terminating at a Critical Cyber Asset (CCA) as an access point to the Electronic Security Perimeter (ESP). After the Compliance Audit, SERC_URE3 conducted an internal review of all externally connected communication end points and discovered an identical device in addition to the device identified by the SERC audit. The identical device was located outside of the backup energy management system (EMS) ESP and terminated at a CCA inside of the ESP. SERC determined that the violation involved two intrusion detection system (IDS) devices, both of which were outside of an ESP. Each IDS device was connected to a switched port analyzer (SPAN) (mirroring) port on a corresponding switch inside an ESP. The IDS devices were also connected to a management interface that was located in the corporate network. The SPAN ports on both switches were configured to monitoring mode, which allowed information to travel out of the ESP to the IDS devices, but did not allow information to travel into the ESP via the IDS devices. SERC_URE3 did not identify these IDS devices as access points to the ESP, did not protect them as such, and therefore did not include these devices in the CIP-005 R4 Cyber Vulnerability Assessment of access points. SERC_URE3 moved the IDS management interface into a protected ESP. | CIP-005-1 | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The IDS devices used a SPAN port (mirrored) configured to prevent any ingress traffic to the EMS network. Ten individuals had physical or cyber access to the IDS management interface, which could configure the IDS devices. All 10 individuals had valid personnel risk assessments and were current in their annual cyber security training. The management console located outside of the ESP had physical and cyber security controls and protections in place. Security controls were in place on the corporate network including IDS, alerting, monitoring, video surveillance, third-party ESP monitoring, and strong access control restrictions on corporate firewalls. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) removed the IDS management interface from the corporate network and placed it behind the primary and backup EMS network firewalls; and 2) moved the management interfaces for the IDS that monitors the primary EMS network and the backup EMS network behind ESP firewalls. These IDS devices can now only be accessed from within an ESP though the specific ESP's firewall. | 2011-05-31 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2012010737 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE3 did not afford one Electronic Access Control and Monitoring (EACM) device the protective measures specified in CIP-007 R8. Specifically, SERC_URE3 excluded one EACM device from its annual Cyber Vulnerability Assessment (CVA). SERC_URE3 had planned to replace one old Cyber Asset used as an EACM device before the end of the year 2011. SERC_URE3 excluded the old EACM device from its annual CVA and instead included the new EACM device, which was scheduled to replace the old EACM device, in the CVA. SERC reviewed the SERC_URE3 CVA and determined that the CVA covered the new EACM device that was replacing the old EACM device. SERC independently confirmed that the old EACM device was not included in the CVA. Both the old and new EACM devices were logging and monitoring during the period that they were running in parallel. SERC_URE3 put the new EACM device into service and approximately three weeks later SERC_URE3 decommissioned the old EACM device. SERC_URE3 installed the new EACM device in the summer, after which it was running in parallel with the old EACM device. SERC_URE3 completed its CVA in the winter. SERC_URE3 completed its CVA for the following year in the winter of that year and it assessed all applicable Cyber Assets during that CVA. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The old EACM device that was not assessed in the CVA was running in parallel with the new EACM device that was included in the CVA. SERC_URE3 removed the old EACM device from operation. The old and new EACM devices were installed in a demilitarized zone (DMZ), a secure network that contained all the EACM devices, and were running in parallel at the time of the CVA. The DMZ network was also segregated from SERC_URE3's corporate network. The secure DMZ network has electronic access controls, electronic logging and monitoring, intrusion detection systems, and anti-malware. | the first day after SERC_URE3 should have conducted the CVA including the old EACM device | when SERC_URE3 removed the old EACM device from the secure DMZ network | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) supplemented internal CVA procedures with more detailed specifics that require, at least annually, that the EACMs and PACs inventory and classification is confirmed; and 2) ensured that, in addition to Cyber Assets within Electronic Security Perimeters (ESPs) and access points to the ESPs, all EACM and PACS devices are included in the internal CVA procedures and are subject to and included in an annual CVA. | 2012-06-30 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011815 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-006-3c R2.2. SERC_URE3 failed to afford all of its Physical Access Control Systems (PACS) devices with the protective measures specified in CIP-007. SERC_URE3 maintains an authentication monitoring zone (AMZ) at its data center that consists of Electronic Access Control and Monitoring (EACM) devices and PACS devices all secured inside of a locked rack. SERC_URE3 identified the secure rack as a Physical Security Perimeter and protects it as such. The AMZ conducts all the logging and monitoring of all PACS devices and Cyber Assets and uses virtual machines to accomplish the various tasks associated with SERC_URE3's EACM and PACS devices. As part of an internal review, SERC_URE3 determined that it did not apply the CIP-007 requirements to host servers that ran several virtual machines, which in turn were running the virtual PACS database. SERC_URE3 failed to ensure protective measures specified in CIP-007, such as antivirus, monitoring and logging, Cyber Vulnerability Assessments, and testing, were applied to the host servers on which the virtual machines were running. The virtual machines that were running on the host servers were afforded the protective measures specified in CIP-007. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The virtual machines housed on the host servers were afforded the protections of CIP-007. The host servers resided within a segmented AMZ network that has access control and monitoring and required two-factor authentication to access. Access to the host servers was limited to a total of 14 SERC_URE3 personnel, all of whom had active personnel risk assessments and current cyber security training. | when SERC_URE3 moved to virtual PACS devices running on the host servers | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) implemented security control testing; 2) identified and evaluated ports and services associated with the PACS virtual machine host servers; 3) evaluated and assessed all security patches associated with the PACS virtual machine host servers; 4) added the PACS virtual machine host servers to a technical feasibility exception; 5) applied all password requirements to PACS virtual machine host servers; and 6) implemented local logging on the PACS virtual machine host servers. | 2013-02-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011825 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE3 failed to afford its Electronic Access Control and Monitoring (EACM) devices with the protective measures specified in CIP-007. SERC_URE3 maintains an authentication monitoring zone (AMZ) at its data center that consists of EACM devices and Physical Access Control System (PACS) devices all secured inside of a locked rack. SERC_URE3 identified the secure rack as a Physical Security Perimeter and protects it as such. The AMZ conducts all the logging and monitoring of all EACM devices and Cyber Assets and uses virtual machines to accomplish the various tasks associated with SERC_URE3's EACM and PACS devices. As part of an internal review, SERC_URE3 determined that it did not apply the CIP-007 requirements to the host servers that ran virtual machines, which in turn were running virtual EACM devices. SERC_URE3 failed to ensure protective measures specified in CIP-007, such as antivirus, monitoring and logging, Cyber Vulnerability Assessments, and testing, were applied to the host servers on which the virtual machines were running. The virtual machines that were running on the host servers were afforded the protective measures specified in CIP-007. | CIP-005-3 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The virtual machines housed on the host servers were afforded the protections of CIP-007. The host servers resided within a segmented AMZ network that has access control and monitoring and required two-factor authentication to access. Access to the host servers was limited to a total of 14 SERC_URE3 personnel, all of whom had active personnel risk assessments and current cyber security training. | when SERC_URE3 moved to virtual EACM devices running on the host server | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) implemented security control testing; 2) identified and evaluated ports and services associated with the EACM virtual machine host servers; 3) evaluated and assessed all security patches associated with the EACM virtual machine host servers; 4) added the EACM virtual machine host servers to a technical feasibility exception; 5) applied all password requirements to EACM virtual machine host servers; and 6) implemented local logging on the EACM virtual machine host servers. | 2013-02-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012176 | Settlement Agreement | During a Compliance Audit of SPPRE_URE1, SPP RE discovered a possible violation of CIP-005-1 R2.4. SPPRE_URE1, did not implement strong procedural or technical controls to authenticate interactive access into the Electronic Security Perimeter (ESP) at two points that serve as access points to the ESP. Users initiating external access to the ESP must authenticate using a single-factor authentication method. Once authenticated, users have unrestricted access to all Cyber Assets within the ESP. Use of only a username and password does not constitute strong authentication. | CIP-005-1 | R2, R2.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While only utilizing single-factor authentication, the affected devices reside on a network that is protected by a corporate firewall that limits access to the devices. Additionally, the domain and user accounts used to authenticate to the affected devices are different from the corporate domain user accounts initially authenticating access to SPPRE_URE1’s corporate network. Further, the violation did not include instances when SPPRE_URE1 staff connected to the ESP remotely from outside the office. In such instances, VPN was utilized, therefore providing strong authentication. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPPRE_URE1: modified its method of authenticating users onto the ESP so that all users are strongly authenticated before gaining access to the ESP. | 6/14/13 | 7/11/2013 | Neither Admits nor Denies | SPP reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012178 | Settlement Agreement | During a Compliance Audit of SPPRE_URE1 SPP RE discovered that SPPRE_URE1 was in violation of CIP-006-1 R1. SPPRE_URE1 did not create and maintain a written physical security plan addressing all the requirements of R1. SPP RE_URE’s physical security plan primarily restated the language of the requirements rather than outlining specifically how SPPRE_URE1 implemented the requirements. SPPRE_URE1 lacked documentation on the processes, tools, and procedures it used to monitor physical access to its Physical Security Perimeters (PSP) as required by R1.3 and the appropriate use of physical access controls as required by R1.4. Further, SPPRE_URE1 was in violation of R1.5 because its process for issuing temporary physical access badges did not require confirmation that the requester still had authorized, unescorted access to the PSP. SPPRE_URE1 was unable to produce documentation that it reviewed its physical access controls in 2011 as required by R1.9. Additionally, URE failed to identify four devices as Cyber Assets used in the access control and monitoring of the PSP, and as a result did not apply the protective measures enumerated in R1.8 to the devices. SPP RE also found that SPPRE_URE1 failed to include an application and its underlying Database used in provisioning access to the PSP in its 2011 annual Cyber Vulnerability Assessment (CVA) per R1.8. Additionally, in 2012, although SPPRE_URE1 included the application in the CVA, the CVA did not include the Database as required by R1.8. | CIP-006-1 | R1, R1.3; R1.4; R1.5; R1.8; R1.9 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While SPPRE_URE1 did not fully document its physical security plan, SPPRE_URE1 had processes in place to monitor physical access to the PSP and for the physical protection of Critical Cyber Assets. Regarding R1.8, the relevant devices reside within an access-controlled facility. The devices require a username and password that is different from the domain user account and the employee population at the facility containing the devices is small and well-known, thereby reducing the risk that unauthorized access on the devices would go unnoticed. | when the Standard became mandatory and enforceable on SPPRE_URE1 | TBD | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) revised its physical security plan so that it now documents how SPPRE_URE1 physically secures its Cyber Assets and meets the requirements of CIP-006; 2) split the PACS into two separate environments; one for the corporate non-CIP related doors and the other for CIP related doors managed by the contractor; 3) procured, received, and built-up necessary hardware and licensing for software for the new PACS environments; and 4) had its contractors coordinate and implement the split of the PACS environment with the SPPRE_URE1 IT staff. | 11/22/13 (Proposed Completion date) | TBD | Neither admits nor Denies | SPP reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012181 | Settlement Agreement | During a Compliance Audit of SPPRE_URE1, SPP RE discovered that SPPRE_URE1 was in violation of CIP-007-3a R2. SPPRE_URE1 had partially documented the baseline of required ports and services. The port utilized by a device was not documented. Also, all ports and their associated services listening on an IP address were excluded from the list. As a result the documented baselines did not provide information regarding whether these ports and services were required for normal and emergency operations. SPPRE_URE1 documented only services with externally reachable listening ports and thus did not document all required services. | CIP-007-3a | R2, R2.1, R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to fully document port and service configurations can present a risk of incorrect configurations and port vulnerability, port failure, or port inaccessibility in certain situations. However, SPPRE_URE1 documented a ports and services baseline and managed all listening ports and associated services that are externally reachable. The Cyber Assets within the Electronic Security Perimeter (ESP) are behind multiple firewalls, which limited the chance that they could be compromised because of a failure to document all ports and services. | when SPPRE_URE1 deployed the assets at issue in this violation | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) revised its ports and services management procedure to include steps to ensure that all ports and services are documented and that unnecessary ports and services are disabled as technically feasible; 2) performed an annual cyber vulnerability assessment on the Cyber Assets located within the ESPs; and. 3) added the missing ports and services to its baseline documentation. | 2013-06-14 | 2013-09-06 | Neither Admits nor Denies | SPP reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012182 | Settlement Agreement | During a Compliance Audit of SPPRE_URE1, SPP RE discovered that SPPRE_URE1 was in violation of CIP-007-3a R3.2. Although SPPRE_URE1 had documented and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security patches, SPPRE_URE1 did not apply security patches to all its devices within a reasonable timeframe after the evaluation process determined that they were applicable. Overall, 23 patches were not installed to the devices until 11 to 24 months after being deemed applicable. Additionally, no compensating measures were documented for any of these patches until the patches were installed. | CIP-007-3a | R3, R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to test and implement all available security patches or updates for Cyber Assets within the Electronic Security Perimeter (ESP) presented a risk that out-of-date security patches could allow unauthorized electronic access and potential compromise of Critical Cyber Assets that support BPS reliability. The risk posed by SPPRE_URE1’s noncompliance was lessened because the affected Cyber Assets and Critical Cyber Assets were within SPPRE_URE1’s ESP and were afforded protective measures, including firewall protection, malware prevention pursuant to CIP-007-3a R4, account management controls pursuant to CIP-007-3a R5, and security status monitoring pursuant to CIP-007-3a R6. | when SPPRE_URE1 deployed the assets at issue in this violation | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPPRE_URE1 revised its patch management procedure to require that (1) applicable security patches be installed at least on a quarterly basis and (2) development, implementation, and documentation of compensating measures if an applicable security patch cannot be installed within the required timeframe. All patches identified in this violation have been installed. | 2013-06-14 | 2013-07-29 | Neither Admits nor Denies | SPP reviewed SPPRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201100642 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R1. SPP RE_URE2 did not ensure that all significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. Additionally, not all Cyber Assets within the ESP were tested in a manner that reflects the production environment (R1.2). SPP RE_URE2’s cyber security testing procedures did not apply to all Cyber Assets within the ESP, as required by R1 and R.1. The testing procedures required only functional testing after significant changes were implemented on the associated devices, instead of testing to ensure the significant changes did not adversely affect existing cyber security controls, as required by R1 and R1.1. Although not included in the testing procedures, after significant changes were implemented to SPP RE_URE2’s devices, SPP RE_URE2 did test in a manner that reflected the production environment to ensure that the significant changes did not adversely affect existing cyber security controls. However, testing in a production environment was not applied to all Cyber Assets located within the ESP per R1.2. | CIP-007-1 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to test significant changes to existing Cyber Assets located within SPP RE_URE2’s ESP presented a risk that the significant changes would introduce exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2 did, however, conduct compliant cybersecurity testing for most of its Cyber Assets located within the ESP, including the devices involved in the violation. Additionally, some changes related to security control systems were protected by antivirus software. Further, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cyber security incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report | To mitigate this violation, SPP RE_URE2: 1) revised its cybersecurity testing procedures to include all the requirements of R1; 2) documented that testing is performed in a manner that reflects the full production environment to include all Cyber Assets; and 3) trained all affected personnel on the revised procedures. | 7/19/2013 | 7/31/2013 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201100643 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R3 because its security patch management program was not compliant with R3, R3.1, and R3.2. Specifically, SPP RE_URE2’s program did not apply to all Cyber Assets within the Electronic Security Perimeter (ESP). Additionally, SPP RE_URE2’s program relied on SPP RE_URE2’s vendor to track, evaluate, test, and assess cybersecurity software patches and, only some patches were included in the program. As a result, other security patches were not being tracked, evaluated, tested, or assessed. Further, because SPP RE_URE2’s program did not include procedures to address its reliance upon its vendor, SPP RE_URE2 was unable to verify that the vendor actually tracked, evaluated, tested, and assessed all applicable security patches. Moreover, SPP RE_URE2’s security patch management program did not include a process for documenting compensating measures for mitigating risk exposure or accepting risk when security patches or upgrades were not implemented. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to maintain a compliant security patch management program presented a risk of introducing exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. While SPP RE_URE2 was unable to verify that its vender tracked, evaluated, tested, and assessed patches for applicability within thirty (30) calendar days from the date of availability for all devices, SPP RE_URE2 did install available patches and conducted compliant CIP-007 R1 cybersecurity testing. For instance, after implementation of security patches, SPP RE_URE2 tested the devices in a manner that reflected the production environment to ensure that the security patches did not adversely affect existing cybersecurity controls. Additionally, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report | To mitigate this violation, SPP RE_URE2: 1) purchased and installed a security patch management and network security scanner to assist in the: (i) identification of all security software that needs to be tracked, evaluated, tested, and assessed; (ii) assessments of applicable security patches and upgrades; (iii) implementation of automated downloading and installation of applicable patches; and 2) revised its security patch management program to: (i) include all Cyber Assets within the ESP; (ii) reflect the patch management and network security scanner and automated functions for security patches; (iii) include manual procedures for tracking, evaluating, testing, and assessing patches; (iv) ensure vendor confirmation and testing (where applicable) of all available security patches; and (v) include a process for documenting compensating measures when security patches are not implemented. | 2013-07-01 | 2013-08-22 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008244 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-003-1 R5. SPP RE_URE2 did not annually (i) review access privileges to protected Critical Cyber Asset (CCA) information to confirm that the privileges are correct and that they correspond with current needs and current personnel roles and responsibilities as required by R5.2, and (ii) assess and document its processes for controlling access privileges to protected information as required by R5.3. During an ensuing Compliance Audit SPP RE determined that SPP RE_URE2 was also in violation of R5 because it did not document or implement a program for managing access to protected CCA information. | CIP-003-1 | R5; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because failure to document and annually assess its information protection program could have exposed sensitive information related to CCAs. Though SPP RE_URE2 did not document a program for managing access to CCA information, access to the information was controlled. For instance, the information was located and protected within SPP RE_URE2’s Physical Security Perimeter (PSP). As a result, physical and electronic access to the protected information was restricted to those individuals with authorized access. Additionally, SPP RE_URE2 maintained lists of personnel with access to CCA information and personnel with the authority to grant access to such information. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2 developed, documented and implemented procedures for managing access to protected CCA information, which includes a provision for annual review of access privileges, as well as an annual review of the process itself. | 2013-07-01 | 2013-07-10 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008247 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R1 because it had not properly documented its Electronic Security Perimeter (ESP) in accordance with R1.1 and R1.4 through R1.6. SPP RE_URE2 did not: (i) identify and document two of its access points; (ii) identify and document all non-critical Cyber Assets within the ESP; and (iii) address protective measures for systems in its CIP-005-1 policy. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 also failed to maintain a complete list of devices, which led to two devices not being afforded the protective measures of R1.5. | CIP-005-1 | R1; R1.1; R1.4; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because the violation presented a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within SPP RE_URE2’s ESP without its knowledge. Such access and vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. Regarding R1.1, one of the access points was a serial connection and therefore less prone to compromise, and the other was configured to allow only outgoing communication. Regarding R1.5, while the two devices were within a secure area, they were not within a defined Physical Security Perimeter. The risk to the BPS was reduced because SPP RE_URE2 was utilizing an intrusion detection system to analyze network traffic for known and suspect malicious activity. Regarding R1.4 and R1.6, access to CCAs is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) developed and implemented new procedures for identifying, documenting, and providing access control measures for all access points; 2) re-inventoried its networks and revised its ESP-related lists to ensure they are complete and in accordance with CIP-005; and 3) trained all affected personnel on the new procedures. | 2013-07-25 | 2013-08-28 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008248 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R2. SPP RE_URE2 did not document all of the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter (ESP) as required by R2.2, R2.5.3, and R2.6. Regarding R2.2, SPP RE_URE2 did not have an electronic access control process for documenting and approving open ports and services for each device used for operations and monitoring of Cyber Assets located within the ESP. Therefore, SPP RE_URE2 was unable to ensure that only ports and services required for operations and monitoring Cyber Assets within the ESP were enabled. Regarding R2.5.3, SPP RE_URE2 did not have a review process for authorization rights in accordance with CIP-004 R4. As a result, SPP RE_URE2 was unable to locate any documentation to demonstrate that any such reviews had been conducted. Regarding R2.6, SPP RE_URE2 failed to implement its documented appropriate use banner on all electronic access control systems. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 was also in violation of R2.5.2 because a form of authentication was not included in its documented authentication methods. SPP RE consolidated the Self-Report findings with the audit findings. | CIP-005-1 | R2; R2.2; R2.5.2; R2.5.3; R2.6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because the failure to provide all the access control measures specified in CIP-005-1 R2 presented a risk of unauthorized electronic access to Cyber Assets located within SPP RE_URE2’s ESP. SPP RE_URE2 did, however, have compliant CIP-005-1 R2 electronic access control processes and mechanisms in place during the violation duration, including the implementation of an access control model that denies access by default; secured dial-up access to the ESP ; and implementation of strong technical controls at access points to the ESP to ensure authenticity of users who enable external interactive access into the ESP. Additionally, the Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets located within the ESP is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) revised its organizational processes and technical and procedural mechanisms documents to include all the requirements of R2, including: (i) an electronic access control process for documenting and approving open ports and services for each device used for operations and monitoring of Cyber Assets located within the ESP ; (ii) authentication method in its documented authentication methods ; and (iii) a review process for authorization rights in accordance with CIP-004 R4; 2) conducted a review of its open ports and services and compared them to its documented ports and services baseline to ensure that only ports and services required for operations and monitoring Cyber Assets within the ESP were enabled ; 3) where technically feasible, implemented its documented appropriate use banners on all electronic access control system devices; and 4) submitted a Technical Feasible Exception for electronic access control system devices that are incapable of displaying the appropriate use banner. | 2013-06-17 | 2013-08-28 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008249 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-1 R3.2 because it did not monitor and log access at all access points to the Electronic Security Perimeter (ESP) 24 hours a day, seven days a week. Access logs were not captured during a three-week period when the logging server was out of service. Additionally, only approximately ten percent of the access logs were manually reviewed for attempts at or actual unauthorized access within 90 calendar days. | CIP-005-1 | R3.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because the failure to implement an electronic or manual process for monitoring and logging access at all access points to the ESP presented a risk of SPP RE_URE2 not being aware of unauthorized attempts and/or access into its ESP. Such vulnerabilities, if exploited, could have resulted in the loss of highly sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2’s Critical Cyber Assets (CCAs) are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to CCAs is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) purchased, installed, and configured a new server with software that now monitors and logs access at all access points to the ESP 24 hours a day, seven days a week; the server will alert designated response personnel of unauthorized attempts and/or access to the ESP, prompting an immediate investigation; and 2) revised its monitoring procedure to reflect the new logging and monitoring server and updated its log retention requirement. | 2013-07-29 | 2013-08-22 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008250 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-1 R4.3 because it did not perform the necessary steps to ensure that it discovered all access points to its Electronic Security Perimeter (ESP). SPP RE_URE2’s Cyber Vulnerability Assessment (CVA) included an electronic scanning of only the networks inside the ESP. While this identifies the Cyber Assets connected to a network segment within the ESP, this scan alone does not identify Cyber Assets also connected to one or more network segments outside of the ESP. There is no evidence that each Cyber Asset was interrogated, or that a manual tracing of cables or a scan of every network occurred, and there was not any other process documented to determine if there are any Cyber Assets with direct network connectivity both inside and outside of the ESP. | CIP-005-1 | R4.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because a violation of CIP-005-1 R4 presented a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within SPP RE_URE2’s ESP without its knowledge. Such access and vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. However, the risk to the BPS was reduced because SPP RE_URE2’s CCAs were behind a firewall, and SPP RE_URE2 was utilizing a network intrusion detection system to analyze network traffic for known and suspect malicious activity. SPP RE_URE2 attested that there were no security alerts or incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) amended its annual CVA procedures to include a manual inspection of cables to identify possible additional access points; 2) installed new software on each Cyber Asset within the ESP to continually monitor for configuration changes; and 3) conducted a new CVA pursuant to its new procedures to ensure all access points the ESP were identified. | 2013-05-31 | 2013-07-15 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008252 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-006-1 R3 because it failed to monitor physical access to the Physical Security Perimeter (PSP) 24 hours a day, seven days a week. Access logs were reviewed for unauthorized access attempts once a day on business days, which did not meet the R3 requirement to review and respond to unauthorized access attempts immediately. Though SPP RE_URE2 maintained that it performed human observation of access points via video camera in accordance with R3.2, the use of system dispatchers to perform this function as a secondary responsibility in lieu of alarm systems was not effective 24 hours a day and thus did not satisfy the requirement for monitoring physical access at all access points to the PSP 24 hours a day, seven days a week. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failure to monitor physical access to the PSP presented a risk of SPP RE_URE2 not being aware of unauthorized attempts and/or access into its PSP. Such vulnerabilities, if exploited, could have resulted in the loss of highly sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. Once daily review of access logs did not allow the entity to be alerted to or respond to unauthorized access attempts immediately . Although SPP RE_URE2 observed access points as a secondary responsibility, this did not allow for 24 hours a day, seven days a week access monitoring. There were no instances of attempted or actual unauthorized access during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) configured audible and visual alarms to alert personnel 24 hours a day, seven days a week, of unauthorized access attempts to the PSP; 2) revised its monitoring and logging physical access procedure to require personnel to investigate alarms immediately; and 3) trained all affected personnel on the new procedures. | 2013-04-06 | 2012-10-03 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008253 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-006-1 R6 because it did not have a documented maintenance and testing program to ensure its physical security systems functioned properly. Because SPP RE_URE2 did not have a documented maintenance and testing plan as required by R6, it failed to adhere to the testing and maintenance and retention requirements as prescribed in R6.1 through R6.3. | CIP-006-1 | R6; R6.1; R6.2; R6.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because even though the SPP RE_URE2 attested that it was conducting all maintenance and testing to ensure its physical security systems were functioning properly it could not support the attestation with documentation. Although SPP RE_URE2 did not have a documented program for testing and maintaining its physical security systems, SPP RE_URE2 attested that it did perform such testing and maintenance. It further attested that there were no incidents attributable to a failure of the physical security systems during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) developed and implemented a physical security system maintenance and testing plan to meet the requirements of CIP-006; 2) trained all affected personnel on the new program; and 3) tested all physical security systems pursuant to the program. | 2013-05-07 | 2013-06-26 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008254 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R5.1 and R5.3. Regarding R5.1, SPP RE_URE2’s account management policy did not include procedural controls to ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. Additionally, while SPP RE_URE2 maintained a list of approved user accounts, the list did not include the user’s specific electronic access rights, and a central log of account requests and approvals was not maintained. Therefore, SPP RE_URE2 was neither able to ensure that user accounts were implemented as approved by designated personnel per R5.1.1 nor generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of 90 days per R5.1.2. Further, SPP RE_URE2 was unable to demonstrate that it had conducted annual reviews of its user accounts to verify access privileges were in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4 as required by R5.1.3. Regarding R5.2, SPP RE_URE2’s policy did not address the management of scope and acceptable use of administrator, shared, and default accounts. Also, SPP RE_URE2 did not maintain a list of individuals with access to shared accounts as required by R5.2.2. Moreover, SPP RE_URE2’s policy did not include management of shared user accounts per R5.2.3. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 was also in violation of R5.3 because one account password did not contain the required alpha, numeric, and special characters, and two account passwords remained unchanged for 1,024 days. | CIP-007-1 | R5; R5.1; R5.1.1; R5.1.2; R5.1.3; R5.2; R5.2.2; R5.2.3; R5.3.2; R5.3.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to maintain a compliant Account Management program presented a risk of unauthorized access to and the introduction of exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2 did maintain a list of approved users, all of whom had cleared background checks. Additionally, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cyber security incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | when the user access list was revised | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) changed the passwords of the accounts to adhere to the requirements of R5.3 and R5.3.2; 2) revised its Account Management policy to: (i) include procedural controls to ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed; (ii) provide adequate reviews of all user accounts to ensure they were implemented as approved by designated personnel; (iii) ensure that annual reviews of its user accounts are conducted to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement 4 as required by R5.1.3; and (iv) address management of shared, administrator, and default accounts; 3) added specific electronic rights to its list of approved user accounts; 4) added shared user accounts to its electronic access list; 5) generates and maintains logs with sufficient detail to create historical audit trails of all user accounts access activity for a minimum of 90 days; and 6) trained all affected personnel on newly implemented procedures. | 2013-11-13 | 2013-11-13 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008255 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-007-1 R6. Specifically, SPP RE_URE2 did not document the organizational processes and technical and procedural mechanisms for monitoring security events on all Cyber Assets within the Electronic Security Perimeter (ESP) as required by requirement R6.1. In addition, while SPP RE_URE2 utilizes a manual log review process, most available logs were not being reviewed. Moreover, most logs were not retained for at least 90 days per R6.4. Therefore, because the majority of logs were neither retained nor reviewed, SPP RE_URE2 was unable to ensure that it was capable of detecting all Cyber Security Incidents and alerting such incidents to appropriate personnel as required by R6.2. | CIP-007-1 | R6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to properly monitor and alert for Cyber Security Incidents presented a risk of the introduction of exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets within the ESP is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | present | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2 will: 1) purchase and install logging and alerting software that will retain logs for at least 90 calendar days; and 2) implement documented organization processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the ESP. | 2/13/2014 (the accepted proposed completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2011008291 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-006-1 R1 because of deficiencies in its physical security plan. The plan did not include procedures for the appropriate use of physical access control as required by R1.4 and for updating the plan within 90 calendar days of a physical security system redesign or reconfiguration as required by R1.7. During an ensuing Compliance Audit SPP RE determined that SPP RE_URE2 failed to have its physical security plan approved by its senior manager or delegate(s) and protect Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP) with the protective measures specified in R1.8. | CIP-006-1 R1 | R1; R1.4; R1.8 | Medium | Severe | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. . SPP RE_URE2 had a documented physical security plan, albeit deficient. Although senior management failed to formally approve the plan, the senior manager regularly attends the CIP compliance team meetings and was aware of the plan. The failure to provide the devices the required protective measures pursuant to CIP-006-1 R1.8 may have led to unauthorized physical access to Critical Cyber Assets, but no such unauthorized access occurred during the violation period. The PACS devices were located within the designated PSP. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) revised its physical security plan to include: (i) annual review and approval process controls; (ii) the appropriate use of physical access controls; (iii) a requirement to update the plan within 30 calendar days of the completion of any physical security system redesign or reconfiguration; (iv) devices involved in the violation and how they are protected; and (v) senior management approval. | 2013-08-30 | 2013-08-30 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPP RE_URE3) | NCRXXXXX | SPP2012010286 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPP RE_URE3 was in violation of CIP-006-1 R1.8. SPP RE_URE3 failed to afford all the protective measures specified in CIP-005-1 R2, R2.2, R3.2, and CIP-007-1 R4.2 for some Cyber Assets used in the access control and monitoring of SPP RE_URE3 Physical Security Perimeter (PSP). SPP RE_URE3 failed to fully implement CIP-005-2 R2. SPP RE_URE3 did not include two devices located on its network, which are used for controlling physical access to identified PSPs, in its documented processes and mechanisms. SPP RE_URE3 failed to afford the protective measures specified in CIP-005-2 R2.2. SPP RE_URE3's ports and services baseline did not identify ephemeral port ranges required for operations and monitoring of Cyber Assets within an Electronic Security Perimeter (ESP). Without such port ranges, SPP RE_URE3 was unable to identify all ports that could be associated with normal and emergency operations and monitoring of Cyber Assets within the ESP. As a result, SPP RE_URE3 was unable to ensure that each enabled port associated with a particular enabled service for normal and emergency operations and monitoring of Cyber Assets within the ESP was the required port to run the associated service. SPP RE_URE3 failed to fully implement CIP-005-1 R3. SPP RE_URE3 did not include two devices located on the corporate network in its documented processes. SPP RE_URE3 failed to fully implement CIP-007-1 R4.2. SPP RE_URE3 was unable to provide evidence of testing of antivirus signature files before installing them onto the devices. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to provide the protective measures specified in CIP-006-1 R1.8 presented a risk of the introduction of exploitable vulnerabilities in SPP RE_URE3’s system without its knowledge. Such vulnerabilities, if exploited, could have resulted in the loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. The devices, however, resided within a PSP and thus were afforded CIP-006 physical security protective measures. The security measures included physical access controls, monitoring and logging of physical access, and maintenance and testing programs to ensure physical security systems function properly. In addition, physical and electronic access to the devices and Cyber Assets residing within the PSP was limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE3 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SPP RE_URE3 | Mitigation Plan completion | 5000 | Compliance Audit | To mitigate this violation, SPP RE_URE3: 1) developed and implemented a ports and services program, which provided guidance to affected staff in managing and complying with the ports and services requirements in the NERC CIP Standard CIP-005 R2.2 and CIP-007 R2; R2, R2.2, R3.2, and CIP-007-1 R4.2; 2) performed a port scan on the devices to identify all ports that could enable all associated services for operations and monitoring of Cyber Assets and within SPP RE_URE3's ESP, and updated its ports and services baseline document; 3) relocated the devices behind two new firewalls; and 4) revised its document to detail the process of testing antivirus signatures. | 2012-09-13 | 2012-11-13 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE3 internal compliance program (ICP) and considered it, as well as its cooperation throughout the settlement process, to be a mitigating factors in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009123 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3 R7. Upon learning the device was damaged, WECC_URE1 returned the device to the manufacturer for replacement under warranty. However, WECC_URE1 did not document the return. Because the device involved in this violation was used in WECC_URE1's access control and monitoring of one of its Electronic Security Perimeters (ESPs), WECC determined that WECC_URE1 was in violation of CIP-005-3 R1, not CIP-007-3 R7, and referred the matter to WECC Enforcement. WECC Enforcement determined that WECC_URE1 is in violation of CIP-005-3 R1 for failing to afford its device used in the access control and monitoring of one of its ESPs the protections in CIP-007-3 R7.3. | CIP-005-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device in scope is devoid of any markings that would alert a hypothetical bad actor that the device contains information that was used as part of a system belonging to the entity. In addition, the entity stated the information stored on the device alone may not be sufficient for causing damage to ESP since this information is specific to entity's internal network. As compensating measures, the device was returned safely to the manufacturer which has in place rigorous policies for handling such devices, including deleting files from the device's memory, if any. | when WECC_URE1 disposed of the device | Mitigation Plan completion | $7,000 (for WECC2012009123 and WECC2012009124) | Self-Certification | To mitigate this violation, WECC_URE1 counseled its management on the importance of following WECC_URE1's disposing and redeploying of Cyber Asset procedure, as well as to evaluate the methods and processes for interacting with equipment vendors to determine the most appropriate approaches for disposing and redeploying Cyber Assets under warranty. | 2012-05-31 | 2012-07-27 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-14-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009124 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R4. WECC dismissed WECC_URE2's potential violation of CIP-004-3 R4, and determined that the scope of the violation was related to CIP-006-3c R1.4, and all activity would be addressed under NERC tracking number WECC2012009124. Because the employee was granted access to WECC_URE2's CCAs erroneously, WECC concluded that these facts and circumstances constitute a violation of CIP-006-3c R1.4, not CIP-004-3 R4. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE2 stated that the employee had a PRA and cybersecurity training prior to getting the access, and had been cleared to access a different PSP. In addition, the CCA in scope is located in a locked cabinet that had monitoring and logging measures to detect any unauthorized activity. | when the employee was given access to WECC_URE2's CCAs | when the employee's access was revoked | $7,000 (for WECC2012009123 and WECC2012009124) | Self-Report | To mitigate this violation, WECC_URE2: 1) revoked the employee's physical access to WECC_URE2's PSPs; 2) developed an improved process workflow, with additional steps, for system administrators granting physical access to NERC restricted sites; 3) communicated the improved process workflow to all system administrators to ensure the additional steps are followed; and 4) met with the system administrators to describe and reinforce the revised access provisioning process. | 2012-02-15 | 2012-06-07 | Admits | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered compliance history as an aggravating factor in penalty determination.
2013-12-30 | FERC | NP14-14-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012043 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-3a R6. Specifically, WECC_URE3 reported that it failed to implement automated tools or organizational process controls to monitor system events that are related to cybersecurity for Cyber Assets within Electronic Security Perimeters (ESPs). WECC determined that WECC_URE3 was in violation of CIP-007-3a R6 for failing to activate and implement security status monitoring (logging) on the devices after the upgrade. | CIP-007-3a | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because, for over one year, WECC_URE3's failure to ensure that automated tools or organizational process controls were in place to monitor system events related to cybersecurity exposed Cyber Assets to possible unauthorized access attempts. The risk to the reliability of the BPS was mitigated by the following mitigating factors. All the affected devices were located within an identified ESP and Physical Security Perimeter where access is restricted to only authorized individuals. | when WECC_URE3 performed the upgrade | Mitigation Plan completion | 35000 | Self-Certification | To mitigate this violation, WECC_URE3: 1) revised the security test plan form; 2) revised the IT NERC CIP implementation checklist; and 3) revised its process for logging test evidence. | 2013-09-11 | TBD | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE3’s compliance history to be an aggravating factor in the penalty determination
2013-12-30 | FERC | NP14-6-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008540 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-006-1 R1.8. FRCC_URE1 failed to provide evidence that it afforded protection of the annual access privilege review of CIP-003 R5.2 for certain designated Cyber Assets within the annual period required. The annual review was completed eight days beyond the annual review requirement date. Furthermore, FRCC_URE1 failed to provide evidence that the required afforded protections of CIP-005 R2 and R3 were applied to all Cyber Assets in that no access point had been established. | CIP-006-1 | R1; R1.8 | Lower | High | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1's failure posed a moderate risk because it could leave the Cyber Assets unprotected and vulnerable to a cyber threat. This risk was reduced because the Cyber Assets were located within a Physical Security Perimeter (PSP), protected behind a corporate firewall, and were afforded all other required protective measures of the CIP Standards. Failure to review access annually could also leave unwarranted access in place and leave Cyber Assets vulnerable to a cyber threat. The annual review of access risk was reduced because access is continually updated as personnel transfers and terminations occur. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | 2000 | Self-Report | To mitigate this instance of the violation, FRCC_URE1: 1) provided new employee access to the information repository; 2) completed the annual review of access to information repository; 3) added comments to one of the fields to note that a change in approve also requires a change within the repository list. The note also informed the group the appropriate contact for assistance; 4) created procedures to note that the repository list and approvers will be updated by the analyst performing the change in repository owner ; 5) added comments to the protected Critical Cyber Asset (CCA ) information repository list description to ensure that any changes to the list are also reflected in procedures & documentation; 6) submitted a request for interpretation; 7) identified and collected IP addresses for the devices; 8) relocated servers within the ESP; 9) patched and tested servers; 10) tested communication between devices to the relocated servers; 11) deployed devices into an isolated environment; 12) completed testing of the devices; and 13) placed the devices into production. | Present | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-12-30 | FERC | NP14-6-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012421 | Settlement Agreement | RFC_URE1 submitted a Self-Certification to RF stating that it was in violation of CIP-007-1 R3. RFC_URE1 has a security patch management program in place whereby RFC_URE1 assessed and applied security patches twice per year, instead of every 30 days of availability of the security patch or upgrade. RFC_URE1 reviewed vendor-supplied documentation to assess the applicability of security patches and security upgrades for Cyber Assets within the Electronic Security Perimeter (ESP) twice per year. However, RFC_URE1 failed to document its performance of these reviews and cannot provide evidence that it conducted these reviews within 30 days of availability of the security patch or upgrade, as required by the Standard. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation posed a moderate risk because the existing RFC_URE1 program at the time of the violation did not meet the requirements for frequency of review or documentation as required by CIP-007-1 R3. RFC_URE1 failed to detect the violation until approximately three years after it was required to comply with CIP-007. Also, RFC_URE1’s approach to patch management could have resulted in unauthorized access or compromise to its system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE1 maintains a security patch management program for all enterprise information technology (IT) assets where it assesses and applies patches twice per year. In addition, RFC_URE1 conducts periodic review of user failed logins, user logins over time, and reviews of ports and services to identify any events. RFC_URE1 also utilizes a malicious software prevention tool and regularly reviews the logs. Furthermore, RFC_URE1 secures its physical access by implementing visitor control, cameras and recording devices, an electronic key-locking system, and authorization controls. RFC_URE1 also periodically reviews firewall user logins and firewall configurations. Lastly, for the duration of the violation, the Cyber Assets were not exposed to unauthorized access. RFC_URE1 verified this by reviewing its user unauthorized access over time report, its ports and services report, and a firewall rules comparison. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | 0 | Self-Certification | To mitigate this violation, RFC_URE1: 1) recorded baseline versions of all software revisions related to Critical Cyber Assets (CCAs) within the ESP; 2) assessed all available security patches related to CCAs within the ESP; 3) engaged a vendor to provide a complete review and assessment of all security patches associated with the Generation Management System (GMS) application and GMS-related system software; 4) conducted, for all other CCAs inside the ESP, an independent review and assessment of security patches; 5) documented the assessment of the above items, obtained management approval, and stored evidence in the IT Change Management database; and 6) documented compensating measures where necessary, updated its procedure documentation, conducted training regarding procedures, and installed applicable security patches. | 2013-06-14 | TBD | Admits | RF reviewed RFC_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in penalty the determination.
2013-12-30 | FERC | NP14-6-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012425 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RFC_URE2 was in violation of CIP-003-1 R4 because it failed to assess adherence to its Critical Cyber Asset (CCA) information protection program. RFC_URE2 annually reviewed its CCA information permissions, but failed to annually assess adherence to its CCA information protection program to identify, classify, and protect information associated with CCAs. Although RFC_URE2 annually reviewed permissions, such review is not a complete review of adherence to its CCA information protection program to identify, classify, and protect all CCA information. | CIP-003-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because based on two factors. First, ReliabilityFirst considered RFC_URE2's failure to detect the violation as evidenced by its discovery during a Compliance Audit. Second, ReliabilityFirst considered that RFC_URE2's failure to assess adherence to the CCA information program could have resulted in compromise of its CCA information due to improper classification. Discovery as a result of a mandatory compliance monitoring process demonstrates that the Registered Entity was not as likely to detect the violation on its own, which potentially exacerbates the impact of the violation and increases the risk to grid reliability. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE2 has documented procedures to manage access to CCA information, including performing quarterly reviews of access lists. RFC_URE2 also has protective measures to protect CCA information from unauthorized access including file system permissions that provide access control for files and folders, user group permissions controlling access to network resources based on job functions, specific applications to protect, analyze, and control user accounts to the document management system environment, card readers, locking drawers, video surveillance, port and interface security to protect devices from viruses and security breaches, and password and lockout policies. | when the Standard became mandatory and enforceable on RFC_URE2 | Mitigation Plan completion | $0 (for RFC2013012425 and RFC2013012426) | Compliance Audit | To mitigate this violation, RFC_URE2: 1) surveyed all areas of the company to determine where CCA information exists; 2) assessed the results of the survey and documented the location of the CCA information; and 3) created an action plan assigning action items and due dates to migrate CCA information into appropriately protected storage locations as needed. RFC_URE2 also committed to strengthening its internal controls through its implementation of new compliance database control activities, updating security posture verification forms to include verification steps, and reinforcement programs for CCA information such as email, posters, and random searches. | 2013-09-16 | TBD | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factors in the penalty determination. Although ReliabilityFirst discovered the violations during a Compliance Audit, ReliabilityFirst determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE2 's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. ReliabilityFirst is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE2's response to the Compliance Audit findings is behavior that ReliabilityFirst seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. In light of the moderate risk posed by the instant violations and RFC_URE2's improvements following the Compliance Audit, ReliabilityFirst determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability.
2013-12-30 | FERC | NP14-6-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012426 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RFC_URE2 was in violation of CIP-005-1 R1 because it failed to adequately document and identify all electronic access points to the Electronic Security Perimeter (ESP) and the Cyber Assets deployed for the access control and monitoring of these access points. During the Compliance Audit, ReliabilityFirst discovered a noncompliance with CIP-005-3a R1.1 wherein RFC_URE2 had three dial-up accessible devices connected to the ESP. While these devices were configured not to allow interactive access, they were dial-up accessible. Upon discovery during the on-site portion of the Compliance Audit, RFC_URE2 immediately disconnected the devices. As a result, ReliabilityFirst did not include this as part of the violation, although RFC_URE2 noted it in its Mitigation Plan for this violation. RFC_URE2 has one ESP and four Physical Security Perimeters (PSPs), with wide area network (WAN) routers as externally-connected communication end points within the ESPs to communicate among PSPs within the ESP. After a technical review based on an outside contractor’s advice, RFC_URE2 determined that these devices were not access points to the ESP. ReliabilityFirst determined that these devices did constitute access points to the ESP because they are externally connected communication end points terminating at a device within the ESP. However, and as a result, RFC_URE2 failed to identify these devices as electronic access points to the ESP (R1.1 and R1.3) and failed to maintain documentation including these access points and the Cyber Assets deployed for the access control and monitoring of these access points (R1.6). | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that this violation posed a moderate risk because based on two factors. First, ReliabilityFirst considered RFC_URE2's failure to detect the violation as evidenced by its discovery during a Compliance Audit and RFC_URE2's conscious decision to implement the single ESP. Second, ReliabilityFirst considered that malicious attacks are more likely to be successful without proper isolation of ESPs. Discovery as a result of a mandatory compliance monitoring process demonstrates that the Registered Entity was not as likely to detect the violation on its own, which potentially exacerbates the impact of the violation and increases the risk to grid reliability. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Although RFC_URE2 did not identify and document the devices as access points, RFC_URE2 identified and protected all network devices in scope as Critical Cyber Assets (CCAs) and afforded them the protections of CIP-006 and CIP-007, such as ports and services management, change control and testing, account control and password protection, cyber vulnerability assessments, and implementation of recovery plans, and protection from unauthorized physical access behind PSPs. Although the links between the devices were not in a PSP, the devices themselves were in a PSP. RFC_URE2 controlled, logged, and monitored all electronic access. As such, RFC_URE2 protected these trusted corporate networks by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. These protections decrease the likelihood of unauthorized access. Unauthorized access attempts would have triggered alarms alerting personnel of such attempts. RFC_URE2 limited authorized access to the devices to individuals who all completed personnel risk assessments and cybersecurity training. Furthermore, RFC_URE2 maintains documented drawings of the ESP and the interconnected Critical and non-critical Cyber Assets within the ESP; however, the network devices in scope were not labeled on the drawings as access points. | when the Standard became mandatory and enforceable on RFC_URE2 | present | $0 (for RFC2013012425 and RFC2013012426) | Compliance Audit | To mitigate this violation, RFC_URE2 will: 1) identify the router WAN interfaces as communication link end points, verify the existence of appropriate use banners for all WAN routers, perform and document the device-specific elements of the updated cyber vulnerability assessment documented in its procedures; 2) create new compliance database control activities related to the annual ESP vulnerability assessment for individuals who will assess device-specific aspects of the routers, and train key network operations personnel in configuration aspects of new WAN router hardware required for discrete ESP design; 3) define a fully compliant, discrete ESP for the alternate operations center and use the new location to verify the design and test all aspects of discrete ESP design, implementation, and commissioning, and use lessons learned to purchase, configure, install, test, and commission new WAN routers at all locations; and 4) update its network drawings to reflect the new configurations, update its ESP identification and documentation procedure to clarify the expected level and scope of inclusion for the network drawings, update the CIP-007 R1 security posture verification forms to include a verification that appropriate labels have been applied to devices and cabling upon installation or device move, and update the CIP-007 R7 disposal or redeployment form to include a verification that labels have been appropriately removed from devices and cabling upon disposal or redeployment. RFC_URE2 also committed to strengthening its internal controls through its implementation of new compliance database control activities, updating security posture verification forms to include verification steps, and reinforcement programs for CCA information such as email, posters, and random searches. | 3/30/2014 (approved completion date) | TBD | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factors in the penalty determination. Although ReliabilityFirst discovered the violations during a Compliance Audit, ReliabilityFirst determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE2's clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. ReliabilityFirst is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE2's response to the Compliance Audit findings is behavior that ReliabilityFirst seeks to encourage, as these are positive proactive steps to prevent recurrence of noncompliance. In light of the moderate risk posed by the instant violations and RFC_URE2's improvements following the Compliance Audit, ReliabilityFirst determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability.
2013-12-30 | FERC | NP14-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009993 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1. WECC_URE1 failed to secure five devices which provisioned physical access control (PAC) and monitoring to Physical Security Perimeters (PSPs) as described under CIP-006-1 R1.8. Based on additional information disclosed by WECC_URE1, WECC determined that the violation included three sub-requirements of CIP-006-1 R1. WECC_URE1 dispatched two technicians to service a device contained within a PSP cabinet. One of the technicians (T1) was authorized with unescorted physical access to the PSP. The other technician (T2), however, did not have authorization for unescorted physical access to that particular PSP. After unlocking the PSP cabinet door, T1 went to retrieve a tool from his truck, leaving T2 unescorted. After T1 returned , both technicians completed work on the device. The technicians did not, however, lock the cabinet door, nor notify security that they completed work on the device and secured the PSP as required under WECC_URE1's procedure to ensure appropriate use of physical access. Because the technicians failed to lock the PSP cabinet door, alarms were triggered. Security was dispatched to the site to secure the PSP. Within two hours of the technicians' departure from the PSP, WECC_URE1 security identified the unlocked PSP cabinet door. Security locked the PSP cabinet door. WECC_URE1 reported that the PSP cabinet door remained unlocked for approximately two hours. WECC Enforcement determined that compliance with R1.4 and R1.6 requires entities to ensure that its procedures regarding the appropriate use of physical access controls and visitor access are followed. In this case, Enforcement determined that two WECC_URE1 technicians failed to follow WECC_URE1 physical access control procedures, in violation of R1.4. Enforcement determined that the technicians failed to secure the PSP cabinet door after completing their work; and, that the technicians failed to notify WECC_URE1 security that they were leaving the PSP site as required by WECC_URE1's policy. Further, Enforcement determined that T2 gained unescorted physical access to a PSP after T1 left the PSP to retrieve a tool from his truck. Enforcement determined that T2 access constitutes a violation R1.6 and WECC_URE1's visitor access procedure. WECC also determined that WECC_URE1 failed to secure five devices pursuant to R1.8. The devices were associated with WECC_URE1 PSPs. While WECC_URE1 had protections and controls in place to secure the PSP cabinets and SSP devices, the affected SSP device was not protected from unauthorized physical access. | CIP-006-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk involving the violations of R1.4 and R1.6 was mitigated by several factors. No Critical Cyber Assets (CCAs) were located within the PSP cabinet that was involved. Both technicians had completed Personal Risk Assessments (PRAs) and cybersecurity training. The technician who did not have unescorted physical access rights to the PSP cabinet had unescorted physical access rights to other WECC_URE1 PSPs. The PSP cabinet was alarmed, and the failure to lock it triggered an alarm to WECC_URE1 security. Access to the PSP cabinet was monitored 24 hours a day, seven days per week. Further, although the PSP cabinet was left unlocked, access to the cabinet first required authorized access to the room in which the PSP cabinet was located. In regard to the violation of R1.8, the risk to the BPS was mitigated by several factors. The devices were located in a secured facility. Physical access to the facility was controlled and monitored. All individuals granted access to the facility completed PRAs and cybersecurity training required under CIP-004. The devices were within PSPs. In addition, the devices were electronically separated from the general corporate network and access was controlled, logged, and monitored. Also, cyber events would have triggered an alarm within the application. | when WECC_URE1 should have identified the devices and afforded them the protective measures required by R1.8 | Mitigation Plan completion | 45000 | Self-Report | To mitigate this violation in regards to R1.4 and R1.6, WECC_URE1: 1) took personnel actions with the maintenance personnel involved; and 2) implemented and documented maintenance group management staff meeting discussions of the incident which will continue as needed. To mitigate this violation in regards to CIP-006-1 R1.8, WECC_URE1: 1) installed an electronic access control device within each PSP containing the type of device involved; 2) documented the device's features and functions that are necessary for operation; 3) disabled all other features and functions required by CIP-007-3; 4) submitted a technical feasibility exception for the devices; and 5) reviewed existing documentation and procedures to ensure compliance with relevant CIP standards. Any needed updates that were identified during the review were documented and communicated to relevant personnel. | 2012-08-01 | 2013-06-11 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered that WECC_URE1 self-reported the violation as a mitigating factor in the penalty determination. A Settlement Agreement covering violations including one of CIP-006-1 R1 for WECC_URE1 was filed with FERC under NP12-5-000 on November 30, 2011. On December 30, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that WECC_URE1’s previous violations of CIP-006-1 R1 constituted a prior violation and a aggravating factor in the penalty determination.
2013-11-27 | FERC | NP14-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012109 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-006-3c R2 because it failed to ensure that the Cyber Assets used in the control and monitoring of Physical Security Perimeters (PSPs) were afforded the protective measures of CIP-007-3 R3.1. WECC_URE2's security patch management program requires that WECC_URE2 documents the assessment of such security patches and security upgrades for applicability within 30 days from the date the patch or upgrade is available from the vendor. WECC_URE2 reported that for two Cyber Assets used to control and monitor access to 15 PSPs, it failed to assess eight Microsoft security patches within 30 calendar days of their release. The Cyber Assets in scope are the primary and backup servers used as both the application and database server for the Physical Access Control and Monitoring (PACM) System. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risks to the BPS were minimized by measures that existed during the violation period. The two Cyber Assets in scope were located in a secure network protected by restrictive boundary devices that log and restrict all logical access attempts. The devices were within a separate PSP, whose access is restricted, logged, and monitored by a card key system, along with additional monitoring through use of cameras. The PACM device in scope supports the card key system. However, a control panel cached temporary information on a regular basis so that access to the PSP which houses the PACM device continued to be restricted using the last known configuration. Thus, in the event the PACM server in scope crashes, physical access would still be restricted and monitored. The Cyber Assets in scope required two-factor authentication prior to any remote access, and had antivirus and malware prevention tools installed. As additional compensating measures, the PACM server had a Symantec Endpoint protection installed, which provides intrusion detection and firewall protection and had antivirus software installed. Lastly, WECC_URE2 assessed the patches approximately a month after their release, limiting the duration of the exposure to one month. | 30 days following the date when the Microsoft patches were available for assessment | when WECC_URE2 assessed the eight security patches | $40,000 (for WECC2013012109 and WECC2013012110) | Self-Report | To mitigate this violation, WECC_URE2: 1) created escalating reminders that continue to alert until a task is flagged as complete; 2) provided similar reminders/escalations for other groups as needed; 3) assessed and documented the assessment of the security patches; and 4) reviewed all Microsoft patches and other patches to ensure no other issues were discovered. | 2013-03-27 | 2013-05-24 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE2's compliance history to be an aggravating factor in the penalty determination.
2013-11-27 | FERC | NP14-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012110 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3a R3 because it failed to document the assessment of security patches. WECC_URE2's security patch management program requires that WECC_URE2 documents the assessment of such security patches and security upgrades for applicability within 30 days from the date the patch or upgrade is available form the vendor. WECC_URE2 reported that for 76 Critical Cyber Assets (CCAs) and 113 Cyber Assets within an Electronic Security Perimeter (ESP), WECC_URE2 failed to asses eight Microsoft security patches within 30 calendar days of their release. The CCAs and Cyber Assets in scope are servers and workstations used for PI historian application, file servers, domain controllers, energy management system (EMS) servers/work stations, and system operator workstations. The devices in scope represent 92% of WECC_URE2's Windows-based assets and approximately 73% of WECC_URE2's Cyber Assets and CCAs overall. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risks to the BPS were minimized by measures that existed during the violation period. The 189 devices in scope were located within an established ESP protected by restrictive boundary devices that log and restrict all logical access attempts. The devices were within a separate Physical Security Perimeters, whose access is restricted, logged, and monitored by a card key system, along with additional monitoring through use of cameras. Access was restricted to individuals with authorization, training and current personnel risk assessments. All devices had antivirus/malware prevention tools, where technically feasible, and most servers had a host-based intrusion detection system running on the device. Lastly, WECC_URE2 assessed the patches approximately a month after their release, limiting the duration of the exposure. | 30 days following the date when the Microsoft patches were available for assessment | when WECC_URE2 assessed the eight security patches | $40,000 (for WECC2013012109 and WECC2013012110) | Self-Report | To mitigate this violation, WECC_URE2: 1) created escalating reminders that continue to alert until a task is flagged as complete; 2) provided similar reminders/escalations for other groups as needed; 3) assessed and documented the assessment of the security patches; and 4) reviewed all Microsoft patches and other patches to ensure no other issues were discovered. | 2013-03-27 | 2013-05-07 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-11-27 | FERC | NP14-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011176 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE3 had a violation of CIP-005-1 R2. WECC_URE3 failed to use explicit access permissions as required by R2.1 on 17 out of 19 Cisco switch access points. In addition, WECC_URE3 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the ESP at the 17 Cisco switch access points as required by R2.2. WECC determined WECC_URE3 had a violation of CIP-005-1 R2 for failing to: 1) ensure technical and procedural mechanisms for control of electronic access at 17 electronic access points to the ESPs by not implementing explicit access permissions as required by R2.1; and 2) enable only ports and services required for operations and for monitoring Cyber Assets within the ESP, and document, individually or by specified grouping, the configuration of those ports and services as required by R2.2. | CIP-005-1 | R2; R2.1, R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because failure to document and implement mechanisms for control of electronic access to the ESP could potentially expose CCAs within the ESP to security attacks. A failure to ensure that only those ports and services required for operations and monitoring Cyber Assets within the ESP are enabled may pose increased risk to the entity's Cyber Assets. This increased risk may allow for unauthorized internal and/or external access, which could allow for successful cyber attacks against CCAs essential to the operation of the BPS. The risk to the BPS was mitigated by the following factors. The 17 Cisco switch access points forward their frames and route their packets through two upstream firewalls. These access points were configured with explicit access permissions and enabled ports and services required for operations and monitoring. Although the Cisco switches failed to have explicit access permissions and enabled ports and services, they are located in Physical Security Perimeters and require user authentication. | when the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $55,000 (for WECC2012011176 and WECC2012010896) | Compliance Audit | To mitigate this violation, WECC_URE3: 1) enhanced existing access control lists in its energy management system network switches to include restrictions on ports and services and enable further restrictions on network traffic by limiting the range of allowed internet protocol address; and 2) updated its procedures for maintaining its access control lists. | 2013-04-30 | 2013-09-23 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Pursuant to the Settlement Agreement, WECC_URE3 has committed to following additional terms: 1) WECC_URE3 will develop a process to track deadlines and mitigate timely minimizing the need for extension requests; 2) WECC_URE3 will create a monthly coordination meeting between compliance groups. This meeting should focus on increasing communication between entities and centralizing issues stemming from information silos; 3) WECC_URE3 will create an annual compliance awareness training program and measure the degree of understanding. The training will include a section to prevent recurrence of NERC Reliability Standard violations; 4) WECC_URE3 will develop a process or improvements to processes that help identify the full scope of violations promptly. WECC_URE3 will also develop a process for detecting what controls are needed when new devices are installed; and 5) WECC_URE3 must submit a narrative to WECC. The narrative must describe how WECC_URE3 implemented or a plan to implement the above changes. WECC will review WECC_URE3's submission and may elect to provide feedback to WECC_URE3. WECC_URE3 did submit a narrative to WECC, which describes how WECC_URE3 implemented or plans to implement the above changes.
2013-11-27 | FERC | NP14-6-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010896 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3 R4. WECC_URE3 installed new Linux servers to support its energy management system (EMS). At that time, WECC_URE3 installed anti-virus software (McAfee) on the servers to perform active scans and prevent the introduction of malicious software into the EMS. Approximately a week and a half later, a WECC_URE3 system operator discovered that the anti-virus software was not scanning the EMS, and after researching, discovered the anti-virus software was not configured to perform scans. WECC determined that WECC_URE3 was in violation of CIP-007-3 R4 for failing to use anti-virus software and malware prevention tools on its EMS, specifically 48 Linux servers. | CIP-007-3 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because failure to use anti-virus software and other malicious software prevention tools could allow existing and or new malicious software, originating from a security patch, service pack, vendor release or database update to be introduced to the Cyber Assets, thereby exposing cybersecurity vulnerabilities into the Critical Cyber Assets (CCAs) essential to the operation of the BPS. The risk to the BPS was mitigated by the following factors. Although these servers are not running anti-virus prevention software, WECC_URE3 has an in-depth defense strategy that begins with a user awareness program, which all employees are trained on. This training establishes the proper use of CCAs, physical and electronic access controls, the proper handling of CCA information and action plans and procedures to recover or re-establish CCAs and access thereto following a cybersecurity incident. Also, these servers are all located in controlled areas and do not support access to the internet. Additionally, all WECC_URE3 windows devices that do support the internet have anti-virus that includes testing signature files. | when WECC_URE3 installed the affected Linux servers | Mitigation Plan completion | $55,000 (for WECC2012011176 and WECC2012010896) | Self-Report | To mitigate this violation, WECC_URE3 switched to a vendor-certified anti-virus software and worked with the EMS vendor to lay out a plan to migrate the software, ensuring that monitoring tools are installed on all CIP devices. | 6/11/2013 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Pursuant to the Settlement Agreement, WECC_URE3 has committed to following additional terms: 1) WECC_URE3 will develop a process to track deadlines and mitigate timely minimizing the need for extension requests; 2) WECC_URE3 will create a monthly coordination meeting between compliance groups. This meeting should focus on increasing communication between entities and centralizing issues stemming from information silos; 3) WECC_URE3 will create an annual compliance awareness training program and measure the degree of understanding. The training will include a section to prevent recurrence of NERC Reliability Standard violations; 4) WECC_URE3 will develop a process or improvements to processes that help identify the full scope of violations promptly. WECC_URE3 will also develop a process for detecting what controls are needed when new devices are installed; and 5) WECC_URE3 must submit a narrative to WECC. The narrative must describe how WECC_URE3 implemented or a plan to implement the above changes. WECC will review WECC_URE3's submission and may elect to provide feedback to WECC_URE3. WECC_URE3 did submit a narrative to WECC, which describes how WECC_URE3 implemented or plans to implement the above changes.
2013-11-27 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001224 | Settlement Agreement | RF conducted a Compliance Audit and discovered that RFC_URE1 was in violation of CIP-003-1 R6. During the Compliance Audit, RF reviewed documentation related to RFC_URE1's change and configuration management procedures, promulgated pursuant to CIP-003-1 R6. While RFC_URE1 presented several documents related to configuration, RFC_URE1 did not provide evidence supporting its application of configuration management procedures to identify, control, and document all changes to Critical Cyber Asset hardware and software. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, configuration management ensures the network and environment are properly managed with consistent versions and settings so that the environment remains secure. Insufficient implementation and support of configuration management can introduce unwanted security vulnerabilities, unauthorized access points, and impact the availability of critical systems up to and including the BPS. The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE1 had a configuration management process and maintained some documentation of that process. Although RFC_URE1 was unable to produce detailed documentation demonstrating that the process was followed in all cases, RF did not identify any instances of RFC_URE1 failing to implement this process. | when the Standard become mandatory and enforceable as to RFC_URE1 | when RFC_URE1 enacted new configuration management processes | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RFC_URE1: 1) consolidated its processes related to configuration management into a single, high-level, corporate-wide document; and 2) enhanced its configuration management procedures at the Cyber Asset level. | 2012-06-20 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. RF considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, RF considered that although this violation of CIP-003 R6 posed a moderate risk, RFC_URE1's implementation of its configuration management process was short only in documentation and RF did not find any instances of failure to implement the process.
2013-11-27 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001225 | Settlement Agreement | RF conducted a Compliance Audit and discovered that RFC_URE1 was in violation of CIP-005-1 R1. First, RF discovered that RFC_URE1 had granted a vendor access to its Electronic Security Perimeters (ESPs) through a virtual private network (VPN) without documenting that VPN as an access point to the ESPs, as required by CIP-005-1 R1.1. The vendor required access to service RFC_URE1's Supervisory Control and Data Acquisition (SCADA) system. Second, RFC_URE1 maintained Cyber Assets used in the access control and monitoring of its ESPs that were incapable of implementing antivirus or malware prevention tools, as required by CIP-007-1 R4. These Cyber Assets are within the scope of CIP-005-1 R1 and, therefore, in accordance with CIP-005-1 R1.5 RFC_URE1 must afford them the protections specified in CIP-007-1 R4. Because these Cyber Assets could not implement antivirus or malware prevention tools, RFC_URE1 was required to submit Technical Feasibility Exceptions (TFEs) detailing these technical limitations but failed to do so timely. | CIP-005-1 | R1; R1.1, R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation of CIP-005-1 R1.1 posed a moderate risk because the individual worked for a reputable SCADA vendor that provides security training and conducts Personnel Risk Assessments on its employees, in addition to RFC_URE1's processes. RFC_URE1 only enabled the VPN at issue when specifically requested to do so by its SCADA support team, and RFC_URE1's corporate firewalls further controlled access to this VPN. In addition, the mitigating and compensating measures described in the TFE were in place throughout the entire period of time at issue. | For R1.1: when the Standard become mandatory and enforceable as to RFC_URE1; for R1.5: when RFC_URE1 should have submitted the TFE | For R1.1: when RFC_URE1 revoked the vendor’s VPN access; for R1.5: when RFC_URE1 submitted a TFE for the Cyber Assets at issue | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RFC_URE1: 1) revoked the vendor’s VPN access that had previously served as an undocumented access point to an ESP; 2) enhanced its inspections of its ESPs to document more fully access points to ESPs; and 3) submitted an acceptable TFE for the Cyber Assets incapable of having antivirus and malware prevention tools implemented. | 2012-03-16 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. RF considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RFC_URE1 failed to fully comply with CIP-005 R1 at all times, the violation constituted exceptions to an otherwise strong compliance program. For example, although TFEs were not timely submitted for devices that are incapable of implementing antivirus and malware prevention tools, the mitigating and compensating measures were in place at all times.
2013-11-27 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001230 | Settlement Agreement | RF conducted a Compliance Audit and discovered that RFC_URE1 was in violation of CIP-007-1 R1. RF reviewed evidence of RFC_URE1's program for testing new Cyber Assets and significant changes to existing Cyber Assets within Electronic Security Perimeters (ESPs) to ensure that such changes do not adversely impact existing cyber security controls, as required pursuant to CIP-007-1 R1. RF discovered that three devices lacked test procedures for certain periods of time: 1) one device lacked test procedures prior to September 28, 2011; 2) another device lacked test procedures prior to March 4, 2011; and 3) the third lacked test procedures prior to September 22, 2011. Additionally, RF reviewed RFC_URE1's documentation of test results retained pursuant to CIP-007-1 R1.3. Specifically, RF reviewed three test procedures provided by RFC_URE1. In reviewing documentation of RFC_URE1's implementation of these procedures, RF discovered that all three procedures included Cyber Assets for which no documentation of test results existed. | CIP-007-1 | R1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, a violation of CIP-007-1 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity for new Cyber Assets within the ESP and significant changes to existing Cyber Assets within the ESP to adversely affect existing cyber security controls. The risk to the reliability of the BPS was mitigated by the following factors. During the entire period subject to the Compliance Audit, the devices in question were located in ESPs protected by firewalls and physically protected from unauthorized access. Additionally, RFC_URE1 has automated monitoring and notifications in place with respect to the firewall logs to detect and respond to unauthorized access or unauthorized access attempts. Furthermore, only a small subset of the entire list of Cyber Assets lacked test results, namely substation field devices that provide telemetry for the Supervisory Control and Data Acquisition (SCADA) system. These devices had related Technical Feasibility Exceptions, evidencing RFC_URE1's awareness of the devices. Any significant changes to these devices would have required trained technicians and an outage scheduled to perform the necessary work. Firmware updates to these devices cannot be applied through automated processes, and the updates are closely controlled through internal databases. | when the Standard become mandatory and enforceable as to RFC_URE1 | when RFC_URE1 completed and documented testing for each Cyber Asset at issue | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RFC_URE1: 1) reviewed its test procedures for Cyber Assets and recognized that improvements were necessary; 2) created its CIP-007 Cyber Security test procedure, which provides a guideline and checklist to verify that the proper security controls are in place for new or significant changes to existing Cyber Assets; 3) provided sample test results, including results from the testing of monthly patching for security patches and also completed an inventory of all Cyber Assets and ESPs to ensure that all Cyber Asset device types have documented test procedures; and 4) provided training to relevant information technology personnel. | 2012-05-14 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. RF considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RFC_URE1 failed to have test procedures for certain devices, RFC_URE1 demonstrated that it had proper awareness of the devices at issue in this violation, and had afforded other protections such as firewall, physical protection, and automated monitoring to the devices.
2013-11-27 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001237 | Settlement Agreement | RF conducted a Compliance Audit and discovered that RFC_URE1 was in violation of CIP-007-1 R8. Specifically, RFC_URE1 failed to perform cyber vulnerability assessments (CVAs) on Cyber Assets within the Electronic Security Perimeters (ESPs) at RFC_URE1's substations, as required by CIP-007-1 R8. Instead, RFC_URE1 performed only limited scans on those devices; the scans did not meet the requirements of CIP-007-1 R8. Although RFC_URE1 previously performed scans that met the requirements of CIP-007-1 R8 on Cyber Assets in substation ESPs; experienced operational issues on scanned devices and, as a result, began performing the limited scans. | CIP-007-1 | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to perform CVAs on Cyber Assets in the ESPs increase the risk of weaknesses in the security of the Cyber Assets going undetected. The lack of assessment increase the risk to Critical Cyber Assets being compromised and/or rendered inoperable. During the entire period subject to the Compliance Audit, the devices in question were located in ESPs protected by firewalls and physically protected from unauthorized access. Additionally, RFC_URE1 has automated monitoring and notifications in place with respect to the firewall logs to detect and respond to unauthorized access or unauthorized access attempts. The lack of CVA test involved a small subset of the RFC_URE1's Cyber Assets, namely substation field devices that provide telemetry for the Supervisory Control and Data Acquisition (SCADA) system. These devices had related Technical Feasibility Exceptions, evidencing RFC_URE1's awareness of the devices. Any significant changes to these devices would have required trained technicians and an outage scheduled to perform the necessary work. Firmware updates to these devices cannot be applied through automated processes, and the updates are closely controlled through internal databases. RFC_URE1 represents that these devices could not have been easily modified to introduce new vulnerabilities. Furthermore, when RFC_URE1 performed CVAs on these devices in a test environment (the CVAs were performed in a test environment due to the operational issues previously experience by RFC_URE1), the test results were accurate and provided assurance to RFC_URE1 regarding the functioning of these devices. | when the Standard become mandatory and enforceable as to RFC_URE1 | when RFC_URE1 submitted its revised procedures for performing CVAs to RF | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RFC_URE1 drafted a new interim process for manual testing of field devices. RFC_URE1's CVA addressed the issues identified at the Compliance Audit and was a comprehensive process completed within the scope of the new interim process. This interim process incorporated a physical inspection component, which will be added to the CVA process each year. | 2012-05-14 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. RF considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RFC_URE1 failed to conduct CVAs on certain devices, RFC_URE1 demonstrated that it had proper awareness of the devices at issue in this violation, and had afforded other protections such as firewall, physical protection, and automated monitoring to the devices.
2013-11-27 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011566 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-004-3 R4. RFC_URE1 had not timely revoked an individual’s access to Critical Cyber Assets (CCAs) and had not timely updated its list of personnel with access to CCAs. Specifically, RFC_URE1 discovered that it had not revoked an employee’s physical access to certain CCAs. The employee at issue passed away. This employee did not have electronic access to CCAs. Upon discovering this issue, RFC_URE1 immediately revoked the access and documented the revocation of access. RFC_URE1 submitted an additional Self-Report, stating that it failed to revoke physical access to certain CCAs and failed to update its list of personnel with access to account for an employee who transferred to a position within RFC_URE1 that did not require such access. This transfer occurred, but RFC_URE1 did not revoke access eight days later, one day after it was required to do so pursuant to CIP-004-1 R4.2. This delay in revocation was due to RFC_URE1's human resources department not receiving timely notice of the transfer. | CIP-004-3 | R4; R4.1, R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The first instance of the violation related to the deceased employee was an isolated incident. Given that the individual was deceased, he had no ability to access RFC_URE1's facilities, and RFC_URE1 determined that his identification badge was secure during the relevant period. As to the second instance of the violation, the employee at issue remained a RFC_URE1 employee in good standing throughout the period of the violation. In both cases, the individuals at issue had undergone personnel risk assessments and cyber security training. | when RFC_URE1 should have revoked access for the individual at issue in the first occurrence; when access should have been removed for the transferred individual | when access was removed for the deceased individual; when RFC_URE1 revoked access for the transferred individual | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Self-Report | To mitigate this violation, RFC_URE1 transferred responsibility for CIP-004 compliance to its human resources department. To mitigate this violation, RFC_URE1 will implement procedural and technological enhancements to ensure timely access revocations and updates to access lists. | 2013-07-31 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure its continued observance of the NERC Reliability Standards. RF also applied mitigating credit to RFC_URE1's self-reported violations. RFC_URE1's Self-Reports evidence a full understanding of the issues presented, described the immediate steps taken by RFC_URE1 to minimize reliability risks, and provided RF with sufficient information to analyze the violations. Such timely and robust Self-Reports are essential to maintaining the continued reliability of the BPS. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RFC_URE1 failed to fully comply with CIP-004 R4 at all times, the violation constituted an exception to an otherwise strong compliance program. For example, one failure to revoke access involved a deceased employee and in both cases the employees in question had undergone personnel risk assessments and cyber security training.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012173 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-006-3 R5. RFC_URE1's communications group was performing work at a substation identified as a Critical Asset. This work required RFC_URE1 to shut down power to its security system used to monitor access to the Physical Security Perimeter (PSP) protecting this substation. The security system operated on backup battery power until ultimately failing. The failure generated an error message to RFC_URE1's security group, but RFC_URE1 did not recognize the cause as a loss of power. Upon returning to work three days later, RFC_URE1's security group discovered that the security system had lost power, and RFC_URE1 took prompt corrective actions. While this security system was inoperable, RFC_URE1 failed to monitor the access points to the PSP surrounding the substation. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation of CIP-006-3c R5 posed a minimal risk because the security system at issue failed to a secure state, where physical access was locked. Therefore, despite RFC_URE1's inability to monitor access to the substation, the substation was nevertheless protected from physical intrusion. Furthermore, RFC_URE1 investigated for evidence of physical and logical intrusions at the substation and discovered no evidence of any. | when the security system failed due to power loss | when RFC_URE1 restored power to the security system) | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Self-Report | To mitigate this violation, RFC_URE1 will: 1) detail the steps it took to restore power to the security system at issue; 2) investigate the error message; 3) ensure that power is not inadvertently shut off in the future; and 4) implement procedural controls to prevent a similar issue from occurring in the future. | 2013-08-30 | TBD | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program as a mitigating factor in penalty determination. RFC_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RFC_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure its continued observance of the NERC Reliability Standards. RF also applied mitigating credit to RFC_URE1's self-reported violations. RFC_URE1's Self-Reports evidence a full understanding of the issues presented, described the immediate steps taken by RFC_URE1 to minimize reliability risks, and provided RF with sufficient information to analyze the violations. Such timely and robust Self-Reports are essential to maintaining the continued reliability of the BPS. RF assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RFC_URE1 failed to fully comply with CIP-006 R5 at all times, the violation constituted an exception to an otherwise strong compliance program. For example, although RFC_URE1 failed to monitor access points to a PSP during an equipment failure, the equipment was configured to fail to a secure state and RFC_URE1 took prompt corrective action once aware of the problem.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010103 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. RF_URE2 discovered that it did not afford the protective measures specified in CIP-006-1 R2.2 to its Physical Control System. RF_URE2 did not include the device in its original scope of its CIP compliance effort. Further, RF_URE2 did not address testing of signatures in its process for updating antivirus and malware prevention signatures as applicable to the device. | CIP-006-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because if Cyber Assets that authorize and log access to the Physical Security Perimeter (PSP) do not receive the required protective measures, the Critical Cyber Assets within the PSP are at an increased risk of unauthorized access. The risk was mitigated in this case because the devices were located within a PSP during the duration of the violation. Further, one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the one device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter (ESP) capable of performing testing of antivirus and malware signatures. | 2012-12-14 | 2013-03-28 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010167 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R8. RF_URE2 determined that it did not conduct a review of ports and services associated with non-critical Cyber Assets located within an Electronic Security Perimeter (ESP) as part of its annual Cyber Vulnerability Assessments (CVAs). | CIP-007-1 | R8; R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 conducted its CVA at the earliest possible date and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. RF_URE2 now includes a review of all ports and services in its annual Cyber Vulnerability Assessment. | 2012-07-31 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010168 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-003-1 R6. RF_URE2 determined that it did not have a configuration management program to document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs). | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of CIP-003-1 R6 has the potential to affect the reliable operation of the BPS, by providing the opportunity to exploit vulnerable CCAs after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs. The risk was mitigated because RF_URE2 had a change control process in place during the duration of the violation. Additionally, RF_URE2 represents that personnel were aware of system changes and that it reviewed all changes to its CCAs. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2: 1) documented a configuration management process that includes initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-05-08 | 2013-05-29 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010169 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R4. RF_URE2 determined that it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter (ESP) were required for operation when it performed its Cyber Vulnerability Assessments (CVAs). RF_URE2 could provide a list of running ports and services for its CVA, but it could not verify that these ports and services were required for operation. Additionally, RF_URE2 could only provide a table indicating that it completed a review of all ports and services during its later CVA. | CIP-005-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 confirmed upon completion of the CVA that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 completed its CVA during which it verified that only ports and services located on electronic access points and required for operation were enabled. | 2012-05-31 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010170 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R3. RF_URE2 determined that it had not established, documented, or implemented a security patch management program for tracking, evaluating, testing and installing applicable cybersecurity software patches for all Cyber Assets within an Electronic Security Perimeter (ESP). | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 implemented a security patch management program for its CCAs during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 documented a security patch management program and filed Technical Feasibility Exception requests for those Cyber Assets that could not be patched. | 2012-07-31 | 2013-05-02 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010171 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R1. RF_URE2 determined it did not create, implement or maintain test procedures for Cyber Assets residing within one Electronic Security Perimeter (ESP). RF_URE2 did have test procedures for Critical Cyber Assets (CCAs) residing with the ESP during the duration of the violation. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because the Cyber Assets for which RF_URE2 did not have test procedures were non-critical Cyber Assets. Further, during the duration of the violation, none of the non-critical Cyber Assets at issue experienced significant changes that would have necessitated RF_URE2 to implement the test procedures mandated by CIP-007-1 R1. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 developed specific documented testing procedures for all Cyber Assets located within its ESP. | 2012-08-20 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2011001271 | Settlement Agreement | RF_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-1 R2. RF_URE3 discovered that it did not afford the protective measures specified in CIP-006-1 R2.2 to its Physical Control System. RF_URE3 did not include the device in its original scope of its CIP compliance effort. Further, RF_URE3 did not address testing of signatures in its process for updating anti-virus and malware prevention signatures as applicable to the device. | CIP-006-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because if Cyber Assets that authorize and log access to the Physical Security Perimeter (PSP) do not receive the required protective measures, the Critical Cyber Assets within the PSP are at an increased risk of unauthorized access. The risk was mitigated in this case because the devices were located within a Physical Security Perimeter (PSP) during the duration of the violation. Further, the one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Self-Report | To mitigate this violation, RF_URE3: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the one device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter (ESP) capable of performing testing of anti-virus and malware signatures. | 2012-12-14 | 2013-03-28 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010104 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-003-1 R6. ReliabilityFirst discovered that RF_URE3 did not have a configuration management program to document all entity or vendor related changes to hardware and software components of Critical Cyber Assets (CCAs). RF_URE3 did provide an established change control process to ReliabilityFirst during the Compliance Audit. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because a violation of CIP-003-1 R6 has the potential to affect the reliable operation of the BPS, by providing the opportunity to exploit vulnerable CCAs after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs.The risk was mitigated because RF_URE3 had a change control process in place during the duration of the violation. Additionally, RF_URE3 represents that personnel were aware of system changes and that it reviewed all changes to its CCAs. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance-Audit | To mitigate this violation, RF_URE3: 1) documented a configuration management process that includes initial baseline configurations of applicable Cyber Assets: 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-05-08 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010105 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-005-1 R4. ReliabilityFirst determined that RF_URE3 did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter (ESP) were required for operation when it performed its cyber vulnerability assessment (CVA). RF_URE3 provided a list of running ports and services for its CVA, but could not verify that these ports and services were required for operation. RF_URE3 did not provide a list of running ports and services for its CVA, but rather a table indicating that it completed a review. | CIP-005-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 confirmed upon completion of the CVA that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 completed its CVA and verified that only ports and services located on electronic access points and required for operation are enabled. | 2012-05-31 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010106 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R1. ReliabilityFirst determined that RF_URE3 did not create, implement or maintain test procedures for Cyber Assets residing within one Electronic Security Perimeter (ESP). During the Compliance Audit, RF_URE3 was able to provide test procedures to ReliabilityFirst for Critical Cyber Assets (CCAs) residing with the ESP. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because the Cyber Assets for which RF_URE3 did not have test procedures were non-CCAs. Further, during the duration of the violation none of the non-CCAs at issue experienced significant changes that would have necessitated RF_URE3 to implement the test procedures mandated by CIP-007-1 R1. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 developed, implemented, and maintains specific documented testing procedures for all Cyber Assets located within its ESP. | 2012-08-20 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010107 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R3. ReliabilityFirst discovered that RF_URE3 did not establish, document, or implement a security patch management program for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets within an Electronic Security Perimeter (ESP). | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 implemented security patch management program for its CCAs during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 documented a security patch management program and filed Technical Feasibility Exception requests for those Cyber Assets that cannot be patched. | 2012-07-31 | 2013-05-02 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010109 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R8. ReliabilityFirst determined that RF_URE3 could not provide evidence that it conducted a review of ports and services associated with non-Critical Cyber Assets located within an Electronic Security Perimeter (ESP) as part of its annual cyber vulnerability assessments (CVAs). | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 conducted its CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP are enabled. | 2012-06-04 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000743 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R4.1. SERC_URE1 failed to implement anti-virus and malware prevention tools on all Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 had a process in place for updating malware signatures as required by CIP-007-1 R4.2. While conducting a single on-demand scan of Cyber Assets within an ESP in an effort to enhance security, SERC_URE1 discovered that the malware prevention software was not performing as expected on one Cyber Asset, a server used to exchange data with a neighboring utility. After the discovery of the problem with the malware prevention software, SERC_URE1 initiated an immediate investigation. SERC_URE1 preliminarily concluded that the malware prevention software package had been loaded onto the Cyber Asset but the installation package had not been executed to complete the installation. SERC_URE1 rebooted the server and successfully loaded the malware prevention signatures. SERC_URE1 scanned all other Cyber Assets within the control center ESPs and discovered no other security problems. All of SERC_URE1’s remaining Cyber Assets had malware prevention software loaded properly (as technically feasible) and all signatures were found to be current. | CIP-007-1 | R4, R4.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had secured ports and services through its electronic access control and monitoring (EACM) devices to only those required for normal and emergency operations. SERC_URE1 reviewed the access logs from the EACM devices and found they contained no malicious activity that would have created alerts for investigation. All access from outside the ESP requires two-factor (strong) authentication and no internet access is permitted for these isolated networks. SERC_URE1 conducted a full scan of the network after successfully loading the anti-malware software and found no infections or potentially unwanted programs present. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) revised its malware prevention software implementation and monitoring process to ensure that malware prevention software is verified to be functioning as required following installation. IT administrators subsequently monitor the malware prevention software for proper operation, and appropriate IT personnel are promptly notified of any functional concerns; and 2) instituted a quarterly review to verify that the list of Cyber Assets monitored by malware prevention software administrators includes all Cyber Assets within the ESP that, where technically feasible, are required to comply with CIP-007 R4. To accomplish this, SERC_URE1 compared Cyber Asset lists and reconciled discrepancies as appropriate. | 2/28/2011 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000751 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-1 R1.6. SERC_URE1 failed to maintain documentation of all interconnected Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). SERC_URE1 conducted an internal review of its ESP documentation. During that review, SERC_URE1 discovered four types of Cyber Assets within the ESPs that were not documented on the ESP diagrams. The four types of Cyber Assets were: 1) keyboard/video/mouse (KVM) switches (used to toggle between the device interfaces) in one control center ESP; 2) a tape library; 3) routers; and 4) Voice over Internet Protocol (VoIP) phones. While the routers were located within an ESP and Physical Security Perimeter (PSP), the VoIP phones were not. After this discovery, SERC_URE1 conducted a full scan for all devices on its ESPs and found no additional devices. SERC determined that SERC_URE1 failed to maintain the required documentation of all Cyber Assets within the ESP. SERC_URE1 had a process for creating and maintaining ESP documentation, but the process lacked the level of detail required for an employee to know what to include and what to exclude in the ESP documentation. As a result, SERC_URE1 missed four types of Cyber Assets when it created the original list of CCAs and Cyber Assets within the ESP. | CIP-005-1 | R1, R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to maintain documentation of the overlooked Cyber Assets could have left those affected Cyber Assets without proper security measures and presented an attack path for potential hackers. However, the KVM switches, the tape library, and phone system routers resided within a secured PSP and ESP. The VoIP telephones, although not secured within the official PSP and ESP, were in a secured facility that was staffed 24 hours a day, seven days a week, monitored by cameras, and secured with restricted card key access. SERC_URE1's electronic access control and monitoring devices did not detect any conditions for the involved ESPs that required investigation. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 removed the overlooked Cyber Assets from the ESPs | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) revised the existing control center ESP documentation process to ensure that all interconnected non-critical Cyber Assets and CCAs within control center ESPs are addressed in ESP diagrams; 2) modified scan tools to instruct performers directly on how to perform full network scans instead of partial network scans; and 3) relocated the non-essential Cyber Assets that were in the ESP outside of the ESP. | 2011-02-28 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008285 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004 R4.2. SERC_URE1 failed in two instances to revoke an individual’s access to Critical Cyber Assets (CCAs) within seven calendar days when the access was no longer required. In the first instance, an employee’s NERC training qualification expired due to a failure to renew the training by the SERC_URE1 specified deadline. This employee had access to the physical access control system (PACS) via remote token access, which in turn required active directory access. SERC_URE1 had an automated system in place to alert the IT security group responsible for revocation of CCA access to the expiration of the employee's NERC training. Due to human error, SERC_URE1 did not remove the employee’s remote token access until 16 days after the revocation was requested, causing it to be nine days late. The employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. During this period, the employee did not attempt to use his or her access to the PACS. In addition, the employee continued to be in good standing with SERC_URE1 and had a valid Personal Risk Assessment (PRA). In the second instance, SERC_URE1 had an automated process in place to alert the IT security group responsible for revocation of CCA access when an employee with CCA access had a job duties change. The IT security group would be responsible for reviewing and removing CCA access as required. This automated process failed due to the server freezing and did not resume until 15 days later when regular maintenance tasks were performed and the server was rebooted. At this time, SERC_URE1 did not have any means of remotely monitoring whether the server was operating normally. Upon reboot, pending revocation alerts that were hung-up in the server were sent and acted on the same day. One alert required SERC_URE1 to remove an employee’s CCA access due to a job change that did not require CCA access. This employee had access to three Physical Security Perimeters that contained Cyber Assets used as electronic access control and monitoring devices and PACS. SERC_URE1 did not remove the employee’s access until 15 days after the date the revocation was requested, causing it to be eight days late. During this period, the employee did not use his or her physical access privileges. In addition, the employee continues to be in good standing with SERC_URE1 and had a valid PRA. | CIP-004-1 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These failures were limited to two separate instances, and the employees involved were in good standing with the company for the entire period in question, and remained in good standing after the violation end date. Both employees had current PRAs. In the first incident, the employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. Neither individual at issue used or attempted to use his or her access during the violation. | eight days after the first individual no longer needed access | when SERC_URE1 revoked access for the second individual | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: For the first instance: 1) implemented a new access revocation application that lists each task required to be performed; and 2) re-trained the group responsible for completing the revocation on the process and the associated responsibilities and reminded of the critical nature of removing NERC access within the allowed window of time. For the second instance: 1) confirmed that the delayed notifications were processed on the same day they were received; 2) ensured that the process for sending notifications was monitored; 3) determined the scope of the problem resulting from the hung system processes; 4) determined if there were any other previous incidents; 5) ensured that automated monitoring with alerting was in place for access revocation workflows within the future access revocation application; and 6) implemented the rewritten access revocation application and retired the old application. New functionality exists in the rewritten application to provide real-time visibility into the state of revocation tasks associated with NERC assets through automated reports, and through the user interface. | 2011-03-17 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008331 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that, as a Load Serving Entity and Transmission Owner, it was in violation of CIP-007-1 R3.1. SERC_URE1 failed to assess security patches within 30 calendar days. SERC_URE1 had a program that required the assessment of security patches and security upgrades for applicability within 30 calendar days of availability. SERC_URE1 discovered the identified security patches in three separate investigations which found that the missed security patches affected Critical Cyber Assets (CCAs) and non-critical Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 conducted an internal review of its patch management process. SERC_URE1 discovered that it had assessed the applicability of ten security patches for seven software products outside of the 30-day window. SERC_URE1 determined that it had taken between 81 and 313 days from the release dates of these ten security patches to assess their applicability. The individual responsible for conducting the security patch assessment failed to match the released security patches to the software inventory spreadsheet correctly. SERC_URE1 made a second discovery when a subject matter expert familiar with the product realized it was not running the latest software package. SERC_URE1 conducted an immediate review and found that the software in question was not on the software inventory spreadsheet at all. SERC_URE1 determined that it had not assessed the applicability of five security patches within 30 calendar days of their availability. SERC_URE1 assessed the applicability of the five security patches on the same day and determined that it had taken between 41 and 333 days from the release of the five security patches to assess their applicability. SERC_URE1 made a third discovery when a subject matter expert reviewed the software inventory spreadsheet and identified that software for one device was not current. In this case, the individual responsible for the review of newly released security patches incorrectly assessed that the security patch was not applicable. SERC_URE1 determined that it had taken 41 days from the release of the security patch to correctly assess the applicability of the patch. SERC_URE1 submitted a second Self-Report to SERC stating that it was in violation of CIP-007-3 R3.1 because it had failed to include a software application in its inventory of software applications when it was installed. SERC determined that this violation was related to the initial Self-Report and decided to treat the Self-Report as an expansion of scope of the violation. SERC_URE1 discovered this violation during an internal review of the security patch alert process. SERC_URE1 determined that it had not assessed the applicability of two software releases addressing three security vulnerabilities within 30 calendar days as required. The next day SERC_URE1 assessed both security patches for applicability and determined that it had taken between 64 and 275 days from the release of the two security patches to assess their applicability. In total, SERC_URE1 failed to assess 18 security patches for ten different software products within 30 days of the release of the security patches. | CIP-007-1 | R3, R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure timely to assess 18 security patches and updates on ten different software products left software on the involved Cyber Assets vulnerable for extended periods of time, increasing the risk of a successful cyber attack against CCAs or Cyber Assets that could have resulted in operational impacts and potential degradation of the BPS. However, all of SERC_URE1’s Cyber Assets resided within secured ESPs and Physical Security Perimeters and access to Cyber Assets from outside the ESP required two-factor (strong) authentication. SERC_URE1’s electronic access control and monitoring devices did not identify any malicious activity during the violation that would have impacted the involved Cyber Assets. | 31 calendar days after the release of the first security patch | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: For the first Self-Report: 1) modified its patch management alert process procedure to provide additional guidance to check for the version shown or any later versions to ensure that security patch applicability is correctly determined; 2) verified that all security patches issued were assessed based on the software inventory for the affected CCAs and all other Cyber Assets within the ESP; 3) assessed the missed patches identified and documented the assessment. In addition, it reviewed and augmented the software inventory methodology and then ran the new software inventory methodology against the current Cyber Asset list; 4) assessed and implemented the missing patch identified and scheduled the implementation of the missing patch; and 5) modified the patch management alert process procedure to provide additional instructions regarding the alert process and ensured that subject matter experts were made aware of the change. For the second Self-Report: 1) improved the patch assessment process by automating the patch assessment alert process; 2) modified the change management procedures to include a step for adding newly installed software to the NERC patch management inventory and assessing applicable security patches prior to commissioning the asset; 3) enhanced the patch assessment procedures to ensure that all applicable security patches or upgrades were assessed prior to the installation of new software on an existing device; and 4) communicated the changes in the patch assessment procedures to all supporting personnel. | 2012-03-27 | 2013-06-28 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC determined that SERC_URE1's prior compliance history was an aggravating factor in the penalty determination
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009651 | Settlement Agreement | SERC_URE1 submitted a Self-Certification to SERC stating that it was in violation of CIP-007-3 R2.1. SERC_URE1 discovered three ports and two services not used for normal and emergency operations that were enabled on a device. SERC_URE1 had a process in place for ensuring only ports and services required for normal and emergency operations were enabled that involved using the discovery command provided by the vendor of the Cyber Assets. However, SERC_URE1 had three switches in separate Electronic Security Perimeters (ESPs) that retained three default open ports associated with three services that were not required for normal or emergency operations. In addition, SERC_URE1 had four routers in additional ESPs that had the same ports and services enabled as the switches, plus two additional services with no associated ports that were not required for normal or emergency operations. All of the switches and routers were protected by a Physical Security Perimeter (PSP). SERC_URE1 was unaware of these ports and services until it ran a user datagram protocol port scan. SERC_URE1 had disabled all unused ports and services or, in the case where such unused ports and services could not be disabled due to technical limitations, adopted compensating measures and filed a Technical Feasibility Exception request. In addition, SERC_URE1 modified the process for identification of open ports and services to use different tools for the discovery of enabled ports and services. | CIP-007-1 | R2, R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected Cyber Assets resided behind secured firewalls which restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and PSP. The routers and switches were subject to logging and monitoring for cybersecurity events. Firewalls protecting the affected ESPs employed intrusion detection prevention (IDP) controls which monitored the firewall for cybersecurity events. IDP triggered events were sent to the firewall management station in real-time for monitoring and analysis. IDP signatures were downloaded from the firewall vendor daily to ensure they were up-to-date. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Certification | To mitigate this violation, SERC_URE1: 1) disabled unused ports and services on the three identified devices; 2) applied an access control list to block the unnecessary port on the three identified devices; 3) disabled unused services on the four identified routers; and 4) revised and implemented procedure enhancements to the network operations testing process document, which now includes commands used to verify ports. | 2012-05-08 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012010509 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-2 R4.2. SERC_URE1 failed to revoke five contract employees’ access to Critical Cyber Assets (CCAs) within seven calendar days of when the access was no longer required. SERC_URE1 subsequently determined that one of the contractors required ongoing access and should not have been included in the Self-Report. Thus, SERC_URE1 failed to revoke four contractors’ access to CCAs within seven calendar days of when the access was no longer required. SERC_URE1 had a process in place for the revocation of physical access to CCAs for employees by deactivating their enterprise ID, consisting of a username and password, leaving them unable to attain a key card required for physical access. However, this process did not adequately address the contingent workforce (e.g., contractors) utilized by SERC_URE1. SERC_URE1 discovered that it had not revoked a contractor’s physical access to CCAs within seven days of the date on which the contractor no longer required such access. During an internal assessment, SERC_URE1 found that it had not revoked the physical access to CCAs of three other contractors within the required seven days. SERC_URE1 removed the four contractors' physical access to CCAs between 20 and 244 days late. SERC_URE1 determined that its process did not clearly delineate whether SERC_URE1 management or the contingent workforce company should contact SERC_URE1’s access control office to notify it to deactivate the workers’ access at the end of the workers’ assignments. SERC_URE1 collected the contractors’ key cards that gave them physical access to CCAs on or prior to their respective end dates. | CIP-004-2 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These failures were limited to four separate instances, and the contractors involved did not attempt to obtain a key card that would be required to gain physical access to CCAs. The contractors had valid personal risk assessments, were current in their NERC CIP training, and were in good standing with SERC_URE1 during the periods in question and after the violation was resolved. | eight days after the first contractor no longer needed physical access to CCAs | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) established a procedure to run a report twice a week to review all open assignment date requisitions. If an employee's reporting manager does not respond within three days, the employee's enterprise ID will be deactivated, thereby revoking access; 2) changed email notifications to define more clearly the steps the reporting managers must take to end the assignment; and 3) placed a new banner on an internal website to raise awareness and help managers understand what actions are required of them when ending contractor assignments. | 2012-03-16 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011334 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE1 failed to adequately test and ensure that the upgrade of its physical access control system (PACS) did not adversely affect existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 had previously submitted a Self-Report to SERC addressing this violation, but stated that it was in violation of CIP-007-1 R1. After a preliminary review, SERC determined that the violation was more appropriately addressed under CIP-006-1 R1.8. SERC_URE1 had a testing program and procedures for adding new Cyber Assets and for significant changes to existing Cyber Assets within the ESP to ensure that significant changes do not affect existing cybersecurity controls. SERC_URE1 did not test the cybersecurity controls during an upgrade of the PACS. It did, however, confirm that the individuals with physical access to Critical Cyber Assets (CCAs) did not change as a result of the PACS upgrade. SERC_URE1, in following the advice of the vendor, incorrectly classified significant changes to the PACS systems as minor. SERC_URE1 has a process in place that monitors and alerts IT when any change is made to the PACS. This process alerted IT that there had been a change to the PACS as a result of an upgrade. An internal subject matter expert followed up on an inquiry from IT regarding the change and reviewed the change that was implemented. The internal subject matter expert determined that the change was significant and that SERC_URE1 should have tested and documented the PACS upgrade to ensure it did not adversely impact the existing cybersecurity controls. This violation affected five PACS servers used by SERC_URE1 to log and monitor its Physical Security Perimeters (PSPs) and impacted both production and failover systems. Despite this failure, SERC_URE1 completed a review and comparison of security controls after the changes had been implemented. While gathering information to respond to SERC questions regarding the scope of the violation, SERC_URE1 discovered seven earlier instances in which it implemented significant changes to the PACS without testing to ensure the changes did not adversely affect the existing cybersecurity controls. In these prior instances, SERC_URE1 determined that the significant changes to the PACS had no effect on its cybersecurity controls. | CIP-006-1 | R1, R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, potentially altering the existing cybersecurity controls. If the PACS servers were compromised due to an undocumented significant change, unauthorized individuals could gain physical access to CCAs and non-critical Cyber Assets and modify or disrupt their normal operation. However, in all eight instances in which SERC_URE1 implemented significant changes to the PACS without testing, it performed some functional testing on the PACS after implementation on the production environment that demonstrated the PACS’ operational functions were intact. SERC_URE1 utilizes a tool that alerts its IT in real time when changes in cybersecurity controls are detected. The seven earlier significant changes to the PACS had no impact on SERC_URE1’s cybersecurity controls. | when SERC_URE1 implemented the first significant change to the PACS system without testing | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) enhanced its cybersecurity test procedures to incorporate specific steps related to the testing of cybersecurity controls, including user account configuration changes and password configuration and parameter changes; 2) enhanced its cybersecurity test procedures to include a ports and service scan and comparison in coordination with any change that is made to the PACS baseline, regardless of the significance of the change; and 3) implemented a new testing threshold that characterizes all subsequent changes to PACS as significant by default, regardless of the change type, and requires the execution of the cybersecurity test procedures to confirm that cybersecurity controls have not been adversely affected by the changes. | 2012-03-30 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011760 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3 R3.1. SERC_URE1 failed to assess the applicability of security patches within 30 calendar days of their availability. SERC_URE1 had a security patch management program that required the assessment of security patches and security upgrades for applicability within 30 calendar days of their availability. SERC_URE1 identified a security upgrade that was not reviewed for applicability within 30 days. The security upgrade was applicable to four servers that were non-critical Cyber Assets within an Electronic Security Perimeter (ESP). SERC_URE1 assessed the security upgrade 64 days after the vendor released it and 34 days after the required date. SERC_URE1 determined that the root cause of this violation was a human performance failure. While this specific security upgrade was correctly identified and associated with a number of other Cyber Assets, the SERC_URE1 IT security staff responsible for the review and assessment of security patches failed to associate this single security upgrade properly with all associated Cyber Assets. | CIP-007-3a | R3, R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that this violation posed a moderate risk because SERC_URE1’s failure to assess security patches and updates within 30 days of their availability left software on the affected Cyber Assets vulnerable for an extended period, increasing the risk of a cyber attack that could have resulted in operational impacts and potential degradation of the BPS. However, all the affected Cyber Assets resided within secured ESPs and Physical Security Perimeters and access from outside the ESP was limited and restricted. SERC_URE1’s electronic access control and monitoring devices were monitoring and alerting for unusual activity and did not identify any malicious activity that would have impacted the affected Cyber Assets. This violation affected only one security upgrade on four servers that were non-critical Cyber Assets | 31 days after the security patches were available | when SERC_URE1 assessed the applicability of the security patch | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1 implemented an automatic risk alert solution which matches asset inventory to the monitored software products and automatically creates alerts for the asset owners to assess within the 30-day requirement. | 2012-10-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011762 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-3 R4.2. SERC_URE1 failed to revoke access to Critical Cyber Assets (CCAs) within seven calendar days of when the access was no longer required for four personnel. SERC_URE1 had an internally developed application to facilitate the revocation of physical access to CCAs for personnel who no longer required such access. SERC_URE1 discovered that this application had a bug in the code which resulted in a large number of duplicate records. The volume of duplicate records being processed by the application resulted in the production database failing to process alert emails, leaving the emails in a pending state. Once SERC_URE1 discovered and resolved this violation, it discovered that it had not revoked four SERC_URE1 employees’ physical access to CCAs within seven days of when that access was no longer required. Three employees retained access to all substation Physical Security Perimeters (PSPs) containing CCAs and one employee retained access to two substation PSPs containing CCAs. The employees retained access from one day to eight days beyond the seven days allowed by CIP-004-3 R4. | CIP-004-3 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected individuals did not attempt to access the PSPs containing CCAs after they no longer required access. All involved personnel had valid personnel risk assessments and were current in their NERC CIP training. This violation was limited to four individuals who were in good standing with SERC_URE1 for the entire period in question and remained in good standing after this violation was resolved. | eight days after the employees no longer required access to CCAs | when SERC_URE1 revoked the final employee’s access | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) created and implemented a script to remove duplicate records from the application which facilitates the revocation of access to CCAs; 2) enhanced the access revocation application to attempt to resend all failed notifications; and 3) optimized the access revocation database to reduce the likelihood of a notification time-out condition. | 4/6/2013 | 2013-07-17 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011764 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE1 had failed to afford Cyber Assets used in the access control and monitoring of the Physical Security Perimeters (PSPs) the protective measures specified in R1.8 in two instances. In the first instance SERC_URE1 discovered five dial-up modems that were being used to provide communications to the Physical Access Control System (PACS) server. As such, the five modems were Cyber Assets used in the access control and monitoring of the PSP. The communication between the five modems and the PACS server was a serial connection. However, SERC_URE1 failed to afford the five dial-up modems the protective measures specified in CIP-005-1 R2.3. SERC_URE1 failed to maintain a procedure for securing dial-up access to the PACS devices. Upon identification of this violation, SERC_URE1 investigated to ensure and confirm that the newly discovered dial-up connections were secured. SERC_URE1 also verified that no other dial-up connections existed in its broader CIP program. In the second instance, SERC_URE1 learned that its existing interpretation of what Cyber Assets should be included in a PACS was incomplete. A third-party consultant concluded a review of SERC_URE1’s CIP compliance program. After reviewing the consultant’s recommendations, SERC_URE1 determined that it had not been sufficiently inclusive in its assessment of what Cyber Assets made up its PACS. Originally, SERC_URE1 identified the PACS server as the only Cyber Asset associated with the PACS that fell within the scope of the CIP Standards. After the consultant’s review, SERC_URE1 identified additional card reader control panels and PACS workstations that should have been considered as PACS devices. SERC determined that SERC_URE1 was in violation of CIP-006-1 R1.8 because it failed to afford the card readers control panels and workstations used to manage the PACS devices the protective measures specified in CIP-006-1 R2. Specifically, SERC_URE1 could not implement operational and procedural controls to manage physical access at all access points to the PSP without identifying these Cyber Assets as PACS devices. | CIP-006-1 | R1, R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All dial-up communications between the five modems and the PACS server were encrypted and secured using a passcode that was securely maintained by technical security personnel. SERC_URE1 knew of the existence of the Cyber Assets that were newly identified as PACS devices and afforded them defense-in-depth security under a broader corporate security initiative. All card reader control panels were located inside PSPs and were within secured cabinets with tamper alarms. All workstations used to manage the PACS devices were subject to corporate policies for change management, patch management, and access control. System monitoring logs indicated no attempts to compromise or actual compromise of any PACS panels. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) submitted technical feasibility exceptions where it was not technically possible to comply with standards regarding the protections applicable to the PACS panels and dial-up access to the electronic perimeter; 2) implemented primary and secondary dedicated workstations within the PACS PSP and electronic security perimeter (ESP); 3) developed and implemented a procedure for securing dial-up access for modems accessing the PACS ESP or remove the dial-up access points from the ESP altogether; and 4) implemented changes necessary to ensure that PACS panels are afforded the protective measures identified in CIP 006-3 R2.2 where technically feasible. | 8/1/2013 | 2013-10-23 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011766 | Settlement Agreement | SERC_URE1 submitted two Self-Reports to SERC stating that it was in violation of CIP-006-3 R2.2. SERC_URE1 failed to afford its Physical Access Control Systems (PACS) the protective measures specified in R2.2. In the first instance a support vendor for the SERC_URE1 PACS system failed to test appropriately a change to the PACS system prior to implementing the change into production. SERC_URE1 had previously decided that all changes to PACS would be considered significant and would be tested and approved prior to implementation. SERC_URE1 had explained its change control process to the PACS support vendor. The PACS support vendor misunderstood the SERC_URE1 requirements and believed that simple parameter changes in the PACS were not considered significant. A SERC_URE1 subject matter expert (SME) became aware of the implemented change through regular communications with the PACS support vendor. SERC_URE1 rolled back the change in order to ensure the integrity of the PACS system and allow proper testing of the change to occur. However, SERC_URE1 had the untested and unapproved change in service on the production PACS system for three days. SERC determined that SERC_URE1 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R1. After a review by the SERC_URE1 SME and the support vendor, SERC_URE1 determined that no other changes had been implemented outside of the established change management process. In the second instance SERC_URE1 discovered that it had not assessed a security patch for a PACS server for 96 days. The patch was released by the vendor but was not assessed for applicability to the PACS server until 96 days after it was made available by the vendor and 66 days after the required date. This second instance was initially reported under CIP-007-3 R3.1 (NERC Violation ID SERC2013011760), but SERC determined that the violation was more appropriately addressed under CIP-006-3 R2.2 because it involved PACS devices. SERC determined that SERC_URE1 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R3.1. | CIP-006-3c | R2, R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The unauthorized change was to a parameter file that affected reporting capabilities only, and did not impact or affect the security controls of the PACS. Remote panels at the Physical Security Perimeter (PSP) locations would have continued to operate autonomously and any alarms generated would have been queued by the panels and sent to the central server when it became available. SERC_URE1 utilizes a tool for real time alerting when changes in cybersecurity controls are detected. All personnel working for the PACS support vendor had received the required cybersecurity training, had a current personnel risk assessment, and were authorized by SERC_URE1 to work on its PACS. The failure to assess a security patch for the PACS server within 30 days affected only one security upgrade on a single PACS server. The PACS server resided within a secured Electronic Security Perimeter (ESP) and PSP and access from outside the ESP was limited and restricted. SERC_URE1’s electronic access control and monitoring devices did not identify any malicious activity that would have impacted the involved PACS server. | when the SERC_URE1 support vendor made the untested and unauthorized change to the PACS and 31 days after the missed security patch was available for assessment | when SERC_URE1 rolled back the untested and unauthorized change and when SERC_URE1 assessed the security patch | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) sent notification via email to the support vendor informing them to return SERC_URE1's issued laptops and tokens. The email further described that SERC_URE1's IT personnel would be the proxy if any remote access was required going forward; 2) received all three SERC_URE1's issued laptops and tokens from support vendor and submitted requests to have the laptops decommissioned; and 3) implemented an automatic risk alert solution which matches asset inventory to the monitored software products and automatically creates alerts for the asset owners to assess within the 30-day requirement. | 2012-10-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011767 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R2.1. SERC_URE1 failed to enable only those ports required for normal and emergency operations. SERC_URE1 identified four Critical Cyber Assets (CCAs) that had open ports that were not required for normal or emergency operations. SERC_URE1 discovered this violation as a result of its cyber vulnerability assessment. Three of the four routers were located within a SERC_URE1 Electronic Security Perimeter (ESP). The fourth router was located within another ESP. Each router had eight serial interfaces, and each serial interface contained four open transmission control protocol (TCP) ports, resulting in 32 open ports on each router, for a total of 128 open ports. SERC_URE1 started mitigating activities in its testing environment, which included blocking the unused and unneeded ports. SERC_URE1 initiated a review of all other ESPs. SERC_URE1 determined that no other similar violations existed within SERC_URE1 or its affiliates. SERC_URE1 updated the first three production and disabled the unused and unneeded ports. SERC_URE1 updated the fourth router and disabled the unused and unneeded ports. | CIP-007-1 | R2, R2.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to disable open ports on CCAs within the ESP could have allowed access to and the exploitation of the CCAs. This failure could limit, or render inoperable, SERC_URE1’s operational capabilities, remote control of Critical Assets, and situational awareness of BPS components into the energy management system. However, SERC_URE1 provided the devices involved in this violation with a defense-in-depth strategy. The devices resided behind secured firewalls that had a “deny by default” rule and restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and Physical Security Perimeter. The firewalls protecting the devices also employed intrusion detection prevention (IDP) controls that monitored the firewalls for cybersecurity events. IDP-triggered events were sent to the firewall management station in real-time for monitoring and analysis. SERC_URE1 downloaded IDP signatures from the firewall vendor on a daily basis to keep them up-to-date. In addition, the devices were subject to logging and monitoring for cybersecurity events. Where technically feasible, all Cyber Assets within the ESP were running malware protection. There are no known vulnerabilities or exploits associated with the open ports that could be used to disrupt, degrade or otherwise misuse the routers or terminal servers connected to these devices. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) determined the ports and services necessary for normal and emergency operations; 2) performed a TCP port scan; 3) developed an access control list (ACL) which blocked access to unused ports; 4) applied the ACL to the test device, performed a port scan, and verified the unused ports were blocked; 5) applied configuration changes in production which blocked the unused ports; 6) completed production configuration changes which blocked the unused ports; 7) added a task to the network operations group's CIP-007 annual review; 8) communicated the changes in the systems security management procedure to all affected personnel; and 9) completed production configuration changes which blocked the unused ports. | 2013-03-14 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000603 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R6.4. SERC_URE2 failed to retain all system event logs related to cybersecurity for 90 calendar days. SERC_URE2 had implemented and documented organizational processes and technical and procedural tools to monitor for cybersecurity events on all Cyber Assets within the Electronic Security Perimeter (ESP). The automated tools alert on any cybersecurity event detected and would allow for retention of logs associated with any cybersecurity event and for further review as required. However, some device logs were configured to capture all event logs, not just cyber events. Due to the large amount of logs generated by patching, the local memory filled and began to overwrite existing data. SERC_URE2 discovered the violation during an internal review of the 90-day retention requirement and immediately initiated an internal investigation. SERC_URE2 concluded its investigation, and found that six Critical Cyber Assets (CCAs) and four non-critical Cyber Assets, in several ESPs, were missing log data for various periods. SERC_URE2 modified the maximum file size for its cybersecurity logs and the overwrite thresholds on all CCAs and Cyber Assets to prevent overwriting logged events that were less than 90 days old. SERC_URE2 determined that the logs for the ten devices in question had been overwritten and were unrecoverable. SERC_URE2 started conducting daily manual backups of the logs to prevent further overwrites and alleviate any more potential non-compliance. | CIP-007-1 | R6; R6.4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because, in the event of a cybersecurity incident, SERC_URE2’s failure to retain logs related to security events for 90 calendar days on the 10 CCAs and Cyber Assets could have resulted in the loss of important security information required for a thorough investigation. However, this failure was limited to CCAs and Cyber Assets that were spread across four separate ESPs, which further reduced potential attack vectors and impacts. SERC_URE2 reviewed all accesses to the ESP and Physical Security Perimeters and found no unauthorized accesses or access attempts. Malware prevention and other security controls remained operational and up-to-date for the time period in question. SERC_URE2 did not discover or detect any cybersecurity events, including the discovery of malware, during the violation period. | the first day logs were overwritten | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) reviewed and modified, as necessary, the local audit policies associated with the logging of cybersecurity to ensure that only events related to cybersecurity are written to the cybersecurity log; 2) developed automated processes to verify log configuration settings, monitor log events related to cybersecurity, and perform cybersecurity log backup and retention; 3) communicated the intended automated processes changes to the process control vendor, verified with the vendor that the changes would not impact the reliability function of the Cyber Assets, and documented the vendor's review; and 4) implemented the new automated processes, verified that they are functioning as intended, documented the changes to the affected Cyber Assets, and revised documentation as necessary to incorporate the new automated processes. | 2010-11-29 | 2012-08-23 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011008287 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-004 R4.2. SERC_URE2 failed in two instances to revoke an individual’s access to Critical Cyber Assets (CCAs) within seven calendar days when the access was no longer required. In the first instance, an employee’s NERC training qualification expired due to a failure to renew the training by the SERC_URE2-specified deadline. This employee had access to the physical access control system (PACS) via remote token access, which in turn required active directory access. SERC_URE2 had an automated system in place to alert the IT security group responsible for revocation of CCA access to the expiration of the employee's NERC training. Due to human error, SERC_URE2 did not remove the employee’s remote token access until 16 days after the revocation was requested, causing it to be nine days late. The employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. During this period, the employee did not attempt to use his or her access to the PACS. In addition, the employee continued to be in good standing with SERC_URE2 and had a valid Personal Risk Assessment (PRA). In the second instance, SERC_URE2 had an automated process in place to alert the IT security group responsible for revocation of CCA access when an employee with CCA access had a change in job duties. The IT security group would be responsible for reviewing and removing CCA access as required. This automated process failed due to the server freezing and did not resume until 15 days later when regular maintenance tasks were performed and the server was rebooted. At this time, SERC_URE2 did not have any means of remotely monitoring whether the server was operating normally. Upon reboot, pending revocation alerts that were hung-up in the server were sent and acted on the same day. One alert required that SERC_URE2 remove an employee’s CCA access due to a job change that did not require CCA access. This employee had access to three Physical Security Perimeters that contained Cyber Assets used as electronic access control and monitoring devices and PACS. SERC_URE2 did not remove the employee's access until 15 days after the date the revocation was requested, causing it to be eight days late. During this period, the employee did not use his or her physical access privileges. In addition, the employee continues to be in good standing with SERC_URE2 and had a valid PRA. | CIP-004-1 | R4; R4.2 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system. These failures were limited to two separate instances, and the employees involved were in good standing with the company for the entire period in question and remained in good standing after this violation end date. Both employees had current PRAs. In the first incident, the employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. Neither individual used or attempted to use his or her access during the violation. | eight days after the first individual no longer needed access | when SERC_URE2 revoked access for the second individual | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) confirmed that the delayed notifications were processed in a timely manner; 2) ensured that the process for sending access revocation notifications was monitored; 3) determined the scope of the problem resulting from the hung systems processes; 4) performed an extent of condition review to determine if there were any other instances that previously went un-recognized and could have resulted in non-compliance; 5) ensured that automated monitoring with alerting was in place for access revocation workflows within the future access revocation application; 6) implemented the rewritten access revocation application and retired the old application; 7) implemented a new access revocation application that lists each task required to be performed; and 8) re-trained the group responsible for access revocation on the revocation process and associated responsibilities. | 2011-03-17 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009650 | Settlement Agreement | SERC_URE2 submitted a Self-Certification to SERC stating that it was in violation of CIP-007-3 R2.1. SERC_URE2 discovered three ports and three services not used for normal and emergency operations enabled on a device. SERC_URE2 had a process in place for ensuring only ports and services required for normal and emergency operations were enabled that involved using the discovery command provided by the vendor of the Cyber Assets. However, SERC_URE2 had four switches in four separate Electronic Security Perimeters (ESPs) that retained three default open ports associated with three services that were not required for normal or emergency operations. All of the switches were protected by a Physical Security Perimeter (PSP). SERC_URE2 was unaware of these ports and services until it ran a user datagram protocol port scan. SERC_URE2 had disabled all unused ports and services or, in the case where such unused ports and services could not be disabled due to technical limitations, adopted compensating measures and filed a Technical Feasibility Exception request. In addition, SERC_URE2 modified the process for identification of open ports and services to use different tools for discovery of enabled ports and services. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a severe risk to the reliability of the bulk power system. The affected Cyber Assets resided behind secured firewalls which restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and PSP. The routers and switches were subject to logging and monitoring for cybersecurity events. Firewalls protecting the four affected ESPs employed intrusion detection prevention (IDP) controls which monitored the firewall for cybersecurity events. IDP-triggered events were sent to the firewall management station in real time for monitoring and analysis. IDP signatures were downloaded from the firewall vendor daily to maintain currency. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Certification | To mitigate this violation, SERC_URE2: 1) disabled unused ports and services on identified devices; 2) applied an access control list to block the unnecessary ports on the device; and 3) revised and implemented an updated network operations testing process document to include procedures to find and disable unused ports and services. | 2012-01-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012010581 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R3.1. SERC_URE2 failed to document its assessment of a security patch within 30 calendar days of the availability of the security patch. SERC_URE2 had a program that required the documentation of its assessment of security patches and security upgrades for applicability within 30 calendar days of the availability of such patches and upgrades. SERC learned that SERC_URE2 relied on an automated email alert from a security vendor to make it aware of available and applicable security patches. There was no confirmation step to ensure that all required security patch updates had been sent. A SERC_URE2 subject matter expert identified a security patch that had been released by a software vendor and had not been assessed within 30 days. Forty-four days after the security patch was released, SERC_URE2 completed its assessment of the security patch and retained all necessary documentation. SERC_URE2 implemented the patch on all impacted CCAs. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation affected one security patch for one software product on several CCAs. Access to the CCAs from outside the ESP required strong two-factor authentication. SERC_URE2’s electronic access control and monitoring systems did not identify any malicious activity during the violation that would have impacted the CCAs. | 31 calendar days after the release of the security patch | when SERC_URE2 assessed the security patch and documented its assessment | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) conducted a comprehensive review and comparison of the patches/upgrades to look for related problems; and 2) enhanced the patch management procedure to require a daily review of the website that served as the source of patch and upgrade notifications. | 2011-11-18 | 2013-04-23 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012011335 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE2 failed to adequately test and ensure that the upgrade of its physical access control system (PACS) did not adversely affect existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE2 had previously submitted a Self-Report to SERC addressing this violation but stated that it was in violation of CIP-007-1 R1. After a preliminary review, SERC determined that the violation was more appropriately addressed under CIP-006-1 R1.8. SERC_URE2 had a testing program and procedures for adding new Cyber Assets and for significant changes to existing Cyber Assets within the ESP to ensure that significant changes do not affect existing cybersecurity controls. SERC_URE2 did not test the cybersecurity controls during an upgrade of the PACS. It did, however, confirm that the individuals with physical access to Critical Cyber Assets (CCAs) did not change as a result of the PACS upgrade. SERC_URE2, in following the advice of the vendor, incorrectly classified significant changes to the PACS systems as minor. SERC_URE2 has a process in place that monitors and alerts IT when any change is made to the PACS. This process alerted IT that there had been a change to the PACS as a result of an upgrade. An internal subject matter expert followed up on an inquiry from IT regarding the change and reviewed the change that was implemented. The internal subject matter expert determined that the change was significant and that SERC_URE2 should have tested and documented the PACS upgrade to ensure that it did not adversely impact the existing cybersecurity controls. This violation affected five PACS servers used by SERC_URE2 to log and monitor its Physical Security Perimeters (PSPs) and impacted both production and failover systems. Despite this failure SERC_URE2 completed a review and comparison of security controls after the changes had been implemented. While gathering information to respond to SERC questions regarding the scope of the violation, SERC_URE2 discovered seven earlier instances in which it implemented significant changes to the PACS without testing to ensure the changes did not adversely impact the existing cybersecurity controls. In these prior instances, SERC_URE2 determined that the significant changes to the PACS had no impact on its cybersecurity controls. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE2’s failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, potentially altering the existing cybersecurity controls. If the PACS servers were compromised due to an undocumented significant change, unauthorized individuals could gain physical access to CCAs and non-critical Cyber Assets and modify or disrupt their normal operation. However, in all eight instances in which SERC_URE2 implemented significant changes to the PACS without testing, it performed some functional testing on the PACS after implementation on the production environment that demonstrated the PACS’ operational functions were intact. SERC_URE2 utilizes a tool that alerts its IT in real time when changes in cybersecurity controls are detected. The seven earlier significant changes to the PACS had no impact on SERC_URE2's cybersecurity controls. | when SERC_URE2 implemented the first significant change to the PACS system without testing | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) enhanced test procedures; 2) added ports and service scans to testing process; and 3) invoked a new testing threshold. | 2012-03-30 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011755 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8 . SERC_URE2 failed to afford Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) (PSPs) the protective measures specified in R1.8 in two instances. In the first instance SERC_URE2 discovered five dial-up modems that were being used to provide communications to the physical access control system (PACS) server. As such, the five modems were Cyber Assets used in the access control and monitoring of the PSP. The communication between the five modems and the PACS server was a serial connection. However, SERC_URE2 failed to afford the five dial-up modems the protective measures specified in CIP-005-1 R2.3. SERC_URE2 failed to maintain a procedure for securing dial-up access to the PACS devices. Upon identification of this violation, SERC_URE2 investigated to ensure and confirm that the newly discovered dial-up connections were secured. SERC_URE2 also verified that no other dial-up connections existed in its broader CIP program. In the second instance, SERC_URE2 learned that its existing interpretation of what Cyber Assets should be included in a PACS was incomplete. A third-party consultant concluded a review of SERC_URE2’s CIP compliance program. After reviewing the consultant’s recommendations, SERC_URE2 determined that it had not been sufficiently inclusive in its assessment of what Cyber Assets made up its PACS. Originally, SERC_URE2 identified the PACS server as the only Cyber Asset that fell within the scope of the CIP Standards. After the consultant’s review, SERC_URE2 identified additional card reader control panels and PACS workstations that should have been considered as PACS devices. SERC determined that SERC_URE2 was in violation of CIP-006-1 R1.8 because it failed to afford the card reader control panels and workstations used to managed the PACS devices the protective measures specified in CIP-006-1 R2. Specifically, SERC_URE2 could not implement operational and procedural controls to manage physical access to all access points to the PSP without identifying these Cyber Assets as PACS devices. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All dial-up communications between the five modems and the PACS server were encrypted and secured using a passcode that was securely maintained by technical security personnel. SERC_URE2 knew of the existence of the Cyber Assets that were newly identified as PACS devices and afforded them defense-in-depth security under a broader corporate security initiative. All card reader control panels were located inside PSPs and within secured cabinets with tamper alarms. All workstations used to manage the PACS devices were subject to corporate policies for change management, patch management, and access control. System monitoring logs indicated no attempts or actual compromise of any PACS panels. | when the Standard became mandatory and enforceable for SERC_URE2 | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2 implemented an off-cycle RBAM and determined that it does not have any CCAs. | 2012-06-26 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP14-4-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011757 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3 R2.2. SERC_URE2 failed to afford its Physical Access Control Systems (PACS) the protective measures specified in R2.2. A support vendor for the SERC_URE2 PACS system failed to appropriately test a change to the PACS system prior to implementing the change into production. SERC_URE2 had previously decided that all changes to PACS would be considered significant and would be tested and approved prior to implementation. SERC_URE2 had explained its change control process to the PACS support vendor. The PACS support vendor misunderstood the SERC_URE2 requirements and believed that simple parameter changes in the PACS were not considered significant. A SERC_URE2 subject matter expert (SME) became aware of the implemented change through regular communications with the PACS support vendor. SERC_URE2 rolled back the change in order to ensure the integrity of the PACS system and allow proper testing of the change to occur. However, SERC_URE2 had the untested and unapproved change in service on the production PACS system for three days. SERC determined that SERC_URE2 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R1. After a review by the SERC_URE2 SME and the support vendor, SERC_URE2 determined that no other changes had been implemented outside of the established change management process. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This unauthorized change was to a parameter file that affected reporting capabilities only, and did not impact or affect the security controls of the PACS. Remote panels at the Physical Security Perimeter locations would have continued to operate autonomously and any alarms generated would have been queued by the panels and sent to the central server when it was available. SERC_URE2 utilizes a tool for real time alerting when changes in cybersecurity controls are detected. All personnel working for the PACS support vendor had received the required cybersecurity training, had a current personnel risk assessment, and were authorized by SERC_URE2 to work on its PACS. | when the SERC_URE2 support vendor made the untested and unauthorized change to the PACS | when SERC_URE2 rolled back the untested and unauthorized change | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2 implemented an off-cycle RBAM and determined that it does not have any CCAs. | 2012-06-26 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008539 | Settlement Agreement | FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R2.1, R2.2. FRCC_URE1 did not apply explicit access permissions at access points such that they are specified for a certain set of source IP addresses. Furthermore, for the same set of configurations, FRCC_URE1 did not ensure only ports necessary for operations and monitoring are enabled. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to apply explicit access permissions and ensure that only ports and services necessary for operations and monitoring are enabled could leave the devices within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. This risk was reduced because the ACLs did limit access from designated FRCC_URE1 trusted hosts by specifying certain source IP addresses. Centralized electronic access control and monitoring systems are in place and configured to detect and alert on security events. Furthermore, FRCC_URE1 requires two-factor authentication for all interactive access into the ESP. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of milestone updating firewall rules | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Spot Check | To mitigate this violation, FRCC_URE1: 1) restricted the use of a parameter with rule reconfigurations and restricted and documented ports and services required for operation and monitoring of Cyber Assets within the ESPs; 2) performed a review of firewall rules on access points to all other Critical Cyber Asset ESPs; 3) performed a review of policies and procedures relating to the control of electronic access at electronic access points to the ESPs; 4) established action plans for policy and procedure enhancements to address areas of improvement identified as a result of the review performed; 5) reported additional findings covered during mitigation plan implementation and consulted with FRCC enforcement; 6) consulted with FRCC with recommendations for the mitigation plan; 7) performed a review of technical controls relating to the control of electronic access at electronic access points to the ESPs; 8) established action plans for technical control enhancements to address areas of improvement identified as a result of the review performed; 9) completed implementation of policy and procedure enhancements previously identified; 10) conducted training and awareness with FRCC_URE1's NERC CIP personnel responsible for managing electronic access points to ESPs; and 11) completed implementation of technical control enhancements identified as a result of the review previously performed. | 2013-02-28 | 2013-04-25 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011023 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1.5. FRCC_URE1 failed to afford the required protective measures for multiple Cyber Assets that were used for the electronic access control and monitoring system (EACMS) of the Electronic Security Perimeter (ESP). | CIP-005-1 | R1; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to afford all required protective measures can leave the Cyber Assets unprotected and vulnerable to a cyber threat. Even with the multiple instances of violation on several Cyber Assets, the risk was reduced as the devices were located within ESPs for which interactive access was limited and required authentication. The devices were also located in a Physical Security Perimeter (PSP), and policy enforcement and training was in place for users to create strong passwords in accordance with the Standards. Additionally, all of the Cyber Assets were afforded the other protective measures required by the Standards. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation FRCC_URE1: 1) performed an assessment and extent of condition review of asset type classification for Cyber Assets in scope of CIP-005 R1.5; 2) filed technical feasibility exceptions (TFEs) for the Cyber Assets identified in the Self-Report as they relate to CIP-007 R5.3 requirements; 3) performed a cyber vulnerability assessment (CVA); 4) performed a review of personnel with access to the Cyber Asset. FRCC_URE1 then removed access to applicable Cyber Assets, where necessary; 5) assessed the Personnel Risk Assessment (PRA) program as per CIP-004 R3 to identify possible improvements for validating PRAs prior to granting access to Cyber Assets used in the access control and/or monitoring of the ESPs. Also, FRCC_URE1 assessed the controls defined for updating PRAs pursuant to standard CIP-004 R3.2. FRCC_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 6) performed training and education on the applicability of standards and requirements associated with Cyber Assets used in the access control and/or monitoring of the ESPs as per CIP-005 R1.5; 7) performed an assessment of compliance to CIP-005 R1.5 for Cyber Assets subject to NERC CIP requirements identified as Cyber Assets used in electronic access control and/or monitoring of the ESPs but not properly classified in a previous milestone; 8) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R2. Additionally, FRCC_URE1 performed an extent of condition review of CIP-005 R2 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs. FRCC_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 9) performed an extent of condition review of CIP-007 R3 controls for Cyber Assets used in the access control and/or monitoring of the ESPs. FRCC_URE1 established a corrective action plan to address any issues or improvements identified during the reviews; 10) performed an extent of condition review of account management controls for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs pursuant to CIP-007 R5 (including the need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews; 11) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R3. Additionally, FRCC_URE1 performed an extent of condition review of CIP-005 R3 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs, and established a corrective action plan to address any issues or improvements identified during the reviews; and 12) implemented corrective actions as identified in action plans created in the Mitigation Plan milestones for applicable Cyber Assets used in the access control and/or monitoring of the ESPs across business units. | 2013-07-11 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010621 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R2.1, R2.2, and R2.3. FRCC_URE1 failed to enable only those ports and services required for normal and emergency operations, disable other ports and services not needed, and apply and document compensating measure(s) to mitigate risk exposure for a number of Cyber Assets. FRCC_URE1 did review configurations of the Cyber Assets for services, but not ports. In addition, a cyber vulnerability assessment (CVA) report revealed a Cyber Asset with two new ports; but no actions were taken to disable the ports or file an appropriate technical feasibility exception (TFE). The CVA report also revealed a power distribution Cyber Asset that relied on a configuration validation; thus, all ports and services were not validated. | CIP-007-3 | R2; R2.1; R2.2; R2.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to document only ports and services required for normal and emergency operations could allow Cyber Assets within the Electronic Security Perimeter (ESP) to be configured incorrectly, and thus leave them unprotected and vulnerable to a cyber threat. The risk was reduced because all Cyber Assets were protected within an ESP and a physical security perimeter, and all personnel with access to the Cyber Assets had current personnel risk assessments and cyber training. Furthermore, external interactive access required authentication and was limited. | annual assessment discovery | completion of Mitigation Plan milestone validating ports and services | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) ascertained required ports and services for normal and emergency operations; 2) determined if any updates to procedures were needed; 3) updated process documents as needed from prior milestone; 4) trained personnel responsible for assessing ports and services and completing CVAs as to the requirements of the standard and FRCC_URE1's processes; 5) reviewed current CIP assets and validated that required ports for normal and emergency operations of the asset were correctly documented; and 6) reviewed current CIP assets and validated that the CVAs performed were adequate and any discrepancies identified. | 3/31/2013 | 2013-05-01 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010625 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R6, R6.1, R6.2, R6.4, and R6.5. FRCC_URE1 failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP), as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. Security event logs were not retained for 90 days for several non-Critical Cyber Assets within the ESP. Some of the Cyber Assets were not configured to send log files to the centralized tool used to review security logs, nor issue automated or manual alerts. A Cyber Assets was configured correctly to send security logs to the centralized tool; however, a malfunction occurred resulting in a gap in the activity. Lastly, FRCC_URE1 failed to review logs of system events related to cyber security and maintain records documenting review of logs for several of the Cyber Assets that were logging locally. | CIP-007-1 | R6; R6.1; R6.2; R6.4; R6.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to implement automated tools or organizational process controls to monitor system events that are related to cyber security, not perform manual reviews of logs, and not properly retain such logs can let potential cyber security events go undetected and leave devices vulnerable to a cyber threat. Other Cyber Assets within the ESP which are connected to these Cyber Assets have alerting and logging enabled in addition to the ESP access points. The risk was reduced because these non-critical Cyber Assets are located within an ESP and a Physical Security Perimeter, and external interactive access to the ESP is limited and restricted with authentication. Furthermore, access was limited to authorized personnel with proper cyber training and current personnel risk assessments. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of Mitigation Plan milestone of updating processing and controls to close the gaps identified | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) completed inventory of applicable Cyber Assets and validated logging is functional; 2) filed technical feasibility exceptions as necessary; 3) completed a review of current process and controls for remaining Critical Assets to identify gaps; 4) updated processes and controls as necessary to close gaps identified; and 5) trained personnel on updated processes and controls. | 2012-12-14 | 2013-04-25 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-10-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010626 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R8.2. FRCC_URE1 failed to properly perform a complete review to verify that only ports and services required for operation for Cyber Assets within the Electronic Security Perimeter (ESP) were enabled during its annual cyber vulnerability assessment (CVA). The review performed was automated and either missed the Cyber Asset entirely or did not address what actions would occur when scans returned unexpected or invalid results or unexpected ports. | CIP-007-3 | R8; R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This risk was reduced because all Cyber Assets were afforded the protection of the ESP and Physical Security Perimeter (PSP). These Cyber Assets also require authentication, and access was limited to authorized personnel with proper cyber training and current personnel risk assessments. While FRCC_URE1 failed to conduct a proper CVA for ports and services in the required manner, evidence demonstrated that all ESP Cyber Assets were well-hardened and known vulnerabilities were addressed. Ultimately, all open ports and services were ascertained as required. | required completion of annual CVA | Mitigation Plan completion | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) ascertained required ports for normal and emergency operations of the assets; 2) reviewed processes and procedures related to required ports and services; 3) updated procedures based on results of prior milestone; 4) trained personnel; 5) performed review of current CIP assets and validated required ports for normal and emergency operations are correctly documented; and 6) performed a review of current CIP assets and validated CVAs were adequate and updated discrepancies identified. | 2013-03-31 | 2013-05-01 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC_URE1 had a documented ICP that was recently reviewed by FRCC to verify that the program included corrective action processes, internal controls, upper management involvement, and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
2013-09-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011024 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.8. FRCC_URE1 failed to afford all the required protections to two Cyber Assets. First, both of these Cyber Assets lacked patching controls for CIP-007 R3.1.1; specifically, FRCC_URE1 failed to assess security patches within the required 30 calendar days. Second, for a number of accounts on these Cyber Assets, FRCC_URE1 did not enforce the password controls of CIP-007 R5.3.3 (password annual change frequency). | CIP-006-1 | R1; R1.8 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to afford all required protective measures of patching and proper password controls can leave the Cyber Assets unprotected and vulnerable to a cyber threat. In this instance, the patches were properly assessed within 120 days rather than the required 30 days. The risk was reduced because the PACS Cyber Assets were located within an ESP which required authentication for external interactive access and within a Physical Security Perimeter (PSP). Additionally, all of the Cyber Assets were afforded all other protective measures required by the Standards. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of Mitigation Plan milestone communicating changes | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) collaborated with manufacturer to confirm the issue is not specific to FRCC_URE1’s environment; 2) created a script that will automatically notify users via email if their password has not been changed in required time frames; 3) created a script that will automatically notify via email the access control administrators if any account password has not been properly changed and request the administrator to terminate and/or disable the account; 4) updated corporate security document to reflect the notifications outlined in previous two milestones. The on-call administrator will delete the account and record in a service ticket upon receipt of the notification of account passwords exceeding the required interval; 5) trained corporate security personnel responsible for the updates made to corporate security systems security management document; 6) communicated to users in the access control the requirement to change their passwords and that failure to change their passwords would result in their accounts being terminated; 7) conducted an extent of condition analysis on all the devices; 8) conducted an extent of condition analysis on all the devices in regards to CIP-006-3 R2.2 (the effective version equivalent) protective measures in CIP-003-3 R6 in relation to the change management procedure/change ticket process and CIP-004-3 R3 PRA process and determined if there were any gaps that needed to be addressed in the outlined protective measures; 9) conducted an extent of condition analysis of the devices in regards to CIP-006-3 R 2.2 of specified protective measures in CIP-007-3 and determined if there were any gaps that needed to be addressed with the outlined protective measures; 10) reviewed the results of the extent of condition analysis in the three previous milestones to develop a corrective action plan to address any identified gaps; 11) completed the corrective action plan developed in previous milestone; 12) communicated to and trained affected personnel on the changes from the corrective action plans completed in the previous milestone; 13) performed an extent of condition review for the devices in relation to CIP-007 R3 controls, and established a corrective action plan to address any issues or improvements identified during the reviews; 14) performed an extent of condition review of account management controls for the devices in regards to CIP-007 R5 (including need to file additional TFE’s), and established a corrective action plan to address any issues or improvements identified during the reviews; and 15) implemented corrective actions as identified in action plans created in previous two milestones for Cyber Assets across business units. | 2013-07-11 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. .
2013-09-30 | FERC | NP13-57-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011050 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R3.2. FRCC_URE1 failed to implement security monitoring process(es) to detect and alert for attempts at or actual unauthorized accesses at access point; and did not review access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | CIP-005-3a | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This risk was reduced because only users with a proper personnel risk assessment and cyber training were granted physical or cyber access into the Electronic Security Perimeter (ESP). External interactive access to the ESP is limited and requires authentication. Furthermore, users are trained on password complexity requirements and the need to keep their passwords private. These multiple layers (defense in depth) of password controls, physical protections, and monitoring further mitigated the risk to the BPS. | annual assessment discovery | completion of Mitigation Plan milestone submitting TFEs and confirming Cyber Assets in compliance | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) researched how to implement technically a mechanism to detect and alert for actual unauthorized accesses or determine if a process can be implemented should a technical solution not be available; 2) submitted a Technical Feasibility Exception (TFE); 3) created procedures to detect and alert for actual unauthorized accesses for any Cyber Assets where it is not technically feasible to do so. In addition, FRCC_URE1's remaining departments that operate the rest of its Critical Assets; 4) performed a review of build/test plans for Cyber Assets subject to CIP-005 R3 to ensure that they include steps for validating that the Cyber Assets are configured to detect and alert for attempts at or actual unauthorized accesses 24 hours a day, seven days a week; Additionally, language will be enhanced to ensure that when automated alerting is not technically feasible, a TFE will be filed and the Cyber Assets will be subject to processes and procedures created in the previous milestone to assess access logs for attempts at or actual unauthorized accesses; 5) trained all personnel responsible for performing the new procedures created in the previous milestone as needed; and 6) implemented any new processes created in the previous milestone. | 2013-06-27 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100312 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO_URE1 failed to demonstrate that all personnel having authorized cyber or authorized unescorted physical access were subject to identity verification as required by CIP-004-1 R3.1. Specifically, 28 of the 216 individuals with access to Critical Cyber Assets (CCAs) were not subject to any sort of identity verification. Upon discovering the issue, MRO_URE1 performed Personnel Risk Assessments (PRAs) for the 28 individuals, and it changed its program to utilize an identity verification tool with better documentation of PRAs. Of the 28 individuals with inadequate PRAs, 24 were MRO_URE1 employees with physical access to a single substation, three individuals were third-party security personnel that had physical access to both the primary and secondary control centers (including their associated data centers), as well as electronic access to the physical control system, and one individual was a third-party cleaning contractor that had physical access to the control center (but not to the associated data center). Although MRO_URE1 failed to perform the identity verifications on 28 individuals, it did perform seven-year criminal background checks on those individuals. | CIP-004-1 | R3; R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By not performing identity verifications on 28 individuals, MRO_URE1 could not be certain that the individuals with access to its CCAs, including its control centers, had backgrounds appropriate for such access. Of the 28 individuals with inadequate PRAs, three were third-party security contractors that had physical access to both the primary and secondary control centers (including the associated data centers), as well as electronic access to the physical control system. One individual was a third-party cleaning service contractor that had physical access to the control center. MRO_URE1 performed seven-year criminal background checks on each of the 28 individuals, although the background checks were not necessarily as accurate without the identity verification in place to ensure that the correct individual was being assessed. However, out of the 28 individuals with inadequate PRAs, 24 individuals were MRO_URE1 employees. Each of these employees had physical access to one substation. Furthermore, each of the 24 employees has been with the entity for at least two decades. Therefore, the violation posed a moderate risk, but not a serious or substantial risk, to reliability of the BPS. | The date MRO_URE1 was required to comply with the Reliability Standard | When MRO_URE1 performed all of the necessary PRAs | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of PRAs for all personnel having authorized cyber or authorized unescorted physical access to CCAs; 2) conducted full or partial PRAs on personnel found to have discrepancies with the comprehensive review; 3) performed training for human resources personnel to ensure proper steps are followed when initiating PRAs; and 4) revised its PRA procedure to include verification of completion (internal control) of the PRA for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | 2012-05-25 | 2012-05-25 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
2013-09-30 | FERC | NP13-57-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100314 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO_URE1 failed to provide evidence of a security patch management program which meets the requirements of CIP-007-1 R3. Specifically, MRO_URE1 failed to provide evidence that all security patches were assessed for applicability within 30 calendar days, and it failed to provide patch documentation for many of its older legacy Energy Management System (EMS) subsystems. Most of MRO_URE1's EMS subsystems require the certification of patches by MRO_URE1's EMS vendor (per MRO_URE1's program) prior to MRO_URE1 assessing or installing third-party patches on the EMS. However, MRO_URE1's EMS vendor refused to certify any patches for mainframe units in use within MRO_URE1's EMS. A review of MRO_URE1's patch management program and legacy devices revealed that most of MRO_URE1's older systems were no longer supported by vendors, and consequently no longer had patches available. For some subsystems such as the primary database for the EMS, the EMS vendor did not certify patches. MRO_URE1, after experiencing system failures when installing non-certified patches, ceased the patching of the database (and any other software not certified by the EMS vendor). MRO_URE1 changed EMS vendors, partially due to problems with patch management. Mitigation focused on revising MRO_URE1's policies and procedures with patching the new EMS, as well as ensuring that all systems were up to date. A comprehensive review of MRO_URE1's software patch levels revealed issues on approximately 24% of its devices. The average length of time these devices went without patch assessments was 13 months, with two devices not having had any patches for several years. Most of the devices without patches were part of MRO_URE1's EMS and associated security subsystems, although the devices with the longest duration between patch assessments involved subsystems such as network monitoring and printing. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation posed a moderate risk because approximately 24% of MRO_URE1's devices had patch issues, potentially increasing the vulnerability of those devices to new cyber security threats. Many of these devices were part of MRO_URE1's EMS and associated security subsystems. The average length of time these devices went without patch assessments was 13 months, and two devices did not have any patches for several years. The following factors mitigated the risk. First, the EMS servers and consoles themselves were not among the devices that had an extended duration between patch assessments. In addition, MRO_URE1 has network security controls, such as host-based routing and network isolation, as well as an intrusion detection system. However, based upon the duration of the violation and the number and types of devices that required updates, MRO determined that this violation posed a moderate risk to the BPS. | The date MRO_URE1 was required to comply with the Reliability Standard | Mitigation Plan completion | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated and implemented its security patch management program; 2) performed a comprehensive review of its patch management status; 3) prioritized and addressed discrepancies according to patch management program; and 4) submitted Technical Feasibility Exception requests to MRO, where necessary. | 2012-12-21 | 2013-01-24 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
2013-09-30 | FERC | NP13-57-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100315 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO discovered that MRO_URE1 failed to establish, implement, and document technical and procedural controls which enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access in accordance with CIP-007-1 R5. Specifically, MRO discovered inconsistent password complexity and password change controls being implemented on MRO_URE1's Critical Cyber Assets (CCAs). Multiple CCAs did not have technical controls enabled, as required by CIP-007-1 R5. MRO_URE1 performed a comprehensive review of technical controls for accounts subject to CIP-007-1 R5 as part of mitigation. Of the accounts subject to CIP-007-1 R5, approximately 2% did not have passwords changed annually. Most notably, MRO_URE1 did not have evidence of a password change for a shared administrative system account prior to the date of the most recent change, indicating that the passwords were not changed for over three years. These account devices are used in MRO_URE1's Energy Management System (EMS) network system. Additionally, the password for one system administrative account was changed only twice, with the instances being over two years apart. This device is configured to require a digital certificate for Secure Shell remote access, with the password being the primary control for the local console within the Physical Security Perimeter. The password for one system account, a shared administrative account on two devices, was last changed over eighteen months before the start of the Compliance Audit. The devices accessed through this account are used for network segregation, and both devices also required the use of both a digital certificate and key as additional methods of authentication for access. The same five individuals have access to all of these accounts. None of the individuals with access to these accounts has left employment at MRO_URE1 since July 1, 2007, and the Personnel Risk Assessments and training for the five individuals with account access was confirmed. Additionally, a thorough review of MRO_URE1's CCAs resulted in a large number of devices requiring Technical Feasibility Exceptions (TFEs) for the implementation of technical controls for both password complexity and annual change control, in addition to revising MRO_URE1's policies and procedures around account management. | CIP-007-1 | R5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation posed a moderate risk because the shared administrative system account passwords were not changed for over three years. These accounts have a critical function of monitoring and managing the EMS network. The associated devices did not have any additional compensating authentication controls such as a digital certificate or key. However, MRO did not consider this violation to pose a serious risk to the BPS because the same five individuals have access to all of these accounts, none of the individuals with access to these accounts left employment at MRO_URE1 since July 1, 2007, and each of the individuals had proper Personnel Risk Assessments and CIP training. Additionally, a large number of MRO_URE1's other devices required TFEs for the implementation of technical controls for both password complexity and annual change control. Furthermore, although MRO_URE1 was primarily using a manual process to change passwords, only approximately 2% of accounts did not have their passwords changed at least annually. | The date MRO_URE1 was required to comply with the Reliability Standard | Mitigation Plan completion | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of documentation and Cyber Asset system capability; 2) updated account management processes and procedures; 3) verified and applied password complexity and expiration enforcement; and 4) changed Cyber Asset user account passwords. | 2012-12-31 | 2013-01-24 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010161 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-003-3 R6. RFC_URE1's control and configuration management process did not have a configuration management program to document current and ongoing hardware and software configurations of Critical Cyber Assets (CCAs). RFC_URE1's change control and configuration management process in place at the time of the violation only addressed controlling and documenting future changes made to the configurations of CCAs; it did not establish baseline configurations for all CCAs. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RFC_URE1's of failure to memorialize its baseline configuration as part of the configuration management. Without the baseline RFC_URE1 would not be able to accurately predict how change to CCAs could impact the changed CCA or other CCAs and non Critical systems. Further, the duration of the violation stretched out for over 2 years. Finally, although RFC_URE1 had an informal process to track changes, RF could not verify the thoroughness or rigor or the process. Although RFC_URE1 did not establish baseline configurations for all CCAs, they did have a change control and configuration management process in place during the duration of the violation. Also, RFC_URE1 represented that personnel were aware of system changes. Additionally, RFC_URE1 reviewed all changes to its CCAs. Further, RFC_URE1 conducted cyber vulnerability assessments of the CCAs at issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1: 1) altered the change control and configuration management procedures to document initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010162 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-005-3 R4. RFC_URE1 determined that, although it performs a cyber vulnerability assessment (CVA) annually, during the 2010 and 2011 CVAs, it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter was required for operation. | CIP-005-3 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because the risk to the reliability of the bulk power system was mitigated by the fact that upon completion of the 2012 CVA, RFC_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 completed its 2012 CVA. During the 2012 CVA, RFC_URE1 verified that only ports and services located on electronic access points and required for operation are enabled. | 2012-12-21 | 2013-05-02 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010163 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R1. RFC_URE1 discovered that it had not documented its test procedures and therefore could not demonstrate that it performed testing in a manner that reflects the production environment or provide documented test results. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because RFC_URE1 represents that it performed testing on all Cyber Assets as required during the duration of the violation and, although undocumented, RFC_URE1 followed its informal change management process. RFC_URE1 represents that this process required RFC_URE1 to perform test procedures and that testing did occur during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 developed specific documented testing procedures for all Cyber Assets located within its Electronic Security Perimeter. | 2012-09-21 | 2012-12-26 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010164 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R8. RFC_URE1 discovered that during the cyber vulnerability assessments (CVAs), it did not verify that only those ports and services required for operation of Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. | CIP-007-3a | R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because upon completion of the CVA, RFC_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 conducted its 2012 CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. | 2012-12-21 | 2013-05-02 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010165 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-006-3a R2 because RFC_URE1 discovered that it did not afford the protective measures specified in CIP-006-3a R2.2 to its system. Further, RFC_URE1 did not address testing of signatures in process for updating anti-virus and malware prevention signatures as applicable to a device. | CIP-006-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RFC_URE1 did not include the device in the original scope of its CIP compliance effort. Further, RF considered RFC_URE1's failure to test signatures on the other device thereby leaving it vulnerable to virus and malware. However, the risk was mitigated because the devices were located within a Physical Security Perimeter for the duration of the violation. Further, the one device is password protected and further restricted through the use of local, as well as domain, firewall, and security policies. Finally, throughout the duration of the violation, access to the device authentication. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the device to a serial connection, thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter capable of performing testing of anti-virus and malware signatures. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010166 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R3. RFC_URE1 discovered it did not establish, document, or implement a security patch management process for all Cyber Assets within its Electronic Security Perimeter (ESP). | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because it demonstrated a general lack of awareness about the requirements of CIP-007-3a R3. Further, RF could not verify the effectiveness of RFC_URE1's informal security patch management program. Additionally, the violation involved Cyber Assets within the ESP which concerned RF due to the increased vulnerability of those assets to infiltration of unauthorized network traffic. Finally, the duration of the violation was over two years. RFC_URE1 implemented an informal procedure for reviewing updates to its servers throughout the duration of the violation. RFC_URE1 tracked available and applicable updates for its assets and accessed various online vendors for tracking non-windows updates throughout the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 documented a security patch management program and filed technical feasibility exception (TFE) requests for all Cyber Assets that could not be patched. | 2012-12-11 | 2013-05-02 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010172 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R3. RFC_URE1 discovered it did not establish, document, or implement a security patch management process for all Cyber Assets within its Electronic Security Perimeter (ESP). | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because it demonstrated a general lack of awareness about the requirements of CIP-007-3a R3. Further, RF could not verify the effectiveness of RFC_URE1's informal security patch management program. Additionally, the violation involved Cyber Assets within the ESP which concerned RF due to the increased vulnerability of those assets to infiltration of unauthorized network traffic. Finally, the duration of the violation was over two years. RFC_URE1 implemented an informal procedure for reviewing updates to its servers throughout the duration of the violation. RFC_URE1 tracked available and applicable updates for its assets and accessed various online vendors for tracking non-windows updates throughout the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 documented a security patch management program and filed technical feasibility exception requests for all Cyber Assets that could not be patched. | 2012-12-21 | 2013-03-22 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010173 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that, as a Generator Operator, it was in violation of CIP-007-3a R8. RFC_URE1 discovered that during the cyber vulnerability assessments (CVAs), it did not verify that only those ports and services required for operation of Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. | CIP-007-3a | R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because upon completion of the CVA, RFC_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 conducted its CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. | 2012-12-21 | 2013-03-21 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010174 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-003-3 R6. RFC_URE1 change control and configuration management process did not have a configuration management program to document current and ongoing hardware and software configurations of Critical Cyber Assets (CCAs). RFC_URE1's change control and configuration management process in place at the time of the violation only addressed controlling and documenting future changes made to the configurations of CCAs; it did not establish baseline configurations for all CCAs. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RFC_URE1's failure to memorialize its baseline configuration as part of the configuration management. Without the baseline RFC_URE1 would not be able to accurately predict how change to CCAs could impact the changed CCA or other CCAs and non Critical systems. Further, the duration of the violation stretched out for over 2 years. Finally, although RFC_URE1 had an informal process to track changes, RF could not verify the thoroughness or rigor or the process. RFC_URE1 did have a change control and configuration management process in place during the duration of the violation. Also, RFC_URE1 represented that personnel were aware of system changes. Additionally, RFC_URE1 reviewed all changes to its CCAs. Further, RFC_URE1 conducted cyber vulnerability assessments of the CCAs at issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1: 1) altered the change control and configuration management procedures to document initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-03-18 | 2013-04-25 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010175 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-005-3 R4. RFC_URE1 determined that, although it performs a cyber vulnerability assessment (CVA) annually, during past CVAs, it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter were required for operation. | CIP-005-3 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because the risk to the reliability of the bulk power system was mitigated by the fact that upon completion of the recent CVA, RFC_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 completed its CVA. During the CVA, RFC_URE1 verified that only ports and services located on electronic access points and required for operation were enabled. | 2012-12-21 | 2013-03-22 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010176 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-006-3a R2. RFC_URE1 discovered that it did not afford the protective measures specified in CIP-006-3a R2.2 to its system. RFC_URE1 did not include the one device in the original scope of its CIP compliance effort. Further, RFC_URE1 did not address testing of signatures in their process for updating anti-virus and malware prevention signatures as applicable to the other device. | CIP-006-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RFC_URE1 did not include the device in the original scope of its CIP compliance effort. Further, RF considered RFC_URE1's failure to test signatures on its other device thereby leaving it vulnerable to virus and malware. However, the risk was mitigated because the devices were located within a Physical Security Perimeter for the duration of the violation. Further, one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. Finally, throughout the duration of the violation, access to the device required authentication. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1: 1) filed the necessary technical feasibility exception requests; 2) modified the device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter capable of performing testing of anti-virus and malware signatures. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RFC_URE1 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010177 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R1. RFC_URE1 discovered that it had not documented its test procedures and therefore could not demonstrate that it performed testing in a manner that reflects the production environment or provide documented test results. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because RFC_URE1 performed testing on all Cyber Assets as required during the duration of the violation and, although undocumented, RFC_URE1 followed its informal change management process. RFC_URE1 performed test procedures and that testing did occur during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RFC_URE1 developed specific documented testing procedures for all Cyber Assets located within its Electronic Security Perimeter. | 2012-09-21 | 2012-12-18 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012045 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3a R2. WECC_URE1 reported that it failed to complete assessment and documentation for the review of ports and services on two servers, in violation of CIP-007-3a R2.1 and R2.2. For each device, WECC_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled. | CIP-007-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices in scope resided within a Physical Security Perimeter (PSP) where physical access was restricted. All individuals with access to the PSP had current training, personnel risk assessments, and had approved authorized access. In addition, the devices were in an Electronic Security Perimeter (ESP) and were logged and monitored. All network traffic to the ESP is logged and monitored by a system that sends alerts to WECC_URE1 personnel after any unusual traffic is detected. | when WECC_URE1 commissioned the devices | Mitigation Plan completion | $25,000 (for WECC2013012045 and WECC2013012047) | Self-Certification | To mitigate this violation, WECC_URE1: 1) developed and conducted a change control training for personnel with NERC CIP responsibilities; and 2) completed a ports and services review for applicable devices. | 2013-06-28 | TBD | Does Not Contest | WECC_URE1 was cooperative throughout the process. WECC_URE1 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE1 to conceal the violation. There was no evidence that WECC_URE1’s violation was intentional.
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012047 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-1 R5. WECC_URE1 failed to remove, disable, or rename administrator accounts and failed to change passwords prior to putting systems into service. Specifically, WECC_URE1 failed to ensure that one factory default shared administrator account on each of eight devices was removed, disabled, or renamed. It also failed to ensure the default password was changed prior to putting the equipment into production. In addition, WECC_URE1 failed to change the passwords on eight accounts in scope during the 2010, 2011, and 2012 calendar years. | CIP-007-1 | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because the generating units associated with this violation are blackstart units that are critical for system restoration. Although WECC_URE1 did have a policy in place for these devices, the personnel responsible for implementing the policy did not know how to properly manage these types of switches. The risk was mitigated because the devices resided within a Physical Security Perimeter where access was restricted to individuals with current training, approved personnel risk assessments, and approved authorized access. Electronic Security Perimeter (ESP) and access attempts were logged and monitored. All network traffic to the ESP is logged an monitored by a system that sends alerts to WECC_URE1 personnel after any unusual traffic is detected. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $25,000 (for WECC2013012045 and WECC2013012047) | Self-Certification | To mitigate this violation, WECC_URE1: 1) reviewed the device accounts and supplied documentation of the review and password changes; 2) developed and conducted supplemental change control and account management refresher training for personnel; and 3) reassigned workflow tasks for the devices to the IT network support team. | 2013-06-28 | TBD | Does Not Contest | WECC_URE1 was cooperative throughout the process. WECC_URE1 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE1 to conceal the violation. There was no evidence that WECC_URE1 ’s violation was intentional.
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012055 | Settlement Agreement | WECC_URE2 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3a R2. WECC_URE2 failed to establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. Specifically, two devices were commissioned that did not undergo testing or change control prior to implementation. WECC_URE2 failed to appropriately identify a server as a Critical Cyber Asst (CCA). Additionally, because of the misclassification, WECC_URE2 failed to ensure that the second server, which resided on the same network, was afforded CCA protections. WECC discovered a third device which should have been afforded CCA protection. Therefore, WECC_URE2 commissioned one CCA and two Cyber Assets residing within an Electronic Security Perimeter (ESP) without testing, change control, or verifying that only ports and services required for normal and emergency operations were enabled,. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within scope resided within a Physical Security Perimeter where physical access was restricted to individuals with current training, approved Personal Risk Assessments, and approved authorized access. The devices also were protected by an Electronic Security Perimeter (ESP) and behind a device that logs, monitors, and restricts all access in and out of the ESP. In addition, all network traffic that is within the ESP is logged and monitored by its system log server which is configured to send alerts to WECC_URE2 personnel after any unusual traffic is suspected. | when WECC_URE2 commissioned the devices | Mitigation Plan completion | 10000 | Self-Certification | To mitigate this violation, WECC_URE2: 1) completed review of ports and services to ensure that only those ports and services required for normal and emergency operation are enabled; and 2) developed and conducted supplemental training for personnel with NERC CIP responsibilities. | 2013-06-28 | TBD | Does Not Contest | WECC_URE2 was cooperative throughout the process. WECC_URE2 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE2 to conceal the violation. WECC determined that a prior violation should serve as a basis for aggravating the penalty .
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009389 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-004-1 R4. Specifically, WECC_URE3 stated there were three incidents where individuals whose physical access rights to Physical Security Perimeters (PSPs) were not revoked as required by the Standard. WECC_URE3 failed to revoke access to Critical Cyber Assets (CCAs) within seven days for eight individuals who no longer require such access. The first incident occurred when a contingent worker WECC_URE3 did not have physical access rights revoked within seven days of his separation with WECC_URE3. The contingent worker had authorized physical access rights to WECC_URE3's PSPs which should have been revoked. However, due to an administrative oversight, the access was not revoked until approximately eight months later. WECC_URE3 identified the second incident when a manager was reviewing documentation related to two contract security guards who had been given authorized unescorted physical access to PSPs. The security guards were terminated; however, the access was not revoked until approximately one month and three months after the security guards were terminated. The third incident involved five WECC_URE3 employees who had physical access to CCAs. For the five employees, WECC_URE3 did not have records for when access was no longer required, and therefore did not have dates for when access should have been revoked. It was determined that the five individuals were terminated and access was revoked for the five employees approximately for eight months, three weeks, three months and one month after termination. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although these individuals had physical access, they did not have electronic access to CCAs. Moreover, all the individuals in scope had Personnel Risk Assessments and all of the PSPs are monitored by human observation 24 hours a day seven days a week, including security video monitoring. Also, each PSP access point is configured to generate an alarm for any unauthorized physical access and no alarms occurred during the incidents. | when the access should have been revoked for the first incident | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3: 1) revoked access for the affected employees; 2) conducts regular training sessions on its procedure regarding physical access revocations with employees; and 3) conducts regular monthly meetings with vendors to reinforce the contractual requirements related to terminations. | 2011-06-09 | 2013-08-21 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE3's compliance history and determined it to be an aggravating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009391 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-006-3c R5. WECC_URE3 stated that on seven instances it failed to maintain 24-hour physical monitoring of all 35 of its Physical Security Perimeters (PSPs). Specifically, WECC_URE3 experienced seven monitoring outages over a period of an approximate year. During each outage, WECC_URE3 maintained local logs at each PSP to log physical access attempts. In addition, with the exception of one substation, all of WECC_URE3's substations where the outages occurred were manned 24 hours a day. The substation that was not manned is WECC_URE3's facility which contains various devices used to support WECC_URE3's energy management system such as servers, firewalls and switches. The outage at this facility lasted more than four hours. During the outage, WECC_URE3 did not dispatch personnel to the facility. | CIP-006-3a | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP in scope is located in a remote substation and is manned by operators approximately 15 hours of the day and the PSP access points are locked and require card key access even if monitoring is down. Further, all PSP access points are located to default to "fail-safe" and all doors and cabinets are locked and secured. | when the first of seven outages occurred at the facility | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3 developed a procedure to address unplanned CCURE outages involving WECC_URE3 substations. Pursuant to the procedure, corporate security is to contact specific personnel and notify them when manual monitoring at the PSPs is required. | 2012-06-27 | 2013-06-10 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-57-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009392 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R5. WECC_URE3 stated that on three occasions a trainee was allowed by his supervisor to access an energy management system (EMS) using another operator's account. Specifically, the operator, at the direction of the supervisor, left his workstation unlocked to allow the trainee to work on the EMS workstation. The EMS workstation is a Critical Cyber Asset (CCA) located in the control substation facility within an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). | CIP-007-1 | R5; R5.2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The person in scope had a current Personnel Risk Assessment, cybersecurity training, and was required to access the EMS workstation to perform work duties. Also, this person was in training and was under complete supervision the entire time during all three instances. Finally, the ESP and PSP were monitored and manned 24 hours a day. | when access to the account was obtained by the trainee | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3: 1) affixed a sign to the EMS workstation to remind employees to log-off after their shifts and not to share log-in tokens or passwords with others; 2) secured log-in credentials for the in-scope trainee; and 3) reinforced the cybersecurity policy with the supervisor. | 2012-06-28 | TBD | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008323 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R1.5. FRCC_URE1 did not afford all protective measures, specifically CIP-005 R2.1 and R2.2, for a number of electronic access control and monitoring system (EACMS) Cyber Assets. In addition, FRCC_URE1 reported it lacked documentation listing the approved ports and services required for normal and emergency operation at the access points. Furthermore, FRCC_URE1 failed to identify additional EACMS Cyber Assets and afford the protective measures as required by CIP-005-2 R1.5. The specific protective measures excluded were CIP-003 R5, CIP-005 R2, CIP-005 R3, CIP-007 R1, CIP-007 R3, CIP-007 R4, CIP-007 R5, and CIP-007 R6. | CIP-005-1 | R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because EACMS Cyber Assets are critical to ESP protection. Although FRCC_URE1 or the contractor managing them did not document all the afforded security measures, specifically CIP-005 R2.1 and R2.2, that could demonstrate compliance with CIP-005 R1.5, most of the essential secured measures were always enforced, such as monitoring for user access control, intrusion detection, and logging. Furthermore, FRCC_URE1 maintained all EACMS Cyber Assets behind a corporate firewall and within a Physical Security Perimeter (PSP), thereby limiting any potential serious impact from failure of any individual EACMS Cyber Asset reported under this violation. In addition, all personnel with logical and physical access had proper personnel risk assessments (PRAs) and cyber training. The risk for additional EACMS Cyber Asset was mitigated as it was afforded the protective measures from all other CIP requirements. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) created new access points into the ESP by purchasing and installing new firewalls on the outside perimeter of the headquarters energy management system (EMS) and backup EMS switches. This action created two separate ESPs and eliminated the need for any access control on the switches. The new firewalls enabled FRCC_URE1 to establish deny-by-default access methodology to control ports and services at the newly defined access points; 2) changed the firewall rule set to reflect the approved ports and services, as configured on the headquarters EMS firewall, for access to the safe room. This revised rule set is similar to the rule set defined on the headquarters EMS firewall, but with the source and destinations for services and internet protocol (IP) reversed; 3) updated the documents identifying the approved ports and services on the firewalls. These documents list the defined ports and services on the firewalls along with an explanation for their use; 4) moved the old firewalls outside the new firewalls, and thus outside the ESP. FRCC_URE1 had originally planned to update the old firewalls’ configuration to define explicitly the IP addresses allowed for communications, and deny by default all non-defined IP addresses. The new firewalls became the EACM for the ESP, and were configured to define explicitly the IP addresses allowed for communication. Monitoring is performed via syslog to the application already deployed; 5) updated affected NERC CIP-related documentation such as the ESP drawing and CCA list, to reflect these changes; and 6) reviewed FRCC_URE1's recovery plans for firewall recovery in the case of a disaster and updated its recovery plan practice. | 2012-03-14 | 2013-05-09 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008324 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-006-2 R1.1. FRCC_URE1 did not deploy and document alternative measures for the Cyber Assets (non-FRCC_URE1 owned) along the path of the leased fiber cable where a completely enclosed border could not be established. The fiber cable travels between the two Physical Security Perimeters (PSPs) using a dedicated optical circuit managed by a communications provider. The Cyber Assets on each end of the circuit were not identified nor acting as access points and thus a single Electronic Security Perimeter (ESP) existed between the two PSPs. | CIP-006-1 | R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to deploy alternative measures could lead to a potential cyber threat on the unprotected Cyber Assets and the optical circuit between the two PSPs. The risk was reduced as the end points of the communication links were protected by switches that are contained within a defined PSP with machine access control lists (ACLs) and port security. The risk was further reduced as the communication link was a dedicated optical circuit making it difficult to sniff or inject traffic without advanced telecommunications equipment. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) redefined the former single ESP into two distinctly separate ESPs at FRCC_URE1 headquarters and backup facilities. These two locations continue to be connected via the optical carrier 3 (OC-3) circuit, but the leased line is now classified as a data communication link between discrete ESPs. The OC-3 circuit does not require a 6-walled border, since it is no longer part of a defined ESP; 2) purchased and installed firewalls that enable them to establish a deny-by-default access methodology to control ports and services at these newly defined access points; 3) established appropriate electronic access controls on the newly defined ESPs. Since the OC-3 circuit is no longer defined as part of the ESP, FRCC_URE1 implemented protective Cyber Assets to control electronic access at the points of connection between the leased circuit and the two separate energy management system networks; and 4) completed migration of the EMS network. | 2011-12-30 | 2013-02-19 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008325 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-006-1 R1.8. FRCC_URE1 did not afford all protective measures required by CIP-006-1 R1.8 to a number of deployed physical access control system (PACS) Cyber Assets for almost two years, and additional PACS Cyber Assets for a year. Specifically, the protective measures excluded were CIP-003 R5, CIP-005 R2, CIP-005 R3, CIP-007 R2, CIP-007 R3, CIP-007 R4, and CIP-007 R6.2. | CIP-006-1 | R1.8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to properly provide protective measures for the Cyber Assets left them unprotected and vulnerable to a cyber threat. The risk was mitigated, however, as the PACS Cyber Assets were secured behind the corporate firewall and within a required Physical Security Perimeter (PSP). Furthermore the PACS Cyber Assets were accessible only to internal users with appropriate clearance and personnel risk assessments (PRAs). All other CIP requirements were met for these Cyber Assets. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) initiated a project to assess each CIP Reliability Standard and sub-requirement that pertains to the PACS. The project included mitigation initiation, assessment, solution, implementation, operations, and documentation and addressed all standards captured by the CIP-006-1 R1.8 requirement; 2) implemented an information technology infrastructure library ready software application and revised its change control and configuration management practice to address the protective measures required by CIP-003 R6; 3) discussed electronic access point (EAP) architecture and design with third-party vendor, implemented new EAP solution in-house, verified operational readiness, gathered evidence including new EAP diagram to support changes, and revised its ESP practices to address the protective measures required by CIP 005 R2-R3; 4) implemented a vulnerability and patch management software application and revised its test procedures and security patch management practice to address the protective measures required by CIP-007 R1 and R3; 5) documented applications and services using user datagram protocol/ transmission control protocol ports and revised its firewall ports and services practice to address the protective measures required by CIP-007 R2; 6) evaluated and installed malicious software and anti-malware software application, tested and verified application and process, and revised its malicious software prevention practice to address the protective measures required by CIP-007 R4; 7) ensured and documented that all system accounts are compliant with password length, password age, and password complexity requirements. If any of these conditions were not met due to technical infeasibility, a technical feasibility exception (TFE) was submitted with reference to this mitigation plan. Revised its system account management practice to address the protective measures required by CIP-007 R5; 8) implemented a security status monitoring and alerting software application, and revised its monitoring system cybersecurity events practice to address the protective measures required by CIP-007 R6; 9) performed operational readiness exercise on disposal process and revised its disposal/redeployment of Cyber Assets practice to address the protective measures required by CIP-007 R7; 10) revised its cybersecurity incident response and reporting practice to include EAP Cyber Assets addressed in CIP-005 R2 and R3 to address the protective measures required by CIP-008 R1; 11) revised its cyber recovery plans practice to incorporate additional criteria to address varying degree impact or incident to initiate a full recovery, as well as additional roles and responsibilities to address actions taken when responding to a recovery event to address the protective measures required by CIP-009 R1; 12) filed new TFEs, as appropriate, to implement compensating measures to address the access control panels associated with the PACS; and 13) completed final compliance review of activities and evidence. | 2012-10-02 | 2013-05-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008326 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-007-1 R2, R2.1, and R2.2. FRCC_URE1 did not establish and document the process for ensuring that only ports required for normal and emergency operations are enabled for a number of Cyber Assets during the violation period. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to enable only ports and services required for normal and emergency operations can leave the Cyber Assets unprotected and vulnerable to a cyber threat. FRCC_URE1 had mitigated the risk because all workstations and servers had anti-malware for threat detection from services that may be exploited, and all Cyber Assets were behind a corporate firewall. All workstations and servers were also kept up-to-date with operating system security patches. Furthermore, all personnel with access to these Cyber Assets had current personnel risk assessments (PRAs) and cybersecurity training. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) conducted comprehensive port scans on existing Cyber Assets for ports and services; 2) checked all scanned assets against the Cyber Asset document and confirmed by manual inspection to ensure that all Cyber Assets were included and accounted for; 3) included all user datagram protocol ports as well as the entire range of transmission control protocol ports in the port scans; 4) ran scans against all Cyber Assets within the Electronic Security Perimeters (ESP) as well as all ESP access point Cyber Assets; 5) conducted port scans of ESP access point Cyber Assets against internal interfaces; 6) implemented a new energy management system (EMS) and rescanned all equipment for any additional ports and services required for operation; 7) updated the ports and services documentation with the new scan results; 8) analyzed the new scan results to determine which ports and services are required for operation and modified its ports & services documentation to define and describe the purpose of each port or service, which became the revised ports and services baseline; 9) reviewed all services currently running within the EMS local area network; 10) turned off or disabled all unnecessary services and provided justification for all required services; 11) rescanned all servers and workstations for any additional services required for operation and modified services documentation to incorporate changes; and 12) opened a ticket with the firewall vendor and attached a port scan for its review of the required firewall ports and services; the vendor reviewed the ports that were open on the interface and suggested actions for FRCC_URE1 to address; reviewed the rule sets and determined which ports and services were required for operation; and submitted the findings to the vendor to implement only the required ports and services on the firewall’s internal interface. | 2012-08-30 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-09-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010357 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R2, R2.1, R2.2, R2.3, R2.4, and R2.6. FRCC_URE1 failed to demonstrate that its process and mechanisms used an access control model that denies access by default, such that explicit access permissions were specified as required. FRCC_URE1 also failed to demonstrate that only the required ports were enabled. FRCC_URE1 also failed to demonstrate that strong procedural or technical controls at access points to ensure the authenticity of the accessing party were enforced for Cyber Assets used to communicate to analog circuits. Furthermore, a procedure for securing dial-up access to the Electronic Security Perimeters (ESPs) did not exist. | CIP-005-1 | R2; R2.1; R2.2; R2.3; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to establish an access control model of deny by default, and enable only ports and services required for normal and emergency operations can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was reduced because the access points connected down-stream ESPs and were protected to only allow trusted sources to communicate through these access points. Furthermore, the access points were afforded all protective measures from all other CIP requirements. | when the Standard became mandatory and enforceable for FRCC_URE1 | when FRCC_URE1 placed the necessary firewalls, implemented access point rule sets, and wrote a procedure for allowing access to ESP | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) moved the Cyber Assets outside the ESP by placing new firewalls between the routers and energy management system network to ensure that they are no longer access points nor classified as Cyber Assets within the ESP; 2) verified that the new firewalls became the access points and provide a deny-by-default access control model and enable only ports and services required for operation; 3) refined the rule sets on the existing access points specifically to identify the allowed IP addresses to ensure that, unless specifically noted and justified, all access point rule sets explicitly identify the permitted network addresses across the perimeter; and 4) wrote a procedure for securing dial-up access to the ESP. | 2013-02-21 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-08-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010359 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R3, R3.1, and R3.2. FRCC_URE1 failed to implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeters (ESPs) 24 hours a day, seven days a week. Specifically, some Cyber Asset failed to log access for a period of eight hours. In addition, FRCC_URE1 failed to log all the successful attempts at access points for all Cyber Assets. Lastly, FRCC_URE1 failed to detect and alert for attempts at or actual unauthorized accesses for a number of access points; no technical feasibility exceptions (TFE) were filed, and FRCC_URE1 had not performed a manual review of logs every 90 days. | CIP-005-1 | R3; R3.1; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to implement electronic or manual processes for monitoring and logging access can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was mitigated because the lack of logging was limited to successful access at only 30% of the access points and only a few Cyber Assets during an outage for a period of eight hours. Additionally, all the denied attempts were being logged at the IP-accessible access points. | when the Standard became mandatory and enforceable for FRCC_URE1 | when FRCC_URE1 finalized the process for logging and monitoring access | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) developed a process for logging and capturing internal log buffer during logging disruptions for access points; 2) purchased, tested, and implemented backup syslog server; 3) implemented the logging process and tested logging of successful and unsuccessful login attempts at all access points; 4) finalized logging process document and added reference to process in appropriate FRCC_URE1 practice; and 5) performed compliance department final review of mitigation plan completion. | 2013-05-14 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-08-30 | FERC | NP13-51-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010358 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-007-1 R3, R3.1, and R3.2. FRCC_URE1 failed to establish, document, and implement a security patch management program for tracking, evaluating, testing, and installing applicable cybersecurity software patches for all Cyber Assets within the Electronic Security Perimeters (ESPs). Specifically, for some Cyber Assets and workstation/server applications, FRCC_URE1 documentation was insufficient to demonstrate that available patches were evaluated for applicability. Also, FRCC_URE1 did not evaluate new software releases containing security upgrades. Further, FRCC_URE1 documents were insufficient to demonstrate that FRCC_URE1 assessed security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to establish, document, and implement a complete security patch management program can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was mitigated because FRCC_URE1 patched operating systems on all of the servers and workstations, which made up most of the Cyber Assets (between 79% and 94%) over the duration of the violation. | when the Standard became mandatory and enforceable for FRCC_URE1 | present | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) scanned Critical Cyber Assets and Cyber Assets, and generated a list of installed applications running on each asset; 2) reviewed the Cyber Asset application inventory spreadsheet, and identified the applications that could be removed; and 3) had a vendor remove unnecessary applications from the Cyber Assets and hired a vendor to conduct security patch assessment and testing. To mitigate this violation, FRCC_URE1 will: 1) develop interim processes to bring Cyber Assets into compliance and to assess non-vendor-supported security patches; 2) start the process of bringing Cyber Assets into compliance; 3) modify or replace FRCC_URE1 documentation to include new processes for non-vendor security patches; 4) remove all non-approved software from all Cyber Assets; 5) assess all non-vendor security patches for all Cyber Assets; 6) either install security patches or implement compensating measures, and place all Cyber Assets under FRCC_URE1's process documentation; and 7) perform corporate compliance department final review. | 12/20/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-08-30 | FERC | NP13-51-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100371 | Notice of Confirmed Violation | During a Spot Check, MRO discovered that MRO_URE1 was in violation of CIP-002-1 R3. MRO_URE1 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of Critical Assets. During the Spot Check, MRO_URE1 failed to present sufficient evidence to demonstrate that Cyber Assets outside of a given Critical Asset’s Electronic Security Perimeter (ESP) and not co-located with the Critical Asset were properly evaluated (i.e., determined to be essential or not essential to the operation of the Critical Asset). MRO_URE1 originally identified 130 Cyber Assets that needed to be evaluated for criticality. During mitigation, MRO_URE1 identified 1,296 Cyber Assets that needed to be evaluated for criticality, including all Cyber Assets at substations with routable connectivity to MRO_URE1's control centers (two Critical Assets). The assessment of the new list did not result in the identification of any additional CCAs. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although there was a large increase in the number of Cyber Assets included in MRO_URE1's evaluation, the additional Cyber Assets consisted of remote terminal units, substation intelligent electronic devices, and substation routers. These devices reside on a network separate from the control centers, with firewalls in place between the networks. Furthermore, these firewalls were sampled in a previous Compliance Audit for another CIP standard, and MRO did not identify any issues with the configuration to protect the control center ESP. Additionally, because MRO_URE1 does not possess any substations that are identified as Critical Assets, the evaluation of the substation Cyber Assets focused only on their impact on the control center's CCAs; these CCAs reside in a different Physical Security Perimeter and in a different ESP than the Cyber Assets added to the evaluation. | when the Standard became mandatory and enforceable for MRO_URE1 | when MRO_URE1 developed a list of associated CCAs essential to the operation of Critical Assets | 6000 | Spot Check | To mitigate this violation, MRO_URE1: 1) developed a list of associated CCAs essential to the operation of Critical Assets; 2) revised its assessment procedure for its next annual risk-based assessment methodology; and 3) provided training to the individuals responsible for implementing the modified procedure. | 2012-09-10 | 2012-09-12 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination.
2013-08-30 | FERC | NP13-51-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100470 | Settlement Agreement | Texas RE conducted an on-site Compliance Audit of Texas RE_URE1. During the Compliance Audit, Texas RE discovered Texas RE_URE1 had a violation of CIP-007-2a R2. A review of Texas RE_URE1's CIP-007 policy, required ports and services listings, firewall configuration, and Critical Cyber Asset (CCA) cyber vulnerability assessment (CVA) suggested that despite having an established and documented process, Texas RE_URE1 failed to implement its process fully to ensure that only those ports and services required for normal and emergency operations are enabled, a violation of CIP-007 R2. Texas RE_URE1's Electronic Security Perimeter (ESP) policy states that firewalls are configured to allow for only the ports and services necessary for normal and emergency operations. However, in comparing Texas RE_URE1's listings of required ports and services with its CVA, open ports and services were identified during the CVA that were not documented in the applicable listings. All the required ports and services referenced in the three listings at minimum were expected to be identified in the CVA. The CVA was performed to identify all the open ports and services required to conduct normal and emergency cyber operations. Subsequently, Texas RE_URE1 provided supplemental documentation that identified additional open ports and services that were used for Texas RE_URE1's Supervisory Control and Data Acquisition (SCADA) that were not included in the CVA. This misalignment between the subject documents demonstrates that Texas RE_URE1 failed to follow its process to identify and ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-2a | R2 | Medium | Severe | This violation posed a moderate risk but not a serious or substantial risk to the reliability of the bulk power system. The moderate risk was partially mitigated by Texas RE_URE1 providing a layered approach to protecting its Cyber Assets. Texas RE_URE1's layered approach includes firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and ESP/Physical Security Perimeter access authentication. Additionally, Texas RE_URE1 has an established CIP-007 program it relies upon, which has been in place since the Standard became mandatory and enforceable. | when the Standard became mandatory and enforceable to Texas RE_URE1 | Mitigation Plan completion | $15,000 (for TRE201100470 and TRE201100472) | Compliance Audit | To mitigate this violation Texas RE_URE1: 1) performed a CVA to include all the applicable open ports and services required to conduct normal and emergency operations; 2) updated its CVA procedures to ensure all open ports and services are included in future assessments; and 3) updated the CVA process version to prevent the likelihood of reoccurrence. | 2011-12-22 | 2013-05-24 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
2013-08-30 | FERC | NP13-51-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100472 | Settlement Agreement | Texas RE conducted an on-site Compliance Audit of Texas RE_URE1. During the Compliance Audit, Texas RE discovered Texas RE_URE1 had a violation of CIP-007-2a R8.2. A review of Texas RE_URE1's CIP-007 policy, required ports and services listings, firewall configuration, Critical Cyber Asset cyber vulnerability assessment (CVA), CVA Procedure, and a statement from Texas RE_URE1 revealed that the required user datagram protocol (UDP) ports were not included in the CVA or reviewed, in violation of CIP-007-2a R8.2. CIP-007 R2 required Texas RE_URE1 to perform a CVA on all Cyber Assets within its Electronic Security Perimeter (ESP) at least annually and to verify that only ports and services required for operation of the Cyber Assets within the ESP are enabled. Texas RE_URE1 has a documented process to ensure vulnerabilities are discovered in the equipment residing inside Texas RE_URE1's ESPs. The evidence showed the transport control protocol (TCP) and UDP ports are required for the operation of Cyber Assets residing in the ESP. However, the ports and services scan and CVA report revealed the CVA only included the ports and attached services associated with the TCP ports and not the UDP ports. Pursuant to the Standard, Texas RE_URE1 was also expected to conduct a verification and review on the UDP ports, which it did not. Further, there was no evidence provided to show attempts by Texas RE_URE1 to discover the UDP ports. During the Compliance Audit Texas RE_URE1 stated the UDP ports were inadvertently left off the port scan. | CIP-007-2a | R8; R8.2 | Medium | Severe | This violation posed a moderate risk but not a serious or substantial risk to the reliability of the bulk power system. The moderate risk was partially mitigated by Texas RE_URE1 providing a layered approach to protecting its Cyber Assets. Texas RE_URE1's layered approach includes firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and ESP/Physical Security Perimeter access authentication. Additionally, Texas RE_URE1 has an established CIP-007 program it relies upon, which has been in place since the Standard became mandatory and enforceable. | when the Standard became mandatory and enforceable to Texas RE_URE1 | Mitigation Plan completion | $15,000 (for TRE201100470 and TRE201100472) | Compliance Audit | To mitigate this violation Texas RE_URE1: 1) performed a CVA to include all the applicable open ports and services required to conduct normal and emergency operations; 2) updated its CVA procedures to ensure UDP ports are included in future assessments; and 3) updated the CVA process version to prevent the likelihood of reoccurrence. | 2011-12-22 | 2013-05-24 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
2013-08-30 | FERC | NP13-51-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100556 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE2 and determined that it had a violation of CIP-005-1 R4.3. Texas RE_URE2 failed to identify multiple Electronic Security Perimeter (ESP) access points as required by CIP-005-1 R4.3. A review of Texas RE_URE2's Cyber Vulnerability Assessment (CVA) procedures, electronic access procedures, the scan report, and the CVA revealed that several routers and network sub sets were absent from the CVA, the scan, and the manual access point identification process. Consequently, the discrepancies between the access point identification methodologies, the access point identification results, the documented access points, and the lack of the discovery of all the ESP access points demonstrates non-compliance with CIP-005-1 R4.3. | CIP-005-1 | R4; R4.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk was mitigated by Texas RE_URE2 evidencing that an annual CVA and review was conducted on all of the ESP access points except the referenced routers and network sub sets and the report revealed no material issues. A review of the enabled ports and services for operations at the identified access points was conducted. Further, Texas RE_URE2 implemented a CVA program that has been in place since the standard became enforceable. | when the Standard became mandatory and enforceable on Texas RE_URE2 | Mitigation Plan completion | $17,200 (for TRE201100556 and TRE201100559) | Compliance Audit | To mitigate this violation, Texas RE_URE2: 1) conducted a CVA to demonstrate a vulnerability assessment was conducted on all the access points identified within the subject ESP; and 2) conducted training on its updated ESP access point evaluation and identification processes. In addition, Texas RE_URE2 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2011-09-01 | 2013-04-17 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
2013-08-30 | FERC | NP13-51-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100559 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE2 and determined that it had a violation of CIP-007-1 R8. Texas RE_URE2 performed a cyber vulnerability assessment (CVA) on the Cyber Assets within its defined Electronic Security Perimeter (ESP), but the annual assessment did not include all the Cyber Assets in its two ESPs as identified on its network diagram. Based upon the review of the CVA provided by Texas RE_URE2 during the Compliance Audit, no evidence was provided to demonstrate that a CVA was performed on two Cyber Asset groups residing within the ESP. Several servers and web user interface devices identified by Texas RE_URE2 as Cyber Assets and shown within the ESP on the network diagram were not included in the CVA, the scan report, or manual scan results. This is a violation of CIP-007-1 R8, because the standard requires all Cyber Assets within an ESP to be included in a CVA assessment. | CIP-007-1 | R8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk was mitigated by Texas RE_URE2 evidencing an annual CVA and a review was conducted on all of the Cyber Assets within the ESP except the referenced routers and network sub sets and the report revealed no material issues. A review of the enabled ports and services required for operation of the identified Cyber Assets also was conducted. Further, Texas RE_URE2 has implemented a CVA program that has been in place since the standard became enforceable. | when the Standard became mandatory and enforceable on Texas RE_URE2 | Mitigation Plan completion | $17,200 (for TRE201100556 and TRE201100559) | Compliance Audit | To mitigate this violation, Texas RE_URE2: 1) completed its cyber vulnerability assessment on the missed devices; 2) reviewed and updated the Critical Cyber Asset (CCA) list and the drawing for the CCA ESP during change control meetings; and 3) compared the vulnerability assessment report to the CCA list and the ESP network drawing to ensure that the three documents match and are correct. In addition, Texas RE_URE2 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2013-07-11 | 2013-07-16 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
2013-08-30 | FERC | NP13-51-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012010292 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE3 and determined that Texas RE_URE3 had a violation of CIP-004-1 R4. Texas RE_URE3 was able to provide evidence that it maintained a list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). However, Texas RE determined that Texas RE_URE3 did not include the user’s specific electronic and physical access rights to CCAs. Although Texas RE_URE3 provided an Access Control List (List) that listed users with authorized cyber or authorized unescorted physical access to CCAs, Texas RE_URE3's List did not provide dates when: 1) the List was generated; 2) access for users and contractors was effective; and/or 3) specific electronic and physical rights to CCAs were granted to individually approved personnel. | CIP-004-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Texas RE_URE3 did not include each user’s specific electronic and physical access rights to CCAs, the Texas RE_URE3 infrastructure is protected from penetration by various layers of protection including firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and Electronic Security Perimeter (ESP)/Physical Security Perimeter (PSP) access authentication. | when the Standard became mandatory and enforceable on Texas RE_URE3 | Mitigation Plan completion | 4800 | Compliance Audit | To mitigate this violation, Texas RE_URE3 developed a master spreadsheet to detail the granted access duration dates and to indicate the specific access rights for each user. In addition, Texas RE_URE3 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2010-12-31 | 2013-06-05 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
2013-08-30 | FERC | NP13-51-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010764 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-2 R3. Specifically, WECC_URE1 stated that on two separate instances it failed to monitor and log access at all access points to its Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. The first instance occurred for four days, and the second occurred for one day. WECC_URE1's firewalls controlling the sites' ESPs send access logs to a firewall manager device that retains the logs and then sends the logs to another device for analysis and detection. However, during two separate instances, the firewall manager failed, and the firewall logs were not retained and sent to the analysis and detection device. Because of the failure of the firewall manager device, WECC_URE1 was unable to monitor and log access at the access points to its primary and backup ESPs for one day. These access points contain a total of eleven Critical Cyber Assets (CCAs). | CIP-005-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE1 stated that during these occasions, the firewalls were working to control access at both the sites. In addition, the management system was being monitored by the system personnel for any unusual activity. | when WECC_URE1 failed to monitor and log access at all access points to its ESPs when WECC_URE1 failed to monitor and log access at all access points to its ESPs | when WECC_URE1 replaced the firewall manager and continued to monitor and log access at all access points to its ESPs when WECC_URE1 replaced the firewall manager and continued to monitor and log access at all access points to its ESPs | 20000 | Self-Certification | To mitigate this violation, WECC_URE1 replaced the failed firewall manager with a new unit. | 2012-03-28 | 2013-04-30 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's above and beyond measures to be a mitigating factor in the penalty determination. Specifically, WECC_URE1 will: 1) develop a process to track deadlines and mitigate timely minimizing the need for Mitigation Plan extension requests; 2) create a monthly coordination meeting between compliance groups that will focus on increasing communication between entities and centralizing issues stemming from information silos; 3) create an annual compliance awareness training program and measure the degree of understanding; 4) develop a process or improvements to processes that help identify the full scope of violations promptly; and 5) develop a process for detecting what controls are needed when new devices are installed.
2013-08-30 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100340 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-002-1 R1. MRO_URE1 failed to have a risk-based assessment methodology (RBAM) that adequately considered control centers, load shedding, and any additional assets that support the reliable operation of the bulk power system (BPS) that MRO_URE1 deems appropriate to include in its assessment. Specifically, MRO_URE1’s RBAM did not contain adequate evaluation criteria for control centers which would justify a classification of an asset as either critical or non-critical. MRO_URE1 performed a new risk-based assessment to update its RBAM documentation. MRO_URE1’s RBAM did not declare any Critical Assets. | CIP-002-1 | R1; R1.2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s security controls, lack of Critical Assets, and its size. After revising its RBAM to comply with its Mitigation Plan, MRO_URE1 did not have any Critical Assets. Additionally, MRO_URE1 performed a vulnerability assessment on its inter-control center communications protocol (ICCP) links connecting its energy management system (EMS) with its Reliability Coordinator’s EMS. The assessment revealed that the security controls in place on those connections during the pendency of the violation included an ICCP configuration on its servers and firewalls for the ICCP links. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) reviewed and revised a large portion of its RBAM specifically addresses each of the assets identified in CIP-002-3 R1 CIP Compliance Audit as not being assessed. This new version specifically addresses each of the assets identified in CIP-002-3 R1, even if MRO_URE1 does not own or operate some of those assets; 2) identified additional criteria for its RBAM to delineate more clearly the methodology from the assessment; 3) revised its RBAM based on the results of the evaluation conducted in Step 2. Significant modifications were made to separate the methodology completely from the assessment; and, 4) conducted a risk-based assessment of all applicable facilities by applying the RBAM developed in Step 3. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-08-30 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100343 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-003-1 R6. MRO_URE1 failed to document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs) pursuant to the change control process. Although MRO_URE1 had a documented change control program, it did not document all patch changes to CCAs. MRO_URE1 provided samples of the change ticket process. However, MRO determined that security patches were applied to CCAs that were not documented using the change management process as required. MRO_URE1 applied changes to CCAs, but change tickets were not generated for the changes. | CIP-003-1 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1’s had no Critical Assets. MRO determined that security patches were applied to CCAs although they were not documented using the change management process as required. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-08-30 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100344 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-004-1 R3. MRO_URE1 failed to have Personnel Risk Assessments (PRAs) for all personnel with authorized cyber or authorized unescorted access to Critical Cyber Assets (CCAs), in accordance with CIP-004-1 R3. Although MRO_URE1 implemented a PRA program to conduct seven-year criminal background checks and identity verification, one sampled individual was considered "escorted with card access" and was given card access. However, the individual did not receive a PRA until after access was granted. | CIP-004-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-08-30 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100345 | Notice of Confirmed Violation | During a Compliance Audit was in violation of CIP-004-1 R4. MRO_URE1 failed to demonstrate that it performed reviews of cyber access privileges in accordance with CIP-004-1 R4.1. MRO_URE1 performed quarterly reviews on physical privileges only, and policy and procedure documents did not demonstrate that electronic access was also reviewed when reviewing physical access. Additionally, MRO_URE1’s access list included individuals with cyber access and no physical access, as well as individuals with identical physical privileges and differing electronic privileges. | CIP-004-1 | R4; R4.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-08-30 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100346 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R1. MRO_URE1 failed to afford Cyber Assets used in the access control and monitoring of the Electronic Security Perimeters (ESPs) with protective measures as specified in Standard CIP-007 R1, in accordance with CIP-005-1 R1.5. Specifically, MRO_URE1 failed to provide documentation of test procedures for review and failed to document that test procedures reflected the MRO_URE1 production environment, in accordance with CIP-007-1 R1.2. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100347 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R2. MRO_URE1 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter in accordance with CIP-005-1 R2. MRO_URE1 performed a cyber vulnerability assessment (CVA). During the review, the list of open ports required did not include the purpose or function of the open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operations. Additionally, MRO Audit staff found that multiple CVA recommendations were not identified properly as vulnerabilities. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100348 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R3. MRO_URE1 failed to configure its security monitoring process to detect and alert for attempts at or actual unauthorized access, in accordance with CIP-005-1 R3.2. Additionally, MRO_URE1 failed to review firewall logs every 90 calendar days. MRO_URE1 policy states that reviews will be documented with a sample. However, MRO_URE1 did not provide any documentation to demonstrate that the logs were reviewed. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100349 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R4. MRO_URE1 failed to have a cyber vulnerability assessment (CVA) which included a review to verify that only ports and services required for operations at these access points are enabled, in accordance with CIP-005-1 R4.2. MRO_URE1 performed a CVA. During the review, the list of open ports required did not include the purpose or function of the open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operations. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. MRO_URE1 also failed to document the action plan to remediate vulnerabilities and document the execution status in accordance with CIP-005-1 R4.5. | CIP-005-1 | R4.2; R4.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100352 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R1. MRO_URE1 failed to document cybersecurity test procedures in a manner that minimizes adverse effects on the production system or its operation, in accordance with CIP-007-1 R1.1; and failed to document that test procedures by MRO_URE1 or by the application vendor reflected the MRO_URE1 production environment, in accordance with CIP-007-1 R1.2. Additionally, MRO_URE1 did not test all changes to Critical Cyber Assets (CCAs). Although MRO_URE1 provided samples of the change ticket process, the security patches were applied to CCAs without the required testing. MRO_URE1 also failed to document its test results in several cases in accordance with CIP-007-1 R1.3. MRO sampled two server changes. In both cases, configuration changes to the application and server communication ports occurred, but no testing occurred prior to implementation. | CIP-007-1 | R1; R1.1; R1.2; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100353 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R2. MRO_URE1 failed to enable only those ports and services required for normal and emergency operations in accordance with CIP-007-1 R2. MRO_URE1 performed a cyber vulnerability assessment (CVA). During the review, the list of open ports required did not include the purpose or function of the open ports. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operation. | CIP-007-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100354 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R3. MRO_URE1 failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades in accordance with CIP-007-1 R3. MRO_URE1 provided evidence that a third-party contractor had been certifying the security patches, although MRO_URE1 failed to provide any of the supporting documentation, including tracking, evaluating, and testing. MRO also sampled one of MRO_URE1’s Cyber Assets for patches. MRO_URE1 failed to document the assessment and implementation of the patch within 30 days of its release. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100355 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1. MRO_URE1 failed to document and implement a process for the update of anti-virus and malware prevention “signatures” in accordance with CIP-007-1 R4.2. Specifically, MRO_URE1 did not have a documented process for updating the anti-virus signatures of Critical Cyber Assets (CCAs). MRO_URE1 described its process to the MRO Compliance Audit staff verbally, but did not provide any documentation to demonstrate that testing occurred prior to implementation. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100356 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R5. MRO_URE1 failed to establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access in accordance with CIP-007-1 R5. MRO_URE1 failed to ensure that user accounts are implemented as approved by designated personnel, in accordance with CIP-007-1 R5.1.1. Specifically, the MRO_URE1 security management controls policy contained four conflicting definitions regarding who is responsible for approval of logical access changes. MRO_URE1 also failed to establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety 90 days, in accordance with CIP-007-1 R5.1.2. Although MRO_URE1 provided sample logs which contained successful and failed login data, the logs did not contain detail to create historical audit trails of individual user account activity. Also, the sample logs provided did not demonstrate that logs were being reviewed every 90 days. MRO_URE1 also failed to review, at least annually, user accounts to verify access privileges are in accordance with Standards CIP-003 R5 and CIP-004 R4, as required by CIP-007-1 R5.1.3. Quarterly reviews were based on physical privileges only, and policy and procedure documents did not reflect the assertion that electronic access was implicitly reviewed when reviewing physical access. Additionally, the access list included individuals with cyber access and no physical access, as well as individuals with identical physical privileges and differing electronic privileges. MRO_URE1 also failed to implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts, in accordance with CIP-007-1 R5.2. Although the MRO_URE1 systems security management policy defined the policy for default accounts and shared online supplier inquiry (OSI) administrator accounts, it did not define the scope and acceptable use of firewall and switch administrator accounts. The systems security management policy also did not require that the enabled firewall and switch shared administrator account passwords must be changed prior to being put into service in accordance with CIP-007-1 R5.2.1; failed to identify those individuals with access to firewall and switch administrator accounts and did not identify a policy to manage these accounts, in accordance with CIP-007-1 R5.2.2; and did not provide manual or automated audit trails on shared accounts in accordance with CIP-007-1 R5.2.3. | CIP-007-1 | R5; R5.1.1; R5.1.2; R5.1.3; R5.2; R5.2.1; R5.2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. control center was no longer a Critical Asset. Additionally, MRO_URE1’s highest voltage level is 161 kV. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100357 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R6. MRO_URE1 failed to implement automated tools or process controls which are capable of issuing automated or manual alerts for detected cyber security incidents in accordance with CIP-007-1 R6.2. Per the compensating measures described in a technical feasibility exception, MRO_URE1 is supposed to review logs every 90 days. Although MRO_URE1 provided sample logs with successful and failed login data, the samples did not contain detail to determine whether security incidents had occurred during the period. While the network monitoring screen can detect a Cyber Asset shutdown after a security incident has occurred, the monitoring process did not detect the Cyber Asset intrusion and other security incidents. Also, the logs provided did not demonstrate that logs were being reviewed every 90 days in accordance with CIP-007-1 R6.4. | CIP-007-1 | R6; R6.2; R6.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating/neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100358 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R8. MRO_URE1 failed to have a cyber vulnerability assessment (CVA) which: 1) verified that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter were enabled, in accordance with CIP-008-1 R8.2; 2) reviewed controls for default accounts, in accordance with CIP-008-1 R8.3; and 3) documented the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan, in accordance with CIP-008-1 R8.4. MRO_URE1 did not provide documentation to determine whether ports were needed only for normal and emergency operations. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. MRO_URE1 also failed to demonstrate that the default accounts on two servers were reviewed. | CIP-007-1 | R8; R8.2; R8.3; R8.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100359 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-009-1 R4. MRO_URE1 failed to provide a recovery plan with processes and procedures for the backup and storage of information required to restore Critical Cyber Assets (CCAs). | CIP-009-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2011008257 | Settlement Agreement | SPPRE_URE1 self-reported a violation of CIP-007-3a R2.1 and R2.2. SPPRE_URE1 discovered that ports were enabled on its Energy Management System (EMS) system that were not required for normal or emergency operations. During a cyber vulnerability assessment (CVA), SPPRE_URE1 identified five enabled ports affecting ten EMS Cyber Assets that were not required for either normal or emergency operations. | CIP-007-3a | R2; 2.1; 2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was minimal because the affected Cyber Assets were within an Electronic Security Perimeter (ESP) and thereby afforded the required protective measures. For instance, the EMS Cyber Assets are guarded by electronic access point firewalls, which utilize anti-virus software to scan and block malicious software crossing the firewall. The EMS Cyber Assets are also protected by an intrusion prevention system (IPS), which further prevents malicious inbound and outbound traffic. Furthermore, the EMS Cyber Assets are running anti-virus software, which provides a third layer of protection against malware beyond the firewalls and IPS. Moreover, physical access to all Cyber Assets within the SPPRE_URE1 ESP is limited to authorized personnel via badge access. Finally, no malicious exploitation of the erroneously enabled ports was identified by SPPRE_URE1. | when the five ports were enabled | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Self-Report | To mitigate this violation, SPPRE_URE1: 1) disabled the non-required ports and services identified in its Self-Report; 2) performed an additional review of all enabled ports associated with Cyber Assets within the ESP to ensure the ports were required for either normal or emergency operations; and 3) retained a vendor to complete on-site work for scanning all devices within the ESP. | 7/16/2012 | 8/15/2012 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPPRE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPPRE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009927 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 did not implement access monitoring, access logging, or alerting capabilities for unauthorized access on six devices, in violation of CIP-005-1 R3.2. The devices at issue included four network switches and two security management systems. SPP RE subsequently determined that only the four network switches were Electronic Security Perimeter (ESP) access points and subject to CIP-005-1 R3.2. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Other than the four network switches, was monitoring and logging access at all access points to the ESP and had security alerting capability to detect and alert for unauthorized attempts and or access to the ESP. Additionally, the four network switches resided behind two firewalls that filtered all external communications entering the ESP and were continuously monitored, logged, and providing alerts to SPPRE_URE1 personnel. Therefore, any unauthorized external access attempts would have been monitored, logged, and alerts would have been sent to appropriate security personnel. Moreover, SPPRE_URE1's intrusion prevention system (IPS) was monitoring traffic between the firewalls and the four network switches. The IPS is configured to prevent identified malicious communication from entering the switches. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) added the four network switches to the monitoring and logging system provided by its third-party network security provider. The system monitors and logs activity at all times and alerts appropriate security personnel of any unauthorized attempts and access to SPPRE_URE1's ESP. | 2012-09-07 | 2012-10-10 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPPRE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPPRE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009936 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had not implemented automated tools or organizational process controls to monitor, log, and alert SPPRE_URE1 of possible security events on two Cyber Assets (vulnerability scanners) within its Electronic Security Perimeter (ESP). For the two vulnerability scanners, SPPRE_URE1 did not: 1) document and implement the processes for monitoring (R6.1); 2) institute automated or manual alerting (R6.2); 3) maintain logs in support of incident response (R6.3); 4) retain logs for 90 calendar days (R6.4); and, 5) review logs of security events related to cyber security and maintain records documenting review of logs (R6.5). | CIP-007-1 | R6; R6.1; R6.2; R6.3; R6.4; R6.5 | Medium; | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Except for the two vulnerability scanners, SPPRE_URE1 implemented and documented automated tools or organizational process controls to monitor, log, and alert for possible security events on all Cyber Assets within the ESP. Additionally, SPPRE_URE1's intrusion protection and detection system (IPS/IDS) monitors, alerts, and prevents security events inside the SPPRE_URE1 ESP on a continuous basis and was doing so for the duration of this violation. As a result, malicious traffic impacting the two vulnerability scanners would have been subject to identification and prevention by the IDS/IPS, which would also have alerted SPPRE_URE1 personnel. Additionally, SPPRE_URE1 attested that there were no cyber security system events during the duration of the violation. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) removed the two vulnerability scanners from the ESP and from its Cyber Asset list; and 2) added the devices to its monitoring service, which provides 24- hour, seven days a week monitoring and alerting for unauthorized access attempts. | 2012-07-25 | 2012-08-03 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPPRE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPPRE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011103 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPPRE_URE1 violated CIP-007-1 R3.2 because it failed to document adequately the application of security patches and compensating measures for 6.0 % of patches published during an approximate three year period. SPP RE subsequently determined that for those patches lacking documentation: 1) the vulnerability posed was remediated by a separately released patch; 2) the patch itself was determined to present a risk to cyber systems, and therefore not installed; or 3) the patch was not a “security” patch. | CIP-007-1 | R3.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was minimal because the affected Cyber Assets were within an Electronic Security Perimeter (ESP) and thereby afforded substantial protective measures. For instance, the affected Cyber Assets are guarded by electronic access point firewalls, which utilize anti-virus software to scan and block malicious software crossing the firewall. Additionally, SPPRE_URE1's ESP is continuously monitored and protected by an intrusion prevention and detection system (IPS/IDS), which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Furthermore, the affected Cyber Assets were running anti-virus software, which provided a third layer of protection against malware beyond the firewalls and IPS. Moreover, physical access to all Cyber Assets within the SPPRE_URE1 ESP was limited to authorized personnel via badge access. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPPRE_URE1: 1) reviewed all patches that lacked documentation of compensating measures or a patch being applied; and 2) ensured all patches were up to date for all Cyber Assets within the scope of this violation. | 2012-04-11 | 2013-04-30 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPPRE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPPRE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010414 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R4. WECC_URE1 reported that on five occasions it failed to update Critical Cyber Asset (CCA) access lists within seven days of a change in personnel with access to CCAs, or any change in the access rights of such personnel. Further, WECC_URE1 reported that it failed to revoke access within seven days for personnel who no longer required such access to CCAs. Based on the Self-Report and additional information provided by WECC_URE1, WECC determined that physical access to CCAs was revoked for one WECC_URE1 employee and the access list was updated three months later. In another instance, physical access was granted to two WECC_URE1 employees and the access list was updated two weeks later. In addition, an individual left WECC_URE1 and the individual’s electronic access rights were revoked almost two months later. Finally, an individual left WECC_URE1 and the individual’s electronic access was revoked two weeks later. WECC determined that WECC_URE1’s failure to update access lists within seven days constituted a violation of CIP-004-3 R4.1. WECC also determined that WECC_URE1’s failure to revoke access rights within seven days constituted a violation of CIP-004-3 R4.2. | CIP-004-3 | R4; R4.1; R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the violation was limited to four individuals and all four individuals had completed cybersecurity training and personnel risk assessments. All CCAs to which the individuals had access were secured within Electronic Security Perimeters (ESPs). In addition, electronic access to the ESPs was controlled and monitored. CCAs were monitored for system events and unauthorized access attempts, which trigger alarms. All CCAs, to which individuals had access, were secured within Physical Security Perimeters (PSPs). All PSPs were monitored by security personnel on a continual basis, and unauthorized access attempts would trigger alarms. Further, physical access and physical access attempts were logged per CIP-006 R6. | seven days after WECC_URE1 failed to update the access list | Mitigation Plan completion | $10,000 | Self-Report | To mitigate this violation, WECC_URE1: 1) developed and provided additional procedural training to top managers and administrative officers, as well as supervisors and administrative staff at each facility, to ensure that they understand their responsibilities with regard to NERC Standards compliance; 2) finalized and packaged training materials; 3) provided specialized CIP training to top managers and administrative officers as well as to supervisors and administrative staff; and 4) finalized any associated documentation. | 2012-09-05 | TBD | Does Not Contest | WECC did not review WECC_URE1's internal compliance program (ICP) and therefore did not consider it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011961 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R4. WECC_URE2 stated that during a quarterly review it failed to ensure a number of instances of change in personnel were updated on the Critical Cyber Assets (CCAs) access list within seven days of making the change. The instances involved employees that no longer required access and employees that required and obtained access. | CIP-004-1 | R4 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE2 failed to update its access list within seven days, physical and electronic access was timely revoked for individuals that no longer required access, including accounts disabled, shared passwords changes, and physical access revoked. Additionally, the individuals were not terminated for cause and left in good standing with WECC_URE2. All CCAs were within defined Physical Security Perimeters (PSPs) where access is restricted to individuals with authorization, training, and current personnel risk assessments (PRAs), and all access to PSPs requires valid identification badges. The individuals whose access was granted had valid identification badges which restrict and monitor all physical access. The individuals had authorized physical and cyber access, training, and current PRAs. Additionally, the violation affected less than 5% of authorized WECC_URE2 employees or contractors. Lastly, the required changes with respect to access were made but the administrative task of updating the access list was not performed. | seven days after WECC_URE2 failed to update the access list for the first change in personnel | Mitigation Plan completion | $15,000 | Self-Report | To mitigate this violation, WECC_URE2: 1) updated the access list; and 2) reassigned responsibility for updating the access list to different individuals. | 2013-02-24 | 2013-03-29 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009451 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-005-3 R1.5. Two firewalls were commissioned that were not afforded all of the protections required under the Standard. The two firewalls commissioned by WECC_URE3 were Electronic Security Perimeter (ESP) access control and monitoring (ACM) devices. Under CIP-005-3a R1.5, entities must afford ACM devices 24 different protective measures. In this case, WECC found that WECC_URE3 afforded two protective measures by securing the ACM devices within a Physical Security Perimeter (PSP) and ensuring that all personnel with access to the two ACM devices completed a personnel risk assessment (PRA). However, WECC also determined that WECC_URE3 failed to afford 22 additional protective measures required under CIP-005-3a R1.5. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) given the scope of the violation and compensating measures in place during the violation period. The scope of the violation is limited to 2.9% of WECC_URE3's ACM devices. Both of the devices are located within an ESP and a PSP. Physical and electronic access to the 2.9% ACM devices is controlled and monitored and individuals with specific access to the two devices had completed PRAs. | when WECC_URE3 commissioned two firewalls without all of the protections required under CIP-005-3 R1.5 | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: a) reviewed existing CIP documentation as well as the applicable devices to determine which of the protections/controls enumerated in this Requirement have been put into place, and which still need to be applied; b) updated the documentation to reflect current implementation of the two firewalls and implement any missing protections/controls; c) created an install/modify/removal policy to ensure equipment installations, modifications and removals follow appropriate change management procedures in accordance with the CIP requirements; and d) provided training for a network data team on the new process and policy. | 2012-06-28 | 2013-06-25 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009453 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-005-3 R5. WECC_URE3 reported two instances of noncompliance. The first instance occurred when WECC_URE3 implemented a change in its technical and procedural mechanisms for electronic access to access points to ESPs for WECC_URE3's energy management system (EMS). WECC_URE3, however, discovered that it failed to update documentation to reflect modification of network controls within 90 days, in violation of CIP-005-3 R5.2. WECC found that WECC_URE3 implemented significant changes to network controls, without updating network control procedural documentation within 90 days of the change. WECC determined that WECC_URE3 failed to update changes to electronic access control procedures within ninety days, in violation of R5.2. The second instance of noncompliance occurred approximately a year later, when WECC_URE3 implemented a configuration change to its electronic security monitoring system that resulted in a failure to retain electronic access logs for 90 days, in violation of R5.3. WECC determined that WECC_URE3 was in violation of R5.3 for not maintaining electronic access logs for 90 days. | CIP-005-3a | R5; R5.2; R5.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because of mitigating factors in place during the duration of the violation. Electronic access logs were generated and retained on local cyber assets. In the event of a system event, these local logs would have been available for review. Access to ESPs was controlled and monitored during the duration of the violation. Lastly, WECC_URE3 implemented intrusion detection and prevention controls that would have immediately detected and alerted unauthorized access or malicious activity within the ESP. | when WECC_URE3 implemented significant changes to network controls | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: a) For CIP-005-3 R5.2: 1) conducted a review of the existing documentation against the current processes and procedures. WECC_URE3 identified any discrepancies and updated documentation. Once the documentation was updated and approved, all network data team members were trained on the current processes; 2) created a new documentation review procedure to ensure that documentation related to CIP-005 is reviewed and updated within 90 days of any significant changes and again annually to ensure that WECC_URE3 is compliant with the R5 requirement; b) For CIP-005-3 R5.3: 1) ensured that the CIP-applicable devices are only creating those logs that are necessary and appropriate. There may have been too many legitimate event logs being generated by the CIP-applicable devices and negatively impacting log management. Not all of these log events were necessary for security review and incident response processes. WECC_URE3 reduced the unnecessary log generation to help with log storage, management, and review processes; 2) ensured that its Security Incident and Event Management (SIEM) tools were licensed appropriately. Once the aforementioned process was been completed, WECC_URE3 was able to determine if sufficient license thresholds have been purchased. WECC_URE3 then created alerts that will be triggered if applicable devices are creating an unexpected number of events; and 3) developed better alerting conditions designed to more quickly identify logging levels that threaten WECC_URE3's ability to be alerted to certain security issues or sufficiently retain logs to respond to potential incidents. WECC_URE3 also reviewed its current monitoring process for efficiencies and possible improvements that may help mitigate future risk from similar issues. | 2012-06-28 | 2012-10-08 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009459 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3 R6.3. WECC_URE3 implemented a configuration change to its electronic security monitoring system that resulted in a failure to retain electronic system event logs for 90 days, in violation of CIP-007-3 R6.3. WECC determined that the configuration change made by WECC_URE3 resulted in the generation of approximately 20,000 to 30,000 logs per minute. The space on the two devices used to store logs, the Security Incident and Event Management (SIEM) server and secondary server, was quickly filled. WECC determined that because the two devices were overwhelmed, both devices were not able to retain the logs for 90 days. WECC determined that WECC_URE3's failure to maintain system event logs for 90 days constitutes a violation of CIP-007-3 R6.3. | CIP-007-3a | R6; R6.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because access logs were generated and retained on local Cyber Assets. In the event of a system event, these local logs would have been available for review. In addition, access to Electronic Security Perimeters (ESPs) and devices therein was controlled and monitored during the duration of the violation. Lastly, WECC_URE3 implemented intrusion detection and prevention controls that would have immediately detected and alerted unauthorized access or malicious activity within the ESP. | when WECC_URE3 implemented the configuration change | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: 1) ensured that the CIP-applicable devices are only creating those logs that are necessary and appropriate. 2) ensured that its SIEM tools were licensed appropriately. 3) Once the aforementioned process has been completed, WECC_URE3 will be able to determine if sufficient license thresholds have been purchased. 4) created alerts that will be triggered if applicable devices are creating an unexpected number of events. In conjunction with the two items listed above, WECC_URE3 developed better alerting conditions designed to more quickly identify logging levels that threaten WECC_URE3's ability to be alerted to certain security issues or sufficiently retain logs to respond to potential incidents. 5) reviewed its current monitoring process for efficiencies and possible improvements that may help mitigate future risk from similar issues. | 2012-06-28 | 2012-08-08 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011953 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-005-3a R1, specifically, R1.5 because it failed to provide CIP-007-3 R1 and CIP-007-3 R5.3.3 protections required by the Standard. WECC_URE4 reported that it failed to change passwords for two electronic access and control monitoring (EACM) devices. In addition, WECC_URE4 reported that it installed four EACM devices without documenting the test procedures and their results. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 installed the first EACM device without documenting the test procedures and their results | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation,WECC_URE4: 1) modified the Critical Cyber Asset installation job plan to provide better detail on the steps necessary to document CIP-007 R1 test procedures and results adequately ; 2) changed the passwords on the affected devices; 3) revised and updated its password monitoring documents to include password last set date and local accounts; 4) developed an annual password reset job plan that all passwords are changed annually; and 5) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-14 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4’s prior compliance history to be an aggravating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011954 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-006-3c R2, specifically R2.2, because it failed to provide CIP-007-3 R5.3.3 protections as required by the Standard. WECC_URE4 reported that it failed to afford CIP-007-3 R5.3.3 protections to five out of ten Physical Access Control Systems (PACs) devices. WECC_URE4 also reported that it had not changed the passwords on five PACs devices. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 was required to change passwords on the five PACs devices | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: 1) changed the passwords on the affected devices; 2) revised and updated its password monitoring documents to include password last set date and local accounts; 3) developed an annual password reset job plan that all passwords are changed annually; and 4) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-13 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4’s prior compliance history to be an aggravating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011959 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5.3.3 because WECC_URE4 did not change the user account passwords on 17 out of 27 Critical Cyber Assets. | CIP-007-1 | R5; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 was required to change passwords on the devices | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: 1) changed the passwords on the affected devices; 2) revised and updated its password monitoring documents to include password last set date and local accounts; and 3) developed an annual password reset job plan that all passwords are changed annually; and 4) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-22 | 2013-03-29 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011958 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3a R1. WECC_URE4 failed to document test procedures and their associated results for one Critical Cyber Asset (CCA) and two non critical Cyber Assets. WECC_URE4 tested one device with ad hoc testing procedures and did not follow documented test procedures as required by the Standard. Additionally, WECC_URE4 failed to document properly the results associated with that testing. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 does not allow remote access into its network and the Electronic Security Perimeters in scope are segregated from the corporate network and public internet. Additionally, the devices were installed in an existing CIP managed network where access is controlled and monitored. WECC_URE4 conducted some testing on one of the devices in question prior to installation. The testing included verification that cybersecurity control applications were installed and functioning correctly, that only ports and services required for normal operation were enabled, and default accounts were disabled prior to installation. All devices are located within a Physical Security Perimeter. Furthermore, if any unusual traffic occurs on the network, alerts are sent via email to WECC_URE4 staff. | when the first device was installed | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: updated its CCA installation job plan to ensure that devices are installed in accordance with the requirements of CIP-007-3 R1. | 2013-02-14 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012167 | Settlement Agreement | WECC conducted an onsite Compliance Audit of WECC_URE4 and discovered that it was in violation of CIP-005-1 R1. WECC_URE4 did not include five Critical Cyber Assets (CCAs) in its Electronic Security Perimeters. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 has a defense-in-depth architecture of administrative, physical, and logical Cyber Security controls. WECC_URE4 has physical security measures which include guards, special locks, and CCTV for devices which reside within its Physical Security Perimeter. Additionally, WECC_URE4 has implemented various logical controls to protect its CCAs. These controls include firewalls, vulnerability scanning tools, and a security incident and events management program. These programs allow WECC_URE4 to detect promptly any potential threats to its CCAs. Additionally, WECC_URE4's procedures ensure that proper steps are taken following any potential threats. | when the Standard became mandatory and enforceable to WECC_URE4 | when WECC_URE4 decommissioned the ESP | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Compliance Audit | To mitigate this violation,WECC_URE4: 1) relocated one CCA; 2) created a new subnet; and 3) updated its CIP SQL database, its network diagram for CIP assets, and other documentation. | 2013-05-03 | TBD | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012168 | Settlement Agreement | WECC conducted an onsite Compliance Audit of WECC_URE4 and discovered that it was in violation of CIP-005-3 R2. WECC_URE4 failed to use a proper access control model that denies access by default, such that explicit access permissions must be specified. | CIP-005-3 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 has a defense-in-depth architecture of administrative, physical and logical Cyber Security controls. WECC_URE4 has physical security measures which include guards, special locks, and CCTV for devices which reside within its Physical Security Perimeter. Additionally, WECC_URE4 has implemented various logical controls to protect its CCAs. These controls include firewalls, vulnerability scanning tools, and a security incident and events management program. These programs allow WECC_URE4 to promptly detect any potential threats to its CCAs. Additionally, WECC_URE4's procedures ensure that proper steps are taken following any potential threats. | when the Standard became mandatory and enforceable to WECC_URE4 | when WECC_URE4 decommissioned the ESP | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Compliance Audit | To mitigate this violation, WECC_URE4: 1) relocated one CCA; 2) created a new subnet; and 3) updated its CIP SQL database, its network diagram for CIP assets, and other documentation. | 2013-05-03 | TBD | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4's compliance history to be an aggravating factor in the penalty determination.
2013-07-31 | FERC | NP13-41-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007727 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-1 R2.2 because it failed to enable only the ports and services required for normal and emergency operations and for monitoring Cyber Assets within two Electronic Security Perimeters (ESP). NPCC_URE1 also failed to document, individually or by specified grouping, the configuration of those ports and services. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC determined that the violation posed a moderate risk because of the opportunity for inconsistent application of technical and organizational processes for the control of electronic access at some of the electronic access points to the ESP. Such inconsistent application can leave access points, and therefore the ESP, exposed to unauthorized access. However, the risk was mitigated by deploying an encrypted tunnel between the access points, which expressly denies access from sources external to the two ESPs. All communications that travel through the encrypted tunnel must originate, by internal distributed control system (DCS) network design, from Cyber Assets within the two ESPs. The affected access point logs are collected, monitored, and alarmed for specific cybersecurity issues. Additionally, communication attempts that originate from outside the ESPs are routed to a separate ESP access point, and are challenged with a two-factor authentication mechanism. | when the Standard became mandatory and enforceable on NPCC_URE1 | when all on-site work associated with testing, installation, and validation was completed | $7,000 (for NPCC2011007727 and NPCC2011007867) | Self-Report | To mitigate this violation, NPCC_URE1: 1) performed a review of CIP-005-1 and implemented and tested configuration changes according to its CIP Policy and Procedure; 2) reviewed similar infrastructure at other Critical Assets to ensure that lessons learned and concepts from this violation are deployed throughout the enterprise to avoid similar issues in the future; 3) conducted a review of CIP-005 procedures associated with access points to ensure that procedures are current with the new solution at the affected Critical Asset; 4) developed a training program associated with the new implementation at the affected Critical Asset to communicate changes in policy, procedure, and technology to affected personnel; and 5) conducted training after development of the program. | 2011-10-31 | 2012-07-17 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-41-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007867 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-006-1 R1.8 because it failed to apply all the protective measures for Cyber Assets used in the access control and monitoring of a Physical Security Perimeter (PSP). NPCC_URE1 operates a generation site with Critical Cyber Assets (CCAs) that are essential to the operation of one of its Critical Assets. The CCAs are within a PSP which utilizes Cyber Assets that authorize and/or log access to the PSP's access points. CIP-006-1 R1.8 requires that Cyber Assets used in the access control and monitoring of PSPs be afforded the protected measures specified in CIP-005 R2 and R3. Pursuant to CIP-005 R2, the Cyber Assets used in access control and monitoring of the PSP at the generation site resided within a logical secured network segment protected by a firewall cluster, which included both technical and procedural mechanisms for control of electronic access. However, these firewalls were not configured properly to detect and generate alerts on all attempts for unauthorized access. Additionally, the registered entity did not review or assess access logs for attempts at, or actual, unauthorized access at least every 90 calendar days. | CIP-006-1 | R1; R1.8 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 defense in depth approach includes several mitigating and compensating measures. Even though these firewalls were not properly configured to detect and generate alerts regarding unauthorized access, the registered entity’s centralized electronic control and monitoring systems detected and alerted on security events based on application interface events as well as firewall traffic information. During the time of potential violation, the RE did not identify any cyber security incidents. Also personnel who have authorized unescorted physical and authorized cyber access must meet the requirements prescribed in CIP-004 R3 and R4. The generation site in scope of this potential violation is manned by personnel twenty-four hours a day, seven days a week. | when the Standard became mandatory and enforceable on NPCC_URE1 | when NPCC_URE1 configured the centralized electronic monitoring solution to detect and generate alerts | $7,000 (for NPCC2011007727 and NPCC2011007867) | Self-Report | To mitigate this violation, NPCC_URE1: 1) reconfigured the firewall and the electronic monitoring solution to capture and log all attempts at, or actual, unauthorized access; 2) assessed the logs for attempts at, or actual, unauthorized access and responded accordingly to cybersecurity incidents; 3) modified existing processes related to the detection and monitoring of attempts at, or actual, unauthorized access to ensure that the solution is capturing, logging, and alerting on all attempts at, or actual, unauthorized access. The process also included a requirement that personnel will validate that data has been received from each of the Cyber Assets that must adhere to CIP-005-3 R3; 4) assigned personnel to configure the centralized electronic monitoring solution to detect and generate alerts on all attempts at, or actual, unauthorized access, and implement the changes within the electronic access and monitoring system to adhere and fulfill the requirements related to CIP-005-3 R3. Additionally, the personnel validated that the information from the firewalls is generated, captured, stored, reported upon, and accessible within the electronic monitoring solution; 5) trained personnel responsible for administering centralized electronic monitoring solution and responding and reviewing unauthorized access attempt detections; and 6) assigned personnel to assess the remaining firewall logs and to identify any attempts at, or actual, unauthorized access or unauthorized configuration changes. | 2011-05-31 | 2012-07-17 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-07-31 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012010401 (for RFC_URE1 and MRO_URE1) | Settlement Agreement | RFC_URE1 self-certified noncompliance with CIP-002-3 R3. MRO_URE1 submitted a Self-Report identifying a violation of CIP-002-3 R3. In the second quarter, RFC_URE1 and MRO_URE1 conducted an internal self-assessment of compliance with CIP-002 R3 during which it was discovered that certain Critical Cyber Assets (CCAs) were not included on the CCA lists. RFC_URE1 and MRO_URE1 both failed to include one relay on their lists of CCAs. | CIP-002-3 | R3 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE1 and MRO_URE1 provided the same CCA protections to the two relays at issue that were provided to the CCAs included on the CCA lists. | when RFC_URE1 and MRO_URE1 were required to include the relays on the lists of CCAs | when RFC_URE1 and MRO_URE1 listed the missing relays as CCAs | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Certification; Self-Report | To mitigate this violation, RFC_URE1 and MRO_URE1: 1) implemented technical controls for managing substation Cyber Assets; and 2) listed the relays at issue on the CCA lists. | 4/30/2012 | 2/19/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-07-31 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012011588 (for RFC_URE1); RFC2012011589 (for RFC_URE2) | Settlement Agreement | RFC_URE1 and RFC_URE2 submitted two Self-Reports identifying violations of CIP-003-3 R5. RFC_URE1 and RFC_URE2 have a documented program for managing access to protected Critical Cyber Asset (CCA) information but failed to implement that program in one instance. Specifically, RFC_URE1 and RFC_URE2 granted access for one individual to a tool that allows viewing of an indicator on each Cyber Asset showing whether it is a CCA, which is protected CCA information. The individual at issue, a contractor, previously had authorized access to this information for many years until the access was deactivated. Approximately two weeks prior to the access being granted for the individual, RFC_URE1 and RFC_URE2 reactivated this individual’s account with standard read and write access privileges. Upon reactivation, RFC_URE1 and RFC_URE2 granted the individual access to the CCA information because the technical controls to eliminate the ability to add security keys to inactive users was not implemented. The individual’s access appeared as “unapproved” in RFC_URE1 and RFC_URE2's corporate security system, and the director of facilities reported it as such. | CIP-003-3 | R5 | Lower | Severe | These violations posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violations posed a moderate risk because a violation of CIP-003-3 R5 has the potential to affect the reliable operation of the BPS by decreasing the protections in place for managing access to protected CCA information. RFC_URE1 and RFC_URE2 failed to implement technical controls to eliminate the ability to add security keys to inactive users, increasing the risk of unauthorized access to CCA information. However, the risk was mitigated by the following factors. The individual only had access allowing him to see which Cyber Assets were CCAs, but did not have access to those CCAs. The individual had cybersecurity training and did not access the tool containing the CCA information. Furthermore, the individual previously had authorized access to this information for many years until the access was deactivated. | when RFC_URE1 and RFC_URE2 failed to implement the programs for managing access to protected CCA information | Mitigation Plans completion | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Reports | To mitigate these violations, RFC_URE1 and RFC_URE2: 1) developed a technical solution to prevent reoccurrence of this violation; 2) released and implemented new technical controls to revoke access to inactive accounts; and 3) developed, released, and implemented technical controls to eliminate the ability to add security keys to inactive users. | 1/18/2013 | 5/2/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-07-31 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012010403 (for RFC_URE2) | Settlement Agreement | RFC_URE2 self-certified noncompliance with CIP-003-3 R6. Two and a half months after submitting the Self-Certification, RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R2. Three months later RFC_URE2 submitted another Self-Report identifying a violation of CIP-007-3 R1. At the beginning of the year, RFC_URE2 commissioned a router at a substation, which RFC_URE2 determined to be a Critical Cyber Asset (CCA). In the second quarter, RFC_URE2 conducted an internal self-assessment and discovered that this CCA router was missing a configuration baseline, as required by CIP-003-3 R6. In addition, RFC_URE2 failed to follow test procedures for this router. RFC_URE2 failed to implement its cybersecurity test procedures on the router and switch, as required by CIP-007-3 R1.1; failed to document that testing was performed in a manner that reflects the production environment, as required by CIP-007-3 R1.2; and failed to document test results, as required by CIP-007-3 R1.3. Finally, RFC_URE2 failed to document that it enabled only those ports and services required for normal and emergency operations for this router. As a result, RFC_URE2 could not demonstrate that it enabled only the required ports and services and disabled the non-required ports and services, as required by CIP-007-3 R2. | CIP-003-3 | R6 | Lower; | Severe; | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because it has the potential to provide an opportunity for exploitation of vulnerable CCAs; to provide the opportunity for new Cyber Assets within the Electronic Security Perimeter (ESP) and significant changes to existing Cyber Assets within the ESP to adversely affect existing cybersecurity controls; and to provide the opportunity for infiltration of unauthorized network traffic into the ESP. However, the risk was mitigated by the following factors. RFC_URE2 protected the router with domain identification and password, with authentication within the network, and with a security group membership. In addition, the network-supported devices are built and deployed using management templates to enable only those ports and services required for normal and emergency operations, although RFC_URE2 failed to document that this had occurred for this router. | when RFC_URE2 commissioned the router | Mitigation Plans completion | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Certification; Self-Report | To mitigate thesis violation, RFC_URE2: 1) opened and closed a change control ticket to demonstrate compliance with the change control process; 2) created new test plan documentation to reflect the requirements of CIP-007 R1; 3) provided evidence demonstrating that it completed the test plan for a new substation build; 4) created internal procedures for ports and services documentation for network group-supported devices; 5) documented all ports and services at the substation; documented all ports and services for the device-types at issue; 6) notified appropriate personnel of the change in these procedures; and 7) provided training on the new procedures to appropriate personnel. | 12/13/2012 | 5/7/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-06-27 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012011281 (for RFC_URE2) | Settlement Agreement | RFC_URE2 self-certified noncompliance with CIP-003-3 R6. Two and a half months after submitting the Self-Certification, RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R2. Three months later, RFC_URE2 submitted another Self-Report identifying a violation of CIP-007-3 R1. At the beginning of the year, RFC_URE2 commissioned a router at a substation, which RFC_URE2 determined to be a Critical Cyber Asset (CCA). In the second quarter, RFC_URE2 conducted an internal self-assessment and discovered that this CCA router was missing a configuration baseline, as required by CIP-003-3 R6. In addition, RFC_URE2 failed to follow test procedures for this router. RFC_URE2 failed to implement its cybersecurity test procedures on the router and switch, as required by CIP-007-3 R1.1; failed to document that testing was performed in a manner that reflects the production environment, as required by CIP-007-3 R1.2; and failed to document test results, as required by CIP-007-3 R1.3. Finally, RFC_URE2 failed to document that it enabled only those ports and services required for normal and emergency operations for this router. As a result, RFC_URE2 could not demonstrate that it enabled only the required ports and services and disabled the non-required ports and services, as required by CIP-007-3 R2. | CIP-007-3 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because it has the potential to provide an opportunity for exploitation of vulnerable CCAs; to provide the opportunity for new Cyber Assets within the Electronic Security Perimeter (ESP) and significant changes to existing Cyber Assets within the ESP to adversely affect existing cybersecurity controls; and to provide the opportunity for infiltration of unauthorized network traffic into the ESP. However, the risk was mitigated by the following factors. RFC_URE2 protected the router with domain identification and password, with authentication within the network, and with a security group membership. In addition, the network-supported devices are built and deployed using management templates to enable only those ports and services required for normal and emergency operations, although RFC_URE2 failed to document that this had occurred for this router. | when RFC_URE2 commissioned the router | Mitigation Plans completion | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Certification; Self-Report | To mitigate this violation, RFC_URE2: 1) opened and closed a change control ticket to demonstrate compliance with the change control process; 2) created new test plan documentation to reflect the requirements of CIP-007 R1; 3) provided evidence demonstrating that it completed the test plan for a new substation build; 4) created internal procedures for ports and services documentation for network group-supported devices; 5) documented all ports and services at the substation; documented all ports and services for the device-types at issue; 6) notified appropriate personnel of the change in these procedures; and 7) provided training on the new procedures to appropriate personnel. | 12/13/2012 | 5/7/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-06-27 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012010773 (for RFC_URE2) | Settlement Agreement | RFC_URE2 self-certified noncompliance with CIP-003-3 R6. Two and a half months after submitting the Self-Certification, RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R2. Three months later, RFC_URE2 submitted another Self-Report identifying a violation of CIP-007-3 R1. At the beginning of the year, RFC_URE2 commissioned a router at a substation, which RFC_URE2 determined to be a Critical Cyber Asset (CCA). In the second quarter, RFC_URE2 conducted an internal self-assessment and discovered that this CCA router was missing a configuration baseline, as required by CIP-003-3 R6. In addition, RFC_URE2 failed to follow test procedures for this router. RFC_URE2 failed to implement its cybersecurity test procedures on the router and switch, as required by CIP-007-3 R1.1; failed to document that testing was performed in a manner that reflects the production environment, as required by CIP-007-3 R1.2; and failed to document test results, as required by CIP-007-3 R1.3. Finally, RFC_URE2 failed to document that it enabled only those ports and services required for normal and emergency operations for this router. As a result, RFC_URE2 could not demonstrate that it enabled only the required ports and services and disabled the non-required ports and services, as required by CIP-007-3 R2. | CIP-007-3 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because it has the potential to provide an opportunity for exploitation of vulnerable CCAs; to provide the opportunity for new Cyber Assets within the Electronic Security Perimeter (ESP) and significant changes to existing Cyber Assets within the ESP to adversely affect existing cybersecurity controls; and to provide the opportunity for infiltration of unauthorized network traffic into the ESP. However, the risk was mitigated by the following factors. RFC_URE2 protected the router with domain identification and password, with authentication within the network, and with a security group membership. In addition, the network-supported devices are built and deployed using management templates to enable only those ports and services required for normal and emergency operations, although RFC_URE2 failed to document that this had occurred for this router. | when RFC_URE2 commissioned the router | Mitigation Plans completion | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Certification; Self-Report | To mitigate this violation, RFC_URE2: 1) opened and closed a change control ticket to demonstrate compliance with the change control process; 2) created new test plan documentation to reflect the requirements of CIP-007 R1; 3) provided evidence demonstrating that it completed the test plan for a new substation build; 4) created internal procedures for ports and services documentation for network group-supported devices; 5) documented all ports and services at the substation; documented all ports and services for the device-types at issue; 6) notified appropriate personnel of the change in these procedures; and 7) provided training on the new procedures to appropriate personnel. | 12/13/2012 | 5/2/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-06-27 | FERC | NP13-41-000 | ReliabilityFirst Corporation (ReliabilityFirst); Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (RFC_URE1); Unidentified Registered Entity 2 (RFC_URE2); Unidentified Registered Entity 3 (RFC_URE3); and Unidentified Registered Entity 4 (MRO_URE1) (collectively the RFC-MRO_UREs) | NCRXXXXX (RFC_URE1); NCRXXXXX (RFC_URE2; NCRXXXXX (RFC_URE3); and NCRXXXXX (MRO_URE1) | RFC2012011446 (for RFC_URE1 and MRO_URE1); RFC2012011447 (for RFC_URE2); RFC2012011448 (for RFC_URE3) | Settlement Agreement | RFC_URE1, RFC-URE2, and RFC_URE3 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-004-3 R3. MRO_URE1 self-certified noncompliance with CIP-004-3 R4 to MRO. RFC-MRO_UREs discovered that the personnel risk assessment (PRA) for one individual was not conducted every seven years as required by the Standard. The requirement was exceeded by seven days. The next day, RFC-MRO_UREs revoked authorized cyber and authorized unescorted physical access to Critical Cyber Assets (CCAs) for this individual until a new PRA was conducted. RFC-MRO_UREs reinstated the individual’s access a week later. RFC-MRO_UREs discovered this issue because the security manager ran a periodic review to double-check the status of PRAs. The RFC-MRO_UREs subsequently discovered that the process for PRAs was not a formal documented procedure. Instead, two individuals managed PRAs pursuant to an informal process until their departure that year. As a result, the RFC-MRO_UREs determined that there was a programmatic issue with the PRA procedure. | CIP-004-1 | R3 | Medium | Severe | These violations posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violations posed a moderate risk because a violation of CIP-004 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for unknown and unverified individuals to access CCAs, which could result in harm to the integrity of the CCAs. However, the risk to the reliability of the BPS was mitigated by the fact that the individual at issue was a trusted employee with cybersecurity training. The employee is still employed by the RFC-MRO_UREs and has a valid PRA. | when the Standard became mandatory and enforceable for RFC_URE1, RFC_URE2 and RFC_URE3 when the PRA should have been conducted for MRO_URE1 | Mitigation Plans completion | $20,000 (for RFC2012010401; RFC2012010403; RFC2012010446; RFC2012010447; RFC2012011448 ; RFC2012010773; RFC2012011281; RFC2012011588; and RFC2012011589) | Self-Certification; Self-Report | To mitigate these violations, MRO_URE1, RFC_URE1, RFC_URE2, and RFC_URE3: 1) published the PRA process and included steps that require the generation and review of a quarterly report. The report is designed to indicate any PRAs that will expire in the next 12 months for all individuals that have authorized unescorted physical or cyber access to CCAs; and 2) trained appropriate personnel on the new procedure and ran the first quarterly report. | 2013-04-30 | 5/7/2013 | Admits | ReliabilityFirst reviewed the RFC-MRO_UREs' internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. ReliabilityFirst considered this history of noncompliance as an aggravating factor in the penalty determination. ReliabilityFirst determined that the instant violations of CIP-003-3 R6; CIP-007-3 R1 and R2; and CIP-004-3 R3 demonstrate programmatic failures similar to previous violations, and considered this fact as an aggravating factor in the penalty determination. Specifically, the RFC-MRO_UREs previously underwent a review and revision of programs and procedures wherein significant deficiencies in the CIP programs were discovered and remedied. The instant violations of CIP-003-3 R6 and CIP-007-3 R1 and R2, however, demonstrate a failure of RFC_URE2's change control and testing program, and the RFC-MRO_UREs' instant violations of CIP-004-3 demonstrate a failure of the RFC-MRO_UREs' personnel risk assessment program. These programmatic failures are similar to prior violations and because the RFC-MRO_UREs did not completely address these programmatic issues in the previous review, ReliabilityFirst determined that an aggravation of the monetary penalty was warranted. ReliabilityFirst considered the fact that it discovered eight of the violations through Self-Reports as a mitigating factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by the registered entities. The RFC-MRO_UREs promptly identified and reported the violations at issue due to the effective execution of their ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing a reduced monetary penalty for these violations. MRO issued a letter to MRO_URE1 stating that MRO and ReliabilityFirst will utilize a coordinated process to resolve the violations of CIP-002-3 R3 and CIP-004-3 R3. In the letter, MRO transferred the enforcement and mitigating responsibilities to ReliabilityFirst for the two MRO_URE1 violations discussed herein, as they relate to a corporate-wide CIP compliance program and are identical across the RFC-MRO_UREs. Because the responsibility for processing the violations for MRO_URE1 was transferred to ReliabilityFirst, the MRO_URE1 violations identified as MRO2012011288 and MRO2012011420 were dismissed by MRO. These violations for MRO_URE1 are nevertheless resolved by the Settlement Agreement and included in this Notice of Penalty.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010702 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-2a R2.2. WECC_URE1 failed to provide one workstation, a Cyber Asset used in the access control and monitoring of one Physical Security Perimeter (PSP), the protections required by CIP-006 R2.2. Specifically, as required by CIP-007 R5.1, WECC_URE1 failed to ensure that access permissions for certain employees were consistent with their work functions. In addition, as required by CIP-007 R5.1.1, WECC_URE1 failed to ensure that user accounts were implemented and approved by designated personnel; and, as required by CIP-007 R5.1.2, WECC_URE1 failed to ensure that a historical audit trail of user activity was available. Specifically, an employee shared his credentials with other employees who used the credentials to log onto the workstation without approved access. Further, WECC_URE1 granted certain other employees system administrator access to this workstation; however, their specific job function did not require this level of access, and WECC_URE1 could not provide logs for historical activities that had occurred on this workstation. | CIP-006-2a | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All personnel associated with this violation required some level of access per their job functions. All personnel had completed personnel risk assessments and NERC CIP training. In addition, each PSP had defense-in-depth using multiple access controls such as card readers, video, and human observation. Finally, the PSP in scope had monitoring and alerting for unauthorized and invalid access | when the employees were granted access to the workstation without ensuring access permissions | Mitigation Plan completion | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Self-Report | To mitigate this violation, WECC_URE1: 1) verified that each authorized physical access control system user had an individual login and password; 2) restricted physical access control system permission levels, which included a review of all personnel with system administrator permissions and a reduction of such access to only those that need such access; 3) developed a role-based matrix to ensure that personnel are assigned permissions appropriate to job functions; 4) applied appropriate disciplinary action for the employee acts of noncompliance; 5) reviewed and strengthened WECC_URE1’s campus operations processes; and 6) reinforced training and awareness. | 2013-01-10 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009105 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2. WECC_URE1 had developed a process of identifying, approving, and documenting ports and services on an application basis but not on a Cyber Asset basis. WECC_URE1's document identified the standard operating system ports and services required for normal and emergency operations and identified what ports and service had been approved, but failed to categorize ports and services on a Cyber Asset basis. Although WECC_URE1 did not document ports and services on an asset-by-asset basis for all Cyber Assets within Electronic Security Perimeters (ESPs), it did document ports and services on an application basis. However, because WECC_URE1 did not have a mapping document that would map an application to the Cyber Asset on which the application was installed, WECC_URE1 could not confirm that all enabled ports and services on all Cyber Assets within its ESPs were required for normal and emergency operation. WECC conducted a Compliance Audit of WECC_URE1. During the Compliance Audit, the auditors reviewed WECC_URE1's evidence of completion of this Mitigation Plan. Based on evidence provided by WECC_URE1 at the Compliance Audit, WECC determined that, in fact, a business justification was not made for all ports and services determined to be in-scope Cyber Assets. WECC_URE1, therefore, did not ensure that only those ports and services required for normal and emergency operations were enabled as required by CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to categorize its ports and services enabled on a Cyber Asset level, it did document ports and services on an application basis. WECC_URE1 stated that it implemented controls to log and monitor electronic and physical access to Critical Cyber Assets within the four ESPs. In addition, WECC_URE1 conducts periodic automated scanning for ports and services and vulnerabilities in the Cyber Assets within the ESP. Additionally, WECC_URE1 has automated continuous monitoring software installed on all devices so that any configuration change is tracked and will issue an alert to the security department in the event a device is compromised. Security alerts are reviewed daily to mitigate quickly any risks associated with the devices. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented monitoring technology that will actively query Cyber Assets in scope for active ports and services; 2) implemented a project plan to document ports and services on each individual Cyber Asset in scope; and 3) created ports and services configuration baseline documentation for each Cyber Asset in scope. | 2012-11-16 | 2012-12-06 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009106 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3. WECC_URE1 failed to document its patching determinations for security patches applicable to Cyber Assets located in Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The patches were primarily security updates. | CIP-007-1 | R3; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because of the number of patches and the number of devices pertaining to this violation. Although WECC_URE1 failed to document its security patch determinations fully, WECC_URE1 has represented that all applicable security patches have been installed. WECC_URE1 also had implemented controls to log and monitor electronic and physical access to Critical Cyber Assets within ESPs. Specifically, WECC_URE1 periodically conducts automated scanning for ports and services and vulnerabilities in the Cyber Assets within the ESP. Additionally, WECC_URE1 has automated continuous monitoring software installed on all devices so that any configuration change is tracked and will issue an alert to the security department in the event a device is compromised. Security alerts are reviewed daily to mitigate quickly any risks associated with the device. | when WECC_URE1 failed to document the patching determination for the first identified patch | Mitigation Plan completion | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Self-Report | To mitigate this violation, WECC_URE1: 1) evaluated the current patch management process and identified areas requiring improvement; and 2) based on the evaluation results, implemented new and revised processes as necessary. | 2012-07-09 | 2012-10-08 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011414 | Settlement Agreement | WECC conducted a Compliance Audit of WECC_URE1. WECC determined that WECC_URE1 had a violation of CIP-007-1 R4. During the course of the Compliance Audit, the audit team visually verified anti-virus software and other malware software programs installed on all Cyber Assets. According to the evidence, WECC_URE1 failed to use anti-virus software and other malicious software prevention tools to detect, deter, prevent, and mitigate the introduction, exposure, and propagation of malware on 4.42% Cyber Assets within the Electronic Security Perimeters (ESPs). For four of those assets, it was not feasible to use anti-virus or malicious software tools. WECC_URE1, however, had not filed timely Technical Feasibility Exceptions (TFEs) for those devices. | CIP-007-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Cyber Assets did not have anti-virus software installed, they are located in controlled areas behind restricted firewalls. Access is limited. The Cyber Assets are logically located within an ESP, and logical ports and services access to the network are limited to normal and emergency operations. Further, all ESPs are monitored 24 hours a day 7 days a week. WECC_URE1 submitted TFEs and WECC approved the TFEs. Finally, WECC_URE1 has installed anti-virus and malware prevention tools where feasible, and the Cyber Assets do not support installation of anti-malware software. | when the first Cyber Asset was placed into production without any malware or anti-virus prevention tools without filing a TFE | when WECC_URE1 submitted TFEs for the Cyber Assets | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) submitted TFEs for the Cyber Assets; 2) removed a Cyber Asset from the network; and 3) modified the EMS group policy to check for functioning trend anti-virus installed on every device in the ESP. | 2012-11-30 | 2013-02-08 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009107 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5. While WECC_URE1 had documented and followed a quarterly user account access review process, the document used for reviewing permissions did not distinguish between whether an account user had read-only or more privileged access. The reviews were instead done based on the assumption that each user had more privileged access. For shared accounts, WECC_URE1's technical and procedural mechanisms produced, through automated or manual processes, a documented audit trail only for some, but not all, of WECC_URE1's shared accounts. While WECC_URE1 has policies and procedures requiring passwords to be changed on an annual (or more frequent) basis and technical and policy mechanisms in place to enforce this requirement, WECC_URE1 did not have the capability to document and provide evidence of such password changes in every instance. WECC conducted a Compliance Audit of WECC_URE1. During the Compliance Audit, the auditors reviewed WECC_URE1's evidence of completion of this Mitigation Plan and concluded that user account passwords did not appear to have been changed annually. In response to an associated data request during the WECC Compliance Audit, WECC_URE1 provided evidence that passwords had been changed for two-thirds of the accounts identified. However, WECC_URE1 determined that the password for the other third had been overlooked during the manual review of passwords. | CIP-007-1 | R5; 5.1.3; R5.2.3; R5.3.2 and R5.3.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because of the number of devices at issue and the number of failed account management controls leading to this violation. The Cyber Assets at issue are located in all of the primary and backup control center Electronic Security Perimeters (ESPs). Although WECC_URE1's controls had shortcomings, WECC_URE1 implemented policies and procedures that provided some protections. These protections included: 1) policies and procedures for quarterly review of account access privileges at the account level; 2) a documented policy for maintaining an audit trail for shared accounts; and 3) policies and procedures requiring passwords to be changed on an annual (or more frequent) basis, as well as technical and policy mechanisms to enforce this requirement. WECC_URE1 also implemented controls to log and monitor electronic and physical access to Critical Cyber Assets within ESPs. Specifically, WECC_URE1 periodically conducts automated scanning for ports and services and vulnerabilities in the Cyber Assets within the ESP. Additionally, WECC_URE1 has automated continuous monitoring software installed on all devices so that any configuration change is tracked and will issue an alert to the security department in the event a device is compromised. Security alerts are reviewed daily to mitigate quickly any risks associated with the device. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Self-Report | To mitigate this violation, WECC_URE1: 1) filed a TFE regarding password complexity; 2) evaluated the current account management process to identify areas needing process improvement; 3) based on evaluation results, implemented new or revised processes and tools as necessary; and 4) changed passwords for user accounts. | 2012-11-01 | 2012-12-06 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011417 | Settlement Agreement | WECC conducted a Compliance Audit of WECC_URE1. WECC determined that WECC_URE1 had a violation of CIP-007-3a R8. WECC_URE1 was unable to provide evidence that a complete cyber vulnerability assessment (CVA) was conducted on all Cyber Assets within the Electronic Security Perimeter (ESP) for two calendar years. According to the two versions of the information security vulnerability management process documents given to the Audit Team, WECC_URE1's vulnerability scanning tool should have been used to scan all Cyber Assets that reside within an ESP. WECC_URE1 provided insufficient evidence to demonstrate that all of the default accounts were assessed for two years within WECC_URE1's ESPs. WECC_URE1 did provide evidence that a full CVA was conducted the following year that fully addressed CIP-007 R8. | CIP-007-3a | R8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE1's failure to sufficiently demonstrate performance of a complete CVA of all Cyber Assets for two years could, in the absence of other protective measures, potentially allow cyber vulnerabilities in such assets to go unchecked and undetected. Such vulnerabilities could be exploited by malicious access, thereby providing an attack vector for launching cyber attacks against Critical Cyber Assets essential to the operation of the BPS. To protect against such vulnerabilities, however, WECC_URE1 implemented compensating measures, such as a defense-in-depth architecture of physical and logical cybersecurity controls. All Cyber Assets were physically secure with guards and special locks. Access to these assets was limited to only individuals who were approved and trained. All Cyber Assets have internal cybersecurity controls, including firewalls, vulnerability scanning tools, netflow analysis, and a system integrity tool. | when WECC_URE1 failed to complete its CVA | When WECC_URE1 completed its CVA | $60,000 (for WECC2012009105, WECC2012009106, WECC2012009107, WECC2012010702, WECC2012011414, and WECC2012011417) | Compliance Audit | To mitigate this violation, WECC_URE1 established a baseline of authorized ports and services for its Cyber Assets that reside within an ESP. | 2012-11-09 | 2013-04-05 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103043 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating it was in violation of CIP-003-3 R6 because it failed to follow its change control and configuration management process when removing and re-introducing a workstation into its Electronic Security Perimeter (ESP). The workstation was located inside of an ESP and physically placed inside of a Physical Security Perimeter (PSP). The workstation involved in this violation was removed from the ESP and placed in a box. The workstation remained in the box and stored inside the PSP until the date when the workstation was re-installed onto the local area network. WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-003-3 R6 because it failed to follow its change control and configuration management process when it removed and then re-installed a workstation on one of its ESPs. | CIP-003-3 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation is, however, offset given the limited scope of the violation and compensating measures in place during the violation period. The scope of the violation is limited to a single workstation. The workstation in scope was located in a PSP. Physical access thereto was limited to individuals who completed personnel risk assessments (PRAs) and cyber security training. Physical access to the devices was monitored. The workstation was in an area that was monitored by video surveillance 24 hours a day, seven days a week. Unauthorized access attempts would have triggered alarming, notifying security personnel of a physical security breach. Further, the workstation had authentication protections making it electronically secured while connected to the network within the ESP. Unauthorized electronic access attempts would have been logged and identified. The device was contained within an ESP. Individuals with electronic access rights to the ESP completed PRAs and cyber security training. | when the workstation was removed from the ESP | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) completed its change control procedure for the in-scope device and updated the CIP-005 R1 Critical Cyber Asset (CCA) List to reflect when the in-scope console was out of service; 2) reviewed the CIP-003 R6 change control procedure and edited it as necessary. WECC_URE2 ensured that the requirements to update the CCA List, as required by CIP-005 R1, and the need to perform CIP-007 R1 testing for all changes were addressed in the procedure; 3) provided guidance on how to do change control under emergency conditions; and 4) trained staff on changes to the CIP-003-R6 change control procedure. | 2012-02-10 | 2012-08-13 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination. WECC also considered the fact that WECC_URE2 self-reported this violation and took voluntary corrective action to remediate the violation.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010299 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating it was in violation of CIP-005-3a R5. WECC_URE2 indicated that it was in violation of CIP-005-3a R5 because it failed to update its network documentation within ninety days of changes made to its network. WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-005-3a for failing to update its network documentation within ninety days of changes made to its network. | CIP-005-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation was lessened given the limited scope of the violation and compensating measures in place during the violation period. All devices were located within the Electronic Security Perimeter (ESP). All electronic access thereto was monitored, logged, and controlled. Individuals with electronic access to the devices completed personnel risk assessments and cyber security training. WECC_URE2 enabled only those ports and services necessary for normal and emergency operations at the access points. Additionally, CCAs within the ESP require usernames and passwords to access the devices. Further, the devices were located within a Physical Security Perimeter (PSP). Physical access was controlled by technical and procedural controls including 24 hours a day, seven days a week logging and monitoring of physical access. | when the CIP-005-3 network documentation should have been updated | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) updated the current identification data of all servers on the CIP-005 Critical Asset /CCA list; 2) updated the Critical Asset/CCA list’s revision history table to reflect the changes for the server devices; 3) provided training to subject matter experts (SMEs) on the proper methods for checking documents in and out of the document management system; and 4) reviewed the training roster and provided make-up training sessions for SMEs not included in the first training session. | 2012-05-25 | 2012-10-01 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination. WECC also considered the fact that WECC_URE2 self-reported this violation and took voluntary corrective action to remediate the violation.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010366 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating, that it was in violation of CIP-007-3 R1. WECC_URE2 indicated that it was in violation of CIP-007-3 because it failed to perform a cyber security test prior to installing equipment into its Electronic Security Perimeter (ESP). WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-007-3 R1 for failing to perform a cyber security test prior to placing the server into its ESP. | CIP-007-3 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The risk posed by this violation was offset given compensating measures in place during the violation period. The devices in scope were located in an ESP and had technical and procedural mechanisms for control of electronic access at all access points. WECC_URE2 enabled only those ports and services necessary for normal and emergency operations at the access points. Additionally, Critical Cyber Assets within the ESP require usernames and passwords to access the devices. In addition, WECC_URE2 stated that the device was located within a Physical Security Perimeter (PSP) which had technical and procedural controls to manage physical access including 24 hours a day, seven days a week logging and monitoring of physical access. Additionally, if the device were to lose connectivity, the entity would be alerted immediately. | when the server was placed in WECC_URE2's ESP | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) obtained a copy of the configuration file of the development server from a vendor to establish a pre-configuration file to reflect the configuration prior to introducing the new device to the system; 2) performed configuration analysis to establish a configuration baseline on each of the server devices after all changes had been performed to remediate items identified in the Self-Report; and 3) performed a comparison analysis of R1 test data prior to and after the introduction of the new device to ensure no changes resulted from replacing the server. | 2012-07-11 | 2013-02-08 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010371 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2. WECC_URE2 indicated that it was in violation of CIP-007-1 R2 for failing to document ports, services, and compensating measures that applied where unused ports and services could not be disabled. WECC_URE2 also failed to disable certain ports and services. WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-007-1 R2 for failing to document ports, services, and compensating measures that applied where unused ports and services could not be disabled. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation was offset given compensating measures in place during the violation period. The devices in scope were located in an Electronic Security Perimeter (ESP). Access was controlled by technical and procedural mechanisms at all ESP access points. Electronic access to the ESP was logged and monitored. Further, the devices in scope of the violation were physically secured. The devices were located within a Physical Security Perimeter (PSP). Access to the PSP is managed using technical and procedural controls. Access is logged and monitored on a 24 hour a day, seven day a week basis. Unauthorized access attempts would trigger alarming. Individuals with physical and electronic access to the devices completed personnel risk assessments and cyber security training. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) analyzed the known ports and services on each of the servers to identify if there are any that need to be disabled; 2) disabled any unnecessary ports and services; and 3) documented changes and updates to the configuration for each of the devices, including the aforementioned analysis and disabling of the ports and services on each of the servers. | 2012-06-22 | 2012-12-31 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010367 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5. WECC_URE2 indicated that it was in violation of CIP-007-1 R5 for failing to implement and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity for the servers inside its Electronic Security Perimeter (ESP). WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-007-1 R5 for failing to implement and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity for the servers inside its ESP. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation was offset given the limited scope of the violation and the compensating measures in place during the violation period. The devices in scope were located in an ESP and had technical and procedural mechanisms for control of electronic access at all access points. Electronic access, including access gained through shared and individual user accounts, was monitored and logged. In addition, all devices were located within a Physical Security Perimeter (PSP). Physical access was managed through the use of technical and procedural controls. Access to the PSP was monitored and logged on a 24 hours a day, seven days a week basis. Unauthorized physical access attempts would have triggered alarming. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) added the shared user accounts for the server devices to the account management tracking spreadsheet; and 2) changed the passwords for all shared user accounts for each of the server devices. | 2012-07-11 | 2013-02-21 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010370 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R6. WECC_URE2 indicated that it was in violation of CIP-007-1 for failing to implement, as technically feasible, automated tools or organizational process controls to monitor system events related to cyber security on the servers within its Electronic Security Perimeter (ESP). WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-007-1 R6 for failing to implement, as technically feasible, automated tools or organizational process controls to monitor system events related to cyber security on the servers within its ESP. | CIP-007-1 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation was limited given compensating measures in place during the violation period. The devices in scope were located in an ESP which had technical and procedural mechanisms for control of electronic access at all access points. Electronic access was logged and monitored. Electronic access to the ESP requires authentication, a username, and password to access the devices. In addition, all the devices were located within a Physical Security Perimeter (PSP). Physical access was managed by technical and procedural controls. Physical access was restricted to certain authorized individuals. Access to the PSP was logged and monitored on a 24 hours a day, seven days a week basis. Unauthorized access attempts would have triggered alarming. All individuals with electronic or physical access completed personnel risk assessments and cyber security training. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) configured the servers to log system events; 2) setup the syslog sync to deliver logging to the server; and 3) conducted a qualitative review of the servers' logs to confirm the logs contain the expected, appropriate information. | 2012-06-22 | 2012-12-31 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010006 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1. WECC_URE2 indicated that it was in violation of CIP-007-1 for failing to perform cyber vulnerability assessments (CVAs) on a number of its Cyber Assets. WECC enforcement reviewed the Self-Report and determined that WECC_URE2 was in violation of CIP-007-1 for failing to perform CVAs on a number of its Cyber Assets. | CIP-007-1 | R8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this violation was limited, given compensating measures in place during the violation period. The devices in scope are located in an Electronic Security Perimeter (ESP) and have technical and procedural mechanisms for control of electronic access at all access points. Access to the ESP requires authentication, usernames, and passwords to access the devices. Electronic access is monitored and logged. In addition, all devices are located within a Physical Security Perimeter (PSP). The PSP is equipped with technical and procedural controls to manage physical access. Physical access is logged and monitored on a 24 hours a day, seven days a week basis. Unauthorized physical access attempts trigger alarming. Further, individuals with electronic or physical access to the devices have completed personnel risk assessments and cyber security training. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $36,000 (for WECC201103043, WECC2012010299, WECC2012010366, WECC2012010371, WECC2012010367, WECC2012010370, and WECC2012010006) | Self-Report | To mitigate this violation, WECC_URE2: 1) performed CVAs on the servers; 2) prepared a report of the vulnerability assessment findings; 3) created a work plan based on the CVA findings; 4) completed the tasks identified on the CVA work plan; 5) performed a follow-up CVA; and 6) created and executed an action plan for any additional addressable vulnerabilities. | 2012-06-25 | 2013-04-03 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010362 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-006-3c R2 because it failed to ensure the Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP) were afforded the protective measures of CIP-007-3 R1. WECC_URE3 updated a physical access control and monitoring (PACM) server without documentation of proper test procedures prior to deployment of the service pack. WECC determined that WECC_URE3 failed to follow test procedures, in accordance with CIP-007-3 R1, because upon commissioning the new PACM devices, a configuration issue allowed patches to be installed prior to being tested. WECC_URE3 stated that a local configuration on the devices overrode the centralized configuration of WECC_URE3's server update services . As a result, patches were automatically installed upon release of the patch without first sending them to WECC_URE3's test environment. The devices in scope are the backup and primary PACM servers for the entity. Each server is a standalone database and application server. WECC_URE3 personnel stated that the devices were put into production and the first patch was installed, but not tested. | CIP-006-3c | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although, WECC_URE3 failed to afford the protective measures of CIP-007-3 R1 to Cyber Assets that authorize or log access to the PSP, the two devices in scope were located in a secure network protected by boundary devices that log and restrict all logical access attempts. The devices were within a separate PSP with restricted access which was logged and monitored by a card key system, along with additional monitoring through use of cameras. The PACM device in scope supports the card key system. A control panel caches temporary information on a regular basis so that access to the PSP which houses the PACM device continues to be restricted using the last known configuration, thus in the event the PACM server in scope crashes, physical access would still be restricted and monitored. The devices in scope require two-factor authentication prior to any remote access and had anti-virus and malware prevention tools installed. Additionally, the PACM server had intrusion detection, firewall protection, and anti-virus software installed. | when WECC_URE3 missed the required testing on the first patch | Mitigation Plan completion | $65,000 (for WECC2012010362, WECC2012011087, and WECC2012011396) | Self-Report | To mitigate this violation, WECC_URE3: 1) documented server baseline configurations for production servers subject to the NERC CIP Reliability Standards; 2) documented centralized patching procedures; and 3) trained all personnel with administrative permissions to modify server settings to the new baseline configuration and centralized patching. | 2012-08-31 | 2013-01-31 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011087 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3 R5 because it failed to ensure that user accounts were implemented and approved by designated personnel, as required by CIP-007-3 R5.1.1. Specifically, WECC_URE3 reported that while logged into a domain server for its Electronic Security Perimeter (ESP), a systems administrator used his domain administrator privileges to reset the password of a disabled account, which belonged to a terminated employee. The administrator then re-enabled the account and logged into a local system in order to access certain files that were previously secured using a certificate tied to the user account. WECC_URE3's procedures for CIP-007 R5 account management require that user accounts be formally requested and approved by the Cyber Asset business owner and that Cyber Asset business owners document all account access approvals granted to individuals. Although the access rights of the accounts were essentially identical since both users performed the same role within the same department, the actions taken did not follow WECC_URE3's CIP-007-3 R5 account management procedures as required by CIP-007 R5. The Cyber Asset business owner did not receive a request for access, nor was there documented access approval. WECC_URE3 stated the account was set back to "disabled" on the same day it was re-enabled. WECC_URE3 submitted a second Self-Report expanding the scope of the violation. WECC_URE3 reported that it failed to change the password of a shared account, as required by CIP-007-3 R5.3.3. WECC_URE3 reported that during an annual review of password changes for shared accounts, it discovered that the password for a generic account was not being changed on an annual basis. WECC_URE3 informed WECC that a supervisory control and data acquisition (SCADA) technician requested an account be set up to manage internet protocol (IP) SCADA remote terminal unit (RTU) devices. The account was properly approved and setup as a shared account. The account was added to the shared account list and had fewer than 10 users identified as having access to the account. WECC_URE3 further stated that the business owner of the account had intended the account to be set up as a non-interactive service account and was unaware that it had been implemented as a shared account. Therefore, the business owner did not recognize that the password was required to be changed annually per WECC_URE3's CIP-007 R5 account management procedures. The issue was discovered during WECC_URE3's annual review of password changes, and upon discovery, WECC_URE3 changed the password for the account. The devices in scope were servers and workstations, which were the same types of devices in scope of WECC_URE3's CIP-007-3 R5.1.1 violation. | CIP-007-3 | R5; R5.1.1; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE3 re-enabled an administrator account without approval by designated personnel, the system administrator did not gain access to any system that was not already accessible per system administrator rights. Additionally, the individual had authorized access to the same privilege levels as the account that was enabled and the individual was authorized to view the information contained in the files. The administrator reset the account password upon activating it, to ensure only the administrator who activated the account had access. Furthermore, no Critical Cyber Assets (CCAs) were accessed as a result of these actions, and the person who re-enabled the account had a current personnel risk assessment, CIP training, and approval for access to CCAs. Finally, the ESP which this account could access had continuous logging and monitoring of cyber access so that WECC_URE3 would be alerted if suspicious or unauthorized access had occurred. With respect to CIP-007-3 R5.3.3, although WECC_URE3 failed to change passwords at least annually to a shared account, the shared account had little to no privileges on the system, and WECC_URE3 manages accounts with active directory and security agent policies that prevent users from elevating privileges. WECC_URE3 also had continuous logging and monitoring of cyber access and would be alerted if suspicious or unauthorized access had occurred. Further, fewer than 10 SCADA technicians had access to the account that did not have administrative rights and would not allow users to access any systems considered to be critical, such as the energy management system (EMS) application. | when WECC_URE3 failed to change the password of a shared account | Mitigation Plan completion | $65,000 (for WECC2012010362, WECC2012011087, and WECC2012011396) | Self-Report | To mitigate this violation, WECC_URE3: 1) sent a memo to all domain administrators of certain domains regarding access authorization; 2) created a security event monitoring (SEM) alert for changes to domain administrator accounts that are tracked for CIP compliance; 3) trained personnel on SEM alert investigation; 4) established a process to perform quarterly review and validation of password changes for all shared accounts; 5) updated CIP-007 R5 account management procedures; 6) trained personnel on updated access authorization process; and 7) disabled the interactive logon for the account. | 2012-12-14 | 2013-03-26 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011396 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3 R7 because it failed to follow its CIP-007 R7 process when disposing of certain Cyber Assets. WECC_URE3 had formal procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter (ESP), which included requiring change control documentation for the removal of storage media from the host equipment. The procedure required that each storage media device must be included on a disposal manifest detailing the storage media number, the specific Cyber Asset from which the storage media was removed, and the change control documentation associated with the Cyber Asset. Prior to disposal, all items on the manifest must be reconciled with an associated change control to ensure proper accounting of all storage media on the list. WECC_URE3 was unable to find the corresponding change control documentation for media devices that were disposed of, indicating that the reconciliation of the disposal manifest was not completed. WECC_URE3 delivered the devices to a vendor for disposal, maintaining physical control of the devices until they were physically destroyed. WECC_URE3's CIP-007-3 R7 process requires that prior to disposal, the devices on the disposal manifest be reconciled with an associated change control. In this instance, the devices on the disposal manifest were not reconciled until after they had been shredded. As a result, WECC_URE3 found it had shredded a number of hard drives that did not have a corresponding change control ticket. WECC_URE3 stated that both Cyber Assets within the ESP and Cyber Assets that do not reside within the ESP were inadvertently placed in the CIP lockbox for disposal. However, after a thorough review it was discovered that every Cyber Asset that was disposed of within the ESP had a corresponding change control which reconciled correctly with the disposal manifest. The devices that did not have corresponding change control documentation were not Cyber Assets within the ESP. WECC determined that because WECC_URE3 failed to follow its documented disposal and redeployment process for about 90% of the Cyber Assets within the ESP by not reconciling the list prior to disposal, it was in violation of CIP-007-3 R7. | CIP-007-3 | R7 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 stored the devices in scope within a locked storage bin within a Physical Security Perimeter prior to the destruction of the devices, which was performed by a third-party and witnessed by WECC_URE3 personnel. Additionally, the data storage media devices were never exposed, thus making the possibility of compromise low. | when WECC_URE3 failed to reconcile the disposal manifest prior to the disposal of Cyber Assets | Mitigation Plan completion | $65,000 (for WECC2012010362, WECC2012011087, and WECC2012011396) | Self-Report | To mitigate this violation, WECC_URE3: 1) updated the compliance procedures used for CIP disposal and redeployment to separate the objective of the procedure from the specific steps utilized to achieve that objective and move those specific steps to a business process; and 2) provided refresher training to all Critical Cyber Asset administrators and all workstation support analysts on the updated procedures used for CIP disposal and deployment. | 2013-01-31 | 2013-03-26 | Agrees/Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012009396 | Settlement Agreement | WECC_URE4, submitted a Self-Certification to WECC stating that it was in violation of CIP-004-3 R4. WECC_URE4 failed to revoke access to Critical Cyber Assets (CCAs) within 24 hours for personnel terminated for cause, and within seven calendar days for personnel who no longer required such access. WECC_URE4 failed to revoke physical access to CCAs for 11 contract employees. Specifically, one janitor was terminated for cause and another janitor resigned. WECC_URE4 revoked access for both janitors more than seven calendar days after these personnel no longer required such access. In addition, nine contract security officers left their WECC_URE4 work assignments on various dates. Those individuals had their physical access revoked, but access was not revoked to WECC_URE4's system. WECC_URE4 revoked the nine individuals' access to the system more than seven calendar days after these personnel no longer required such access. WECC_URE4 submitted a Self-Report for an additional instance of non-compliance with the Standard. WECC_URE4 failed to review and authorize access authorization requests for four personnel to Physical Security Perimeters (PSPs) which contained CCAs. WECC_URE4 incorrectly granted access to the four individuals, prior to authorization. WECC_URE4's process is to check for personnel risk assessments (PRAs) and CIP training and obtain authorization from the asset owner before granting access to such assets. For the four individuals in scope, WECC_URE4 failed to get authorization from the asset owners. Physical access was granted in each case without this approval. All four of the individuals had authorized cyber access to the CCAs within the PSPs. | CIP-004-3 | R4; R4.1;R4.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Compensating measures were in place to mitigate the risk created by the 11 WECC_URE4 personnel who were either terminated for cause or resigned. The PSPs in scope were staffed 24 hours per day seven days per week and were logged. Compensating measures were also in place to mitigate the risk created by the four personnel given unauthorized physical access for seven days. Each had current CIP training and updated PRAs, and were authorized for cyber access to the CCAs inside the PSPs in scope. The PSPs were monitored 24 hours per day seven days per week with logging and monitoring of physical and cyber access. Also, video cameras monitor access at all the access points to the PSPs in scope. | when access should have been revoked for the first employee | Mitigation Plan Completion | $10,000 (for WECC2012009396 and WECC2012009729) | Self-Certification | To mitigate this violation, WECC_URE4: 1) revoked CIP PSP and cyber access for the personnel involved; 2) met with the janitorial vendor to review NERC CIP compliance requirements and to request employee termination notifications; 3) reinforced the policy with staff to ensure that both physical and cyber access are disabled when an employee leaves a job assignment; and 4) developed a temporary software program to track, notify, and document the access. | 2012-11-29 | TBD | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-41-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012009729 | Settlement Agreement | WECC_URE4, submitted a Self-Certification to WECC stating that it was in violation of CIP-006-3c R1.4. On two occasions, WECC_URE4 issued temporary access badges to employees without erasing the prior access rights on the badges and reformatting the access rights on the badges to reflect the actual access rights of the employees, in accordance with WECC_URE4's procedures. In the first instance, an employee was intended to have all the access rights granted by the temporary badge. In the second instance, the employee should not have had the full scope of access granted by the temporary badge. The badges provided access to the Physical Security Perimeters (PSPs) at the control center that housed relays, switches, and emergency management system workstations. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The personnel in scope had CIP training and personnel risk assessments prior to access. In addition, the personnel were on WECC_URE4's access list, and the control center involved has twenty-four hour video and human monitoring. | the date of the first instance of noncompliance with CIP-006-3c R1 | Mitigation Plan Completion | $10,000 (for WECC2012009396 and WECC2012009729) | Self-Certification | To mitigate this violation, WECC_URE4: 1) reviewed the procedures and checklists and confirmed removing access levels from temporary badges was included; and 2) amended the temporary access badge procedure to require a guard at a satellite location and at the security operations center both maintain a log of any temporary access cards that are issued NERC and CIP PSP access. | 2011-11-14 | 2013-01-31 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-39-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011278 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-005-1 R1. As part of a vendor assessment of its CIP compliance program, RFC_URE1 discovered that it failed to identify and protect certain devices that are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP) pursuant to CIP-005-1 R1.5. RFC_URE1 utilizes its security event and incident management (SEIM) servers to aggregate security event logs from ESP access points and to issue automated alerts for the investigation of potential cybersecurity incidents. The SEIM system consists of collector servers and a logging database server, and RFC_URE1 failed to afford these servers certain of the protective measures required by CIP-005-1 R1.5. Specifically, RFC_URE1 failed to afford the SEIM servers the protections of CIP-003-1 R6, CIP-006-1 R3, and CIP-007-1 R3, R4, R5, R6, and R9. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation posed a moderate risk because it implicated a significant class of assets that could pose a threat to the ESP, is not a documentation error, and spans a lengthy duration. The risk posed to the BPS was mitigated by the following factors. The SEIM system is located within RFC_URE1’s staffed corporate data center that has controlled access in place. RFC_URE1 afforded the SEIM servers certain protective measures, including the protective measures of CIP-003-1 R1 through R5, CIP-004-1 R3, CIP-005-1 R2 and R3, CIP-007-1 R1, R7, and R8, CIP-008-1, and CIP-009-1. Specifically, RFC_URE1 had the following: a documented personnel risk assessment program, organizational processes and technical and procedural mechanisms for control of electronic access, electronic or manual processes for continuous monitoring and logging access, test procedures, established formal methods, processes, and procedures for disposal or redeployment of Cyber Assets used in the access control and monitoring of the ESP, as identified and documented in Standard CIP-005, and annual performance of a cyber vulnerability assessment. | when the Standard became mandatory and enforceable for RFC_URE1 | Mitigation Plan completion | $0 (for RFC2012011278 and RFC2012011280) | Self-Report | To mitigate this violation, RFC_URE1: 1) added the devices to the list of Cyber Assets such to ensure that SEIM servers are identified as Cyber Assets used in the access control and/or monitoring of the ESP; that they are have become subject to the same requirements as applied to other Cyber Assets and applied the protections required by CIP-005-3a R1.5; 2) ensured that appropriate change management procedures are used to manage changes to SEIM servers per CIP-003-3 R6; 3) moved the SEIM servers within an identified Physical Security Perimeter per CIP-006-3 R3; 4) ensured that appropriate security posture verification is performed on SEIM servers for significant changes per CIP-007-3 R1; 5) developed a baseline of required ports and services for SEIM servers and ensured that the baseline is monitored per CIP-007-3 R2; 6) verified that the SEIM servers are included in RFC_URE1's corporate security patch management program and that all related documentation is in place per CIP-007-3 R3; 7) implemented anti-virus software or submitted Technical Feasibility Exception documentation for the SEIM servers as necessary per CIP-007-3 R4; 8) verified that all shared accounts used to administer the SEIM servers are managed according to the company’s NERC CIP shared account management procedure per CIP-007-3 R5; 9) verified that appropriate security status monitoring is performed for the SEIM servers per CIP-007-3 R6; 10) ensured that any disposal or redeployment activity related to SEIM servers follows the company’s NERC CIP Cyber Asset disposal or redeployment procedure per CIP-007-3 R7; 11) ensured that vulnerability assessments have been performed for SEIM servers per CIP-007-3 R8; 12) updated procedures related reviewing and updating documentation per CIP-007-3 R9; and 13) ensured that support personnel for the SEIM servers received appropriate training and awareness information related to the classification of the servers as Cyber Assets. | 2012-11-15 | 2013-04-03 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF also considered that it discovered the violations through Self-Reports and applied mitigating credit. RFC_URE1 promptly reported these violations as a result of the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. RF seeks to encourage this type of behavior including self-reporting characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action and periodic outside examination of the compliance program, by imposing a zero dollar monetary penalty for these violations.
2013-06-27 | FERC | NP13-39-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011280 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF, stating that it was in violation of CIP-006-1 R1.8. As part of a vendor assessment of its CIP compliance program, RFC_URE1 discovered that it failed to afford certain protective measures to Cyber Assets used to authorize and/or log access to the Physical Security Perimeter (PSP) pursuant to CIP-006-1 R1.8. RFC_URE1 utilizes specific operator workstations for badge creation and provisioning, user access rights management, monitoring alarms related to the PSP, and remote control of lock mechanisms. RFC_URE1 failed to afford these workstations certain protective measures specified in CIP-006-1 R1.8. Specifically, RFC_URE1 failed to ensure that it protected these workstations from unauthorized physical access and failed to afford these workstations the protections of CIP-003-1 R6 and CIP-007-1 R1, R2, R3, R6, R7, and R9. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because a violation of CIP-006-1 R1.8 provides the opportunity to access the PSP by leaving Cyber Assets that authorize and/or log access to the PSP unprotected. The risk posed to the BPS by the foregoing facts and circumstances was mitigated by the following factors. The workstations are located within secured buildings with controlled access. RFC_URE1 protected the workstations with user identifications and passwords, and access was limited to those who have personnel risk assessments and cybersecurity training. RFC_URE1 afforded the workstations certain protective measures, including the protective measures of CIP-003-1 R1 through R5, CIP-004-1 R3, CIP-005-1 R2 and R3, CIP-006-1 R4 and R5, CIP-007-1 R4, R5, and R8, CIP-008-1, and CIP-009-1. Specifically, RFC_URE1 had: a documented personnel risk assessment program, organizational processes and technical and procedural mechanisms for control of electronic access, electronic or manual processes for monitoring and logging access, operational and procedural controls to continuously manage physical access, technical and procedural controls for continuous monitoring of physical access, a security patch management program for tracking, evaluating, testing, and installing applicable cybersecurity software patches, anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware, technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access, established formal methods, processes, and procedures for disposal or redeployment as identified and documented in Standard CIP-005, annual performance of a cyber vulnerability assessment, and a cybersecurity incident response plan and implement the plan in response to cybersecurity incidents; and recovery plans for the subject assets. Furthermore, RFC_URE1 implements several other security solutions designed to minimize overall cybersecurity and physical security risk, including intrusion detection, anti-virus, security logging, and access control. | when the Standard became mandatory and enforceable for RFC_URE1 | Mitigation Plan completion | $0 (for RFC2012011278 and RFC2012011280) | Self-Report | To mitigate this violation, RFC_URE1: 1) added the devices to the list of Cyber Assets such that they have become subject to the same requirements as applied to other Cyber Assets and applied the protections required by CIP-006-3c R2.2; 2) updated the company’s CIP-006 compliance procedures to ensure that operator workstations (for NERC CIP PSP functions) were identified as Cyber Assets used in the access control and/or monitoring of the PSP; 3) identified workstations which were, or could have been, used as operator workstations for NERC CIP PSP functions, but are not needed and identified as Cyber Assets in item 1 above, and removed or restricted functionality that was not needed on such workstations, 4) ensured that appropriate change management procedures are used to manage changes to operator workstations per CIP-003-3 R6; 5) implemented measures to ensure that the operator workstations are protected from unauthorized physical access per CIP-006-3 R2.1; 6) ensured that appropriate security posture verification is performed on operator workstations for significant changes per CIP-007-3 R1; 7) developed a baseline of required ports and services for operator workstations and ensured that the baseline is monitored per CIP-007-3 R2; 8) verified that the operator workstations are included in the corporate security patch management program and that all related documentation is in place per CIP-007-3 R3; 9) implemented anti-virus software on the operator workstations as necessary per CIP-007-3 R4; 10) verified that all shared accounts used to administer operator workstations are managed according to the company’s NERC CIP shared account management procedure per CIP-007-3 R5; 11) verified that appropriate security status monitoring is performed for the operator workstations per CIP-007-3 R6; 12) ensured that any disposal or redeployment activity related to operator workstations follows the company’s NERC CIP Cyber Asset disposal or redeployment procedure per CIP-007-3 R7; 13) ensured that vulnerability assessments have been performed for operator workstations per CIP-007-3 R8; 14) updated procedures related reviewing and updating documentation per CIP-007-3 R9; and 15) ensured that support personnel for the operator workstations received appropriate training and awareness information related to the classification of the workstations as Cyber Assets. | 2012-11-15 | 2013-04-03 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RF also considered that it discovered the violations through Self-Reports and applied mitigating credit. RFC_URE1 promptly reported these violations as a result of the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. RF seeks to encourage this type of behavior including self-reporting characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action and periodic outside examination of the compliance program, by imposing a zero dollar monetary penalty for these violations.
2013-06-27 | FERC | NP13-39-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012141 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-002-1 R1 because it had a deficient risk-based assessment methodology (RBAM) which it used to identify its Critical Assets. Specifically, SERC_URE1's RBAM failed to include evaluation criteria to determine if an asset considered pursuant to CIP-002-1 R1.2 was in fact a "Critical Asset," as that term is defined in the NERC Glossary of Terms. The SERC_URE1 RBAM evaluated whether a control center was a Critical Asset by asking whether there would be a loss of central control and/or situational awareness of SERC_URE1's operations in the event that the control center was severely damaged, destroyed, compromised, or misused. Using this criterion, SERC_URE1 applied its RBAM and identified certain control centers as Critical Assets. SERC_URE1 revised its RBAM by adding two additional questions to its evaluation criteria to determine whether a control center was a Critical Asset. The first question asked whether the failure, misuse, or compromise of a control center would result in a negative impact to the reliability of the Bulk Electric System (BES). The second question asked whether the failure or misuse of a control center would significantly impact a third party's Critical Asset. Pursuant to its revised RBAM, SERC_URE1 would determine that a control center was a Critical Asset only if the answer was "yes" to the original evaluation criterion and "yes" to one or both of the two additional evaluation criteria. Using these new criteria, SERC_URE1 applied its revised RBAM and determined that the control centers were not Critical Assets. The NERC Glossary of Terms defines the term "Critical Assets" as "[f]acilities, systems, and equipment which, if destroyed, degraded, or otherwise rendered unavailable, would affect the reliability or operability of the Bulk Electric System." Based on this definition, SERC determined that SERC_URE1's previous RBAM lacked sufficient evaluation criteria to determine if an asset considered pursuant to CIP-002-1 R1.2 was in fact a Critical Asset. Instead, the evaluation criterion that SERC_URE1 used was overly broad and resulted in the incorrect identification of assets as Critical Assets, when in fact those assets did not meet the definition of "Critical Assets" set forth in the NERC Glossary of Terms. SERC determined that the control centers should never have been identified as Critical Assets because they failed to meet the definition of that term. | CIP-002-1 | R1; R1.1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's RBAM used an overly broad evaluation criterion that would result in the incorrect identification of certain assets as Critical Assets, resulting in extra protection for those assets and any associated Cyber Assets. SERC_URE1 conducted engineering studies and consulted with the registered entities it connects to in order to determine whether the control centers should be considered Critical Assets. SERC_URE1 determined that the loss or misoperation of all of the generation and transmission assets it controls and monitors with the control centers would not result in a negative impact to the reliability or operability of the BES. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | when the Standard became mandatory and enforceable for SERC_URE1 | Mitigation Plan completion | 0 | Self-Report | To mitigate this violation, SERC_URE1: 1) revised its RBAM to include evaluation criteria that examined the risk to the BES; and 2) applied its revised RBAM and determined that it had no Critical Assets. | 12/28/2012 | 2013-04-18 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-39-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012139 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-002-1 R1 because it had a deficient risk-based assessment methodology (RBAM) which it used to identify its Critical Assets. Specifically, SERC_URE2's RBAM failed to include evaluation criteria to determine if an asset considered pursuant to CIP-002-1 R1.2 was in fact a "Critical Asset," as that term is defined in the NERC Glossary of Terms. The SERC_URE2 RBAM evaluated whether a control center was a Critical Asset by asking whether there would be a loss of central control and/or situational awareness of SERC_URE2's operations in the event that the control center was severely damaged, destroyed, compromised, or misused. Using this criterion, SERC_URE2 applied its RBAM and identified certain control centers as Critical Assets. SERC_URE2 revised its RBAM by adding two additional questions to its evaluation criteria to determine whether a control center was a Critical Asset. The first question asked whether the failure, misuse, or compromise of a control center would result in a negative impact to the reliability of the Bulk Electric System (BES). The second question asked whether the failure or misuse of a control center would significantly impact a third party's Critical Asset. Pursuant to its revised RBAM, SERC_URE2 would determine that a control center was a Critical Asset only if the answer was "yes" to the original evaluation criterion and "yes" to one or both of the two additional evaluation criteria. Using these new criteria, SERC_URE2 applied its revised RBAM and determined that the control centers were not Critical Assets. The NERC Glossary of Terms defines the term "Critical Assets" as "[f]acilities, systems, and equipment which, if destroyed, degraded, or otherwise rendered unavailable, would affect the reliability or operability of the Bulk Electric System." Based on this definition, SERC determined that SERC_URE2's previous RBAM lacked sufficient evaluation criteria to determine if an asset considered pursuant to CIP-002-1 R1.2 was in fact a Critical Asset. Instead, the evaluation criterion that SERC_URE2 used was overly broad and resulted in the incorrect identification of assets as Critical Assets, when in fact those assets did not meet the definition of "Critical Assets" set forth in the NERC Glossary of Terms. SERC determined that the control centers should never have been identified as Critical Assets because they failed to meet the definition of that term. | CIP-002-1 | R1; R1.1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2's RBAM used an overly broad evaluation criterion that would result in the incorrect identification of certain assets as Critical Assets, resulting in extra protection for those assets and any associated Cyber Assets. SERC_URE2 conducted engineering studies and consulted with the registered entities it connects to in order to determine whether the control centers should be considered Critical Assets. SERC_URE2 determined that the loss or misoperation of all of the generation and transmission assets it controls and monitors with the control centers would not result in a negative impact to the reliability or operability of the BES. SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | when the Standard became mandatory and enforceable for SERC_URE2 | Mitigation Plan completion | 0 | Self-Report | To mitigate this violation, SERC_URE2: 1) revised its RBAM to include evaluation criteria that examined the risk to the BES; and 2) applied its revised RBAM and determined that it had no Critical Assets. | 12/28/2012 | 2013-04-18 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-06-27 | FERC | NP13-39-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC201000561 | Settlement Agreement | SERC_URE3 submitted a Self-Report to SERC stating it was in violation of CIP-007-2 R5 because it did not enforce access authentication of, and accountability for, all user activity for a single Critical Cyber Asset (CCA), due to the unauthorized sharing of a username and password. A SERC_URE3 technician supervisor gave two other technicians the supervisor’s username and password to access the Energy Management System (EMS). The technicians shared the supervisor’s username and password on one CCA workstation that had the EMS client installed, which SERC_URE3 used for troubleshooting Supervisory Control and Data Acquisition communications issues. The technicians engaged in this behavior in order to monitor the EMS continuously, as switching accounts between individual users was time consuming. This unauthorized sharing of the supervisor’s username and password created a situation in which SERC_URE3 could not authenticate which individual was using the supervisor’s account. The two technicians requested that the EMS supervisor create user accounts for them on the EMS. This request triggered a SERC_URE3 investigation that discovered the account sharing. A system administrator changed the technician supervisor’s password to end the account sharing. SERC_URE3 completed its investigation and determined that there were no other instances of user passwords being shared. SERC_URE3 was unable to determine the exact start date of the violation. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The unauthorized access was limited to two SERC_URE3 employees who had completed cyber security training, had valid personnel risk assessments, and were authorized to access the CCA using their own credentials. The CCA is located in a room that is monitored by a video camera and requires scanning an access badge to both enter and exit the room, making identification of the CCA users possible. The unauthorized access was limited to on CCA. Finally, SERC_URE3’s investigation did not reveal any unauthorized activity on the account. | when the Standard became mandatory and enforceable for SERC_URE3 | when SERC_URE3 changed the supervisor's password to end the unauthorized access | $5,000 (for SERC201000561 and SERC2011008332) | Self-Report | To mitigate this violation, SERC_URE3: 1) counseled all affected employees as to the proper manner of sharing computer terminals; 2) disciplined the EMS technicians pursuant to SERC_URE3's corporate discipline system; and 3) acquired additional workstations with licenses to enable more technicians to be able to log into and lock out their respective workstations without affecting the performance of the other technicians. | 2010-10-27 | 2013-03-18 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011008332 | Settlement Agreement | SERC_URE3 submitted a Self-Report to SERC stating it was in violation of CIP-006-3c R2.2, because it did not perform an annual cyber vulnerability assessment (CVA) of Physical Access Control Systems (PACS) devices. SERC_URE3 did not include a review of its PACS devices in its annual CVAs, extending this issue back to Version 1 of the Standard. SERC_URE3 discovered this violation when it conducted an internal review of its PACS device compliance. SERC_URE3’s review revealed that it had not afforded its PACS devices the protective measures specified in CIP-007-1 R8. Specifically, SERC_URE3 had not conducted annual cyber vulnerability testing on its PACS devices. SERC_URE3’s PACS devices included one door access system consisting of servers and control panels. SERC_URE3 included these PACS devices in the CVA it had previously completed. | CIP-006-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3’s PACS were on a separate interface that limited user access and disabled all external internet connectivity. SERC_URE3 had an independent door access system that protected access to the building which contained identified Physical Security Perimeters (PSPs) and was protected within a secured area. SERC_URE3’s internal review revealed that it had afforded its PACS devices all other protective measures required by CIP-006-1 R1.8. Finally, SERC_URE3 did not identify any PACS device vulnerabilities in its CVA. | the day after SERC_URE3 should have conducted its annual CVA including PACS devices) | when SERC_URE3 completed its CVA including PACS devices | $5,000 (for SERC201000561 and SERC2011008332) | Self-Report | To mitigate this violation, SERC_URE3: 1) completed a CVA for PACS devices; 2) ensured that PACS devices would be included in CVAs in the future; and 3) completed a CVA for the following year, which included the PACS devices. | 12/31/2012 | 2013-02-28 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102616 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004 R3 because an employee was granted authorized unescorted physical access to Critical Cyber Assets (CCAs) without having a personnel risk assessment (PRA). The employee was given unescorted access to WECC_URE1's control center for one day. | CIP-004-3 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, for one person, WECC_URE1 failed to conduct a PRA prior to granting that person access to CCAs, for one day. As a compensating measure, the individual having access had been a WECC_URE1 contractor for about seven years and had cybersecurity training. WECC_URE1 had twenty-four hour logging and monitoring of physical and electronic access in place at the facility. | when the employee was granted unescorted physical access | when the employee's unescorted physical access was terminated | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Self-Report | To mitigate this violation, WECC_URE1: 1) performed a PRA for the employee; 2) implemented procedures to minimize errors; and 3) upgraded permissions to gain access to its critical facilities. | 2011-05-05 | 2011-06-30 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. A Settlement Agreement covering violations of CIP-004-1 R3 for WECC_URE1 was filed with FERC under NP11-140-000 on March 30, 2011. On April 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that this prior violation should not serve as a basis for aggravating the penalty. The conduct of the prior violation was not the same or similar to the instant violation.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102901 | Settlement Agreement | During a Compliance Audit, WECC discovered that WECC_URE1 was in violation of CIP-005-1 R2 because it failed to implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter (ESP). Specifically, WECC_URE1 did not enable only ports and services required for operations and for monitoring its Cyber Assets within its ESP. Also, WECC discovered that WECC_URE1 was in violation of CIP-005-1 R2.4 because it did not implement strong procedural or technical controls to ensure authenticity at the access points to its ESPs where there was external interactive access. In addition, WECC discovered that WECC_URE1 was in violation of CIP-005-1 R2.6 because it did not display an appropriate use banner on its associated user screen upon all access attempts. | CIP-005-1 | R2; R2.4; R2.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because the use of non-restrictive rules on the firewalls allows for potential malicious activities from a source to a destination device. This activity could have resulted in compromise, degradation of performance, and possible denial of service of an asset. Interactive access to a device within an ESP must always provide a warning banner to ensure that the user is knowledgeable that the asset they are connected to is for restricted access only. The lack of strong controls at the access point for all traffic entering the ESP allows direct access to a device prior to formal authorization. The risk was mitigated because WECC_URE1 authenticates all access prior to network access. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) configured its firewall to block and prevent applications and services through its ESP access points; 2) replaced the firewall with another firewall with the ability to implement the security policies; 3) established procedural controls at firewall access points to ensure authenticity of the accessing party; and 4) added acceptable use banners to firewall access points. | 2012-12-11 | 2/25/2013 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102902 | Settlement Agreement | During a Compliance Audit, WECC discovered that WECC_URE1 was in violation of CIP-006-1 R1.8 because it did not afford Cyber Assets used in the access control and monitoring of the Physical Security Perimeter, the protective measures specified in CIP-007 R5.3.2 and R5.3.3. Specifically, WECC_URE1 stated in response to a data request that "passwords have not been changed for account users annually," as required by CIP-007-1 5.3.3. In addition, WECC discovered that at least one employee with access to WECC_URE1's system did not have passwords that consisted of a combination of alpha, numeric, and "special characters" required in CIP-007 R5.3.2. | CIP-006-1 | R1.8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As a mitigating factor, WECC_URE1 had twenty-four hour logging and monitoring of physical and electronic access in place at all facilities, including the facility involved in this violation. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) updated its system with complex passwords that consist of a combination of alpha, numeric, and special characters; and 2) established a compliance tracking and management tool to ensure that passwords are changed annually, or more frequently, based on risk. | 2011-12-11 | 2012-01-26 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102859 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006 R1.4 because it did not use physical access controls as described in R4, including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. One contract employee was given physical access without having CIP training. | CIP-006-3c | R1.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As a mitigating factor, WECC_URE1 had twenty-four hour logging and monitoring of physical and electronic access in place at all facilities, including the facility involved in this violation. | when the contract employee was first given physical access | when the contract employee's access was removed | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Self-Certification | To mitigate this violation, WECC_URE1: 1) revoked the access of the individual involved; and 2) implemented a procedure that acts as a double-check on access rights to prevent future inadvertent granting of access rights. | 2011-07-14 | 2011-07-20 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102903 | Settlement Agreement | During a Compliance Audit, WECC discovered that WECC_URE1 was in violation of CIP-006-1 R3 because it failed to have alarms to indicate a door, gate, or window has been opened without authorization and provide immediate notification to personnel responsible for response. Specifically, WECC_URE1 failed to monitor physical access at five access points (three Critical Asset locations) to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to have alarms that provide for an immediate response could allow unauthorized individuals access to WECC_URE1's PSP. If an unauthorized individual gained access to WECC_URE1's PSP, that person could use that access to engage in malicious conduct and cause damage to WECC_URE1's system. As a mitigating factor, WECC_URE1 had twenty-four hour logging and monitoring of physical and electronic access in place at all facilities, including the facility involved in this violation. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) established operational requirements for its physical security system that define the operation and alarming of access points at PSPs; 2) installed door alarms, including door held open and forced entry alarms on the doors cited in the violation; 3) established procedures for response to events/alarms and trained users and maintainers of the system on the new security system functionality and features; 4) updated its Physical Security Procedures and Plan document and other security system documentation; and 5) developed system test procedures and maintenance forms to assure proper system operation. | 2012-03-22 | 2012-06-21 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102904 | Settlement Agreement | During a Compliance Audit, WECC discovered that WECC_URE1 was in violation of CIP-007-1 R5. Specifically, WECC_URE1 did not provide sufficient evidence to demonstrate that it renamed administrator and factory default accounts as required by CIP-007-1 R5.2.1. In addition, WECC_URE1 did not provide sufficient evidence to establish that it identified individuals with access to shared accounts as required by CIP-007 R5.2.2. The Audit team did not find evidence of an audit trail of the shared account use, automated or manual. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated because WECC_URE1 had an account management policy in place, even though it was not implemented completely. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) reviewed its account management procedure; 2) determined the number of shared or generic accounts on its system and determined the number of individuals with access to shared or other generic accounts; 3) removed shares to other generic accounts; 4) implemented an audit trail for use of shared accounts; and 5) implemented an manual process for capturing shared account use. | 2012-08-31 | 2012-09-21 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-39-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102905 | Settlement Agreement | During a Compliance Audit WECC discovered that WECC_URE1 was in violation of CIP-007-1 R8 because it did not perform a cyber vulnerability assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter (ESP) at least annually and did not perform the CVA per the requirements of the Standard. In addition, WECC_URE1's CVA for other calendar years did not include all Critical Cyber Assets (CCAs) within its ESP. Also, WECC_URE1 did not provide sufficient evidence to demonstrate that only those ports and services required for operation of the Cyber Assets within the ESP were reviewed and enabled. Finally, WECC_URE1 did not document action plans to remediate or mitigate vulnerabilities identified in the an assessment. | CIP-007-1 | R8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated because WECC_URE1 had an account management policy. WECC_URE1 performed vulnerability assessments in past years and would have been able to address vulnerabilities during the year prior to and after the year it failed to perform the vulnerability assessment. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $62,500 (for WECC201102616, WECC201102901, WECC201102902, WECC201102859, WECC201102903, WECC201102904, and WECC201102905) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) updated its vulnerability assessment process document; 2) trained technical personnel on the activities and documentation necessary to perform a compliant vulnerability assessment; 3) performed a CVA of all CCAs based on its updated vulnerability assessment process document; and 4) established a yearly task for a CVA. | 2012-05-30 | 2012-07-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-33-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009757 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO stating that, it was in violation of CIP-006-1 R1 because it discovered that its Physical Security Plan was not approved by a senior manager as required by its corporate CIP cyber security policy. To mitigate this issue, a full review of the MRO_URE1 Physical Security Plan was performed. While conducting the review, MRO_URE1 discovered that a required six-wall Physical Security Perimeter (PSP) was not established at a control center. MRO_URE1 also identified two other non-continuous six-wall barriers at two different facilities. Each PSP opening was greater than 96 square inches. One facility had motion detectors, which are monitored by security personnel; however, the motion detectors were not documented as "alternative measures," as required by CIP-006-1 R1.1. MRO_URE1's other facility also did not have continuous six-wall barriers, and there were no alternative measures in place. Two rooms had walls that did not extend above the dropped ceiling. Additionally, one room had large openings in a concrete block wall above the ceiling tiles. All openings were remediated through installation of wire mesh fencing material. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. Approximately 150 individuals had physical access to the PSP for one facility while an additional 676 individuals only had access to the building containing the PSP. The facility was manned continuously and thus, provided monitoring and detection of unauthorized access. At the other facility, one room was continuously manned, but the other room was not. The alternative measures (motion detectors) were a mitigating control for a non-continuous six-wall barrier. The fact that the measures were not previously documented resulted in a documentation deficiency issue. Additionally, although the Physical Security Plan was not initially approved by the senior manager, it was reviewed and updated at least annually. | When the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | 15000 | Self-Certification | To mitigate this violation, MRO_URE1: 1) performed a full PSP inspection on all MRO_URE1 NERC CIP Cyber Assets; 2) updated its physical security policy on findings from the physical security inspections; and 3) closed any gaps discovered to ensure a continuous six-wall border. | 2012-09-25 | 2012-10-30 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination.
2013-05-30 | FERC | NP13-33-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100439 | Settlement Agreement | During a Spot Check, MRO discovered that MRO_URE2 failed to require that each password has a combination of alpha, numeric, and "special" characters as required by CIP-007-1 R5.3.2. MRO_URE2's policy states that passwords must contain three of the following categories: upper case letters, lower case letters, and special characters (any nonletter or number, such as ! @ # * <), and/or numbers. However, upon reviewing password settings on several devices, MRO discovered that the operating system's default setting was used and the setting did not meet the CIP-007 R5.3.2 requirements on complexity settings. More specifically, MRO discovered that one device was not enabled for password complexity settings and another device had system limitations which did not allow it to systematically enforce password requirements. MRO_URE2 had not submitted a Technical Feasibility Exception (TFE) for the device with system limitations. Additionally, MRO discovered that passwords were not changed annually as required by R5.3.3. Specifically, MRO_URE2 failed to change passwords annually on multiple separate accounts. Of those multiple accounts, some were domain administrative accounts, administrative accounts on Front End Processors (FEPs), administrative accounts on Inter-Control Center Communications Protocol (ICCP) servers, and administrative accounts on Supervisory Control and Data Acquisition (SCADA) servers. The FEPs and SCADA servers are the devices used to monitor and control the bulk power system (BPS) and serve as the interface between field devices and the Energy Management System (EMS). The remaining accounts were non-administrative accounts on EMS servers, as well as accounts on MRO_URE2's system used for testing, but no BPS control and system used to retrieve historical operating data. These administrative accounts were also shared accounts, with access being granted to different individuals at the entity. Some of the devices had accounts with passwords that had not been changed since 2009. | CIP-007-1 | R5.3; R5.3.2; R5.3.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. MRO determined that this violation posed a moderate risk because it affected a substantial number of separate accounts. The lack of secure passwords could have resulted in unauthorized access to the devices on which these shared administrative accounts resided. The risk to the reliability of the BPS was mitigated because all the affected devices, including the domain controllers, are within the protected Electronic Security Perimeter (ESP). In addition, all of the individuals with shared access to the administrative accounts had proper cybersecurity training and personnel risk assessments. Furthermore, MRO_URE2 did not experience any cyber incidents during this period. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Spot Check | To mitigate this violation, MRO_URE2: 1) set password complexity to meet the complexity requirements of CIP-007-3 R5.3.2; 2) revised its cybersecurity policy to reflect specific password complexity requirements of CIP-007-3 R5.3.2; 3) disabled defunct accounts that were overlooked in the access reviews; 4) researched use of operating system custom password filters to supplement the directory service default password complexity; 5) documented and submitted TFE requests for devices with technical limitations that do not support enforcement of the password control requirements of R5.3; 6) revised the cybersecurity training program to emphasize specific password complexity requirements of CIP-007-3 R5.3.2; and 7) reset local account passwords to ensure they meet the requirements of CIP-007-3 R5.3. | 2012-03-26 | 2012-07-31 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination. Also, MRO determined that the concurrently filed violation of CIP-007-1 R5 (MRO2012010180) should not serve as an aggravating factor in penalty determination because it occurred concurrently with the instant violation. Additionally, MRO_URE2 completed or will complete the following above and beyond measures, which MRO considered as a mitigating factor in the penalty determination: 1) MRO_URE2 will hire an external consultant to provide a professional and knowledgeable perspective on the configuration of MRO_URE2’s security appliances that define and protect the Electronic Security Perimeter. This expertise will include reviewing the following configurations: a) intrusion detection system management; b) system information and event management; c) adaptive security appliance; and d) firewall services module. In reviewing these configurations, the consultant: will identify any ports or services that are not essential for providing effective security configuration for the environment; assess virtual local area network, firewall services, and security event management configurations for optimal protection of the ESP; provide additional insight and scrutiny in identifying any potential vulnerabilities; and assist with the complex configuration of the existing intrusion detection module which will enhance detection of intrusion attempts and provide defense in depth for the ESP environment. The services are anticipated to be conducted over a 40 hour consulting period; and 2) MRO_URE2 will purchase vulnerability port scan software including physical servers. MRO_URE2 currently uses another type of scan software and manual assessment of results. The new scanning tool will reduce the potential for human error by automating performance. Currently, MRO_URE2 manually performs an annual review of the ports and services assessment. The vulnerability port scan software will be automated to periodically perform this assessment and the tool can be customized to conduct analytic comparisons to identify changes that a subject matter expert can further investigate to enhance and improve the security and reliability of the CIP environment.
2013-05-30 | FERC | NP13-33-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010180 | Settlement Agreement | This violation was discovered by MRO during verification of MRO_URE2's certification of Mitigation Plan completion for another violation of CIP-007-1 R5 (NERC Violation ID MRO201100439). MRO discovered that technical controls for the automatic expiration of passwords were not enabled for one device. MRO_URE2 submitted its access policy platform appliances' configuration in an effort to show completion of mitigation for MRO201100439. Upon MRO's recommendation, MRO_URE2 submitted a Self-Report to MRO stating that it had a violation of CIP-007-1 R5 for failing to implement technical controls that ensure annual password changes. While updating technical password complexity requirements on its access policy platform appliance, MRO_URE2 discovered that an option to enable restricted password duration was inadvertently left unchecked. Consequently, no technical control was implemented to enforce annual password changes for this appliance as required by R5.3.3. | CIP-007-1 | R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access policy platform appliance only has a few individuals with access to it. Both of those individuals have appropriate personnel risk assessments and are current with cybersecurity training as required by the Standards. Additionally, although MRO_URE2 did not implement technical control, it did have procedural controls such as internal processes with annual reminders to change passwords, which meet the requirements of CIP-007 R5.3.3. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Self-Report | To mitigate this violation, MRO_URE2, upon discovering the violation, enabled the password lifetime option on the access policy platform appliance to enforce systematically the password change requirements of CIP-007-3 R5.3.3. | 2012-03-26 | 2012-07-31 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination. Also, MRO determined that the concurrently filed violation of CIP-007-1 R5 (MRO2012010180) should not serve as an aggravating factor in penalty determination because it occurred concurrently with the instant violation. Additionally, MRO_URE2 completed or will complete the following above and beyond measures, which MRO considered as a mitigating factor in the penalty determination: 1) MRO_URE2 will hire an external consultant to provide a professional and knowledgeable perspective on the configuration of MRO_URE2’s security appliances that define and protect the Electronic Security Perimeter. This expertise will include reviewing the following configurations: a) intrusion detection system management; b) system information and event management; c) adaptive security appliance; and d) firewall services module. In reviewing these configurations, the consultant: will identify any ports or services that are not essential for providing effective security configuration for the environment; assess virtual local area network, firewall services, and security event management configurations for optimal protection of the ESP; provide additional insight and scrutiny in identifying any potential vulnerabilities; and assist with the complex configuration of the existing intrusion detection module which will enhance detection of intrusion attempts and provide defense in depth for the ESP environment. The services are anticipated to be conducted over a 40 hour consulting period; and 2) MRO_URE2 will purchase vulnerability port scan software including physical servers. MRO_URE2 currently uses another type of scan software and manual assessment of results. The new scanning tool will reduce the potential for human error by automating performance. Currently, MRO_URE2 manually performs an annual review of the ports and services assessment. The vulnerability port scan software will be automated to periodically perform this assessment and the tool can be customized to conduct analytic comparisons to identify changes that a subject matter expert can further investigate to enhance and improve the security and reliability of the CIP environment.
2013-05-30 | FERC | NP13-33-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012009156 | Settlement Agreement | MRO_URE2 submitted a Self-Report to MRO stating that it had a violation of CIP-006-1 R1.1 because its Physical Security Perimeter (PSP) was not completely enclosed within a "six-wall" border and no documented alternative measures were deployed. MRO_URE2 identified areas of the PSP above ceiling tiles that were not fully enclosed to the solid ceiling. MRO_URE2 personnel subsequently completed a review of the PSP and identified openings in the PSP large enough to constitute a deficiency in the complete six-wall border of the PSP. When MRO_URE2 originally constructed additional barriers from the top of solid walls to the solid ceiling in the area above dropped ceilings to create a complete six-wall security perimeter, the barrier was not extended fully from the existing solid wall to the solid ceiling in the areas identified. Therefore, openings existed above the dropped ceiling where the solid surface wall did not extend completely to the solid surface ceiling. Because the dropped ceiling kept this area from view, it was not identified until HVAC work required access to the area. | CIP-006-1 | R1; R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO determined that the violation posed a moderate risk because although the PSP is located within a secured building, there were large gaps and the violation duration was almost two and a half years. While most of the individuals with approved access to the PSP are MRO_URE2 employees, some individuals were contractors such as janitorial staff. Additionally, not all of the individuals with access to the secured building had approved access to the PSP. The risk to the BPS was mitigated because, for the duration of the violation, the secured building was staffed 24 hours per day, seven days per week. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Self-Report | To mitigate this violation, MRO_URE2: 1) implemented additional security measures to reinforce security awareness and physical access controls; 2) heightened awareness messages sent to affected personnel; 3) configured main external entrances to building for continuous authentication; 4) conducted a comprehensive review of the PSPs to assess compliance with the requirements of CIP-006-3 R1.1, and acceptable opening dimensions; and 5) closed identified gaps in the PSP and installed restrictions in ductwork that traverse the perimeter boundaries. | 2011-12-22 | 2012-06-13 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination.
2013-05-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008334 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-005-1 R2.2 because NPCC_URE1 did not complete all of the activities required by CIP-005-3 R2.2 for one firewall and one switch. Specifically, NPCC_URE1 failed to complete assessment and documentation for the review of ports and services for the firewall and the switch. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. The switch resided within an ESP protected by a firewall that is monitored per CIP-005-1 R4 and only authorized personnel per CIP-004 requirements had access to the ESP. In addition, risk was also mitigated because of network isolation, which prevented exposure of the device to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE1 | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-11-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008340 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-007-1 R2.1 and R2.2 because NPCC_URE1 failed to meet the requirements of the Standard for one firewall and one switch. Although NPCC_URE1 established, documented, and implemented a process to ensure that only ports and services required for normal and emergency operations were enabled, the process failed to have complete assessment and documentation for the review of ports and services for the firewall and the switch. | CIP-007-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of these devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP. All individuals were required to have an authorized access card per CIP-004-1 requirements for entry into the PSP or were required be escorted per CIP-006-1. The switch resided within an ESP which was protected by a firewall. The ESP was monitored per CIP-005-1 R4 and only authorized personnel per CIP requirements have access to the ESP. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. In addition, all personnel authorized for unescorted physical and electronic access were trained annually on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE1 | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-11-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009745 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-004-3 R4.1 because an employee that retired from the company did not have his access to Critical Cyber Assets (CCAs) revoked within seven days of his last day of employment. The revocation of the employee's access was not completed until nine days after his retirement date. | CIP-004-3 | R4; R4.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee's access and identification (ID) card was turned in to the plant on the employee's last day on-site. The employee cannot access the Physical Security Perimeter containing all CCAs without the access and ID card. Also, the revocation of the employee's access was completed in nine days, two days after the required date. | When NPCC_URE1 was required to revoke access to the CCAs | When NPCC_URE1 revoked access to the CCAs | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) identified and trained a designated backup gate keeper to assure authorized availability to revoke access; 2) revised the site process document to include responsibility for taking possession of physical access card from employee on last day of employment; 3) modified the termination notification process from human resources to generate a work order to the site gate keeper and designated backup to revoke access; and 4) modified termination procedure to initiate a reminder on open termination tickets after 48 hours. | 2012-04-02 | 2013-01-11 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009937 | Notice of Confirmed Violation | On March 17, 2012, NPCC_URE1 submitted a Self-Report to NPCC stating that, as a Generator Owner and as a Generator Operator, it had a violation of CIP-007-3 R5.3.3. Two administrative passwords were not changed within the annual period as defined by its parent company for certain devices as required by the Standard. | CIP-007-3 | R5; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 had a designated site gatekeeper, who is the only employee that administers authorized access to the devices. The gatekeeper is responsible for issuing passwords to authorized personnel. Also, these devices resided within a Physical Security Perimeter (PSP). All individuals were required to have authorized access cards per CIP-004-3 requirements for entry into the PSP or were required to be escorted per CIP-006-3. All devices resided within an Electronic Secure Perimeter (ESP) protected by a firewall that is monitored per CIP-005-3 R4. Only authorized personnel per CIP-004-3 had access to the ESP. Network isolation prevented exposure of device to untrusted networks, including the Internet and business network. | When the passwords should have been changed | When the passwords were changed | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) changed the administrator password for certain devices; 2) cataloged the accounts with passwords for use with future annual password changes and created vulnerability script to run twice a year to verify password age; 3) changed the current compliance activity frequency for password changes to semi-annually; and 4) added language to check password age. | 2012-03-19 | 2013-01-11 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010466 | Notice of Confirmed Violation | During an on-site Compliance Audit, NPCC discovered that NPCC_URE1 was in violation of CIP-007-3 R3.1. NPCC_URE1 did not document the assessment of security patches and security upgrades for applicability for three personal computers and one switch within 30 calendar days as required by CIP-007-3 R3.1. | CIP-007-3 | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of these devices were protected by the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP. All individuals were required to have an authorized access card per CIP-004-3 requirements for entry into the PSP or were required to be escorted per CIP-006-3. The switch resided within an ESP protected by a firewall that is monitored per CIP-005-3 R4. Only authorized personnel per CIP-004-3 requirements had access to the ESP. Network isolation prevented exposure of the device to untrusted networks, including the internet and business network. In addition, all personnel that were authorized for unescorted physical and electronic access were trained annually on the requirements of CIP-007-3. | When NPCC_URE1 was required to document the assessment of security patches and security upgrades | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Compliance Audit | To mitigate this violation NPCC_URE1: 1) created unique device identifiers for each device for ease of tracking data collection; 2) created a master spreadsheet of all third-party applications; 3) created a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; 5) tested applicable patches from assessment stage using the established process; and 6) documented and deployed the applicable patches to production. | 2012-07-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008438 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-1 R2.2 because it failed to document, individually or by specified grouping, the configuration of ports and services required for operation and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) for one firewall. A CIP management program had been established, documented, and implemented per CIP-005-1 R2, however, not all of the activities to meet requirements of CIP-005-1 R2.2 were completed for one firewall. These deficiencies were incomplete assessment and documentation for review of ports and services for the firewall. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. In addition, risk was also mitigated because of network isolation, which prevented exposure of the device to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-12-22 | 2013-02-05 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008439 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R2.2 because it failed to disable ports and services not required for normal and emergency operations, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP). A CIP management program had been established, documented, and implemented per CIP-007-1 R2, however, not all of the activities to meet CIP-007-1 R2.2 were completed. The deficiencies included incomplete assessment and documentation for review of ports and services for the switches, programmable logic controllers (PLCs), and media converters. More than 15% of total Cyber Assets within the ESP were affected by this violation. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by the ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. In addition, the risk was also mitigated because of network isolation, which prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-12-22 | 2013-02-06 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008440 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 because it did not document the assessment of security patches and security upgrades for applicability for personal computers (PCs), network switches, programmable logic controllers (PLCs), and media converters within 30 calendar days. In addition, it was in violation of CIP-007-1 R3.2 because of incomplete documentation for the implementation of security patches for the operating system of the network switches. | CIP-007-1 | R3.1; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were protected by the Electronic Security Perimeter (ESP) protected by a firewall and were monitored per CIP-005 requirements. The devices resided in a Physical Security Perimeter (PSP) which is secured with a card access system as per CIP-006 requirements. Additionally, network isolation prevented exposure of devices to untrusted networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) created unique device identifiers for each device for ease of tracking data collection; 2) established a master spreadsheet of all third party applications, including patch levels for all PC assets, PLC patches for all assets, media converter patches for all assets; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; and 5) tested applicable patches from assessment stage using established process and documented and deployed to production. | 2012-07-08 | 2013-02-06 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009111 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-3 R2.2 because it failed to document, individually or by specified grouping, the configuration of ports and services required for operations and for monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). Not all the activities required by the Standard were completed for seven firewalls and one personal computer (PC). NPCC_URE3 failed to complete the assessment and documentation for review of ports and services for the firewalls and the PC. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed the ports and services of the seven firewalls and PC in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained the engineering personnel on the revised procedure. | 2011-12-08 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009112 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of NERC CIP-007-1 R2.2 because it failed to disable ports and services not required for normal and emergency operations, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP). NPCC_URE3 failed to complete the activities required for 12 switches, 20 programmable logic controllers (PLCs), 2 personal computers (PCs), 2 remote terminal units (RTUs), 10 demand meters, 9 card-reader interfaces, 1 network attached storage drive, and 2 media converters. The deficiencies included incomplete assessment and documentation for review of ports and services for the switches, PLCs, PCs, RTUs, demand meters, card-reader interfaces, network attached storage drive, and media converters. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained the engineering personnel on the revised procedure. | 2012-10-01 | 2013-02-07 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009119 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 because it failed to document the assessment of security patches and security upgrades according to the Standard. NPCC_URE3 did not complete the assessment of security patches and security upgrades for 8 programmable logic controllers (PLCs), 12 switches, 10 demand meters, 9 card-reader interfaces, 1 network hard drive, and 2 remote terminal units within the 30 calendar day requirement. Also, there was insufficient documentation to determine whether ports and services were originally disabled. NPCC_URE3 also failed to provide complete documentation for the implementation of security patches on the operating systems of the network switches, as required by CIP-007-1 R3.2. | CIP-007-1 | R3.1; R3.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. Network isolation prevented exposure of these devices to untrusted networks, including internet and business networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) established a master spreadsheet of all third party applications; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the using the guidance document; and 5) tested applicable patches from the assessment stage using an established process of documenting and deploying to production. | 2012-08-06 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009120 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R4 because anti-virus and anti-malware software was not tested and applied for one personal computer (PC) that performs monitoring, alerting, and logging functions. | CIP-007-1 | R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Network isolation prevented exposure to untrusted networks, including the internet and business network. This device was protected by the Electronic Security Perimeter (ESP) protected by a firewall and was monitored per CIP-005 requirements. The device was configured with trend micro office scan. The device resides in a Physical Security Perimeter (PSP), and the PSP is secured with a card access system as per CIP-006 requirements. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) applied and updated anti-virus and anti-malware for the PC; and 3) provided evidence that anti-virus and anti-malware are being properly maintained and tested. | 2012-11-15 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009121 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5.1.1 and R5.1.3 because there was no documentation to show that monitoring, alerting and logging devices were managed as required by the Standard. One personal computer (PC), 2 remote terminal units (RTU), nine DSX land cards, 11 ION demand meters (IED) and 20 programmable logic controllers (PLC) devices did not have factory default passwords changed in accordance with CIP-007 R5.2.1; and one PC, 20 PLC, 2 RTU, and 11 IED devices did not have documentation to show that the passwords were updated in the intervals as required by CIP-007-1 R5.3.3. | CIP-007-1 | R5.1; R5.1.1; R5.1.3; R5.2; R5.2.1; R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. All devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-006. A Site Keeper, must verify that proper credentials are in place before granting electronic local or remote interactive access to Critical Cyber Assets (CCAs) or unescorted physical access to CCAs. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 Requirement 5. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) changed all existing administrator passwords; 3) created a process to run vulnerability script twice per year to verify password age; and 4) changed the frequency for password changes to biannually to assure compliance with CIP-007. | 2012-09-04 | 2013-03-07 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009122 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that, as a Generator Owner and as a Generator Operator, it was in violation of CIP-007-1 R6.5 because a monitoring, alerting and logging device was not managed according to the Standard. Logs were generated but not reviewed on a regular basis for one personal computer. | CIP-007-1 | R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS was mitigated by the fact that this issue was a documentation issue. This device did not control any other devices. The device resided within an Electronic Security Perimeter protected by firewall and network isolation prevented exposure of this device to untrusted networks. The device was previously configured with symantec endpoint protection that provided additional cybersecurity. Finally, review of the logs showed normal activity for the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed logs and set an initial baseline date for review; and 2) established a procedure for reviewing logs from the alerting and logging devices to ensure compliance with CIP-007. | 2011-12-19 | 2013-03-08 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008476 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-006-3c R5 because the telephone line failed at an unmanned blackstart unit. The line was from the unit to the remote control room. The loss of the communication line affected two functions: real-time alarm monitoring capabilities were lost from the unit to the remote control room, and the ability to quick-start the unit remotely was lost. The loss of monitoring lasted until an operator manned the station. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the alarm capability was lost for the time period, the unit still had functional physical access controls because the access control systems were still activated. In addition, logging capabilities were still functional and showed no intrusions during the period. The loss of monitoring was for approximately seven hours. | When NPCC_URE3's unit lost real-time alarm capability at the unit | Mitigation Plan completion | $30,000 for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed and updated the procedure for operator response when there is a loss of communication to the remote site; 2) trained control room operators on their responsibility to notify the appropriate entities when communication to a remote site is lost; and 3) added a backup line to the remote sites to reduce the chance of remote communication malfunction. | 2011-11-29 | 2013-03-06 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008477 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of TOP-002-2a R14.1 because NPCC_URE3 failed to notify the appropriate entities of a change in real and reactive capabilities as required by the Standard. A telephone line failed at an unmanned blackstart unit. Since the line failed, NPCC_URE3 was unable to remote start the unit. The blackstart unit was later manned for local dispatch. The result was no real-time alarm monitoring capability for the unit. The loss of communication may have also affected the availability of the unit, but the control room operator did not notify Operations that the unit's availability had been affected by the loss. Therefore the appropriate entities were not promptly notified that the unit could not be quick-started remotely. Operations was notified by the on-call person upon arrival at the unit to change availability to "available for dispatch." The appropriate entities were later notified that the unit was available for verbal dispatch. | TOP-002-2a | R14.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The loss of communication made the unit unavailable for quick-start and the appropriate entity was unaware of the condition. The condition was for a short period at which time the station was manned and the appropriate entity was notified of the loss of communication and could order the unit dispatched manually through Operations. | When NPCC_URE3 failed to notify appropriate entity of changes in real output capability | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed and updated the procedure for operator response when there is a loss of communication to the remote site; 2) trained control room operators on their responsibility to notify the appropriate entities when communication to a remote site is lost; and 3) added a backup line to the remote sites to reduce the chance of remote communication malfunction. | 2011-11-29 | 2013-03-06 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009113 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-005 R2.2 because it failed to complete assessments and provide documentation for a review of ports and services for one firewall and one personal computer (PC). | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) reviewed the ports and services of the firewall and PC in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2012-04-26 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009114 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R2.2 because it failed to complete assessments and provide documentation for a review of ports and services for fifteen percent several of it's Cyber Assets, including two switches, one programmable logic controller (PLC), seven personal computers (PCs), and one media converter. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation were enabled 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2012-05-31 | 2013-02-07 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009115 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 and R3.2 because it did not perform the assessment of security patches and upgrades for one equipment including a programmable logic controller (PLC), 2 switches, and seven personal computers (PCs) within 30 calendar days of availability, as required by CIP-007-1 R3.1. NPCC_URE4 also failed to provide complete documentation for the assessment of security patches on the operating systems of the network switches, as required by CIP-007-1 R3.2. | CIP-007-1 | R3.1; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. Network isolation prevented exposure of these devices to untrusted networks, including internet and business networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) created a master spreadsheet of all third party applications; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; and 5) tested applicable patches from assessment stage using established processes documented all results and deployed to production in a manner that minimized risk to the BPS. | 2012-08-06 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009116 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R4.1 and R4.2 because it failed to test and apply anti-virus and anti-malware software to one personal computer (PC) that performs monitoring, alerting, and logging functions. | CIP-007-1 | R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This device was protected by the Electronic Security Perimeter (ESP) protected by a firewall and was monitored per CIP-005 requirements. The device resides in a Physical Security Perimeter (PSP) and the PSP is secured with a card access system as per CIP-006 requirements. The device was previously configured with third-party software. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) applied and updated anti-virus and anti-malware for the PC; and 3) provided evidence that anti-virus and anti-malware were being properly maintained and tested. | 2012-11-15 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009117 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating it was in violation of CIP-007-1 R5 because it failed to produced documentation showing that the monitoring, alerting and logging device was properly managed as required by CIP-007-1 R5.1.1 and R5.1.3. Additionally, the monitoring, alerting, and logging device, one PLC, and one media converter did not have factory default passwords changed in accordance with CIP-007 R5.2.1 and passwords changed in the intervals as required by R5.3.3. | CIP-007-1 | R5.1; R5.1.1; R5.1.3; R5.2; R5.2.1; R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. All devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-006. A Site Keeper must verify that proper credentials are in place before granting electronic local or remote interactive access to CCAs or unescorted physical access to CCAs. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 Requirement 5. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) changed all existing administrator passwords; 3) created a process to run a vulnerability script twice a year to verify password age; 4) changed passwords for all affected devices; and 5) changed frequency for password change to bi-annual to assure compliance with CIP-007. | 2012-09-17 | 2013-03-07 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009118 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating it was in violation of CIP-007-1 R6.5 because its monitoring, alerting and logging device had not been managed by site personnel from the onset of its installation. Additionally, logs were being generated but were not being reviewed on a regular basis. | CIP-007-1 | R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS was mitigated by the fact that this issue was a documentation issue. This device did not control any other devices. The device resided within an ESP protected by firewall and Network isolation that prevented exposure of this device to untrusted networks. The device was previously configured with third-party software that provided additional cyber security. Finally, review of the logs showed normal activity for the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) reviewed logs and set an initial date for a baseline review; and 2) established a procedure for review of logs from the alerting and logging device to assure compliance with CIP-007. | 2012-02-29 | 2013-03-08 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
2013-04-30 | FERC | NP13-33-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010322 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-006-1 R1. During the 2011 cyber vulnerability assessment, RFC_URE1 discovered that it had only applied operating system patches to its Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP) and had not applied application-based patches, as required by CIP-007-3 R3. Although RFC_URE1 had not installed such patches, once RFC_URE1 discovered the issue it quickly remediated the issue. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation posed a moderate risk because a violation of CIP-006-3c R2.2 that implicates CIP-007 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for known vulnerabilities to allow infiltration of unauthorized network traffic into the Electronic Security Perimeter that required security patches and upgrades could have prevented. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The Cyber Assets that authorize and/or log access to the PSP are located on an isolated, firewall-protected network monitored by an intrusion detection system. In addition, RFC_URE1 monitors these systems through an enterprise security information and event management solution that monitors logging from these devices. Furthermore, the Cyber Assets that authorize and/or log access to the PSP have updated anti-virus protection. | When the Standard became mandatory and enforceable to RFC_URE1 | When RFC_URE1 installed all patches | 0 | Self-Report | To mitigate this violation, RFC_URE1: 1) applied all missing security patches and validate that it resolved all vulnerabilities; and 2) transferred cybersecurity and patch management authority to its cybersecurity and critical infrastructure support department to ensure future patching of these devices. | 2012-07-24 | 2013-03-01 | Admits | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103027 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R1.1 because it had failed to address all the Requirements in Standards CIP-002 through CIP-009 in its cybersecurity policy. Specifically, WECC_URE1 failed to address: CIP-004-1 R4, CIP-005-1 R3, CIP-006-1 R2, CIP-006-1 R3, CIP-007-1 R2, CIP-007-1 R4, CIP-007-1 R6, CIP-009-1 R1, CIP-009-1 R2, CIP-009-1 R3, CIP-009-1 R4, and CIP-009-1 R5. The violation was due to lack of a complete policy map to ensure the controlling polices and procedures addressed all of the CIP-002 through CIP-009 requirements. | CIP-003-1 | R1; R1.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1's Cyber Security Policy did not adequately document a policy map addressing the CIP-002 through CIP-009 requirements, WECC_URE1 stated that all its Critical Cyber Assets (CCAs) are located inside Physical Security Perimeters and Electronic Security Perimeters and are provided the protections specified in CIP-005 and CIP-006. In addition, WECC_URE1 stated that all its employees with access to CCAs are trained as required by CIP-004 R2 and the training program provides a high level overview of the CIP Standards and WECC_URE1's various policies regarding the Reliability Standards. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) completed a thorough policy mapping project; 2) finalized its policy map; 3) updated, reviewed, and approved applicable documentation; and 4) conducted awareness communication to all individuals with cyber or unescorted access to CCAs. | 2011-10-11 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103028 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R4 because it had failed to identify its disaster recovery plan as protected information, as required by WECC_URE1's information protection program and the Standard. | CIP-003-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's disaster recovery plan was in electronic format only and was protected from unauthorized access. Security measures were in place, including folder share security. Individuals with access to the disaster recovery plan had current training that addressed proper handling of Critical Cyber Asset information. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated and classified the disaster recovery plan appropriately; 2) conducted a root cause analysis; and 3) conducted awareness and training on the above corrective actions. | 2011-12-29 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103029 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R1 for failing to provide evidence that it provided quarterly refresher security awareness for certain contractors. Specifically, contractors from one company did not receive security awareness updates on a quarterly basis. WECC_URE1’s process for distributing awareness media to these contractors was to email with the awareness media and then use a spreadsheet to track the dates the media was disseminated. The WECC_URE1 employee responsible for tracking awareness reinforcement for these contractors retired. The spreadsheet used to track vendor awareness was located in the employee’s secured home folder, which was inadvertently deleted when she left the company. For this reason, WECC_URE1 could not produce any evidence that would support that awareness media was distributed to these contractors. | CIP-004-1 | R1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All involved individuals had current CIP training and personnel risk assessments. In addition, all devices were in a Physical Security Perimeter and Electronic Security Perimeter, and thus were afforded the protections of CIP-005 and CIP-006 | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) re-established formal document detailing security awareness program and security awareness job role functions; 2) created a process to track documentation of indirect communication to contractors to ensure personnel having authorized cyber or authorized unescorted physical access received ongoing security awareness and trained the personnel responsible for this process; and 3) added a section to the applicable monthly status report from the employee responsible for quarterly indirect awareness distribution to the manager documenting completion of duty, thus ensuring management oversight and continuation of duties upon personnel changes. | 2010-09-22 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008992 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1 because it had failed to identify devices as access points to its Electronic Security Perimeters (ESPs). The devices WECC_URE1 reported are port servers, communication switches, and internal network switches. These devices have externally connected communication end points terminating at devices within the ESP and, as required by CIP 005 R1.1, need to be classified as access points. Additionally, WECC_URE1 reported devices that were not afforded the protections of CIP-005-1 R1.5. Specifically, active directory servers, active control server, intrusion detection system, and security information and event management devices were not afforded the protections of CIP-005-1 R1.5. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failing to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded protection measures puts such assets at risk to be manipulated. For instance, if the ports and services required for normal operation of these access control and monitoring assets are not enabled, such ports and services could be utilized to gain unauthorized access to the ESP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets contained in the ESP. Such access may then be used to cause harm to Critical Cyber Assets (CCAs) essential to the operation of the BPS, thereby potentially negatively impacting the BPS. The risk was mitigated because all CCAs are located inside an ESP and Physical Security Perimeter and afforded the protections of CIP-005 and CIP-006. The switches in scope are identified and protected as CCAs, and WECC_URE1 only failed to document the switches as access points. Lastly, the active directory servers and active control servers were located in physically secure areas and located in its corporate network which was protected by restrictive firewalls. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 updated its diagrams and inventory lists designating access points to its ESPs. | 2012-07-31 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010449 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2 because it had failed to update its firewall rules to reflect certain devices that were decommissioned from its network and, as a result, the firewalls were allowing traffic to devices that were no longer on its network. In addition, WECC_URE1 did not have an approved list of ports and services for certain logical access points to its Electronic Security Perimeters (ESPs). WECC_URE1 did have a draft list of approved ports and services; however, the list was never approved by a specific WECC_URE1 director and placed into its document management system as required by WECC_URE1’s procedures. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 did have a draft list of required ports and services for all logical access points that was approved by subject matter experts, but not the required director of technology services. All CCAs are protected by an intrusion detection system which will alert on abnormal traffic. All CCAs are within a designated Physical Security Perimeter with restrictive access points which only allows physical access to approved, vetted, and trained individuals. All CCAs had antivirus/malware prevention tools and have unique accounts with strong passwords. Finally, although WECC_URE1 was allowing its network to host traffic, it was only allowing traffic from approved (trusted) networks. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented firewall rules between hosts; 2) removed the network-to-network trust rules; 3) removed unnecessary firewall rules; 4) updated the firewall change processes; 5) required on an ongoing basis a one-year review of rules via the annual Cyber Vulnerability Assessment; 6) established an expiration time for temporary rules; and 7) generated an alert when the time period expires to facilitate timely review and removal of temporary rules. | 2012-11-08 | 2012-12-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010450 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R4. WECC_URE1 had deficiencies in its Cyber Vulnerability Assessments (CVAs) for two years. The first year, WECC_URE1 failed to conduct a CVA for logical access points to Electronic Security Perimeters (ESPs). The second year, WECC_URE1 failed to perform a CVA for switches, which are access points to its ESPs. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because a failure to perform a CVA of the electronic access points to the ESPs may allow for unauthorized internal and or external access, which could allow for successful cyber attacks against Critical Cyber Assets (CCAs) essential to the operation of BPS. As compensating measures, WECC_URE1 employs an anomaly-based network intrusion detection system, which will alert upon detecting any abnormal usage of ports and services. In addition, all CCAs implement antivirus/malware prevention tools and have unique accounts and passwords required to gain access. WECC_URE1 also states it monitors and logs all traffic entering the ESP(s) at all times with daily manual reviews of the logs. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) completed the CVA; 2) reviewed the ESP; and 3) documented the results of the review including the process used, the results, and any mitigation steps/resolutions identified in the CVA. | 2012-11-08 | 2013-02-19 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103031 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because it had failed to afford certain protections listed in CIP-006-1 R1 to certain of its Cyber Assets used in the access control and monitoring of all of its Physical Security Perimeters (PSPs). The devices are WECC_URE1's application server and database server. Specifically, the CIP-006-1 R1 protections WECC_URE1 failed to afford the devices were: CIP-003-1 R5.2, CIP-004-1 R3, CIP-005-1 R2, CIP-007-1 R2, CIP-007-1 R5, CIP-007-1 R8, CIP-009-1 R1, and CIP-009-1 R4. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because the failure to afford the protections in CIP-006-1 R1 to Cyber Assets used in the access control and monitoring of a PSP can hinder an entity's ability to monitor and control access to its PSP, potentially allowing unauthorized individuals access to the PSP. That access can then be used to conduct malicious activities. As compensating measures, WECC_URE1 stated the devices were in a physically secure facility, which is manned and monitored at all times. WECC_URE1 also stated all electronic access to the devices required multi-factor authentication. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) reviewed access privileges for its Physical Access Control (PAC) system; 2) secured computer racks; 3) reviewed ports and services; 4) performed a CIP-004 R4 quarterly audit; and 5) performed a PAC Cyber Vulnerability Assessment. | 2012-08-10 | 2012-12-05 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008993 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-2 R3 because it failed to ensure that certain devices used in the access control and monitoring of its Electronic Security Perimeter (ESP) were located inside a Physical Security Perimeter (PSP). The devices involved in the violation were active directory servers, access control servers (ACS), intrusion detection systems (IDS), and security information and event management devices. These devices are used to monitor users with access to WECC_URE1's ESPs, as well as to grant and verify authentication and authorization of users with access to WECC_URE1's ESPs. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the devices were not in a designated PSP, they were provided the protections of CIP 006-2 R4 and R5. All locations were restricted to authorized access by use of card key, and monitored to detect unauthorized access attempts by use of alarm systems and video monitoring. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) installed and configured card readers on its computer racks; 2) established a new management perimeter network environment; and 3) created a PSP for additional devices. | 2012-06-27 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103032 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2 because it had failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. WECC_URE1 did use a network mapping scan to view what ports and services were running on all the Cyber Assets within Electronic Security Perimeters (ESPs), but did not document the results of the scan. Additionally, WECC_URE1 did not provide any other evidence that it established and documented a process to ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to ensure that only those ports and services required for normal and emergency operations are enabled may allow for unauthorized internal and/or external access, which could allow for successful cyber attacks against Critical Cyber Assets essential to operation of the BPS. As a compensating measure, WECC_URE1 uses an intrusion detection system, with automated alerting, and manual reviews daily during the work-week, to monitor ports and internal traffic. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 created ports and services processes and documentation. | 2012-05-31 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011009032 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because it failed to implement its security patch management program on all of its devices located inside its Electronic Security Perimeters (ESPs). WECC_URE1 was implementing some security patches on 55% of the devices involved, but was not following its documented security patch management program. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against Critical Cyber Assets essential to the operation of the BPS. As compensating measures, all devices are located inside ESPs and Physical Security Perimeters, afforded the protections of CIP-005 and CIP-006, and are monitored by a security information and event management protection program. The program logs are reviewed regularly during normal business hours and are configured for automatic alerting upon detecting cybersecurity events. Vulnerability scans are performed regularly on the entity's test system, and all individuals with access to devices located inside ESPs and PSPs have current personnel risk assessments and cybersecurity training. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) enhanced its security patch management procedure to include tracking, gathering, and evaluating patches; 2) expanded security vulnerability threat meetings; and 3) implemented security patches. | 2012-06-21 | 2012-07-20 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008640 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it had failed to establish, implement, and document technical and procedural controls to ensure passwords consist of a combination of alpha, numeric, and "special" characters. The technical and procedural controls in place required only two of the three criteria specified in the Standard: alpha and numeric characters or alpha and "special" characters. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's password complexity controls require user passwords to be a minimum of eight characters and reset every 60 days. In addition, all remote access requires two-factor authentication and is configured to lockout the user upon five failed login attempts. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its policies and procedures to include annual audit trails; 2) created a logging process; 3) implemented a process to manually log the use of shared accounts; and 4) conducted awareness training for its employees. | 2012-03-30 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008641 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R8 because WECC_URE1 failed to perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets located in both of its Electronic Security Perimeters (ESPs). The Cyber Assets within the ESPs include workstations, servers, and networking equipment related to the entity's supervisory control and data acquisition (SCADA) system. Specifically, WECC_URE1 identified three failures with respect to its CVA process. First, WECC_URE1 stated that it failed to perform a CVA when the Standard became mandatory and enforceable. Second, WECC_URE1 did not perform a CVA on the Cyber Assets, and instead performed a CVA on the Cyber Assets in its test environment. WECC_URE1's understanding was that, if a testing environment mirrored the production ESP, it could run a CVA on only the Cyber Assets in the test system and, for this reason, WECC_URE1 believed it was not required to conduct a CVA on the Cyber Assets. Finally, the CVA performed did not include a review to verify that only ports and services required for operation of the Cyber Asset within the ESPs are enabled. | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within the ESPs are monitored with an intrusion detection system that is configured for automated alerting. All devices have antivirus/malware prevention tools software installed and send logs to a centralized log correlation server. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 performed its CVA in accordance with its procedures and documented the results. | 2012-05-31 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103026 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-008-1 R1 because WECC_URE1's incident reporting and response plan (Plan) did not address CIP-008-1 R1.4, R1.5, and R1.6. Specifically, the Plan stipulated that the Plan needed to be updated annually instead of within 90 days as required by R1.4. The Plan also did not include a process for annual review as required by R1.5. Finally, the Plan did not contain a process for testing the Plan as required by R1.6. | CIP-008-1 | R1; R1.4; R1.5; R1.6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's Plan was tested annually, and WECC_URE1 has a small working group responsible for the Plan. Although the processes in scope were not formally documented, the individuals in the working group were familiar with the processes. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its security handling incident procedure to review annually and audit changes; and 2) tested its security incident handling through a full operational exercise. | 2011-10-31 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103033 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R1 because it failed to address all the Requirements in Standards CIP-002 through CIP-009 in its cyber security policy. Specifically, WECC_URE2 failed to address: CIP-004-1 R4, CIP-005-1 R3, CIP-006-1 R2, CIP-006-1 R3, CIP-007-1 R2, CIP-007-1 R4, CIP-007-1 R6, CIP-009-1 R1, CIP-009-1 R2, CIP-009-1 R3, CIP-009-1 R4, and CIP-009-1 R5. The violation was due to the lack of a complete policy map to ensure the controlling polices and procedures addressed all of the CIP-002 through CIP-009 requirements. | CIP-003-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 stated that all of its Critical Cyber Assets (CCAs) are located inside Physical Security Perimeters and Electronic Security Perimeters and are provided the protections specified in CIP-005 and CIP-006. In addition, WECC_URE2 stated that all its employees with access to CCAs are trained as required by CIP-004 R2 and the training program provides a high level overview of the CIP Standards, and of WECC_URE2's various policies regarding the Reliability Standards. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) finalized its policy map; 2) updated, reviewed, and approved applicable documentation; and 3) conducted awareness communication to all individuals with cyber or unescorted access to CCAs. | 2011-10-11 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103034 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R4 because it had failed to identify its disaster recovery plan as protected information, as required by WECC_URE2's program and the Standard. | CIP-003-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's disaster recovery plan was in electronic format only and was protected from unauthorized access. Security measures were in place, including folder share security. Individuals with access to the disaster recovery plan had current training that addressed proper handling of Critical Cyber Asset information. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) updated and classified the disaster recovery plan appropriately; 2) conducted a root cause analysis; and 3) conducted awareness and training on the above corrective actions. | 2011-12-29 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103035 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R1 because it had failed to reinforce its security awareness program on at least a quarterly basis, for contractors with authorized cyber or authorized unescorted physical access to Critical Cyber Assets. Specifically, contractors from the Supervisory Control and Data Acquisition (SCADA) vendor did not receive security awareness updates on a quarterly basis. There were six contractors involved with electronic access to the electric reliability center Electronic Security Perimeter (ESP) which contains workstations and servers related to WECC_URE2's SCADA. These contractors did not receive the security awareness reinforcement update in the fourth quarter. In addition, contractors did not receive updated security awareness reinforcement until the next year. There are 11 contractors involved who had authorized unescorted physical access to the electric reliability center and Physical Security Perimeters (PSPs), which contained SCADA workstations, SCADA servers, and Inter-Control Center Communications Protocol servers. | CIP-004-1 | R1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All involved individuals had current CIP training and personnel risk assessments. In addition, all devices were in a Physical Security Perimeter and Electronic Security Perimeter, and thus were afforded the protections of CIP-005 and CIP-006. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) re-established formal document detailing security awareness program and security awareness job role functions; 2) created a process to track documentation of indirect communication to contractors to ensure personnel having authorized cyber or authorized unescorted physical access received ongoing security awareness reinforcement, and trained the personnel responsible for this process; and 3) added a section to the applicable monthly status report from the employee responsible for quarterly indirect awareness distribution to the manager documenting completion of duty, thus ensuring management oversight and continuation of duties upon personnel changes. | 2010-09-22 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008638 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-2 R3 because WECC_URE2 failed to ensure one individual had a completed personnel risk assessment (PRA) prior to being granted authorized unescorted physical access to a Physical Security Perimeter (PSP). The PSP contains servers, workstations, and networking equipment comprising its Supervisory Control and Data Acquisition (SCADA) system. The individual was granted access and required physical access as back-up support for WECC_URE2's communications equipment located at a PSP. | CIP-004-2 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual in scope had completed CIP-004 R2 training and the PSP in scope was manned continuously by operators and monitored continuously by the security operations center. The Critical Cyber Assets in the PSP were protected with intrusion detection software, antivirus, and anti-malware. | When the employee was granted physical access | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) removed the physical access of the individual involved; and 2) completed the PRA. | 2011-10-31 | 2012-03-16 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008994 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1 because it had failed to identify three types of devices as access points to its Electronic Security Perimeters (ESPs). The devices WECC_URE2 reported are 8 port servers, 2 communication switches, and 6 internal network switches. These devices have externally connected communication end points terminating at devices within the ESP and, as required by CIP-005 R1.1, need to be classified as access points. The port servers and communication switches are located at the perimeter of the defined ESP with one IP routable interface connected inside the ESP and one serially connected interface connected outside of the ESP. The internal switches are located inside the ESP and have IP management interfaces that reside outside of the identified ESP. This connectivity allows devices located outside the ESP to communicate with devices inside the ESP without traversing an identified access point protected as per CIP-005. Additionally, WECC_URE2 reported devices that were not afforded the protections of CIP-005-1 R1.5. Specifically, active directory servers, active control server, intrusion detection system, and security information and event management devices were not afforded the protections of CIP-005-1 R1.5. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failing to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded protection measures puts such assets at risk to be manipulated. For instance, if the ports and services required for normal operation of these access control and monitoring assets are not enabled, such ports and services could be utilized to gain unauthorized access to the ESP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets contained in the ESP. Such access may then be used to cause harm to Critical Cyber Assets (CCAs) essential to the operation of the BPS, thereby potentially negatively impacting the BPS. The risk was mitigated because all CCAs are located inside an ESP and Physical Security Perimeter and afforded the protections of CIP-005 and CIP-006. The switches in scope are identified and protected as CCAs, and WECC_URE2 only failed to document the switches as access points. Lastly, the active directory servers and active control servers were located in physically secure areas and located in its corporate network which was protected by restrictive firewalls. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 updated its diagrams and inventory lists designating access points to the ESPs. | 2012-07-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010446 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2. WECC conducted a Compliance Audit of WECC_URE2 and reviewed WECC_URE2's Self-Report and determined WECC_URE2 was in violation of the Standard because it failed to ensure that only ports and services required for normal operations were enabled for all Electronic Security Perimeter (ESP) access points. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 did have a draft list of required ports and services for all 10 logical (13 physical) access points that was approved by subject matter experts, but not the required director of technology services. All CCAs are protected by an intrusion detection system which will alert on abnormal traffic. All CCAs are within a designated Physical Security Perimeter with restrictive access points which only allows physical access to approved, vetted, and trained individuals. All CCAs had antivirus/malware prevention tools, and have unique accounts with strong passwords. Finally, although WECC_URE2 was allowing its network to host traffic, it was only allowing traffic from approved, trusted networks. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) implemented firewall rules; 2) reviewed the rules during the annual Cyber Vulnerability Assessment; 3) required an expiration time for temporary rules; 4) reviewed ports and services; and 5) documented ports and services justification and authentication methods. | 2012-11-08 | 2012-12-21 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC did not apply mitigating credit for the Self-Report because WECC_URE2 submitted the Self-Report following the "Notice of Compliance Audit," issued by WECC.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010448 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R4. WECC conducted a Compliance Audit of WECC_URE2 and reviewed WECC_URE2's Self-Report and determined WECC_URE2 was in violation of the Standard because WECC_URE2 failed to perform a complete Cyber Vulnerability Assessment (CVA) of the electronic access points on its Electronic Security Perimeters (ESPs) at certain locations. Specifically, WECC_URE2 failed to fully complete a ports and services review of the following ESPs. In addition, WECC_URE2 failed to discover the access points on the ESPs listed above. Finally, WECC_URE2 did not perform a review of all default accounts, passwords, and network management community strings. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because failing to perform an annual CVA can result in an entity being unaware of the vulnerabilities on its ESPs or risk the possibility of unidentified vulnerabilities being introduced or exploited. WECC_URE2 did have compensating measures in place. WECC_URE2 had restrictive firewalls, centralized network monitoring, intrusion detection systems, applicable system anti-virus protection, network segmentation, and a monitored physical security infrastructure. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) conducted a CVA; 2) reviewed the ESPs; and 3) documented the results, including the process used, the results, and mitigation steps and resolutions identified in the CVA. | 2012-06-29 | 2012-12-21 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103037 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because it had failed to afford certain protections listed in CIP-006-1 R1 to two of its Cyber Assets used in the access control and monitoring of all 13 of its Physical Security Perimeters (PSPs). The two devices are WECC_URE2's application server and database server. Specifically, the CIP-006-1 R1 protections WECC_URE2 failed to afford the devices were: CIP-003-1 R5.2, CIP-004-1 R3, CIP-005-1 R2, CIP-007-1 R2, CIP-007-1 R5, CIP-007-1 R8, CIP-009-1 R1, and CIP-009-1 R4. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because the failure to afford the protections in CIP-006-1 R1 to Cyber Assets used in the access control and monitoring of a PSP can hinder an entity's ability to monitor and control access to its PSP, potentially allowing unauthorized individuals access to the PSP. That access can then be used to conduct malicious activities. As compensating measures, WECC_URE2 stated the devices were in a physically secure facility, which is manned and monitored at all times. WECC_URE2 also stated all electronic access to the devices required multi-factor authentication. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) reviewed access privileges for its physical access control system; 2) secured computer racks; 3) reviewed WECC_URE2's ports and services; 4) performed a CIP-004 R4 quarterly audit; and 5) performed a physical access control Cyber Vulnerability Assessment. | 2012-08-10 | 2012-12-05 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008991 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-006-2 R3 because it failed to ensure that certain devices used in the access control and monitoring of its Electronic Security Perimeter (ESP) were located inside a Physical Security Perimeter (PSP). The devices involved in the violation were active directory servers, access control servers (ACS), intrusion detection system (IDS), and security information and event management devices. These devices are used to monitor users with access to WECC_URE2's ESPs, as well as to grant and verify authentication and authorization of users with access to WECC_URE2's ESPs. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the devices were not in a designated PSP, they were provided the protections of CIP 006-2 R4 and R5. All locations were restricted to authorized access by use of card key, and monitored to detect unauthorized access attempts by use of alarm systems and video monitoring. | When WECC_URE2 failed to ensure the Cyber Assets involved were located inside a PSP | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) installed and configured card readers on its computer racks; 2) established a new management perimeter network environment; and 3) created a PSP for additional devices. | 2012-06-27 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103038 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2 because it had failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. WECC_URE2 did use a network mapping scan to view that ports and services were running on all the Cyber Assets within Electronic Security Perimeters (ESPs), but did not document the results of the scan. Additionally, WECC_URE2 did not provide any other evidence that it established and documented a process to ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to ensure that only those ports and services required for normal and emergency operations are enabled may allow for unauthorized internal and/or external access, which could allow for successful cyber attacks against Critical Cyber Assets essential to operation of the BPS. As a compensating measure, WECC_URE2 uses an intrusion detection system, with automated alerting, and manual reviews daily during the work-week, to monitor ports and internal traffic. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 created ports and services processes and documentation. | 2012-05-31 | 2012-07-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009030 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because it failed to implement its security patch management program on all 75 of its devices located inside its five Electronic Security Perimeters (ESPs). WECC_URE2 was implementing some security patches on 55% of the devices involved, but was not following its documented security patch management program. The devices in scope are inter-control center communications protocol servers, energy management system devices, and networking equipment. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against Critical Cyber Assets essential to the operation of the BPS. As compensating measures, all devices are located inside ESPs and Physical Security Perimeters, afforded the protections of CIP-005 and CIP-006, and are monitored by a security information and event management protection program. The program logs are reviewed regularly during normal business hours and are configured for automatic alerting upon detecting cybersecurity events. Vulnerability scans are performed regularly on the entity's test system, and all individuals with access to devices located inside ESPs and PSPs have current personnel risk assessments and cybersecurity training. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) enhanced its security patch management procedure to include tracking, gathering, and evaluating patches; 2) expanded the scope of security vulnerability threat meetings; and 3) implemented security patches. | 2012-06-21 | 2012-06-28 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008639 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it had failed to establish, implement, and document technical and procedural controls to ensure passwords consist of a combination of alpha, numeric, and "special" characters. The technical and procedural controls in place required only two of the three criteria specified in the Standard: alpha and numeric characters or alpha and "special" characters. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's password complexity controls require user passwords to be a minimum of eight characters and reset every 60 days. In addition, all remote access requires two-factor authentication and is configured to lockout the user after five failed login attempts. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) updated its policies and procedures to include annual audit trails; 2) created a logging process; 3) implemented a process to manually log the use of shared accounts; and 4) conducted awareness training for its employees. | 2012-05-30 | 2012-06-28 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008642 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R8 because WECC_URE2 failed to perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets located at its Electronic Security Perimeters (ESPs). The Cyber Assets within the ESPs include workstations, servers, and networking equipment related to the entity's supervisory control and data acquisition (SCADA) system. Specifically, WECC_URE2 identified three failures with respect to its CVA process. First, WECC_URE2 stated that it failed to perform a CVA on its ESPs when the Standard became mandatory and enforceable. Second, WECC_URE2 did not perform a CVA on the Cyber Assets in the ESPs, and instead performed a CVA on the Cyber Assets in its test environment for the ESPs. WECC_URE2's understanding was that, if a testing environment mirrored the production ESP, it could run a CVA on only the Cyber Assets in the test system and, for this reason, WECC_URE2 believed it was not required to conduct a CVA on the Cyber Assets ESPs. Finally, one CVA performed did not include a review to verify that only ports and services required for operation of the Cyber Asset within the ESPs are enabled. | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within the ESPs are monitored with an intrusion detection system that is configured for automated alerting. All devices have antivirus/malware prevention tools software installed, and send logs to a centralized log correlation server. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 performed its CVA in accordance with its procedures and documented the results. | 2012-05-31 | 2012-07-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103025 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-008-1 R1 because WECC_URE2's incident reporting and response plan (Plan) did not address CIP-008-1 R1.4, R1.5, and R1.6. Specifically, the Plan stipulated that the Plan needed to be updated annually instead of within 90 days as required by R1.4. The Plan also did not include a process for annual review as required by R1.5. Finally, the Plan did not contain a process for testing the Plan as required by R1.6. | CIP-008-1 | R1; R1.4, R1.5; R1.6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's Plan was tested annually and WECC_URE2 has a small working group responsible for the Plan. Although the processes in scope were not formally documented, the individuals in the working group were familiar with the processes. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 updated its Security Handling Incident procedure to review it annually and audit changes every 30 days. | 2011-10-31 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009100 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because there was no process or procedure to implement security patches on some of its network devices. WECC_URE3 failed to document the assessment and implementation of security patches for Cyber Assets within its Electronic Security Perimeters (ESPs). Although WECC_URE3 failed to document the assessment and the implementation of these security patches, WECC_URE3 did assess all security patches. As a result, patches were implemented, but WECC_URE3 failed to document this action. Therefore, WECC determined that WECC_URE3 failed to document the assessment of security patches and security upgrades for applicability within 30 days of availability, as required by CIP-007-1 R3.1. In addition, WECC_URE3 failed to document the implementation of security patches, as required by R3.2. | CIP-007-1 | R3 | Lower | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because a failure to document the assessment of security patches could result in vulnerabilities remaining unaddressed for extended periods of time. The risk was mitigated because the Cyber Assets at issue were located within an ESP and had technical and procedural mechanisms for control of electronic access at all access points. These mechanisms included the enabling of only those ports and services necessary at the access points and on the Cyber Assets. In addition, WECC_URE3 required usernames and passwords on all Cyber Assets and used a continuous monitoring system to monitor changes on the Cyber Assets. In addition, while WECC_URE3 failed to document the assessment and the implementation of these security patches, WECC_URE3 did assess all security patches. As a result, patches were implemented. | When the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) developed a process flow chart that defines the end-to-end process which describes the steps required to ensure full compliance with the requirements under CIP-007 R3; 2) performed a full review of noncompliance to confirm the scope of the violation; 3) performed a comprehensive review of its existing procedures related to CIP-007 R3 in order to identify any gaps in its existing process; 4) developed and implemented a procedure including controls to monitor compliance and ensure effective escalation of identified issues or concerns for appropriate action; and 5) trained the appropriate personnel on the new CIP-007-1 R3 policies and procedures. | 2012-10-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009099 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it failed to provide account management protections to all Cyber Assets within its Electronic Security Perimeters (ESPs). WECC_URE3 lacked the required account management procedural controls on several workstations, servers, and network devices located within its 50 ESPs. WECC_URE3 did not ensure that a third of its devices' shared accounts had the protections required by CIP-007 R5.1.3, R5.2.1, R5.2.3, and R5.3.3. Specifically, WECC_URE3 failed to: 1) review annually shared accounts to verify access privileges, as required by R5.1.3; 2) remove, disable, or rename accounts where possible, as required by R5.2.1; 3) remove or change the account in the event of personnel changes, as required by R5.2.3; and 4) change passwords at least annually, as required by R5.3.3. | CIP-007-1 | R5; R5.1.3; R5.2.1; R5.2.3; R5.3.3 | Medium | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE3's failure to establish technical and procedural controls to identify and manage shared accounts could have allowed unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access could then have been used to cause harm to Critical Cyber Assets essential to the operation of the BPS. The shared accounts include administrator, user, and read-only accounts. The administrator accounts provide full system access which allows configuration changes, addition and removal of user accounts, application control, and the starting and stopping of services that are used for the system applications to run properly. A smaller number of the shared accounts provide read-only access which provides limited access to the device and applications. Given the failures described herein, the shared accounts with administrator privileges could have been used by unauthorized personnel to make configuration changes, add unauthorized users to the Cyber Assets within the ESP, and start and stop critical services and applications and potentially misuse the Cyber Assets. Once an unauthorized person has administrator access to a Cyber Asset within the ESP, this person can potentially make changes to the devices and/or applications running, which in turn could impact the reliable operation of those assets which support WECC_URE3's BPS functions. The risk was mitigated because all Cyber Assets were located within an ESP. Additionally, the devices had technical and procedural mechanisms for control of electronic access at all access points, such as enabling only those ports and services necessary at the access points. All of the devices were also located within a Physical Security Perimeter (PSP) and therefore had technical and procedural controls to manage physical access to the PSPs including logging and monitoring of physical access 24 hours a day, seven days a week. Furthermore, WECC_URE3 requires username and passwords on all Cyber Assets and uses a continuous monitoring system to monitor any changes made on the Cyber Assets within the ESPs. | When the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) performed an assessment to identify an effective strategy to manage passwords not addressed in current standards and processes; 2) performed a detailed review of all accounts within the operational data network (ODN) active directory to identify all accounts that are not related to an individual user; 3) developed and implemented a consolidated process for account access reviews and management of ODN accounts which addresses both user and service shared accounts; 4) produced a detailed list of service or shared accounts which includes who has access to those accounts and what the accounts are used for; 5) modified and/or eliminated accounts or account access as appropriate; 6) performed a review of all users who have any logical access to the ODN by asset area; 7) created a detailed document that establishes the methods, processes and procedures to generate logs of sufficient detail to create historical audit trails of individual user account access activity to all accounts and specific retention requirements; and 8) submitted Technical Feasibility Exceptions as appropriate for passwords that cannot be changed. | 2012-08-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010375 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R7. WECC_URE3 did have a process for disposal or redeployment of Cyber Assets within its Electronic Security Perimeters (ESPs); however, this process only tracked assets to destruction. Once storage media was removed from an asset and destroyed, WECC_URE3 did not correlate the destroyed storage media back to the asset it was removed from. Furthermore, WECC_URE3 does not redeploy assets, and as a result, WECC_URE3 was unable to provide evidence of the assets that had been retired. The devices at issue are used to support the supervisory control and data acquisition systems, energy management system, remedial action scheme (RAS), and network and communication equipment. WECC determined that WECC_URE3 failed to have a sufficient security patch management program that documents that it destroyed or erased the data storage media prior to the disposal of a Cyber Asset, as required by CIP-007-1 R7.1, and that documents it erased the data storage media prior to redeployment of a Cyber Asset, as required by R7.2. WECC_URE3 also failed to document that such assets were disposed of or redeployed in accordance with documented procedures, as required by R7.3. | CIP-007-1 | R7 | Lower | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE3's failure to establish controls to dispose of Cyber Assets could allow malicious access to sensitive information related to cybersecurity. Such information could then be used to gain access to Critical Cyber Assets essential to the operation of the BPS. However, the risk was mitigated because the devices at issue were protected through restrictive boundary devices that log and monitor all traffic traveling the ESP. Additionally, WECC_URE3 uses a continuous monitoring system to monitor any changes or configurations that are made to Cyber Assets within the ESPs. | When the Standard became mandatory and enforceable on WECC_URE3 | Present | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) performed an extent of condition evaluation to validate the scope of noncompliance and ensure that non-IT assets (remote terminal units, relays, controllers) are in compliance; 2) completed an assessment and analysis of the existing disposal process; 3) completed and implemented a revised disposal process that includes effective ongoing performance monitoring; and 4) revised its disposal procedure and completed internal reviews of the final processes and procedures prior to the sign-off and submission of the completed Mitigation Plan. | 6/14/2013 (approved completion date) | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-33-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2011008637 | Settlement Agreement | WECC_URE4 self-reported a violation of CIP-002-1 R3. A few fiber switching devices used to support a fiber channel connection to a storage area network solution (SANS) were found also to be using routable connections within WECC_URE4's control center, which is a Critical Asset. In addition, one modem-connected service processor used in the support and operation of the SANS was found to be dial-up accessible when called from an internal corporate phone extension, and was located within the control center, which is also a Critical Asset. The violation was a result of operational personnel failing, in the process of installing a new SANS in one of WECC_URE4's datacenters, to document the Ethernet connections on the switches, as well as WECC_URE4's SANS documentation not adequately identifying the configuration of WECC_URE4's telephony system. WECC determined that WECC_URE4 was in violation of CIP-002-1 R3.2 (the switches) and R3.3 (the modem-connected service processor) for failing to identify or document appropriately components of SANS as Critical Cyber Assets (CCAs). | CIP-002-1 | R3; R3.2; R3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE4 did not identify these assets as CCAs, WECC_URE4 did have the following compensating measures in place: 1) the fiber switches required terminal access controller access-control system authentication; 2) the fiber switches were located within a Physical Security Perimeter (PSP); 3) those with access to the switches required current personnel risk assessments and CIP cybersecurity training; 4) the modem-connected processor was only accessible from the internal phone system; 5) the modem-connected processor could not be dialed from the outside; 6) the modem-connected processor was located within a PSP; 7) the phone switch that the modem was connected to was configured to dial outbound only; and 8) the modem-connected service processor was configured to dial out only to the SANS vendor. | When the Standard became mandatory and enforceable | Mitigation Plan completion | 4250 | Self-Report | To mitigate this violation, WECC_URE4: 1) updated the change control procedure governing NERC-related CIP Cyber Assets to incorporate new corporate controls to help mitigate the risk of noncompliant changes to NERC environments. These changes included establishing that a member of an IT group will now be included in a corporate advisory board (CAB), which reviews and approves all IT changes at WECC_URE4. The IT security and risk group oversees appropriate IT implementation of compliance associated change controls. The change controls will be routed through the CAB and will not be allowed to be implemented until a sufficient review has been approved by the CAB; 2) documented the SANS completely including all NERC-related and security controls to mitigate the risk that further changes to the solution overlook or omit compliance or security controls; 3) audited for CAB change control samples to validate that item 1 above is mitigating the identified issues as expected; 4) removed CCAs from WECC_URE4’s NERC-related CIP SANS and validated that remaining computer systems are not essential to the operation of WECC_URE4 Critical Assets; 5) disabled the routable connection on the fiber switches and the dial-up inbound connection on the modem; 6) disconnected the SANS from any CCAs and validated that remaining computer systems are not essential to the operation of WECC_URE4 Critical Assets, removing any routable or dial-up path from outside or within the Electronic Security Perimeter and removed essentiality components of the SANS device such that the SANS is not a CCA; and 7) trained all IT personnel on change and incident management. | 2012-07-03 | 2013-03-01 | Agrees/ Stipulates | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-04-30 | FERC | NP13-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007853 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-002-1 R3 because it failed, on two separate occasions, to identify Cyber Assets that were essential to the reliable operation of Critical Assets and were dial-up accessible as Critical Cyber Assets (CCAs) and to include them on the list of CCAs, resulting in a violation of CIP-002 R3.3. The first occasion occurred when FRCC_URE1 found that there was a multiplexer, with a dial-up connection, located at a transmission substation that still had the phone line connected. This device should have been identified when the substation was identified as a Critical Asset. The substation multiplexer was disconnected. The multiplexer was located in the low voltage control room which is typically not included in the verification of connection and disconnection of devices at identified sites and therefore had been previously missed. The second occasion occurred when FRCC_URE1 performed Critical Asset site walk-downs to ensure transmission substations were disconnected for continued compliance. During a review of the list of Critical Asset sites to walk-down, FRCC_URE1 personnel discovered that the list provided at for the walk-down did not match the official Critical Asset list. As a result, transmission substation identified as a Critical Asset on the official Critical Asset list had dial-up connectivity for one and half years. On the same day the violation was discovered, all dial-up accessibility was removed and the violation was corrected. | CIP-002-1 | R3; R3.3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to identify CCAs could result in leaving the CCAs unprotected and vulnerable to a cyber threat and therefore, may pose a moderate risk to the operation of the BPS. In this case the entity failed to identify and document one CCA that was dial-up accessible at each of the substations. The affected two CCAs made up .012% percent of total CCAs protected by FRCC_URE1. The risk to the BPS was mitigated by the fact that the dial-up provisions limited security risk. Regarding the first incident, the dial-up device at the substation was accessible only by using a proprietary client and was password protected for authorized access only. For the second incident, the device at the substation was remotely accessible without a password but required proprietary installed client (software) and was not openly available. In addition, only authorized persons were aware of its existence and no unauthorized access was identified after review of all remote activity. Furthermore, for both incidents, the dial-up accessible devices, while connected, were used to collect data that was not real-time data and was not essential or critical to the operation of the Critical Assets or BPS reliability. The function of the devices was to collect data for a historical long-term database supporting off-site storage and/or for collecting fault recorder information. | when FRCC_URE1 failed to include the Cyber Assets on the list of Critical Assets | when dial-up access was removed | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) disconnected the substation multiplexer and labeled phone line cable; 2) disconnected transmission substation multiplexer and labeled phone line cable; and 3) performed a walk-down at all Critical Asset substations. | 2011-07-07 | 2013-03-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
2013-04-30 | FERC | NP13-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008470 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R1 because in multiple instances Cyber Assets used in the access control and monitoring of Electronic Security Perimeters (ESPs) were not afforded the specific protection measures required by CIP-005-1 R1.5 as described below: 1) CIP-003 R5: A group of information repositories did not have the correct individual identified as the designated personnel responsible for authorizing logical access to the protected information as required by CIP-003 R5; 2) CIP-003 R6: A hard drive of an electronic access control and monitoring (EACM) server was replaced without proper documentation in the ticketing system as required by CIP-003 R6; 3) CIP-005 R1.5: None of the CIP-005 R1.5 requirements were met for certain EACM devices; 4) CIP-007 R1: The testing procedure in place as required by CIP-007 R1 was lacking specific details on how not to adversely affect existing cybersecurity controls, resulting in incomplete test results for EACM assets; 5) CIP-007 R3: A group of patches as required by CIP-007 R3, were not assessed on a group of EACM assets for a year and a half; 6) CIP-007 R5.1.3: A group of user accounts for a group of EACMs were not reviewed annually for one year, as required by CIP-007 R5.1.3 to verify access privileges were in accordance with CIP-003 R5 and CIP-004 R4; 7) CIP-007 R5.3.3: A group of passwords for accounts on EACM assets had not been reset in over a year, as required by CIP-007 R5.3.3; 8) CIP-007 R8: The execution status for the action plans for EACMs for one year's vulnerability security assessments were not consistently documented, as required by CIP-007 R8, and in some cases were not available; and 9) CIP-009 R2: There were violations related to disaster recovery plans for two different EACMs. One disaster recovery plan was not reviewed annually for one year for an EACM asset. The other disaster recovery plan was not created for an EACM asset for one year and eight months. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failing to ensure that Cyber Assets used in the electronic access control and monitoring of the ESP are afforded protective measures puts such assets at risk to be manipulated. If successfully manipulated, unauthorized access to the ESP compromises the security of Critical Cyber Assets (CCAs) within the ESP. In this case, FRCC_URE1 failed to provide protections such as change control and testing, account control and password protection, cyber vulnerability assessment, and implementation of recovery plan. However, the risk to the reliability of the BPS was mitigated as all the devices were secured behind a protected electronic access point and FRCC_URE1 maintained the defense-in-depth protection by utilizing both physical (physical security perimeters) and logical controls (ESPs) thereby limiting any potential serious impact on any EACM reported under this violation. In addition, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the first instance of the violation occurred | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) completed a review of authentication and authorization directory service owners of all information repositories where applicable; 2) changed authentication and authorization directory service ownership to designated information repository owners and added comments to appropriate authentication and authorization directory service field denoting a change in approver also requires change within the NERC-CIP repository list and to contact the information security group for assistance; 3) created procedures to note that repository list and authentication and authorization directory service approvers will be updated by the analyst performing the change in repository owner where authentication and authorization directory service group permissions are leveraged; 4) added comments to the protected CCA information repository list description to ensure any changes to the list are also reflected in procedures & documentation; 5) reviewed NERC-CIP asset disposal & redeployment process with team responsible for completing disposals & redeployments and documented future disposal/redeployment in ticketing system; 6) initiated demilitarized zone isolation project to properly secure EACM devices and apply required controls; 7) updated testing procedure to include specific details requiring the use of this procedure change control, configuration management and cybersecurity testing; 8) assessed and applied current patches to mitigate current and previous vulnerabilities and removed unnecessary software from servers where applicable; 9) added identified user accounts to the master account list and conducted annual review of access privileges for identified user accounts; 10) changed group policy for devices integrated with authentication and authorization directory service to require password change frequency in compliance with the standard and changed passwords as required for the identified accounts; 11) implemented use of change tickets to document execution status in the Mitigation Plans for vulnerability assessments and updated procedure with instructions on how to completed; 12) completed annual review of the affected EACM device; 13) developed disaster recovery procedure for the affected EACM device; and 14) revamped disaster recovery drills to require annual reviews in advance of drill. To mitigate this violation, FRCC_URE1 will submit technically feasibility exceptions, where applicable. | 3/31/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
2013-04-30 | FERC | NP13-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008521 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation CIP-005-1 R2.2 because it failed to implement appropriate access rules at its electronic access points (EAPs) that restricted traffic to only the ports and services that were required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP). The access rules, that restrict traffic to only those ports and services that are required for operations and monitoring of Cyber Assets within two control centers' ESPs and to and from appropriate demilitarized zones (DMZ), had not been fully implemented and were not documented individually or by specified grouping. FRCC_URE1 depended on the secure Internet Protocol Security (IPSec) tunnel to limit communication between the connected ESP. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1 reduced the risk by documenting what ports and services were restricted in the implementation and did review as required. FRCC_URE1 was aware of all ports and services enabled on its access points. The documentation and restrictions; however, were not documented individually or by specified grouping of the configuration of ports and services, and the granularity of the access rules in place did not ensure that only those required ports and services were enabled. In addition, all CCAs were within ESPs and protected by restrictive firewalls with limited connectivity to outside networks. Furthermore, all logical traffic is actively monitored through the use of a Security Event and Incident Monitoring (SEIM) system, EMS/supervisory control and data acquisition logs, and an Intrusion Detection System. Thus, FRCC_URE1 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. Lastly, these access points were connected to other access points using an IPSec tunnel limiting any opportunity of external exploitations. | when the Standard became mandatory and enforceable on PEF as a "Table 1" entity | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) developed initial network architecture diagram to meet CIP compliance; 2) developed initial action plan for new network device installation; 3) provided updated action plan for new network device installation; 4) developed project plan for implementation; 5) completed implementation for a generation site; 6) completed implementation for another generation site; 7) provided update on firewall policy changes; 8) installed application clients as needed on EACM devices to minimize the amount of devices which access the ESP; 9) established new group naming standards and first update of firewall rules; 10) incorporated initial findings into new trust rule and update firewall rules; and 11) updated its firewall policy per CIP-005 R2.2; and To mitigate this violation, FRCC_URE1 will: 1) monitor then incorporate any new findings in new trust rule; 2) establish new group naming standards and updated of firewall rules; 3) incorporate initial findings into new trust rule; 4) monitor then incorporated any new findings in new trust rule; and 5) remove finally original trust rule. | 12/29/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
2013-04-30 | FERC | NP13-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008523 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R4.2 because it failed to document the review to verify that only ports and services required for operations at all access points were enabled as part of the cyber vulnerability assessment (CVA). While FRCC_URE1 did perform verification of all other requirements of CIP-005-1 R4, it did not include the verification that all open ports and services are required for operation and monitoring of the Cyber Assets within the Electronic Security Perimeters (ESPs) at the access points. | CIP-005-1 | R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to conduct a complete CVA of all Cyber Assets could allow any cyber vulnerabilities in such assets to go unchecked and undetected. Subsequently, if any such vulnerabilities are not corrected, they could be exploited by malicious access, thereby providing an attack vector for launching cyber attacks against Critical Cyber Assets essential to the operation of BPS. In addition, lack of discovery of unwanted ports at the access point could allow unauthorized persons to compromise access point security and limit effective monitoring of the access points for security compromises. As compensating measures, FRCC_URE1 performed an initial evaluation to determine a baseline for all the access points and reviewed ports required for normal operation. In addition, FRCC_URE1 implemented defense-in-depth utilizing both physical (physical security perimeters) and logical controls (ESPs), including performing a review for enabling only ports required for operation on all the Cyber Assets within the ESP. Furthermore, all the external ESP communications are limited to other trusted sources or trusted ESPs which are connected using Internet Protocol Security tunnels. Lastly, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the non-compliant CVA was conducted | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) updated its procedure document to require a review of the firewall policy as part of the annual CVA; 2) developed initial network architecture diagram to meet CIP compliance; 3) developed initial action plan for new network device installation; 4) provided updated action plan for new network device installation; 5) developed project plan for implementation; 6) completed installation of new device as required at generation sites; and 7) created data flow diagram to demonstrate the required ports & services on specific nodes. | 2012-08-07 | 2013-03-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
2013-04-30 | FERC | NP13-29-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008524 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-007-1 R8.2 because, while FRCC_URE1 did conduct an annual cyber vulnerability assessment (CVA), it failed to maintain sufficient evidence to demonstrate that the annual CVA included a review of all ports and services required for normal and emergency operations. For non-appliance based Cyber Assets, FRCC_URE1 conducted a review based on an in-house developed tool that compares base-line configuration to verify that only ports required for normal and emergency operation were open. For appliance-based Cyber Assets, FRCC_URE1 conducted review of configurations to determine if the ports and services were required for normal and emergency operations. Manual reviews often depend on individual knowledge and in this case lacked comprehensiveness, and FRCC_URE1 failed to document all open ports and in some cases of appliance-based devices the verification of open ports and services did not include verification of many ports and services that are enabled by default and were not required by FRCC_URE1. | CIP-007-1 | R8; R8.2; R8.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Risk to these affected devices was limited as these services were not accessible remotely and FRCC_URE1 implemented defense-in-depth utilizing both physical (physical security perimeters) and logical controls (Electronic Security Perimeters (ESPs)). Furthermore, most of the external communication is limited to other trusted sources or trusted ESPs which are connected using Internet Protocol Security tunnels. In addition, all personnel with logical and physical access had proper personnel risk assessments and cyber training. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | $32,000 (for FRCC2011007853, FRCC2011008470, FRCC2011008521, FRCC2011008523, and FRCC2011008524) | Self-Report | To mitigate this violation, FRCC_URE1: 1) submitted surveys to peer utilities on solutions for performing more comprehensive scans of devices within the ESP; 2) reviewed solutions for performing more comprehensive scans of devices within the ESP; and 3) assessed production feasibility. To mitigate this violation, FRCC_URE1 will: 1) test solution(s)/tool(s); 2) configure and implement a solution identified in item 2 to meet CIP-007 R8.2; 3) document results of test scans and submit and update appropriate Technical Feasibility Exceptions for CIP-007 R2; and 4) perform CVA review for compliance with CIP-007 R8. | 11/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. FRCC found FRCC_URE1's ICP documentation to be insufficient. FRCC applied mitigating credit to FRCC_URE1 for its self-assessment program.
2013-03-27 | FERC | NP13-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010779 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a violation of CIP-002-3 R3. RFC_URE1 installed an upgraded remote terminal unit (RTU) at a substation, a Critical Asset. The individuals upgrading the RTU did not identify the substation as a Critical Asset in its database, and as a result, RFC_URE1 failed to identify the Critical Cyber Assets (CCAs) associated with the substation on its list of CCAs. | CIP-002-3 | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation posed a moderate risk because unidentified CCAs increase the likelihood that a Responsible Entity will fail to afford Cyber Assets which are essential to the operation of the Critical Asset the security protections of CIP-003 through CIP-009. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE1 discovered this violation due to its internal controls when its transmission protection and controls department identified that there was a critical station connected to the network without proper protection. Within one day of discovery, RFC_URE1 disconnected the network until it could apply the proper controls, locked the interior deadbolts on all doors except for one that was padlocked from the outside, and had alerting and manual logging enabled. In addition, the substation is completely fenced with a locked gate, and the doors to the control house were locked. The network and the CCA at issue both require username and password authentication. | RFC_URE1 installed the RTU | When RFC_URE1 disconnected the RTU from the network until it enabled the proper controls | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) immediately disconnected the network until it applied the proper controls and protected all doors to the substation; 2) implemented formal Physical Security Perimeter controls at the substation; 3) reviewed internal processes and procedural controls to propose improvement; and 4) implemented the improvements as agreed upon by the business units involved. | 2013-02-28 | TBD | Agrees/Stipulates | RF reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with RF during the Compliance Audit and in connection with the violations. RF also considered that it discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. RF considered that it discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, RF seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
2013-03-27 | FERC | NP13-29-000 | ReliabilityFirst Corporation (ReliabilityFirst), Southwest Power Pool Regional Entity (SPP RE), and Texas Reliability Entity (Texas RE) (collectively, the Regional Entities) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX NCRXXXXX NCRXXXXX | RFC201100932 SPP201100587 TRE201100370 | Settlement Agreement | RFC_URE1 submitted a Self-Report to the Regional Entities identifying a violation of CIP-007 R1. This violation affected Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP), which involves CIP-005-3a R1.5. RFC_URE1 submitted Self-Reports to the Regional Entities identifying a violation of CIP-005-1 R1. During a periodic review of assets within the ESP and Physical Security Perimeters, RFC_URE1 discovered devices connected to console routers that were not located within an ESP. These devices were Critical Cyber Asset (CCA) firewalls and Cyber Assets used in the access control and monitoring of ESPs. The console routers constituted access points to the ESP, but RFC_URE1 failed to identify and document these access points to the ESP. RFC_URE1 disconnected the console router connections two days after discovering the omission. RFC_URE1 discovered that it had installed Cyber Assets within an ESP without identifying them as CCAs or non-critical Cyber Assets within the ESP. RFC_URE1 had incorrectly configured the gateway router settings. The IP configurations were correct as the devices were located within the ESP, but without the correct gateway router settings, the devices could not communicate outside the ESP. The remainder of these assets were identified CCAs located within the ESP but had multiple IP addresses, only one of which was identified. RFC_URE1 identified these CCAs by performing device scans from within the ESP locally or by reviewing address tables. RFC_URE1 remediated these configurations. The Regional Entities conducted a Compliance Audit during which the Regional Entities discovered violations of CIP-005-1 R1. RFC_URE1 has intrusion detection system (IDS) devices in place, which are located outside the ESP and communicate with the switches that are located within the ESP. RFC_URE1 failed to identify these IDS devices as access points to the ESP. | CIP-005-3a | R1 | Medium | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The console routers were located within a Physical Security Perimeter and similar authentication is required to access the devices. The connection was a nonroutable asynchronous connection, decreasing the likelihood of unauthorized access. Regarding the incorrect configuration of certain CCAs, each device was located within the ESP, and certain of the devices were identified and protected as CCAs. The incorrect configuration of the gateway routers and IP addresses prevented the ability to access the devices remotely. In addition, if someone had physical access to the CCAs, a username and password to authenticate was required for logical access. These devices connected to the substation network which is protected by a firewall, access control list, and IDS. Regarding the IDS devices, the IDS passively monitors networks at RFC_URE1 for malicious activities. The IDS devices consist of a management port to manage the devices remotely and report detected events back to a central monitoring system and monitoring ports to detect malicious activities within a network which are only capable of passively receiving traffic. RFC_URE1 has controls in place to prevent traffic from traversing the IDS to enter the ESP. First, the IDS isolates the management port from the monitoring ports, and the monitoring ports allow inbound traffic only. This configuration decreases the likelihood of malicious traffic using the IDS devices to enter and exit the ESP. Second, these appliances are directly connected to mirrored ports (port mirroring is utilized to monitor network traffic by sending a copy of network packets or data traffic to a network monitoring connection on another switch port on routers within the ESP. Moreover, in certain scenarios, RFC_URE1 uses a third protection, an aggregation device to combine data together from multiple switches for analysis by the IDS, which results in fewer access points to the ESP. The input port cannot be used for output on this device, and vice versa. The input port can only receive data, and it can only receive data from specific protocols that it was designed to handle. The output port can only send data outbound, and it can only send data outbound using specific protocols that it was designed to handle. Furthermore, the devices’ protocol is configured to transmit data from inside the ESP to the IDS device outside the ESP only. | When the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) conducted a system-wide scan and assessed the existing similar devices’ configuration; 2) identified and corrected related erroneous configurations; 3) evaluated alternatives to automate the process to detect device misconfigurations; 4) evaluated other available IP configuration scan tools and developed practical improvement options; 5) increased awareness of the issue to personnel involved with configurations; 6) communicated and issued lessons learned to related staff; 7) tested and piloted preferred alternative solutions; and 8) implemented automated solution for IP configuration, scanning, and detection of device misconfiguration. | 2012-02-29 | 2012-06-01 | Agrees/Stipulates | The Regional Entities reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with the Regional Entities during the Compliance Audit and in connection with the violations. The Regional Entities also considered that they discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. The Regional Entities considered that they discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, the Regional Entities seek to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
2013-03-27 | FERC | NP13-29-000 | ReliabilityFirst Corporation (ReliabilityFirst), Southwest Power Pool Regional Entity (SPP RE), and Texas Reliability Entity (Texas RE) (collectively, the Regional Entities) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX NCRXXXXX NCRXXXXX | RFC2011001088 SPP201100669 TRE201100463 | Settlement Agreement | RFC_URE1 submitted Self-Reports to the Regional Entities identifying a violation of CIP-007-3 R1.7. During its cyber vulnerability assessment, RFC_URE1 discovered that it installed new third-party software on Critical Cyber Asset (CCA) workstations. RFC_URE1 performed testing on the software, but not in accordance with its CIP-007 R1 procedures. In addition, RFC_URE1 discovered that it made significant changes to upgrade firmware on storage area network switches and one storage array, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP), and one server, which is a CCA, without following RFC_URE1’s test procedures. Both instances occurred due to lack of awareness of test procedures by RFC_URE1 personnel. | CIP-007-3 | R1.7 | Medium | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Because the Cyber Assets at issue were located in a Physical Security Perimeter and an ESP, RFC_URE1 afforded the Cyber Assets the remainder of the requisite protections, including electronic access controls, cyber vulnerability assessments, protection through a physical security plan, protection of physical and electronic access control systems, and controlling, monitoring, and logging physical access. | When RFC_URE1 made the first change without testing in accordance with the Standard and Requirement | Mitigation Plan completion | $0 (for RFC201100932, RFC2011001088, RFC2012010779, SPP201100587, SPP201100669, TRE201100370, and TRE201100463) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented controls to review changes to Cyber Assets prior to implementation; 2) revised and published the data service process documentation governing test procedures; 3) revised and published the change management process document to include content governing NERC changes; 4) revised and published the IT process documentation governing test procedures; and 5) provided awareness training to personnel responsible for maintaining the infrastructure. | 2011-11-15 | 2012-01-25 | Agrees/Stipulates | The Regional Entities reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE1 was cooperative throughout its interaction with the Regional Entities during the Compliance Audit and in connection with the violations. The Regional Entities also considered that they discovered all of the violations included in this Settlement Agreement, except one, through Self-Reports and applied mitigating credit for those violations. The Regional Entities considered that they discovered one of the violations during the Compliance Audit and did not apply mitigating credit for that violation. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE1 promptly identified and reported most of these violations due to the effective execution of its ICP and the installation of internal controls that yielded identification of the violations. As a result, the Regional Entities seek to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these violations.
2013-03-27 | FERC | NP13-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009916 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R6. On September 30, 2011, RFC_URE2 discovered that its workstations, which are Cyber Assets within the Electronic Security Perimeter (ESP), can provide access to its physical access control system (PACS) without requiring a separate login to the application. Due to RFC_URE2’s lack of awareness of this access point to the PACS, it failed to implement the requirements of CIP-007-3 R6 for these workstations. Specifically, these Cyber Assets did not implement automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3 R6.1. In addition, there were no automated or manual alerts for detected cyber security incidents on these Cyber Assets, as required by CIP-007-3 R6.2. RFC_URE2 also failed to maintain logs of system events related to cyber security for these Cyber Assets, as required by CIP-007-3 R6.3. These Cyber Assets were not configured to retain logs of system events related to cyber security for 90 calendar days, as required by CIP-007-3 R6.4. As a result, RFC_URE2 failed to review logs of system events related to cyber security for these Cyber Assets, as required by CIP-007-3 R6.5. In addition, RFC_URE2 discovered that the system log file for one Critical Cyber Asset (CCA) in its ESP had stopped sending messages to the security status monitoring application. While this device was in service and operational, it was not creating or maintaining logs of system events related to cyber security, as required by CIP-007-3 R6.3. Furthermore, RFC_URE2 discovered that the security monitoring controls for switches located inside the ESP, which are designated as CCAs, were not issuing automated alerts, as required by CIP-007-3 R6.2. | CIP-007-3 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because the instant violation had the potential to affect the reliable operation of the BPS by providing the opportunity for an undetected compromise of CCAs and other system events that are related to cyber security to occur without RFC_URE2's knowledge. The risk was mitigated because, for the workstations that provide access to the PACS, RFC_URE2 had afforded the PACS all protections as specified by CIP-006-3 R2.2. These systems required authentication. Therefore authorized access would be necessary prior to gaining the ability to access the PACS outside of the PACS software. For the switches that were not generating automated alerts, RFC_URE2 was monitoring the internal switches and it had organizational processes in place to log system events. | when the Standard became mandatory and enforceable on RFC_URE2 | when RFC_URE2 completed its mitigating activities | $0 (for RFC2012009916 and RFC2012009917) | Self-Report | To mitigate the violation, RFC_URE2: 1) rebooted the server, which resulted in the restoration of system status monitoring of the device; 2) configured the switches at issue to alert of security events; 3) increased the size of local security logs on all workstations and servers and increased the size of local logs on all database servers to retain logs for at least 90 days; 4) configured the internal logging and monitoring tool to collect logs and automatically alert on failed logins for the workstations; 5) tested and validated that the workstations are appropriately logging and alerting; 6) performed a manual review data that was available to ensure that there was no unauthorized access; and 7) provided additional information demonstrating that RFC_URE2 is committed to preventing or minimizing the probability of additional occurrences of the violation. RFC_URE2 is conducting a wholesale replacement of the existing technology related to monitoring and alerting that has a more robust, centrally managed solution. | 2012-11-16 | 2013-02-11 | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE2 promptly reported the violation due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues. ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for this violation. RFC_URE2 conducts internal audits of selected Reliability Standards. Furthermore, RFC_URE2 encourages its employees to submit any issues they suspect involve compliance with the Reliability Standards. ReliabilityFirst determined that RFC_URE2's previous violation constituted a prior violation and an aggravating factor in the penalty determination. ReliabilityFirst considered that RFC_URE2 discovered the violations through a Self-Reports and applied mitigating credit. Although ReliabilityFirst considered RFC_URE2’s violation history to constitute an aggravating factor, ReliabilityFirst determined that RFC_URE2’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to RFC_URE2’s compliance history. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-03-27 | FERC | NP13-29-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009917 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-005-3 R3. RFC_URE2 discovered that several of its firewall devices were not configured to alert for all methods of unauthorized administrative access attempts. Instead, they were configured only to alert on a single attack vector (an attack vector is a method or path by which an individual can gain unauthorized access to a system) for unauthorized access, while two such vectors exist. One vector is accessed through the console interactively using the command line, and the other vector is accessed through an internal web server on the firewall. | CIP-005-3 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because the instant violation had the potential to affect the reliable operation of the BPS by providing the opportunity to access RFC_URE2's Electronic Security Perimeter (ESP) while leaving no record of the intrusion. Without having monitoring processes in place at all access points, RFC_URE2 would be unable to detect and alert for unauthorized access to its ESP. Therefore, RFC_URE2 would be unable to prevent or track intrusions that could result in harm to the integrity of Critical Cyber Assets within the ESP. The risk was mitigated because the firewall devices were alerting for unauthorized access attempts. RFC_URE2 installed the monitoring tool on the web service on the firewalls, but it was not configured to alert on authorized access attempts through the other vector. | when the Standard became mandatory and enforceable on RFC_URE2 | when RFC_URE2 enabled the monitoring solution on the firewalls to alert for both types of unauthorized administrative access attempts | $0 (for RFC2012009916 and RFC2012009917) | Self-Report | To mitigate this violation, RFC_URE2: 1) configured the alerting tool to alert upon all possible administrative unauthorized access methods to firewall devices and developed; and 2) performed test cases of firewalls to ensure monitoring and alerting controls were operating as designed. | 2012-11-16 | 2013-01-23 | Admits | ReliabilityFirst reviewed RFC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. RFC_URE2 promptly reported the due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues. ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for this violation. RFC_URE2 conducts internal audits of selected Reliability Standards. Furthermore, RFC_URE2 encourages its employees to submit any issues they suspect involve compliance with the Reliability Standards. ReliabilityFirst determined that RFC_URE2's previous violation constituted a prior violation and an aggravating factor in the penalty determination. ReliabilityFirst considered that RFC_URE2 discovered the violations through a Self-Reports and applied mitigating credit. Although ReliabilityFirst considered RFC_URE2’s violation history to constitute an aggravating factor, ReliabilityFirst determined that RFC_URE2’s violation history does not warrant a monetary penalty when considered together with the mitigating credit ReliabilityFirst assigned for the aforementioned adjustment factors, which wholly offset the potential penalty aggravation attributable to RFC_URE2’s compliance history. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009885 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-002-1 R3, stating that SERC_URE1 failed to identify all associated Critical Cyber Assets (CCAs) essential to the operation of its Critical Assets. During the physical tour of a control center, the SERC audit team observed frequency monitoring devices that were not accounted for on SERC_URE1’s list of CCAs. The SERC audit team considered the frequency monitoring devices, which use a routable protocol to communicate with the control center, to be critical to SERC_URE1's functional operations and thus should be identified as CCAs. The frequency monitoring devices were located inside a Physical Security Perimeter (PSP) but were outside an Electronic Security Perimeter (ESP). The affected frequency monitoring devices feed the energy management system. SERC determined that SERC_URE1 was in violation of CIP-002-1 R3.2 because it failed to add the affected critical frequency monitoring devices to its list of associated CCAs essential to the operation of a Critical Asset. | CIP-002-1 | R3; R3.2 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The violation was limited to 4.8% of SERC_URE1's total. Although the frequency monitoring devices were located inside a declared PSP but were outside a declared ESP, the devices were separated from an ESP behind secure firewalls that were protected pursuant to CIP-005 and CIP-007. In addition, SERC_URE1 had multiple frequency sources which would allow it to switch from one frequency source to another. In an emergency situation, SERC_URE1 could access frequency sources at generating plants and substations. There were no incidents at SERC_URE1 facilities related to these CCAs. Furthermore, although SERC_URE1 failed to include the affected devices on its CCA list, SERC determined that SERC_URE1 had completed an annual review of CCA lists and updated as necessary. Additionally, data sources and network equipment associated with these frequency devices were protected within a PSP and the data sources and network equipment was subjected to performance testing of access control, monitoring, logging controls, and had no identified discrepancies. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) upgraded its control system and moved the frequency monitoring devices inside the defined ESP; 2) added the frequency monitoring devices to the CCA list; 3) updated the network drawing to include the frequency monitoring devices inside the defined ESP; and 4) updated all appropriate procedures as required and requested Technical Feasibility Exceptions for the frequency monitoring devices. Any future frequency monitoring devices added to the SERC_URE1 control system, by default, will be added to the CCA list. | 2012-05-30 | 2013-02-22 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009886 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-003-1 R6, stating that SERC_URE1 failed to document a detailed process on change control and configuration management. SERC_URE1 ’s process for change control was to fill out a change log when SERC_URE1 made any changes to Critical Cyber Assets (CCAs). SERC_URE1 ’s change log contained dates, change details, and the names of individuals who completed actions, but did not show any other evidence of controls such as change approvals, action plans for requested change, or testing of changes prior to implementation. SERC_URE1 provided no other evidence to demonstrate that there were any common program components, such as approvals, back-out procedures, and criteria for what constitutes a significant change, which are critical to proper change control and configuration management. SERC determined that SERC_URE1 was in violation of CIP-003-1 R6 because it failed to have a documented process of change control and configuration management for adding, modifying, replacing, or removing CCA hardware or software, and implement supporting configuration management activities to identify, control, and document all SERC_URE1 or vendor-related changes to hardware and software components of CCAs pursuant to the change control process. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to document and follow common change control and configuration management processes could have resulted in changes that were not approved or were deployed without the ability to recover the previous settings for the production system. In addition, SERC_URE1’s violation could have resulted in changes to the system being improperly configured, which could negatively impact other parts of the system. Furthermore, SERC_URE1’s failure to establish a change control and configuration management process could have resulted in the inability to properly test changes prior to implementing them on the production environment. However, the risk to the BPS was mitigated because SERC_URE1 had a change log in place that was used to keep track of changes to its CCAs. In addition, although SERC_URE1 was unable to provide consistent evidence of such communication, SERC_URE1 indicated that it used emails for change approvals. Furthermore, SERC_URE1 enforced the testing of changes through procedural means and conducted testing on a development system that reflects the production environment. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 added a process of change control specific to its CIP-003 procedure document for adding, modifying, replacing, and removing CCAs hardware and software. The basis of change control is the use of forms whereby personnel seeking change must seek prior approval before making any change specific to the requirements of the procedure. The forms (once approved and changes implemented) are scanned and filed appropriately. | 2012-05-29 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009887 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit scheduled. The SERC audit team reported a violation of CIP-005-1 R1, stating that SERC_URE1 had three issues with CIP-005-1 R1. First, SERC_URE1 failed to identify non-critical Cyber Assets pursuant to CIP-005 R1.4 that were included in SERC_URE1 network diagrams. Second, SERC_URE1 failed to install anti-malware on firewall access points pursuant to CIP-005 R1.5. Finally, SERC_URE1 failed to technically enforce password requirements on firewall access points pursuant to CIP-005 R1.5. After reviewing SERC_URE1’s network Electronic Security Perimeter (ESP) diagram, SERC determined that SERC_URE1 failed to identify the following as non-critical Cyber Assets, as required by CIP-005 R1.4: un-managed switches in a private network; network encryption devices used to bridge the control center Physical Security Perimeters; and microwave devices that were located between the encryption devices. SERC_URE1 was unable to provide any other documentation that identified these devices as non-critical Cyber Assets. SERC_URE1 identified CCAs but failed to identify the affected non-critical Cyber Assets. SERC_URE1 removed the network encryption devices and the un-managed switches from operation. SERC also determined that SERC_URE1 failed to install anti-malware on Electronic Access Control and Monitoring (EACM) devices, specifically: firewalls; storage device; switches; and access control server. SERC_URE1 had strong compensatory measures in place in the form of a security control monitoring application that was set up to detect security control modifications and vulnerabilities. Pursuant to Appendix 4D of the NERC Rules of Procedure, however, these devices needed to be covered under a Technical Feasibility Exception (TFE). SERC_URE1 did not file a timely TFE request for these EACM devices. Finally, SERC determined that SERC_URE1 failed to technically enforce local account password requirements, specifically the password complexity requirements, on some of the aforementioned EACM devices. SERC_URE1 attested that the device passwords met the requirements of CIP-007-1 R5 but that technical controls were not in place to enforce the password complexity requirements. SERC_URE1 had procedural controls in place that ensured that the passwords met the complexity requirements of CIP-007-1 R5. Pursuant to Appendix 4D of the NERC Rules of Procedure, however, these devices needed to be covered under a TFE. SERC_URE1 did not file a timely TFE for these EACM devices. SERC determined that SERC_URE1 was in violation of CIP-005 R1.4 and R1.5 because it failed to identify all non-critical Cyber Assets within a defined ESP and failed to afford protective measures to all Cyber Assets used in access control and monitoring, pursuant to CIP-007 R4 and CIP-007 R5. | CIP-005-1 | R1; R1.4; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to identify all non-critical Cyber Assets within the ESP could have led it to fail to implement all the necessary CIP requirements for those Cyber Assets. Such a failure could result in vulnerabilities that allow an attacker to access or compromise systems within the ESP. In addition, SERC_URE1’s failure to install anti-malware on EACM devices could have left its system unable to prevent, deter, or mitigate the introduction, exposure, or propagation of malware. Such malware could cause system failure, denial of access, or compromise the system. Furthermore, SERC_URE1 ’s failure to technically enforce strong password controls on EACM devices could have left its passwords susceptible to online and offline attacks that could allow an attacker to access or compromise systems within the ESP. Without proper account password management, it is possible to introduce unnecessary new accounts and activate old accounts that may allow an attacker to access or compromise a system. However, the risk to the BPS was mitigated because SERC_URE1 had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. SERC_URE1 also had procedural password controls in place. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 : 1) updated its control system by defining ESPs that eliminated the affected non-critical Cyber Assets from the ESPs; 2) performed, prior to the control system upgrade, a review and identified all the EACM devices that were not technically capable of using antivirus/malware prevention tools and implementing the required password protection; 3) submitted TFE Requests for the EACM devices that were not technically capable of using antivirus/malware prevention tools; 4) updated the CCA list and the network drawing; and 5) updated the appropriate change-control documentation. | 2012-11-26 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009888 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-005-1 R2, stating that SERC_URE1 failed to use a deny-by-default model for firewall traffic and failed to enable only ports and services at access points to the Electric Security Perimeter (ESP) that were required for normal and emergency operations. SERC_URE1’s electronic access control documentation indicated that each firewall (access point) shall use a deny access by default configuration, but SERC_URE1’s firewalls had this configuration for inbound traffic only. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.1 because it failed to use deny-by-default rules for outbound traffic at each firewall. SERC_URE1’s detailed cyber vulnerability assessment (CVA) results for one year indicate that there was at least one access point to the ESP that had superfluous ports and services enabled that were not required for emergency and normal operations. The detailed results also indicated that ports and service documentation was not available for several access points. SERC_URE1 was unable to provide evidence supporting the justification of all open ports and services. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.2 because it failed to allow only those ports and services that are required for normal and emergency operations. SERC determined that SERC_URE1 was in violation of CIP-005-1 R2.1 and R2.2 because it failed to use mechanisms that were configured to deny access by default and it failed to enable only ports and services that are required for normal and emergency operations. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to restrict ports and services at access points to only those required for operations could increase the attack surface into the ESP and result in access out of the ESP to low trust assets that could be leveraged or compromised. In addition, SERC_URE1’s failure to implement deny-by-default rules for outbound traffic could result in internal compromise or vulnerabilities that propagate inside the ESP without restriction. Furthermore, allowing access out of ESP to a potentially unsecure asset could allow unintended extraction of confidential information. However, the risk to the BPS was mitigated because SERC_URE1 had deny-by-default rules for inbound traffic (coming from outside the ESP). SERC_URE1 also had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs and could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) performed an analysis of the organizational processes, and the technical and procedural mechanisms for controlling electronic access to all electronic access points to the defined ESPs; 2) updated its CIP-005 procedure to better define the deny-by-default rules; 3) limited outbound traffic to only those ports and services required for operations and for monitoring Cyber Assets within the ESP; 4) removed unneeded email and network protocol ports; 5) limited access for the hosts to only those ports and services required for operations and for monitoring Cyber Assets; 6) reviewed its electronic access procedures such that each rule or set of rules was reviewed and comments were added to each existing rule or set of rules. This modified firewall rules document template will require a justification prior to implementing any change to or the modification of firewall rules; and 7) implemented a new change control process, which will add a level of protection to the firewall activity. | 2012-11-27 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009890 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-2c R1, stating that SERC_URE1 failed to ensure that all Cyber Assets within an Electronic Security Perimeter (ESP) resided within an identified Physical Security Perimeter (PSP), and failed to file a Technical Feasibility Exception (TFE) that documented the alternative measures it employed. SERC later determined that this violation extended back to Version 2a of the Standard. SERC determined that SERC_URE1 identified control centers as Critical Assets. SERC_URE1’s primary means of communication between the control centers is to use an encrypted microwave signal. SERC_URE1’s backup means of communication between the control centers is to use a dedicated T1 communication line. SERC_URE1 never considered the microwave devices and the connection between them to be Cyber Assets within an ESP and did not view them as critical. SERC determined that these microwave devices and the connection between them should be considered Cyber Assets. SERC_URE1 did not consider the backup T1 communication line to be a Cyber Asset or an access point. Instead, SERC_URE1 considered the access points to be the firewalls that the T1 communication line was connected to. On July 15, 2010, FERC approved an interpretation of CIP-006-2 R1.1. The interpretation allowed a registered entity to use alternate physical or logical measures to control physical access to Cyber Assets where a six-wall border cannot be established, provided that the registered entity submits a TFE request that details the alternate physical or logical measures that protect the Cyber Assets. SERC_URE1 deployed alternative measures by utilizing encryption devices between the control centers but failed to file a TFE with SERC that documented the alternative measures used to protect the microwave devices and the connection between them. Further, SERC_URE1 did not account for additional pieces of microwave network equipment in the communication path in its SERC_URE1’s ESP documentation (addressed in SERC2012009887). SERC determined that SERC_URE1 was in violation of CIP-006-2a R1.1 because SERC_URE1 failed to file a TFE regarding the deployed and documented alternative measures to control physical access to the Cyber Assets where a six-wall border could not be established. | CIP-006-2a | R1; R1.1. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 set up the microwave devices to establish a private connection between the control centers. In addition, SERC_URE1 installed the microwave communication devices inside secure, SERC_URE1-controlled locations with barbed wire fences, cameras, a guard house, and guards. SERC_URE1 also encrypted the microwave data connection. Furthermore, SERC_URE1 had a backup T1 connection in case the microwave communication devices were unavailable. Because of these security measures, an attacker would need a security card authorized to allow physical access to the microwave communication devices in order to gain electronic access to the devices. | 7/15/10 (when SERC_URE1 failed to file a TFE) | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) upgraded its control system by defining separate ESPs at the control centers, thereby eliminating the communication paths from the previously defined ESP and eliminating the need for “alternative protective measures” and a TFE request; 2) placed firewalls at the control center ESP access points and implemented use with the control system upgrade; 3) updated the CCA list and the network drawing; and 4) updated the appropriate change control documentation. | 2012-05-30 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009891 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-1 R1 stating that SERC_URE1 failed to provide evidence that all Cyber Assets used in the access control and monitoring of its Physical Security Perimeters (PSPs) were afforded the protective measures required by CIP-006-1 R1. SERC later determined that SERC_URE1’s physical security procedures failed to adequately address other sub-requirements of CIP-006-1 R1. SERC determined that SERC_URE1 had the following five instances of noncompliance with CIP-006-1 R1: 1) In violation of R1.1, SERC_URE1’s physical security plan contained a process for logging and monitoring the PSP but did not contain a process for the identification of physical access points to the PSP. Access points through each PSP, and measures to control entry to those access points, specifically badge reader controller devices, were not identified on the PSP diagram; 2) In violation of R1.2, SERC_URE1 failed to adequately document that access control panels, which are Cyber Assets within an Electronic Security Perimeter (ESP), also reside within a PSP. SERC_URE1 utilizes Physical Access Control Systems (PACS) to provide access control, monitoring, and logging of its PSPs. SERC_URE1’s PACS devices consist of a virtual server hosted outside of the ESP on a network segregated from the corporate network, and access control panels, which connect to the corporate network. Although SERC_URE1 stated that the panels reside within a PSP, upon review of a control system IP network diagram, SERC determined that the panels are located outside of the PSP, without the protection of six-wall boundaries; 3) In violation of R1.8, SERC_URE1 failed to document testing results for significant changes made to PACS devices as required by CIP-007-1 R1.3. SERC_URE1 was unable to provide any evidence of testing of significant changes to PACS devices. SERC_URE1 has a separate violation of CIP-007-1 R1 that is being addressed in NERC Violation ID SERC2012009893; 4) In violation of R1.8, SERC_URE1’s security patching process did not address security patch management for PACS devices and SERC_URE1 did not provide any evidence of the review and testing of security patches for PACS devices as required by CIP-007-1 R3. SERC_URE1 uses a third-party to monitor for security patches and has a formal process for the testing of security patches for Critical Cyber Assets (CCAs) and Cyber Assets located in an ESP, but this process did not address security patch management for PACS devices; and 5) In violation of R1.8, SERC_URE1 failed to account for PACS devices in its asset disposal and redeployment documentation as required by CIP-007-1 R7. SERC_URE1 had a policy in place that calls for wiping devices but did not address PACS devices specifically and did not provide enough detail to properly address disposal and redeployment of virtual PACS servers. SERC_URE1 has a separate violation of CIP-007-1 R7 that is being addressed in NERC Violation ID SERC2012009895. SERC determined that SERC_URE1 was in violation of CIP-006-1 R1 because it failed to provide all Cyber Assets used in the access control and monitoring of the PSPs the protective measures required by the Standard. | CIP-006-1 | R1; R1.1.; R1.2; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to have a physical security plan that identifies physical access points to the PSP could result in missed devices that are not accounted for, managed, monitored, or not protected pursuant to CIP-006-1 R1.8. If SERC_URE1 failed to afford PACS devices or logging systems the measures listed in CIP-006-1 R1.8, unauthorized individuals could gain access to these Cyber Assets, which could result in unauthorized physical and logical access to the PSP or the suppression of PSP monitoring. This could, in turn, allow unauthorized individuals to gain access to CCAs. However, the risk to the BPS was mitigated because the access control panels were located inside a secured SERC_URE1 facility with limited physical access. In addition, SERC_URE1 monitors physical access using security guards and cameras. Furthermore, SERC_URE1 limits electronic access to authorized badge holders. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) reviewed its physical security plan and associated procedures as they relate to R1.8 and determined the need for modifications to the physical security plan regarding PACS devices; 2) drafted a table in the physical security plan that lists the location, associated PSP, and a description of the identified access point, such as doors and windows; 3) established diagramming and vector graphics application drawings as a basis for reviewing and inventorying SERC_URE1’s PSPs, access points, and control mechanisms. The procedure requires a reconciliation of the drawings and table to ensure accuracy of SERC_URE1’s process for identifying access points to the PSPs at least annually; 4) conducted a review and reconciliation of SERC_URE1’s PSPs and validated the PSPs to be accurate; and 5) updated its physical security plan to better document and ensure protection is afforded as required by R1.8. Specifically, SERC_URE1 added a table that lists all Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s), their physical location, and the PSP in which they reside. Therefore, SERC_URE1's subject matter expert will have clear knowledge of the devices applicable to this requirement. | 2012-11-26 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009892 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-006-1 R3, stating that SERC_URE1 failed to implement the technical controls for monitoring physical access at a single access point to a Physical Security Perimeter (PSP). During the physical tour of a control center, the SERC audit team simulated forcing open a secondary access door to the PSP and found that no alarm was generated or received. Upon further investigation, SERC_URE1 determined that the tested secondary access door was not configured to be monitored for “forced door” access attempts. SERC_URE1 provided screenshots of the device configuration before and after the SERC audit team discovered the violation. The screenshots show that the monitoring device configuration was not monitoring for forced open entries prior to the issue’s discovery. Upon discovery, SERC_URE1 immediately corrected the violation and SERC_URE1 provided evidence showing the corrected configuration after the issue was identified and corrected. SERC_URE1 also provided logs from the monitoring device in question, dated before and after the issue was corrected, which show that the device was correctly generating alarms for other security events. This failure occurred at a single PSP entrance into the control center which is manned 24 hours a day, seven days a week. SERC determined that SERC_URE1 was in violation of CIP-006 R3.1 because a single monitoring system failed to indicate when a door had been opened without authorization and consequently failed to alert SERC_URE1 personnel. | CIP-006-1 | R3; R3.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP access door utilizes a magnetic lock instead of a traditional door strike that would require hundreds of pounds of force to force open the door, unless the door was released by the physical access control system or power to the access system and backup batteries was disrupted. The control center is manned 24 hours a day, seven days a week, and the access door is an internal door that requires passing through several other security controlled doors to reach. SERC_URE1 personnel within the facility are required to display a badge with their name and picture and visitors are escorted at all times. SERC_URE1 had no other PSP access points that failed to alarm or alert. Finally, the device was correctly generating alarms for other security events. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1 reconfigured the door to send alerts upon forced-door events. | 2012-03-01 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009893 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R1, stating that SERC_URE1 failed to document test results for multiple significant changes. SERC reviewed SERC_URE1’s process for testing significant changes and SERC_URE1’s change control log. SERC determined that the SERC_URE1 process for testing significant changes did not address third-party software or firmware and SERC_URE1 could not provide evidence of testing for all significant changes to existing and new Cyber Assets. SERC_URE1 delegated the testing responsibility to a third-party on a system that reflects the production environment prior to implementation on production servers, except for patches on servers that are connected to the corporate local area network (LAN). For patches on servers that are connected to the corporate LAN, the third-party tested patches on corporate servers prior to implementation on production servers. SERC determined that SERC_URE1’s process for testing significant changes did not specifically address third-party software or firmware. The SERC_URE1 change log contains records of all significant changes made to Cyber Assets located inside an Electronic Security Perimeter (ESP), but does not indicate the completed testing of such changes. SERC_URE1 claims that testing communication and requests were conducted via email and the correspondence for some tests were lost. SERC_URE1 primarily relies on the third-party to test significant changes prior to implementation on production. SERC determined that SERC_URE1 failed to provide sufficient evidence to conclude that testing was being completed consistently and successfully for all significant changes prior to implementation on the production environment. SERC determined that SERC_URE1 was in violation of CIP-007 R1 because it failed to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the ESP do not adversely affect existing cybersecurity controls. | CIP-007-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to test changes prior to implementation on a production environment could compromise the functionality of Critical Cyber Assets that reside on the production system. In addition, SERC_URE1’s failure to address all significant changes, including to third-party software and firmware, increases the probability that vulnerabilities could be introduced. SERC_URE1’s failure to maintain test results could leave SERC_URE1 unable to maintain accurate audit trails, and unable to identify significant test errors. Furthermore, SERC_URE1’s failure to document test results could leave SERC_URE1 unable to research a cybersecurity incident and unable to mitigate vulnerabilities quickly and efficiently. However, the risk to the BPS was mitigated because SERC_URE1 had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. In addition, SERC_URE1 indicated that testing communication and requests were conducted via email and the correspondence for some tests were lost. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) performed an analysis of its testing procedures for significant changes; and 2) modified its CIP-007 procedure to address the weak documentation process for recording test results. Specifically, the procedure discusses how SERC_URE1’s change control procedure creates workflow that will properly document test results associated with significant changes. SERC_URE1’s new change control process utilizes approval forms whereby personnel seeking to make any change to a Cyber Asset within the defined ESP must seek approval from their manager or the group’s director. The forms utilize three levels whereby "level three" strictly relates to significant changes and can only be approved by the manager or group’s director when accompanied by an associated test record. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009894 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R5, stating that SERC_URE1 had two issues with the Standard. The SERC audit team stated that: 1) SERC_URE1 implemented a shared account on a Cyber Asset located inside the Electronic Security Perimeter (ESP) that was not authorized, nor required and 2) SERC_URE1 failed to technically enforce password requirements on a single device in the control center. SERC later found an additional violation of CIP-007-1 R5 in which SERC_URE1 failed to remove default accounts on Cyber Assets located within an ESP. SERC reviewed SERC_URE1’s account management procedure and determined that SERC_URE1 had a policy in place for account management but it only addressed shared accounts and failed to specifically address administrator, shared, and other generic account privileges, including factory default accounts, as required by R5.2. In addition, SERC_URE1 failed to follow its established procedures after restoring a device that was located inside the ESP to an earlier date. SERC_URE1’s failure to follow its procedures resurrected an unnecessary shared account. The SERC audit team discovered this unnecessary shared account while onsite. SERC determined that SERC_URE1 violated CIP-007-1 R5.2 because it failed to address administrator, shared, and other generic account privileges, including factory default accounts, in its account management procedure, and failed to follow its account management procedure while restoring a device to an earlier date, which resurrected an unnecessary shared account. SERC_URE1 also had communication devices and servers that were not capable of technically enforcing password requirements and were not covered under a Technical Feasibility Exception (TFE). SERC determined that SERC_URE1 violated CIP-007-1 R5.3 because it had communication devices and services that were not capable of technically enforcing password requirements and did not file a TFE request documenting the compensating measures. In addition to the audit findings, SERC discovered that SERC_URE1 failed to remove default accounts on Cyber Assets located inside an ESP while reviewing SERC_URE1’s cyber vulnerability assessment (CVA) for one year (as discussed in more detail in SERC201209896). The 2010 CVA identified CCAs located within the ESP that were configured with default accounts. These devices were incorrectly identified by the third-party in the CVA as CCAs, when in fact they were non-critical Cyber Assets within an ESP, and SERC_URE1 immediately removed the default accounts upon discovery. SERC_URE1 removed these Cyber Assets from the ESP with the installation of new firewalls, which excluded the Cyber Assets from the new ESP. This violation was not self-reported by SERC_URE1 and the following year's CVA does not indicate any issues with these Cyber Assets or any default accounts. SERC determined that SERC_URE1 violated CIP-007-1 R5.2.1 because it failed to remove default accounts on Cyber Assets within an ESP. SERC determined that SERC_URE1 was in violation of CIP-007-1 R5 because it: 1) failed to implement a policy to minimize and manage the scope and acceptable use of administrator and other generic account privileges including factory default accounts; 2) had an unauthorized and unnecessary shared account on a single asset located inside an ESP without submitting a TFE; 3) had communication devices and services that were not capable of enforcing password requirements and did not file a TFE request documenting the compensating measures; and 4) had 19 the affected Cyber Assets located in an ESP that were configured with default accounts without submitting TFEs. | CIP-007-1 | R5; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to develop and implement a policy that directly addresses the acceptable use of multiple account types could result in the misuse of unaddressed account types and leave them unprotected in a manner that could lead to internal or external compromise. SERC_URE1’s failure to use proper account management could lead to the introduction of unnecessary new accounts and the activation of old accounts that could allow an attacker to access or compromise a system. In addition, SERC_URE1’s failure to use strong password controls could leave passwords susceptible to online and offline attacks that could allow an attacker to access or compromise a system. Furthermore, SERC_URE1’s failure to remove default accounts on the affected Cyber Assets located in an ESP could allow an attacker to access or compromise a system. However, the risk to the BPS was mitigated because SERC_URE1 had procedural password controls in place to ensure compliance with the CIP password requirements as a compensating measure for the lack of technical password controls. SERC_URE1 also had an extensive monitoring system that continually monitors all network traffic at the switch level inside the defined ESPs that could detect intrusions, malware, port changes, unauthorized access, and changes to devices or file structures. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) removed the shared account; 2) decommissioned the test system as required by SERC_URE1’s disposal and redeployment procedure and removed it from the defined ESP; 3) assured that a mechanism for a task review was integrated into the change control process. Therefore, a task similar to that which caused this violation must now be accompanied by a documented job description and review prior to implementing the task on applicable Cyber Assets; 4) performed a thorough review of all Cyber Assets residing in the defined ESPs to determine all applicable devices as they related to necessary TFE request(s); and 5) submitted TFE requests for the affected devices. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009895 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007 R7, stating that SERC_URE1 failed to have adequately documented formal processes and methods for disposal and redeployment of Cyber Assets within the Electronic Security Perimeter (ESP). The process documents did not contain adequate details for the proper erasure of data storage media, and for the disposal or redeployment of Cyber Assets within the ESPs. SERC reviewed the disposal and redeployment process in place at the time of the Compliance Audit and determined that the process was used by all of SERC_URE1's registered functions for all disposal and redeployments of Cyber Assets located within an ESP. SERC determined that the process in place did not adequately address the erasure of data storage media for non-network Cyber Assets within ESPs (e.g., servers and workstations) in regards to decommissioning and redeployment. SERC_URE1’s process for the erasure of media for network Cyber Assets within ESPs (e.g., firewalls, routers, and switches) provided clear detail on how to erase the data storage media. SERC reviewed decommissioned and redeployment records provided by SERC_URE1. Despite SERC_URE1’s inadequate disposal and redeployment process, SERC determined that SERC_URE1’s disposal records were in accordance with SERC_URE1’s documented procedures and demonstrated that SERC_URE1 had properly erased the data storage media upon decommissioning and redeployment of Cyber Assets within the ESP. SERC also determined that SERC_URE1 followed its established process for the disposal and redeployment of Cyber Assets within the ESP, had adequate decommissioning and redeployment evidence, and had the ability to verbally communicate the process. SERC determined that SERC_URE1 was in violation of CIP-007-1 R7 because it did not adequately document its disposal and redeployment process for handling the erasure of data storage media when decommissioning or redeploying non-network Cyber Assets located within an ESP. | CIP-007-1 | R7 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had a written process for handling the decommissioning and redeployment of Critical Cyber Assets and Cyber Assets located inside of an ESP. SERC_URE1 also consistently erased data storage media on redeployed or decommissioned Cyber Assets and maintained records of that erasure. Furthermore, SERC_URE1 was able to verbally describe the process, methods, and tools it used to erase data storage media on redeployed or decommissioned Cyber Assets. Lastly, this was a documentation only issue. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) updated its disposal and redeployment procedure to include more formal definition of “wiping” as it applies and is related to each type or category of Cyber Assets that reside in SERC_URE1’s defined ESPs; and 2) updated its change control procedure to provide more adequate tracking of specific data concerning “who, what, when, and where” regarding each disposal or redeployment event. | 2012-10-15 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-29-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009896 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported a violation of CIP-007-1 R8.2, stating that SERC_URE1 failed to verify that only ports and services required for the operation of the Cyber Assets within the Electronic Security Perimeter (ESP) were enabled in one year's cyber vulnerability assessment (CVA). SERC_URE1 contracted with a third-party for three year's CVAs. SERC_URE1’s first year's CVA report recommended that SERC_URE1 review its ports and services to identify and disable ports that were not needed for emergency or normal operations. SERC_URE1’s second year's CVA report indicated that documentation on ports and services was not adequate in several instances and the third-party conducting the CVA found it impossible to determine if a particular port was actually required for operation. SERC_URE1’s third year's CVA report indicated that SERC_URE1 did not provide sufficient documentation and justification of its enabled and disabled ports and services to allow the third party conducting the CVA to complete its review of SERC_URE1’s ports and services pursuant to SERC_URE1’s established process. The third-party completed all the other sub-requirements of CIP-007-1 R8 for the third year's CVA. SERC determined that SERC_URE1 was in violation of CIP-007-1 R8.2 because it failed to complete a review to verify that only ports and services required for normal and emergency operation of the Cyber Assets within the ESP were enabled. | CIP-007-1 | R8; R8.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1's failure to meet all the requirements of CIP-007-1 R8 when conducting its three year's CVAs, specifically reviewing ports and services, could have left Cyber Assets residing within the ESP open to potential security threats and compromise for an extended period of time. However, the risk to the BPS was mitigated because SERC_URE1 completed all the other sub-requirements of CIP-007 R8 for the third year's CVA and did not discover any other vulnerabilities. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $48,000 (for SERC2012009885, SERC2012009886, SERC2012009887, SERC2012009888, SERC2012009890, SERC2012009891, SERC2012009892, SERC2012009893, SERC2012009894, SERC2012009895, and SERC2012009896) | Compliance Audit | To mitigate this violation, SERC_URE1: 1) conducted a review of its procedures for CVAs; and 2) updated its CVA procedure to include control mechanisms for ensuring that all CVA tasks are performed as required and documented in the statement of work. Specifically, SERC_URE1’s compliance staff will facilitate the process to create more oversight and ensure all aspects of the statement of work are complete; and 3) required compliance staff, after the final report was distributed, to participate in the review of the report and assist in the development of plans to mitigate any identified vulnerabilities. | 2012-12-12 | 2013-02-13 | Neither Admits Nor Denies | SERC reviewed SERC_URE1 's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
2013-03-27 | FERC | NP13-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100297 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO identifying a violation of CIP-005-1 R1.5. MRO_URE1 discovered that it had failed to afford certain Cyber Assets used in the access control and monitoring of the Electronic Security Perimeters (ESPs) the protective measures specified in all CIP Standards listed and required by CIP-005-1 R1.5. Three of MRO_URE1’s Cyber Assets used in the access control and monitoring of the ESP were at issue (collectively, the Devices). For all of the Devices, MRO_URE1 failed to afford the protections of CIP-005-1 R2.2 and CIP-007-1 R3 and R8. MRO_URE1 was not able to provide evidence that only the required ports and services were enabled, as required by CIP-005-1 R2.2. In addition, MRO_URE1 failed to document the assessment and implementation of security patches for the Devices, as required by CIP-007-1 R3.1 and R3.2. For only two Devices, MRO_URE1 failed to afford the protection of CIP-003-1 R6 by failing to document that it followed its established change control and configuration management procedures for adding, modifying, replacing, or removing Critical Cyber Asset (CCA) hardware or software. For only one Device, MRO_URE1 failed to afford the protections of CIP-005-1 R2.6 and CIP-007-1 R1 and R5.1.1. Specifically, MRO_URE1 failed to implement banners in certain log-in instances, as required by CIP-005-1 R2.6. In addition, MRO_URE1 had no documents to verify testing of security configurations in certain instances of significant changes to and the addition of new routers and switches, as required by CIP-007-1 R1 and R1.3. MRO_URE1 also granted an individual logical access to the Device for a three-month period without ensuring approval by the designated personnel as required by CIP-007-1 R5.1.1. The noncompliance related to CIP-007-1 R8 was self-reported and later dismissed because it was related to MRO_URE1's annual cyber vulnerability assessment which was prior to MRO_URE1's mandatory compliance date. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1 does not utilize any of the systems at issue in this violation to operate and control Critical Assets. In addition, the ports and services that MRO_URE1 enabled beyond those which were necessary were only open for communications from other trusted corporate networks. MRO_URE1’s vendor performed the requisite assessments of security patches and upgrades. MRO_URE1 reviewed the vendor’s assessments and partially documented that review. The devices at issue were field tested upon commissioning and the deficiency regarding testing was in the failure to document the baseline configuration, rather than the failure to conduct testing. With regard to the logon banners, MRO_URE1’s violation was documentation related. MRO_URE1 was utilizing logon banners but failed to document the content of the logon banners in a formal document. Moreover, MRO_URE1’s trusted corporate networks were protected by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. While one individual was provided logical access, the individual had received the required cybersecurity training and had undergone a personnel risk assessment, but the access approval was not given by the designated personnel. Additionally, MRO_URE1 identified no unauthorized access that caused a BPS incident during the relevant time period. | when the Standard became mandatory and enforceable to MRO_URE1 | Mitigation Plan completion | $10,000 (for MRO201100297, MRO201100298, MRO201100301, MRO201100303, and MRO201100304) | Self-Report | To mitigate this violation, MRO_URE1: 1) enhanced its change control and configuration management documentation procedures, to address CIP-003-1 R6, by training individuals to use a change management tool to enter all change requests. The change management tool incorporates an approval workflow, testing steps, and all activity related to the change; 2) analyzed its ports and services, to address CIP-005-1 R2.2, as part of its annual cyber vulnerability assessment to ensure that only required ports and services are enabled at the ESP access points. MRO_URE implemented a process to utilize the annual cyber vulnerability assessment along with the revised change management process to ensure that only required ports and services are enabled in the future; 3) created, documented, and implemented a procedure to require standardized logon banner language, to address CIP-005-1 R2.6, where technically feasible; 4) performed testing, to address CIP-007-1 R1 and R1.3, to determine the necessary configuration changes required due to enabling only required ports and services. MRO_URE1 also implemented a standard configuration for all applicable CCAs and the standard configuration; 5) updated its security patch management policy, to address CIP-007-1 R3.1 and R3.2, to include processes for: a) newly released security patches; b) the tracking of the analysis of the patches; c) the determination to implement or not to implement the patch; and d) documentation of the information; 6) updated its access control procedures, to address CIP-007-1 R5.1.1, by developing an electronic access request and approval tool; and 7) included ports and services, to address CIP-007-1 R8.2, for certain Devices in the annual cyber vulnerability assessment. One Device was decommissioned. | 2012-01-31 | 2012-12-19 | Admits | MRO considered certain aspects of MRO_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. MRO did not consider MRO_URE1's compliance history an aggravating factor in the penalty determination.
2013-03-27 | FERC | NP13-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100298 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO identifying a violation of CIP-005-1 R2. MRO_URE1 discovered that it failed to implement all electronic access controls at certain electronic access points to the Electronic Security Perimeter (ESP). MRO_URE1 was not able to provide evidence that only ports and services required for operations and monitoring of Cyber Assets at the access points to the ESP were enabled, as required by CIP-005-1 R2.2. In addition, MRO_URE1 failed to maintain a formal document identifying the content of appropriate use banners, as required by CIP-005-1 R2.6. Although MRO_URE1 was utilizing logon banners during the time period of the violation, MRO_URE1 failed to document the contents of the logon banners. | CIP-005-1 | R2; R2.2; R2.6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The additional ports and services that MRO_URE1 enabled were only open from trusted corporate networks. MRO_URE1’s trusted corporate networks were protected by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. With regard to the logon banners, MRO_URE1’s violation was documentation related. MRO_URE1 was utilizing logon banners but failed to document the content of the logon banners in a formal document. Furthermore, MRO_URE1 identified no cybersecurity incidents throughout the duration of the violation. | when the Standard became mandatory and enforceable to MRO_URE1 | for R2.6, when the logon banner standard language procedure was published); for R2.2, when MRO_URE1 completed its annual cyber vulnerability assessment and enhanced its change control documentation to ensure that only ports and services required for operations and for monitoring Cyber Assets within the ESP were enabled | $10,000 (for MRO201100297, MRO201100298, MRO201100301, MRO201100303, and MRO201100304) | Self-Report | To mitigate this violation, MRO_URE1: 1) performed a cyber vulnerability assessment, during which it conducted a review of the required ports and services at the access points to the ESPs and compared the results to actual ports and services at the access points to the ESPs; 2) made configuration changes to the access control lists of the access points to the ESPs to enable access only to the required ports and services; 3) implemented a process to utilize the annual cyber vulnerability assessment process to determine which ports and services are required; 4) implemented a change control and configuration management process to address incremental changes to the ports and services, which will ensure that only required ports and services are enabled; and 5) standardized and documented logon banner language, to address CIP-005-3 R2.6, and, where technically feasible, implemented the procedure for logon banner language. | 2012-01-01 | 2012-10-24 | Admits | MRO considered certain aspects of MRO_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. MRO did not consider MRO_URE1's compliance history an aggravating factor in the penalty determination.
2013-03-27 | FERC | NP13-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100301 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO identifying a violation of CIP-006-1 R1.8. MRO_URE1 discovered that it failed to afford some of its Cyber Assets that authorize and/or log access to Physical Security Perimeters (PSP) the protective measures specified in several CIP Standards listed in CIP-006-1 R1.8. Two of MRO_URE1’s Cyber Assets that authorize or log access to the PSP are at issue. The first system controls and logs access via cyber keys at PSPs, and the second system controls and logs access via access cards at PSPs (collectively, the Physical Security Servers). MRO_URE1 failed to afford both of the Physical Security Servers the protective measures specified in CIP-003-1 R6, CIP-005-1 R2.2, and CIP-007-1 R1.3, R2, R3, R5.2.3, R5.3.3, R6.5 and R8.2. MRO_URE1 failed to have a documented process for change control and configuration management for adding, modifying, replacing, or removing CCA hardware or software, as required by CIP-003-1 R6. In addition, MRO_URE1 failed to enable only required ports and services, as required by CIP-005-1 R2.2. MRO_URE1 failed to document cybersecurity test results in some instances of significant changes to existing Cyber Assets, as required by CIP-007-1 R1 and R1.3. MRO_URE1 failed to enable only required ports and services, as required by CIP-007-1 R2. MRO_URE1 failed to have documentation regarding security patch assessments and compensating measures to mitigate risk exposure, as required by CIP-007-1 R3. MRO_URE1 failed to maintain audit trails of the account use of a shared account, as required by CIP-007-1 R5.2.3. MRO_URE1 failed to change user account passwords on an annual basis, as required by CIP-007-1 R5.3.3. MRO_URE1 failed to review logs of system events related to cybersecurity, as required by CIP-007-1 R6.5. Finally, MRO_URE1 failed to include a review of required ports and services in its network vulnerability assessment, as required by CIP-007-1 R8.2. Regarding the first system, MRO_URE1 failed to afford the protections of CIP-005-1 R2.6, CIP-007-1 R4, and CIP-007-1 R5.2.1. MRO_URE1 failed to display banners on the user login screen, as required by CIP-005-1 R2.6. In addition, MRO_URE1 failed to have anti-virus software installed, as required by CIP-007-1 R4. MRO_URE1 also failed to change a factory default generic account password prior to placing the system into service, as required by CIP-007-1 R5.2.1. (MRO determined there was no stand alone CIP-007-1 R5.2.1 violation because this failure did not take place within an Electronic Security Perimeter.) Regarding the second system, MRO_URE1 failed to afford the protections of CIP-007-1 R6.1. MRO_URE1 failed to document or implement a process to monitor specific server security event logs, as required by CIP-007-1 R6.1. The noncompliance related to CIP-007-1 R8 was self-reported and later dismissed because it was related to MRO_URE1's annual cyber vulnerability assessment which was prior to MRO_URE1's mandatory compliance date. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that the violation posed a moderate risk because failure to implement operational and procedural controls to manage access to PSPs could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. The ports and services at issue were only open to trusted MRO_URE1 corporate networks that are protected by firewalls, virtual local area network constraints, and domain and local account security. These protections illustrate a defense-in-depth strategy of protection that an intruder would have to overcome to gain access to MRO_URE1’s transmission management system. While MRO considered that MRO_URE1 did not identify any unauthorized access or cybersecurity incident throughout the duration of the violation, the failure to implement a process to monitor PSP server security event logs and the failure to include a review of open ports and services in its network vulnerability assessment posed a moderate risk to the reliability of the BPS. | when the Standard became mandatory and enforceable to MRO_URE1 | Mitigation Plan completion | $10,000 (for MRO201100297, MRO201100298, MRO201100301, MRO201100303, and MRO201100304) | Self-Report | To mitigate this violation, MRO_URE1: 1) revised the change control management system, to address CIP-003-1 R6, to capture significant changes for the Physical Security Servers; 2) performed a cyber vulnerability assessment, to address CIP-005-1 R2.2, during which it conducted a review to ensure only the required ports and services were enabled; 3) implemented logon banners, to address CIP-005-1 R2.6, for the Physical Security Servers; 4) implemented tracking of all significant changes, to address CIP-007-1 R1 and R1.3, to the Physical Security Servers with the change control management system; 5) enabled only required ports and services, and disabled all ports and services not required to address CIP-007-1 R2.1, R2.2, and R2.3; 6) implemented a process to record security patch assessments, to address CIP-007-1 R3, R3.1, and R3.2, for the Physical Security Servers in the change control management tool; 7) tested, documented, and installed anti-virus software and updates on the Physical Security Servers to address CIP-007-1 R4; 8) changed the passwords, to address CIP-007-1 R5.2.1, for the Physical Security Servers and added a clear description of the password change process for shared accounts to its account management and logging policy to address CIP-007-1 R5.2.3; 9) implemented a process to capture the Physical Security Servers’ security access logs and reviews them weekly. In addition, MRO_URE1 changed the passwords for the shared accounts, to address CIP-007-1 R5.3.3, and implemented a process to record such changes in the future in the change control management system; 10) implemented a process to review security audit logs, to address CIP-007-1 R6.1 and R6.5, for the second system weekly; and 11) included the Physical Security Servers in the cyber vulnerability assessment to address CIP-007-1 R8.2. | 2012-06-29 | 2012-08-16 | Admits | MRO considered certain aspects of MRO_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. MRO did not consider MRO_URE1's compliance history an aggravating factor in the penalty determination.
2013-03-27 | FERC | NP13-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100303 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO identifying a violation of CIP-007-1 R2. MRO_URE1 had a documented process to address those ports and services to be enabled for normal and emergency operations. However, MRO_URE1 discovered that it failed to implement that process to ensure that it had only enabled those ports and services required for normal and emergency operations, in violation of CIP-007-1 R2. As a result, MRO_URE1 failed to enable only ports and services required for normal and emergency operations, in violation of CIP-007-1 R2.1. In addition, MRO_URE1 failed to disable other ports and services prior to the production use of all Cyber Assets inside the Electronic Security Perimeter (ESP), in violation of CIP-007-1 R2.2. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While MRO_URE1 had enabled certain ports and services not required for operations, the ports and services were only open from trusted corporate networks. There were two layers of security protecting the ports and services from exploitation, including a firewall and demilitarized zone (DMZ). In order to exploit the open ports and services, both the firewall and DMZ would have had to have been compromised. These protections illustrate a defense-in-depth strategy of protection that an intruder would have to overcome to gain access to MRO_URE1’s transmission management system. Furthermore, MRO_URE1 identified no cybersecurity incidents throughout the duration of the violation. | when the Standard became mandatory and enforceable to MRO_URE1 | Mitigation Plan completion | $10,000 (for MRO201100297, MRO201100298, MRO201100301, MRO201100303, and MRO201100304) | Self-Report | To mitigate this violation, MRO_URE1: 1) performed a cyber vulnerability assessment, during which it conducted a review of the required ports and services and compared the results to actual ports and services, enabled only the required ports and services, and will continue to utilize the annual cyber vulnerability assessment process to determine which ports and services are required; 2) implemented a change control and configuration management process to address incremental changes to the ports and services, which will ensure that only required ports and services are enabled. The change management process clearly describes the process for the analysis of the enabling and disabling of ports and services; and 3) made enhancements to the cyber vulnerability assessment and change control and configuration management procedures documents to clearly describe the steps to be followed for the analysis of ports and services to be enabled or disabled for emergency operations. | 2012-01-01 | 2012-10-24 | Admits | MRO considered certain aspects of MRO_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. MRO did not consider MRO_URE1's compliance history an aggravating factor in the penalty determination. MRO considered that the Mitigation Plan was completed past the approved completion date. MRO considered this a neutral factor in the penalty determination.
2013-03-27 | FERC | NP13-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100304 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO identifying a violation of CIP-007-1 R3. MRO_URE1 had in place a security patch management program. For its transmission management system, MRO_URE1 failed to fully document patch assessments and compensating measures. A vendor performed all assessments of security patches and upgrades within 30 days and supplied that information to MRO_URE1 for review. However, MRO_URE1 failed to document its assessment of security patches and failed to completely document the implementation of security patches pursuant to its security patch management program, in violation of CIP-007-1 R3.1 and R3.2. In addition, for a specific access control and monitoring device, MRO_URE1 failed to have in place a tracking mechanism to monitor or record the 30-day period allowed for analysis of the required software updates. MRO_URE1 also failed to have in place a tracking mechanism to monitor or record the 30-day period allowed for analysis of the required firmware updates for devices within the supervisory control and data acquisition engineering group. Finally, for the physical security access control and monitoring devices, MRO_URE1 failed to have in place a tracking mechanism to monitor or record the 30-day period allowed for analysis of the required software updates. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1’s vendor performed the requisite assessments of security patches and upgrades. MRO_URE1 reviewed the vendor’s assessments and MRO_URE1 partially documented that review. The violation was not related to the lack of implementation of any security patches, but was related to the failure to document the internal assessment and to thoroughly document the implementation of the security patches. | when the Standard became mandatory and enforceable to MRO_URE1 | Mitigation Plan completion | $10,000 (for MRO201100297, MRO201100298, MRO201100301, MRO201100303, and MRO201100304) | Self-Report | To mitigate this violation, MRO_URE1: 1) enhanced its security patch management procedures to clearly describe the mechanisms used to implement a 30-day tracking procedure for security patch releases; 2) trained relevant personnel to follow the new procedures, and the CIP compliance team implemented a process to perform regular internal spot checks to verify implementation of the new processes; and 3) submitted Technical Feasibility Exception requests to MRO. | 2012-01-31 | 2012-12-19 | Admits | MRO considered certain aspects of MRO_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. MRO did not consider MRO_URE1's compliance history an aggravating factor in the penalty determination.
2013-02-28 | FERC | NP13-27-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100661 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating it was in violation of CIP-003-1 R6. During an internal compliance assessment, SPPRE_URE1 discovered that it was not documenting the performance of its change control and configuration management program. SPP RE determined that SPPRE_URE1 had written change control and configuration management procedures in place prior to the Standard becoming mandatory and enforceable to SPPRE_URE1. However, SPPRE_URE1 did not have documentation to demonstrate that it was following the change control and configuration management program for hardware and software changes to Critical Cyber Assets (CCAs). | CIP-003-1 | R6 | Lower | Moderate | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Because of its size, SPPRE_URE1 does not have a large group of system administrators responsible for implementing changes to SPPRE_URE1's CCAs. SPPRE_URE1 confirmed that although it was not documenting its change control and configuration management activities, there was a system administrator following SPPRE_URE1's change control and configuration management procedure. System hardware changes were minimal during the violation period, and software changes were implemented with assistance from a third-party service provider. All of SPPRE_URE1's CCAs were behind a firewall set to deny access by default and were being monitored at all times. | when the Standard became mandatory and enforceable to SPPRE_URE1 | implementation date of revised procedure | $8,000 (for SPP201100661, SPP201100663 and SPP2012009591) | Self-Report | In accordance with its Mitigation Plan, SPPRE_URE1: 1) performed a complete inventory of all software and hardware components of assets covered under CIP-003-3 R6, providing an adequate baseline for developing and managing the documentation of asset modification; 2) implemented a ticketing system for documenting changes to individual assets, modifications to systems and modifications to authorized lists, and addressed the overall approval process for changes to CCAs; and 3) implemented an updated procedure guiding the use of the newly implemented ticket system, which ensures that sufficient evidence is generated regarding the identification, control and documentation of changes to CCAs. | 2012-03-29 | 2012-04-27 | Neither Admits nor Denies | SPPRE_URE1's internal compliance program was considered a neutral factor for penalty determination.
2013-02-28 | FERC | NP13-27-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100663 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating it was in violation of CIP-007-1 R3. SPPRE_URE1 was unable to provide all documentation required by CIP-007-1 R3, related to security patches. SPPRE_URE1 acquired the patch management services of a vendor, which was also the provider of SPPRE_URE1's supervisory control and data acquisition (SCADA) system. The patch management service identified relevant patches for all operating system and application software utilized by the various components of SPPRE_URE1's SCADA system, tested the patches, and provided the patches to SPPRE_URE1 to be installed on the system. | CIP-007-1 | R3 | Lower | Moderate | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Patch management services were being provided for SPPRE_URE1's SCADA system by its SCADA platform vendor, and as a result, those applications were being patched even though there was no documented procedure in place. In addition, all of SPPRE_URE1's Critical Cyber Assets and other Cyber Assets within the Electronic Security Perimeter (ESP) were behind a firewall set to deny access by default and were being monitored at all times. In addition, SPPRE_URE1 utilized a security information and event management tool that monitored for and alerted administrators of anomalous or suspicious activity within the ESP. | when the Standard became mandatory and enforceable to SPPRE_URE1 | Mitigation Plan completion | $8,000 (for SPP201100661, SPP201100663 and SPP2012009591) | Self-Report | In accordance with its Mitigation Plan, SPPRE_URE1: 1) identified all systems and appropriate components for inclusion into the SPPRE_URE1 patch management program; 2) defined a clear process on exactly how security patches will be identified, tracked, tested, and implemented or mitigated; and 3) implemented the necessary changes to the program and trained applicable personnel on the revisions. | 2012-02-15 | 2012-05-14 | Neither Admits nor Denies | SPPRE_URE1's internal compliance program was considered a neutral factor for penalty determination. SPP RE considered SPPRE_URE1's compliance history as a neutral factor in the penalty determination. SPP RE also considered that the Mitigation Plan was completed past the approved completion date. SPP RE considered this a neutral factor in the penalty determination.
2013-02-28 | FERC | NP13-27-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009591 | Settlement Agreement | SPPRE_URE1 submitted a Self-Report to SPP RE stating it was in violation of CIP-006-1 R1.8. SPPRE_URE1 reported that its physical access control (PAC) system was not being afforded all of the protective measures from the standards and requirements referenced by CIP-006-1 R1.8, specifically CIP-007-1 R3, CIP-003-1 R6, CIP-005-1 R2, and CIP-005-1 R3. The deficiencies related to CIP-007-1 R3 (patch management) and CIP-003-1 R6 (change control) are primarily the result of SPPRE_URE1's self-reported violations of those individual requirements, which are being processed concurrently. SPPRE_URE1 was unable to provide all documentation required by CIP-006-1 relating to its PAC system. In addition, SPPRE_URE1 did not document change control and configuration management activities for changes to its PAC system. The CIP-005-1 R2 and R3 deficiencies stem from the configuration and location of the PAC system. | CIP-006-1 | R1; R1.8 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The server hosting the PAC application was physically located within the SPPRE_URE1 control center Physical Security Perimeter (PSP) and only personnel with authorized physical access to the PSP could access the server physically. The PAC system was protected by the corporate firewall, preventing communication with the PAC server from outside the corporate network. Corporate firewall logs were collected and analyzed for anomalous activity. The list of users with credentials for login to the PAC server had received personnel risk assessments and training pursuant to CIP-004 R3 and R2, respectively. Security patches and other updates and changes were applied to the PAC system during the violation period pursuant to SPPRE_URE1 general corporate update process; however, it was not done in compliance with CIP-003 R6 and CIP-007 R3 programs, and evidence of patching or change control records were not maintained to document such changes. | when the Standard became mandatory and enforceable to SPPRE_URE1 | Mitigation Plan completion | $8,000 (for SPP201100661, SPP201100663 and SPP2012009591) | Self-Report | In accordance with its Mitigation Plan, SPPRE_URE1: 1) reviewed options for migrating PAC equipment into a protected network space addressing the requirements of CIP-005 R2 and R3; and 2) tested the migration of the new equipment by introducing a new server to take on the current role that the PAC system has. This new server exists in the protected network environment. This method of migration ensures minimal downtime to PAC systems. | 2012-06-19 | 2012-12-04 | Neither Admits nor Denies | SPPRE_URE1's internal compliance program was considered a neutral factor for penalty determination.
2013-02-28 | FERC | NP13-27-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201100668 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report to SPP RE indicating that it was in violation of CIP-006-3c R5. Specifically, SPP RE_URE2's systems operations center sustained a lightning strike/power surge that damaged several electrical devices and destroyed a remote terminal unit (RTU), which is a component of SPP RE_URE2's physical access monitoring and alarm system for its Physical Security Perimeter (PSP). As a result, real-time monitoring at SPP RE_URE2's control center, the electronic management system (EMS) areas, and the control center server room were compromised during the pendency of the violation. The RTU failure triggered an immediate EMS alarm at the system operators' console, but because of the circumstances at that time, system operators overlooked the alarm, and the RTU failure was not identified until seven days after the RTU failure. Consequently, SPP RE_URE2 was performing widespread system restoration activities at the time of the lightning strike due to a severe weather related event. The already existing weakened system condition coupled with multiple alarms caused by the lightning strike resulted in the RTU failure alarm to be embedded with over 150 other system alarms, all of which required immediate operator attention. Upon discovery of the RTU failure, maintenance personnel promptly assessed the damage to the RTU and ordered necessary replacement components. SPP RE_URE2's personnel repaired the RTU and restored real-time monitoring functions. | CIP-006-3c | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to monitor physical access to access points to its ESP presented a risk that unauthorized intruders could access and compromise SPP RE_URE2's Critical Cyber Assets. Despite the potential risk, the risk was not caused by the conduct of SPP RE_URE2; instead, it was caused by a severe weather related event and an ensuing lighting storm/power surge. Additionally, during the period that real-time physical access monitoring of the facilities at issue was compromised by the RTU failure, security cameras were in place and remained operational, and SPP RE_URE2's system control center staff were in place to monitor the security cameras around-the-clock at all of SPP RE_URE2's remaining facilities. Also, regular physical access/locks and card readers, authorization and logging controls, and data storage were all in place and continued to operate properly. SPP RE_URE2 confirmed that, to the best of its knowledge, no unauthorized access or attempts to any of its access points to the ESP occurred during the duration of the violation. | when real-time monitoring was compromised | when the RTU was repaired and real-time monitoring was restored | 0 | Self-Report | Upon discovery of the RTU failure, SPP RE_URE2 maintenance personnel promptly assessed the damage to the RTU and ordered necessary replacement components. SPP RE_URE2's personnel repaired the RTU and restored real-time monitoring functions. | 2011-06-09 | 2012-04-27 | Neither Admits nor Denies | SPP RE considered the following factors in determining the penalty amount: 1) Extenuating Circumstances: Pursuant to § 4.3.8 of Appendix 4B of the NERC Rules of Procedure, SPP RE did consider the severe weather related event and lightening strike/power surge circumstances to be a mitigating factor in determining the penalty for this violation. 2) Internal compliance program (ICP): At the time of the violation, SPP RE_URE2 maintained a written ICP but SPP RE did not consider it as a mitigating factor for penalty determination purposes.
2013-02-28 | FERC | NP13-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009096 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1.8 because WECC_URE1 failed to assess and document updates and patches to third-party software on 36 Critical Cyber Assets (CCAs) used in the access control and monitoring of Physical Security Perimeters (PSPs), as required by CIP-007-1 R3. WECC_URE1 self-reported that 15 CCAs used in the access control and/or monitoring of 23 PSPs were not afforded all protective measures required under CIP-006-1 R1.8. WECC_URE1, while mitigating the violation described above, identified 21 CCAs used to authenticate access rights, to control access, and to log access attempts to PSPs during server outages. WECC_URE1 failed to assess and document updates and patches to third-party software on the 21 system control panels in violation of CIP-006-1 R1.8. WECC reviewed WECC_URE1's Self-Report and determined that WECC_URE1's failure to assess and document updates and patches to third-party software installed on 36 CCAs used in the physical access control and monitoring of PSPs was a violation of CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Medium | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the risks posed by WECC_URE1's noncompliance were offset by compensating measures in place during the pendency of the violation. All devices were secured within a PSP. All personnel with access to the devices completed personnel risk assessments and cyber security training. Fifteen of the CCAs were afforded protections of 18 requirements as required by CIP-006-1 R1.8. The remaining 21 devices had no internet connectivity. These devices enabled only those ports and services required for normal and emergency operations. These devices are equipped with security measures that detect and mitigate exposure and propagation of malware. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $35,000 (for WECC2012009096 and WECC2012009095) | Self-Report | Pursuant to its Mitigation Plan, WECC_URE1 performed the following actions: 1) WECC_URE1 evaluated the CIP patch management processes and procedures and updated the procedures to include documentation of compensating measures pursuant to CIP-007-3 R3.2. 2) WECC_URE1 identified and assessed all third-party applications and software, identified all applicable and available patches from the primary vendor(s), and applied all patches to the affected platforms or document compensating measures applied to mitigate risk exposure. 3) WECC_URE1 assessed and updated the CIP patch management process document. 4) WECC_URE1 documented that third-party patches will be evaluated and assessed for applicability, criticality and risk exposure within 30 calendar days of availability in accordance with CIP requirements. 5) For all third-party applications on assets: i. WECC_URE1 identified and inventoried all third-party applications and software (by vendor); ii. WECC_URE1 identified and removed any non-essential third-party applications; and iii. For all third-party applications deemed appropriate, WECC_URE1 assessed all available security patches based on applicability, criticality and risk exposure. 6) WECC_URE1 patched third-party applications: i. WECC_URE1 developed and implemented a schedule for tracking and testing third-party software patches prior to deploying on to the assets; and ii. WECC_URE1 deployed, monitored and validated completion of all tested third-party software patches. 7) WECC_URE1's corporate security performed a CIP requirements gap analysis and reliability risk assessment to the assets to identify immediate remediation actions where current compensating measures are not already in place. Based on this gap assessment: i. WECC_URE1 reviewed and assessed protective measures for appropriateness to ensure they are adequate; ii. WECC_URE1 applied all applicable controls that have not already been put into place; and iii. WECC_URE1 updated all operational procedures and documentation related to the assets required by the Standard. | 2012-11-29 | 2013-02-08 | Agrees/ Stipulates | WECC_URE1 had an internal compliance program (ICP) which was in place at the time of the violation and which WECC considered a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and determined that it should not serve as a basis for aggravating the penalty.
2013-02-28 | FERC | NP13-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009095 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because it failed to assess software patches and failed to document compensating measures applied to mitigate risk exposure where patches were not installed for Cyber Assets within the Electronic Security Perimeter (ESP). After submitting the Self-Report, WECC_URE1 reported that during the course of mitigation it discovered 15 network devices for which patches were not reviewed or implemented. WECC determined that the violation scope consisted of 42 devices. WECC further determined that WECC_URE1 failed to assess security patches for third-party software on 27 Critical Cyber Assets (CCAs) and Cyber Assets within ESPs associated with its primary control center and backup control centers as of the compliance enforcement date of the Standard. WECC further determined that WECC_URE1 failed to assess and implement security patches or compensating measures for 15 network devices identified as CCAs. | CIP-007-1 | R3 | Lower | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the 27 CCAs at issue, all other software patches were assessed and implemented. These devices were secured within a Physical Security Perimeter (PSP). Physical access thereto was controlled, logged and monitored 24/7. In the event an unauthorized attempt to access the PSP, onsite security personnel would have been immediately alerted. All individuals with authorized physical access completed personnel risk assessments (PRAs) and cyber security training. The devices were also located in an ESP. Electronic access was limited to individuals who completed PRAs and cyber security training. All electronic access was logged and monitored. The ESP was alarmed to immediately signal a cyber security event, or unauthorized electronic access attempt. Patches and updates for electronic access points were assessed and implemented where appropriate. Furthermore, the 27 devices in scope have no internet connectivity. WECC_URE1 failed to document compensating measures for 15 devices on which it did not install patches and updates. WECC_URE1 did, however, assess and where appropriate, implement patches for all 15 devices. Implementation was documented, as was WECC_URE1’s assessment. Devices were contained within a PSP. All individuals with access to the PSP completed PRAs and cyber security training. Unauthorized access attempts immediately altered onsite security personnel. All access through the PSP was controlled, logged and monitored. Electronic access to the devices was logged, controlled and monitored. The system would have immediately signaled cyber security events. All individuals with electronic access to the devices completed PRAs and cyber security training. These devices were equipped with anti-virus software. | when WECC_URE1 failed to assess and implement security patches or compensating measures for 15 network devices | Mitigation Plan completion | $35,000 (for WECC2012009096 and WECC2012009095) | Self-Report | WECC_URE1 submitted a Mitigation Plan, outlining the following mitigating actions: 1) WECC_URE1 evaluated the CIP patch management processes and procedures and updated the procedures including documentation of compensating measures pursuant to CIP-007-3 R3.2. 2) WECC_URE1 identified and assessed all third-party applications and software, identified all applicable and available patches from the primary vendor(s), and applied all patches to the affected platforms or documented compensating measures applied to mitigate risk exposure. 3) WECC_URE1 assessed and updated CIP patch management process document, and trained employees responsible for implementing and managing the CIP patching process. 4) WECC_URE1 patched third-party applications: i.WECC_URE1 developed and implemented a schedule for tracking and testing third-party software patches prior to deploying on to the assets. ii. WECC_URE1 deployed, monitored and validated completion of all tested third-party software patches. | 2012-09-28 | 2012-10-26 | Agrees/ Stipulates | WECC_URE1 had an internal compliance program (ICP) which was in place at the time of the violation and which WECC considered a mitigating factor in the penalty determination. WECC considered WECC_URE1's compliance history and aggravated the penalty.
2013-02-28 | FERC | NP13-23-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007586 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-007-1 R4.1. Specifically, FRCC_URE1 failed to install and/or use anti-virus software and other malware prevention tools on workstations classified as Critical Cyber Assets (CCAs) even though it was technically feasible to do so. Instead of installing anti-virus software on each CCA, FRCC_URE1 maintained alternate, comparable security measures which included a network-based intrusion detection system (IDS) designed to protect all of the CCAs within FRCC_URE1's Electronic Security Perimeters (ESPs). FRCC_URE1 depended on its perimeter devices such as its IDS and hardened vendor-specified configuration to mitigate the risk of malware and maintained a locked down environment where all updates were evaluated for malware detection. However, FRCC_URE1's anti-virus and malware prevention measures were not sufficient for compliance with CIP-007-1 R4.1. | CIP-007-1 | R4; R4.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The devices were protected within the ESP, and FRCC_URE1 maintained a locked down environment where all updates were validated to ensure that they did not contain any malware, during the pendency of the violation. FRCC_URE1 maintains a hardened system environment where only energy management system (EMS) vendor-approved applications and configurations are installed. Any new application is installed after two levels of testing conducted by FRCC_URE1 and FRCC_URE1's EMS vendor. FRCC_URE1 also maintained an IDS which, for the duration of the violation, scanned and protected all network segments and monitored and logged all activities for these access points. | when the Standard became mandatory and enforceable to FRCC_URE1 | when FRCC_URE1 updated its risk-based assessment methodology (RBAM) | $8,000 (for FRCC2011007586 and FRCC2011007803) | Self-Report | To mitigate this violation, FRCC_URE1 updated its RBAM to apply risk-based criteria based on CIP Version 4 Standards approved by FERC. FRCC_URE1 revised its systems management procedures document to state that all Cyber Assets within the ESP must have anti-virus and malware prevention tools installed, unless technically infeasible. This revision includes the requirement that, where technically infeasible, a Technically Feasibility Exception (TFE) will be submitted and compensating measures must be applied to mitigate risk exposure. Further, FRCC_URE1 updated and corrected its access control list of associated CCAs. The subject assets are no longer classified as CCAs. FRCC_URE1's staff was trained on the revised procedures to provide a clearer understanding of the requirements and further minimize the probability of future violations. | 2012-05-07 | 2012-10-23 | Neither Admits nor Denies | FRCC_URE1 had an internal compliance program (ICP), in place at the time of the violation, which FRCC considered to be a mitigating factor in the penalty determination. Because FRCC_URE1 self-reported this violation shortly before a scheduled Spot Check, FRCC did not award credit for self-reporting the violation.
2013-02-28 | FERC | NP13-23-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007803 | Settlement Agreement | During a NERC CIP Compliance Spot Check, FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R2. Specifically, FRCC_URE1 failed to demonstrate that it applied access mechanisms at access points to the Electronic Security Perimeter (ESP) that use an access control model that denies access by default, such that explicit access permissions are specified. On the access points at issue, FRCC_URE1 did not specify explicit permissions for different trusted subnets, in violation of R2.1. FRCC_URE1 also failed to enable only ports and services required for normal and emergency operations, in violation of R2.2. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). All of the subnets for which FRCC_URE1 failed to specify permissions were trusted subnets that were either owned and operated by FRCC_URE1's corporate groups or owned and operated by a secure vendor. FRCC_URE1 did not provide access to subnets from any unknown sources or other traffic and indicated that other traffic was denied at all of FRCC_URE1's access points. Access to the subnet owned and secured by FRCC_URE1's energy management system (EMS) vendor was controlled and secured by the entity at all times. FRCC_URE1 also maintained a complete intrusion detection system (IDS) which scanned and protected all network segments and monitored and logged all activities for each of the relevant access points. | when the Standard became mandatory and enforceable to FRCC_URE1 | when FRCC_URE1 updated its risk-based assessment methodology (RBAM) | $8,000 (for FRCC2011007586 and FRCC2011007803) | Spot Check | To mitigate this violation, FRCC_URE1 updated its RBAM to apply risk-based criteria based on CIP Version 4 Standards approved by FERC. Further, FRCC_URE1 updated and corrected its access control list of associated Critical Cyber Assets (CCAs) and access points. The assets within the subject ESPs are no longer classified as CCAs. | 2011-11-21 | 2012-10-23 | Neither Admits nor Denies | FRCC_URE1 had an internal compliance program (ICP), in place at the time of the violation, which FRCC considered to be a mitigating factor in the penalty determination. FRCC considered FRCC_URE1's compliance history a neutral factor in the penalty determination. FRCC_URE1 also corrected deficiencies in its firewall rules, which FRCC considered to be a mitigating factor in the penalty determination.
2013-02-28 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001001; RFC2011001070 | Settlement Agreement | RFC_URE1 self-reported non-compliance with CIP-003-3 R6. RFC_URE1 reported that it did not implement its documented change control process when it replaced its anti-virus software with another anti-virus software on April 19, 2011, in violation of this Standard. (Violation ID:RFC2011001001) RFC_URE1 self-reported one additional instance of noncompliance with CIP-003-3 R6. (Violation ID: RFC2011001070) RFC_URE1 reported that on October 21, 2010, RFC_URE1 installed a firewall into its Electronic Security Perimeter (ESP) without implementing the change management procedures required by CIP-003-3 R6. ReliabilityFirst determined that RFC_URE1 violated CIP-003-3 R6 on two occasions, for a failure to implement its configuration management activities to document the changes it made to its firewall and to its anti-virus software. | CIP-003-3 | R6 | Lower | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors. First, RFC_URE1 has a documented change management procedure in which RFC_URE1 addresses adding, modifying, replacing or removing Critical Cyber Asset (CCA) hardware or software as well as communication, resources, tools, configuration control processes, emergency change process, and roles and responsibilities. Second, the two violations at issue were isolated incidents that do not indicate a systemic compliance issue at RFC_URE1. | when RFC_URE1 installed the firewall into the ESP | when RFC_URE1 implemented its change management process and configuration management activities to document the changes it made to its firewall and anti-virus system | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Self-Report | In accordance with its Mitigation Plan, RFC_URE1 took the following actions: 1) Implemented a communications program to ensure all appropriate departments at RFC_URE1 are aware of any changes to its CCAs; and 2) Trained all relevant staff on its change management procedure for adding, modifying, replacing or removing CCA hardware or software. | 2011-07-07 | 2012-04-20 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-02-28 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001001; RFC2011001070 | Settlement Agreement | RFC_URE1 self-reported non-compliance with CIP-003-3 R6. RFC_URE1 reported that it did not implement its documented change control process when it replaced its anti-virus software with another anti-virus software on April 19, 2011, in violation of this Standard. (Violation ID:RFC2011001001) RFC_URE1 self-reported one additional instance of noncompliance with CIP-003-3 R6. (Violation ID: RFC2011001070) RFC_URE1 reported that on October 21, 2010, RFC_URE1 installed a firewall into its Electronic Security Perimeter (ESP) without implementing the change management procedures required by CIP-003-3 R6. ReliabilityFirst determined that RFC_URE1 violated CIP-003-3 R6 on two occasions, for a failure to implement its configuration management activities to document the changes it made to its firewall and to its anti-virus software. | CIP-003-3 | R6 | Lower | Severe | These violations posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors. First, RFC_URE1 has a documented change management procedure in which RFC_URE1 addresses adding, modifying, replacing or removing Critical Cyber Asset (CCA) hardware or software as well as communication, resources, tools, configuration control processes, emergency change process, and roles and responsibilities. Second, the two violations at issue were isolated incidents that do not indicate a systemic compliance issue at RFC_URE1. | when RFC_URE1 installed the firewall into the ESP | when RFC_URE1 implemented its change management process and configuration management activities to document the changes it made to its firewall and anti-virus system | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Self-Report | In accordance with its Mitigation Plan, RFC_URE1 took the following actions: 1) Implemented a communications program to ensure all appropriate departments at RFC_URE1 are aware of any changes to its CCAs; and 2) Trained all relevant staff on its change management procedure for adding, modifying, replacing or removing CCA hardware or software. | 2011-07-07 | 2012-04-20 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-02-28 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001138 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. As a result of the Compliance Audit, ReliabilityFirst discovered that RFC_URE1 was in violation of CIP-004-3 R2.1. ReliabilityFirst discovered that RFC_URE1 granted two employees unescorted physical access and cyber access to Critical Cyber Assets (CCAs) prior to those employees completing required cyber security training. The two employees at issue included a systems administrator, who worked at the corporate helpdesk, and an executive level employee. ReliabilityFirst determined that RFC_URE1 granted two employees access to CCAs prior to providing those two employees with cyber security training, in violation of CIP-004-3 R2.1. | CIP-004-2; CIP-004-3 | R2.1 | Medium | Severe | ReliabilityFirst and RFC_URE1 agreed and stipulated that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NERC, based on evaluation of the facts and circumstances of this violation and similar violations from other regions, determined that this violation posed a minimal risk to the reliability of the BPS. The risk was mitigated by the following factors. First, both employees at issue underwent personnel risk assessments (PRAs) prior to RFC_URE1 authorizing access to CCAs. The PRAs did not identify any criminal history or issues that would have precluded RFC_URE1 from granting these employees access to CCAs. RFC_URE1 never provided the two employees at issue with the key cards necessary for either of the employees to independently access RFC_URE1's Physical Security Perimeter (PSP). Additionally, neither employee at issue ever entered the PSP without an appropriate escort, nor did either employee use their cyber access to gain access to CCAs during the duration of the violation. | when RFC_URE1 granted the employees access to CCAs | when both employees completed the required training | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 took the following actions: 1) Conducted the required cyber security training for the two employees at issue; 2) Revised its cyber security training procedure to minimize the possibility of RFC_URE1 granting an individual physical or cyber access to CCAs prior to completing the required cyber security training; 3) Notified all staff engaged in managing access to the CCAs the changes made to the documentation relevant to CIP-004 R2 and R3; and 4) Committed to perform periodic self-assessments of its access list to help ensure that only those individuals who have completed cyber security training have been granted access to CCAs. | 2012-05-01 | 2012-07-19 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001139 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. During the Compliance Audit, ReliabilityFirst determined that RFC_URE1 granted an employee unescorted physical access to Critical Cyber Assets (CCAs) prior to completing a personnel risk assessment (PRA) for that employee, in violation of CIP-004-3 R3. The employee at issue is RFC_URE1's manager of Federal Energy Regulatory Commission compliance. | CIP-004-2; CIP-004-3 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, the employee at issue completed the required CIP training prior to RFC_URE1 granting unauthorized unescorted physical access to CCAs. Additionally, when RFC_URE1 completed the PRA for the employee at issue, RFC_URE1 did not discover any criminal history or identity issues that would have precluded RFC_URE1 from granting the employee access to CCAs. Further, RFC_URE1 never provided the employee at issue with a key card necessary for the employee to independently access RFC_URE1's Physical Security Perimeter (PSP). Finally, the employee at issue never physically accessed the PSP without an escort during the duration of the violation. | when RFC_URE1 granted the employee unescorted physical access to CCAs | when RFC_URE1 completed the required PRA for the employee | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 took the following actions: 1) Conducted the PRA for the employee; 2) Revised its cyber security training procedure to minimize the possibility of granting an individual physical or cyber access to CCAs prior to the completion of a PRA; and 3) Notified all staff engaged in managing access to the CCAs the changes made to the documentation relevant to CIP-004 R2 and R3; and 4) Committed to perform periodic self-assessments of its access list to ensure only those individuals who have completed cyber security training and PRAs have access to CCAs. | 2012-06-15 | 2012-07-19 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001140 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. During the Compliance Audit, ReliabilityFirst determined that RFC_URE1 did not include the discovery of all access points to the Electronic Security Perimeter (ESP) or controls for default accounts, passwords, and network management community strings in its cyber vulnerability assessment, in violation of CIP-005-3 R4.3 and R4.4. ReliabilityFirst determined RFC_URE1 cyber vulnerability assessment, which RFC_URE1 did not include evidence demonstrating that RFC_URE1 performed an assessment to determine all access points to the ESP. Additionally, ReliabilityFirst determined RFC_URE1 could not provide evidence that it conducted a review of controls for default accounts, passwords, and network management community strings during its cyber vulnerability assessment. Community strings are passwords for network elements and are used to retrieve data from network elements. | CIP-005-2; CIP-005-3 | R4.3; R4.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although RFC_URE1 did not include a review of all access points to the ESP or controls for default accounts, passwords, and network management community strings, during this violation, RFC_URE1 protected all access points into the ESP with an intrusion prevention system that included logging, alerting, and constant monitoring of all access points. | when RFC_URE1 did not include a review of all access points to the ESP or controls for default accounts, passwords, and network management community strings | when RFC_URE1 completed a cyber vulnerability assessment that included the requirements of the Standard at issue | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 performed a cyber vulnerability assessment that included a review of all access points to the ESP, as well as controls for default accounts, passwords, and network management community strings. RFC_URE1 also updated all documentation relevant to the standard to assure that it is aligned with the requirement and establishes the expectations to maintain a state of compliance. After the documentation was updated, RFC_URE1 notified the changes to all staff that are engaged in managing access to the CCAs. | 2012-06-12 | 2012-08-21 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001144 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. During the Compliance Audit, ReliabilityFirst determined that RFC_URE1 violated CIP-007-3 R5 when it did not manage accounts in a manner that minimizes risk of unauthorized system access pursuant to CIP-007-3 R5 and several of this Standard's subrequirements. First, ReliabilityFirst determined RFC_URE1 was unable to demonstrate it granted access to individual and shared system accounts as well as authorized access permissions consistent with the concept of “need to know” with respect to work functions performed, in violation of CIP-007-3 R5.1. Second, ReliabilityFirst determined RFC_URE1 could not demonstrate it conducted an annual review of all its user accounts and access privileges, in violation of CIP-007-3 R5.1.3. Several individuals had access privileges for which RFC_URE1 had no record of granting access privileges. As a result, RFC_URE1 had not included these individuals in its annual review of all user accounts and access privileges as required by this Standard. Third, ReliabilityFirst determined RFC_URE1 could not demonstrate compliance with CIP-007-3 R5.2 and its subparts. Because RFC_URE1 had several individuals with access privileges for which RFC_URE1 had no record of granting such privileges, RFC_URE1 could not demonstrate it implemented its policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts pursuant to CIP-007-3 R5.2. Fourth, ReliabilityFirst determined RFC_URE1 did not have procedural controls in place to require the use of passwords that consist of alpha, numeric, and “special” characters, in violation of CIP-007-3 R5.3.2. | CIP-007-2a; CIP-007-3 | R5.1; R5.1.3; R5.2; R5.3.2 | Lower/ Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors. First, although unable to demonstrate evidence of compliance with CIP-007-3 R5.1, RFC_URE1 limited individual and shared system accounts and authorized access permissions to only those employees with “need to know” status. Further, while RFC_URE1 did not have procedural controls to enforce the password requirements of CIP-007-3 R5.3.2, RFC_URE1 required and used passwords that consisted of alpha, numeric, and “special” characters during the duration of the violation. | when RFC_URE1 was required to comply with CIP-007-3 R5 | Mitigation Plan completion | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 plans to complete the following actions: 1) Establish a complete list of individuals with access privileges; 2) Determine which Cyber Assets have the capability of complying with the password requirements of CIP-007-3 R5.3; 3) In the event any Cyber Assets cannot comply with the password requirements, RFC_URE1 will submit a Technical Feasibility Exception (TFE) request for the Cyber Asset at issue; 4) Review and modify, if necessary, existing documentation to include a procedure that utilizes the baseline documentation to assure continued compliance with this requirement; 5) Update all documentation relevant to CIP-007 R5 to assure that it is aligned with the requirement and establishes the expectations to maintain a state of compliance; and 6) Communicate updates to all relevant staff. | 2012-10-08 | 2013-01-21 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001146 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. During the Compliance Audit, ReliabilityFirst determined that while RFC_URE1 performed a cyber vulnerability assessment, RFC_URE1 could not demonstrate that it enabled only ports and services required for the operation of the Cyber Assets in its Electronic Security Perimeter (ESP). Specifically, RFC_URE1 included a list of all active ports and services in its cyber vulnerability assessment, but did not provide evidence to verify that RFC_URE1 enabled only ports and services required for the operation of the Cyber Assets within the ESP, in violation of CIP-007-3 R8.2. Also during the Compliance Audit, ReliabilityFirst determined RFC_URE1 did not demonstrate it performed a review of all default accounts as part of the cyber vulnerability assessment. Further, RFC_URE1 did not include evidence that it reviewed controls for default accounts, passwords, and network management community strings in its cyber vulnerability assessment, in violation of CIP-007-3 R8.3. | CIP-007-2a; CIP-007-3 | R8.2; R8.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors. First, during the duration of the instant violation, and where technically feasible, RFC_URE1 enabled monitoring, logging and alerting, as well as anti-virus protections on all Critical Cyber Assets (CCAs) within the ESP. Second, RFC_URE1 protected all access points into the ESP with an intrusion prevention system. This system included logging, alerting, and constant monitoring of all access points during the duration of the instant violation. | when RFC_URE1 was required to comply with CIP-007-3 R8 | when RFC_URE1 determined which ports and services are necessary for the operation of Cyber Assets; enabled only those ports and services; performed a review of its default accounts | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 performed a cyber vulnerability assessment that included a review to verify that it enabled only ports and services required for operation of the Cyber Assets within the ESP, as well as a review of controls for default accounts. RFC_URE1 also updated all documentation relevant to the standard to assure that it is aligned with the requirement and establishes the expectations to maintain a state of compliance. After the documentation was updated, RFC_URE1 notified the changes to all staff that are engaged in managing access to the CCAs. | 2012-06-12 | 2012-08-21 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as a mitigating factor when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001147 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit of RFC_URE1. During the Compliance Audit, ReliabilityFirst determined that RFC_URE1 did not include procedures to characterize and classify events as reportable Cyber Security Incidents in its Cyber Response Plan, in violation of CIP-008-3, R1.1. Also, while RFC_URE1 did include roles and responsibilities of its Cyber Security Incident response team in its Cyber Response Plan, RFC_URE1 did not include other response actions, in violation of CIP-008-3 R1.2. Specifically, ReliabilityFirst determined RFC_URE1 did not demonstrate how the communication plan it presented during the Compliance Audit was triggered, executed, or related to its Cyber Response Plan. | CIP-008-2; CIP-008-3 | R1.1; R1.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors. First, RFC_URE1 has a documented Cyber Response Plan that includes examples of potential incidents and categorization of the severity of such incidents. Second, prior to the discovery of the instant violation, RFC_URE1 performed a tabletop test of its response process, which resulted in the successful characterization of an event and the notification of proper individuals. | when RFC_URE1 was required to comply with this Standard | when RFC_URE1 revised its Cyber Response Plan | $40,000 (for RFC2011001001, RFC2011001070, RFC2011001138, RFC2011001139, RFC2011001140, RFC2011001144, RFC2011001146, and RFC2011001147) | Compliance Audit | In accordance with its Mitigation Plan, RFC_URE1 updated its Cyber Response Plan to include the following: 1) procedures to characterize and classify events as reportable Cyber Security Incidents; and 2) a communication response plan. | 2012-06-29 | 2012-10-12 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE1's internal compliance program (ICP) as mitigating when determining the penalty amount.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001125 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007 R6. When RFC_URE2 installed its new log monitoring system, a subset of the devices were not properly configured to send logs to the monitoring system or capture the logs from all devices. RFC_URE2 uses a security monitoring tool for network device to store and monitor the access logs for all electronic access control and monitoring access points and network switches. RFC_URE2 also uses the system to provide alerts for security events RFC_URE2 analyzes to determine if there is a Cyber Security Incident. RFC_URE2 failed to configure two Cyber Assets within an Electronic Security Perimeter (ESP), and one Cyber Asset within another ESP (a backup for the Newark facility) to send their logs to a security monitoring tool for network device. As a result, RFC_URE2 failed to ensure that these Cyber Assets issued automated or manual alerts for detected Cyber Security Incidents (R6.2), and failed to maintain (R6.3), retain (R6.4), and review (R6.5) these logs. RFC_URE2 also failed to configure 17 switches within 16 of its ESPs to send logging information to a security monitoring tool for network device. These switches were sending their information to a server which maintained the logs and retained them for ninety calendar days. As a result, RFC_URE2 failed to ensure that these Cyber Assets issued automated or manual alerts for detected Cyber Security Incidents (R6.2) and failed to review logs of system events related to cybersecurity and to maintain records documenting review of logs (R6.5). | CIP-007-2a | R6; R6.2; R6.3; R6.4; R6.5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors. The corporate monitoring system logged and monitored the traffic to and from the ESPs containing Cyber Assets at two ESPs. Since this was the case, while the corporate log server did not monitor or alarm for attempts to log into the Cyber Assets directly, the corporate monitoring system monitored and alarmed for any attempts to access the ESPs and the devices within them. The corporate log server retained the logs for more than ninety days. Regarding the 17 network switches, the server to which the logs were being sent retained the logs for ninety calendar days, although the server did not provide alerting. In addition, RFC_URE2 restricts electronic access to the network switches for the purpose of managing or configuring the switch. Any unauthorized logical access attempt would require an attacker to first pass through the access point to the ESP or have direct physical access to the device. RFC_URE2's configuration management system monitors any configuration changes. This system was functional during the violation, and no unauthorized changes to the configurations occurred. The foregoing decreases the likelihood of successful unauthorized access. Fourteen of the 17 network switches operate as Open System Interconnection Layer 2 switches, which only function to provide pass-through communications, reducing the likelihood that compromising these switches would affect the system beyond the local area network. Furthermore, the protections provided to the Critical Cyber Assets within the ESPs were not compromised during the violation. The access point protections were operational and did not permit unauthorized traffic into the ESP. | when RFC_URE2 installed new devices | when RFC_URE2 configured all missed devices to send security and event logs to the log monitoring system | 0 | Self-Report | To mitigate this violation, RFC_URE2 : 1) Reviewed all devices that either formed the ESPs or were contained with the ESPs; 2) Configured the individual devices to create logs and send them to the log monitoring system; 3) Ensured the viability of the communications between the reporting devices and the log monitoring system; 4) Configured the log monitoring system to receive the logs; 5) Configured the configuration management system to report all deviations in the device configurations that would disrupt the delivery of logs to the log management system; and 6) Configured all devices to create periodic test log entries to ensure that the log management system is capturing logs from all devices. | 2011-10-28 | 2012-12-26 | Admits | ReliabilityFirst considered certain aspects of the RFC_URE2's internal compliance program (ICP) as mitigating factors. ReliabilityFirst considered that the violation concerns RFC_URE2's logging procedures. ReliabilityFirst also considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE2 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, and imposed a zero dollar penalty for the violation.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012001321 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-006-3c R2. RFC_URE2 utilizes net controllers to control access to the information technology (IT) data center and electric system operations center racks located in the IT data center. Net controllers are proprietary physical devices that are part of the badge access system to control access to doors. When an individual presents a badge at the badge reader, a local database in the net controller is checked to verify whether it should grant access. The badge reader communicates with the net controller through a serial connection, and if the identity of the person presenting the badge matches with an approved person in the local net controller database, it then grants access. The net controller also communicates with a remote server using an IP protocol for updates to its local database. In its Mitigation Plan for a previous violation of CIP-006-1 R5, regarding a malfunctioning badge access system, RFC_URE2 committed to designating and protecting the net controllers as Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP). RFC_URE2 connected the badge access system for the electric system operations center racks located in the IT data center to a net controller that was not protected as a Cyber Asset. Once RFC_URE2 connected the badge access system to this net controller, this net controller became a Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter. RFC_URE2, however, had not afforded the requisite protections to this net controller. Specifically, RFC_URE2 failed to afford the protections of CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3c R5 and CIP-007-3 R6 and R8. | CIP-006-3c | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors. RFC_URE2 provided the protections of CIP-003-3, CIP-007-3 R2, R3, R4, R5, and R7, CIP-008-3, and CIP-009-3 for the net controller. The net controller is physically located inside the IT data center which is staffed 24-hours a day. RFC_URE2 restricts entry to the IT data center through a biometric man trap and badge access control system. The electric system operations center racks are located in the IT data center and are monitored by video. RFC_URE2 monitors and logs access to the Critical Cyber Assets located within the racks. In addition, the racks are protected using magnetic locks and a badge access system. Furthermore, a firewall continuously electronically protects the net controller and segregates the net controller from the general network. Only a limited number of IT associates with background checking have logical access to the firewall. | when RFC_URE2 installed the net controllers | when RFC_URE2 installed and commissioned a new net controller | 0 | Self-Report | To mitigate this violation, RFC_URE2: 1) Installed a new net controller as part of the RFC_URE2 NERC CIP physical security access system to control access to the electric system operations center racks in the IT data center; and 2) Conducted a review of all other net controllers protecting CIP environments to determine if they were protected by the appropriate measures. The review determined that all installed net controllers had the appropriate protections. | 2012-05-11 | 2012-12-27 | Admits | ReliabilityFirst considered certain aspects of the RFC_URE2's internal compliance program (ICP) as mitigating factors. ReliabilityFirst considered that the violation concerns RFC_URE2's logging procedures. ReliabilityFirst also considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE2 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, and imposed a zero dollar penalty for the violation.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010101 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-005-3a R5. RFC_URE2 utilizes two security monitoring tools for network devices to simultaneously log the events from its Cyber Assets within the Electronic Security Perimeter (ESP), Cyber Assets used in access control and/or monitoring of the ESPs, and access points to the ESP. RFC_URE2 configured numerous additional devices to send their events to the security monitoring tool for network devices. The quantity of logs was greater than what RFC_URE2 expected due to the amount of devices installed, and, as a result, some of the logs were overwritten to make space for the new log messages. RFC_URE2 discovered that only 81 days of logs were available on 12 access points to the ESPs, 14 Cyber Assets within the ESP, and 2 Cyber Assets used in access control and/or monitoring of the ESPs. | CIP-005-3a | R5 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors: 1) Nine days of logs were missing for two months; 2) The security logs were alerting properly; 3) RFC_URE2 monitored the security logs daily during the time period of the violation; and 4) RFC_URE2 moved quickly to mitigate the violation. | when RFC_URE2 did not retain logs for 90 calendar days | when RFC_URE2 retained 90 calendar days of logs | 0 | Self-Report | To mitigate this violation, RFC_URE2: 1) Configured the log monitoring system to archive logs to external storage on a daily basis; 2) Manually extracted all available online logs to the external storage location; and 3) Ensured that the revised configuration was accumulating 90 days of logs. | 2012-03-29 | 2012-12-28 | Admits | ReliabilityFirst considered certain aspects of the RFC_URE2's internal compliance program (ICP) as mitigating factors. ReliabilityFirst considered that the violation concerns RFC_URE2's logging procedures. ReliabilityFirst also considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE2 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, and imposed a zero dollar penalty for the violation.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010419 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-3 R6. In the Self-Report, RFC_URE2 also identified a violation of CIP-005-3a R3. Subsequently, RFC_URE2 self-certified that it was non-compliant with CIP-005-3a R3. When RFC_URE2 installed its new log monitoring system, a subset of the devices was not properly configured to send logs to the monitoring system or to capture the logs from all devices. RFC_URE2 uses a security monitoring tool for network device to store and monitor the access logs for Electronic Access and Monitoring (EACM) access points and network switches within the Electronic Security Perimeter (ESP). RFC_URE2 failed to configure one access point for the switching station ESP to send logging information to the security monitoring tool for network device. The Cyber Asset was sending its information to a server as well as to two inactive devices instead of sending it to the security monitoring tool for network device. The server maintained the logs and retained them for 90 calendar days. As a result, RFC_URE2 failed to ensure that this access point detected and alerted for attempts at or actual unauthorized access at least every 90 calendar days. RFC_URE2 also failed to review logs where alerting personnel was not feasible. | CIP-005-2a | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors. The server to which the logs were being sent retained the logs for 90 calendar days, although the server did not provide alerting. In addition, there are ten Critical Cyber Assets at the switching station, including eight remote terminal units (RTUs). One of the Critical Cyber Assets, a separate front-end device that connects the RTU devices to the network, creates and retains logs for attempts to gain access to the RTUs or attempts for unauthorized access. The eight RTUs are the only devices behind the front-end device, and as a result, the RTUs are situated on a private subnet behind the front-end device. The communication ports for the RTUs are not directly accessible from any other network, including the network used to communicate with the energy management system. Furthermore, the protections provided to the Critical Cyber Assets within the ESPs were not compromised during the violation. The access point protections were operational and did not permit unauthorized traffic into the ESP. The 10 devices are located within a Physical Security Perimeter for which RFC_URE2 utilizes electronic badging to permit or deny entry. | when RFC_URE2 installed the new device | when RFC_URE2 configured all missed devices to send security and event logs to the log monitoring system | 0 | Self-Report | To mitigate this violation, RFC_URE2: 1) Reviewed all devices that either formed the ESPs or were contained within the ESPs; 2) Configured the individual devices to create logs and send them to the log monitoring system; 3) Ensured the viability of the communications between the reporting devices and the log monitoring system; 4) Configured the log monitoring system to receive the logs; 5) Configured the configuration management system to report all deviations in the device configurations that would disrupt the delivery of logs to the log management system; and 6) Configured all devices to create periodic test log entries to ensure that the log management system is capturing logs from all devices. | 2011-10-28 | 2012-12-26 | Admits | ReliabilityFirst considered certain aspects of the RFC_URE2's internal compliance program (ICP) as mitigating factors. ReliabilityFirst considered that the violation concerns RFC_URE2's logging procedures. ReliabilityFirst also considered that it discovered the violation through a Self-Report and applied mitigating credit. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by registered entities. RFC_URE2 promptly identified and reported the violation due to the effective execution of its ICP and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, and imposed a zero dollar penalty for the violation.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100866 | Settlement Agreement | RFC_URE3 self-certified non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE3 determined that they had not outfitted their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE3 had not outfitted the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system which RFC_URE3 has been assigned the responsibility to operate and maintain in compliance with NERC CIP Standards. The Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE3 do not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE3 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE3 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE3 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, RFC_URE3 monitored the operational status of the Panels in its systems network operations center. | when the Standard became mandatory and enforceable to RFC_URE3 | when RFC_URE3 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE3 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE3 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into RFC_URE3 recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE3's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201100867 | Settlement Agreement | RFC_URE4 self-certified non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE4 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE4 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system which RFC_URE4 has been assigned the responsibility to operate and maintain in compliance with NERC CIP Standards. The Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE4 does not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE4 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for which it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE4 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE4 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE4 | when RFC_URE4 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE4 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE4 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE4's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100868 | Settlement Agreement | RFC_URE5 self-certified non-compliance with Reliability Standard CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE5 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c, R2.2. Specifically, RFC_URE5 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. RFC_URE5 replaced the Panels used in CIP related areas and replaced them with the Panels used by other entities. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system for RFC_URE5. The Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE5 does not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE5 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for which it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE5 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE5 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE5 | when RFC_URE5 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE5 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE5 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE5's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC201100869 | Settlement Agreement | RFC_URE6 self-certified non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE6 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE6 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. RFC_URE6 replaced the Panels used in CIP related areas and replaced them with the Panels used by other entities. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system for RFC_URE6. The Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE6 does not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE6 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for which it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE6 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE6 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE6 | when RFC_URE6 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE6 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE6 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE6's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC201100870 | Settlement Agreement | RFC_URE7 self-certified non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE7 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE7 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. RFC_URE7 replaced the Panels in CIP related areas and replaced them with the Panels used by other entities. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective Responsible Entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system for RFC_URE7. Therefore, the Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE7 does not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE7 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for which it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE7 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE7 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE7 | when RFC_URE7 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE7 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE7 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE7's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC201100871 | Settlement Agreement | RFC_URE8 self-certified non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE8 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE8 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. RFC_URE8 replaced the Panels used in CIP related areas and replaced them with the Panels used by other entities. The Panels serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system for RFC_URE8. Therefore, the Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE8 do not use the Panels to permanently retain log records of access. The number of Panels varied from an initial low of 22 to a high of 62 over the violation period. RFC_URE8 must be able to demonstrate individual compliance with CIP-006-3c R2.2 based on the respective functions for which it is registered on the NERC Compliance Registry. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE8 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE8 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE8 | when RFC_URE8 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE8 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE8 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE8's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2012009861 | Settlement Agreement | RFC_URE9 self-certified or self-reported non-compliance with CIP-006-3c R2.2 to ReliabilityFirst. RFC_URE9 determined that they had not afforded their remote security system panels (Panels) with the protective measures required by CIP-006-3c R2.2. Specifically, RFC_URE9 had not afforded the Panels the protective measures that authorize and/or log access to physical security perimeters (PSPs), as prescribed in CIP-003-3 R6, CIP-007-3, and CIP-009-3. RFC_URE9 previously used Panels that, although from a different manufacturer than the Panels used by other entities, functionally operated in a similar manner. RFC_URE9 replaced the Panels used in CIP related areas and replaced them with the Panels used by each of the other entities. The Panels, serve as intermediary devices that convert and communicate programmed instructions from centralized servers to the respective entity’s physical security access devices as part of the authorization process necessary to gain access to the PSPs. The Panels are part of an overall security system for RFC_URE9. The Panels qualify as Cyber Assets that authorize access to PSPs and should have received the protective measures described in CIP-006-3 R2.2. The Panels have limited storage capability, but RFC_URE9 does not use the Panels to permanently retain log records of access. | CIP-006-3c | R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. RFC_URE9 afforded the Panels with the protective measures specified by CIP-003-3 (with the exception of R6), CIP-004-3 R3, CIP-005-3 R2 and R3, CIP-006-3 R4 and R5, and CIP-008-3. Additionally, the Panels were within PSPs during the duration of the violations. Further, RFC_URE9 stored the Panels in locked or key carded cabinets with tamper alarms. Only CIP qualified personnel (those with CIP training and personnel risk assessments (PRAs) or individuals escorted by CIP qualified personnel) had access to the Panels. Finally, the operational status of the Panels in its systems network operations center were monitored. | when the Standard became mandatory and enforceable to RFC_URE9 | when RFC_URE9 afforded its Panels with all of the protective measures required by CIP-006-3c R2.2 | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Certification | RFC_URE9 submitted a Mitigation Plan to address the violations of CIP-006-3 R2.2. RFC_URE9 completed the following mitigating actions: 1) Established and implemented a change control and configuration management process for the Panels per CIP-003 R6; 2) Completed Panel testing and associated documentation per CIP-007 R1; 3) Completed records and documentation per CIP-007 R2 and submitted the appropriate technical feasibility exception requests for the Panels per CIP-007 R4, R5 and R6; 4) Performed and documented vulnerability assessments on the Panels per CIP-007 R8; 5) Integrated fully the Panels into recovery plans per CIP-009 R1, R2, R3, R4 and R5; and 6) Replaced its existing Panels with a new upgraded model that includes upgraded security features. | 2012-12-31 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE9's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2012001323 | Settlement Agreement | RFC_URE7 self-reported possible non-compliance with CIP-007-3 R6 to ReliabilityFirst. RFC_URE7 discovered that it had not configured the security monitoring controls on one Critical Cyber Asset (CCA) to issue automated or manual alerts for detected Cyber Security Incidents. The CCA at issue was a Microsoft Windows server that RFC_URE7 uses to collect standard Windows event logs, such as application, system, and security, from other Windows servers at RFC_URE7. As a result of RFC_URE7's not properly configuring the CCA, one local interactive Windows account for this device could not automatically alert for detected Cyber Security Incidents. RFC_URE7 also did not have security monitoring controls in place for this CCA to provide manual alerts for detected Cyber Security Incidents. Further, RFC_URE7 did not review logs of system events related to the CCA at issue or maintain records documenting review of such logs until it discovered the possible violation of CIP-007-3 R6. RFC_URE7 reviewed local server and Windows Domain Control logs and found no evidence of system events associated with the CCA at issue during the duration of the violation. Upon discovery of the violation, RFC_URE7 manually reviewed the 90 days of logs available, but could not recover any logs older than 90 days. RFC_URE7 did not identify any Cyber Security Incidents from the manual review of the available logs. | CIP-007-3 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The CCA at issue does not provide control capability for the BPS. Further, the CCA does not contain any data that could compromise or adversely affect the BPS. | when the Standard became mandatory and enforceable to RFC_URE7 | when RFC_URE7 configured the affected CCA to issue automated alerts for detected Cyber Security Incidents pursuant to CIP-007-3 R6.2) | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Report | In its Self-Report, RFC_URE7 described the mitigating actions it took to address the violation of CIP-007-3 R6. RFC_URE7 configured the CCA at issue to automatically alert for detected Cyber Security Incidents. Additionally, RFC_URE7 implemented supplemental control processes to ensure that logging and monitoring configurations are completed when a device is put in service. Finally, RFC_URE7 implemented an additional daily control process to verify CIP devices are properly configured for logging and monitoring. | 2011-07-29 | 2012-09-04 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE7's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009852 | Settlement Agreement | RFC_URE3 self-reported possible non-compliance with CIP-004-3 R4 to ReliabilityFirst. RFC_URE3 added an employee (Employee 1), for whom it had not granted access rights, to the list of personnel with authorized unescorted physical access rights to one Physical Security Perimeter (PSP). Additionally, RFC_URE3 did not revoke the unescorted physical access rights of another employee (Employee 2) who no longer required such access within seven calendar days. Specifically, Employee 2 resigned on August 4, 2011, but RFC_URE3 did not revoke Employee 2’s access rights until September 14, 2011. | CIP-004-3 | R4 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. Employee 1 completed CIP training and had a current personnel risk assessment prior to RFC_URE3 adding Employee 1 to its access list. Therefore, Employee 1 satisfied all the requirements for unescorted physical access to the PSP except an official grant of access by RFC_URE3. Also, RFC_URE3 collected Employee 2’s access badge on the date of Employee 2’s resignation. Therefore Employee 2 did not have the ability to physically access any RFC_URE3 PSPs during the duration of the violation. Further, Employee 2 did not have electronic access to any Critical Cyber Assets prior to, or following, Employee 2’s resignation. | when RFC_URE3 should have removed Employee 2 from its access list when RFC_URE3 should have removed Employee 1 from the access list | when RFC_URE3 revoked Employee 2's unescorted physical access rights when RFC_URE3 revoked Employee 1's unescorted physical access rights | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Report | RFC_URE3 certified that it completed all necessary mitigating activities associated with the violation of CIP-004-3 R4. Upon discovery of the violation, RFC_URE3 revoked Employee 1 and Employee 2’s access rights. Additionally, RFC_URE3 provided the individuals responsible for the violations with refresher training on properly granting access rights as well as feedback on improving performance. | 2011-10-18 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE3's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2012009907 | Settlement Agreement | RFC_URE8 self-reported two occasions of possible non-compliance with CIP-004-3 R4 to ReliabilityFirst. First, RFC_URE8 added an employee (Employee 1) who had not completed CIP training to the list of personnel with unescorted physical access rights to the Physical Security Perimeters (PSPs) at two generation plants. Security personnel attempted to add a different employee to the list of individuals with unescorted physical access rights, but inadvertently added Employee 1’s name to the list due to Employee 1’s similar name to that of the intended employee. Specifically, Employee 1 and the intended employee have the same first and last name, but Employee 1 has the suffix “Junior” while the intended employee has the suffix “Senior.” The intended employee and Employee 1 are related. Second, on RFC_URE8 added an employee (Employee 2) who had not completed CIP training to the list of personnel with authorized unescorted physical access to three generation plant PSPs. | CIP-004-3 | R4 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. Employee 1 and Employee 2 both had current personnel risk assessments prior to RFC_URE8 adding Employee 1 and Employee 2 to the respective access lists. Additionally, during the duration of the violation, neither Employee 1 nor Employee 2 attempted to access the PSPs to which RFC_URE8 granted them access. | when RFC_URE8 added Employee 1 to its access list when RFC_URE8 added Employee 2 to the list of personnel with authorized unescorted physical access to PSPs | when RFC_URE8 removed Employee 1 from its access list when RFC_URE8 removed Employee 2 from its access list to three generation plant PSPs | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Report | In its Self-Report, RFC_URE8 described the mitigating actions it took to address the violation of CIP-004-3 R4. Upon discovery of the violation, RFC_URE8 revoked Employee 1 and Employee 2’s access rights. Additionally, RFC_URE8 provided the individuals responsible for the violations with additional training on properly granting access as well as feedback on improving performance. | 2012-01-22 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE8's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009859 | Settlement Agreement | RFC_URE3 self-reported possible non-compliance with the CIP-006-3c R1 to ReliabilityFirst. RFC_URE3 self-reported possible non-compliance with CIP-006-3c R1 when it discovered it had not properly logged access to physical security perimeters (PSPs) at a single facility. Specifically, RFC_URE3 logged visitor access to a facility which contained several PSPs, but did not log visitor access to the individual PSPs within the facility pursuant to CIP-006-3c R1. The PSPs at issue protected non-dispatcher energy management system (EMS) workstations. The EMS workstations were used for management oversight, IT support, and distribution operations. RFC_URE3 provided evidence of additional occurrences of possible non-compliance with CIP-006-3c R1. ReliabilityFirst determined the additional information expanded the scope of RFC_URE3's self-reported violation of CIP-006-3c R1 and was nota new possible violation. RFC_URE3 stated that two employees (Employee 1 and Employee 2) inappropriately used physical access controls and were unescorted in the PSP for approximately three minutes in violation of CIP-006-3c R1.4 and R1.6. Specifically, Employee 1 and Employee 2 used a key to enter a PSP for which neither had received authorization from RFC_URE3 and were unescorted in the PSP until security personnel arrived and escorted them out of the PSP. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. Although RFC_URE3 did not properly log access to each specific PSP in the facility at issue, RFC_URE3 did log access for all visitors into and out of the facility which housed the PSPs . Further, all visitors were continuously escorted by a qualified and approved RFC_URE3 employee while inside the PSPs during the duration of the violation. Also, Employee 1 and Employee 2 completed CIP training and received personnel risk assessments prior to entering the specific PSP at issue. RFC_URE3 granted Employee 1 and Employee 2 access to other PSPs within the same facility prior to the violation. Upon using the key to enter the PSP, an alarm alerted RFC_URE3 security personnel that someone had bypassed the normal entry procedure. RFC_URE3 security personnel located Employee 1 and Employee 2 and escorted them out of the PSP within approximately three minutes. | when RFC_URE3 first did not properly log access to its PSPs at the facility at issue | when RFC_URE3 first did not continuously escort a contractor while inside the PSP | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Report | RFC_URE3 submitted its Mitigation Plan to address its alleged violation of CIP-006-3c, R1 to ReliabilityFirst. To mitigate the violation of CIP-006-3c R1.4 RFC_URE3 established a more stringent key control policy at facility where the PSP is located that limits access and use of the key. Specifically, the key control policy allows only a supervisor to have possession of a key and the use of the key is restricted to emergency situations and requires notification of the RFC_URE3 control center prior to use of the key. To mitigate the violation of CIP-006-3c R1.6, RFC_URE3 implemented a new electronic logging system that electronically logs the entrance and exit of each visitor to individual PSPs within the facility. The electronic logging is performed by a security officer or a designee authorized by RFC_URE3's corporate physical security. RFC_URE3 continues to investigate the arrangement of individual PSPs within the facility and will determine whether to rearrange and/or consolidate PSPs in order to reduce the administrative burden of logging movements of visitors among separate PSPs within the facility. | 2012-11-07 | 2013-01-30 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE3's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012009860 | Settlement Agreement | RFC_URE4 self-reported possible non-compliance with CIP-006-3c R1 to ReliabilityFirst. Specifically, RFC_URE4 discovered that in one instance, it did not continuously escort a contractor while inside a physical security perimeter (PSP). The PSP at issue contained two Critical Cyber Assets (CCAs), a dial-up device and a network and data communications device. RFC_URE4 also did not properly log the contractor’s access to the PSP. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. Prior to the violation, RFC_URE4 completed a personnel risk assessment for the contractor which revealed no criminal or identity issues. Also, RFC_URE4 did provide an escort for the contractor who, although not continuously escorting the contractor, remained in the proximity of the contractor and periodically observed the contractor during the duration of the violation. | when RFC_URE4 did not continuously escort a contractor while inside the Physical Security Perimeter (PSP) | when RFC_URE4 did not continuously escort a contractor while inside the PSP | $0 (for RFC201100866, RFC201100867, RFC201100868, RFC201100869, RFC201100870, RFC201100871, RFC2012001323, RFC2012009852, RFC2012009859, RFC2012009860, RFC2012009861, and RFC2012009907) | Self-Report | RFC_URE4 described the mitigating actions it took to address the violation of CIP-006-3c R1.6. RFC_URE4 conducted refresher training with the individual responsible for the violation. Specifically, RFC_URE4 emphasized its Corporate Policy on visitors which states the escort must keep the visitor within sight at all times except when the visitor is in the lavatory. RFC_URE4 also emphasized the need to document the entry and exit of visitors. | 2011-12-20 | 2012-08-27 | Neither Admits nor Denies | ReliabilityFirst favorably considered certain aspects of RFC_URE4's compliance program as a mitigating factor in the penalty assessment. ReliabilityFirst considers the fact that entity self-reported six of the violations described in this Agreement as a mitigating factor. ReliabilityFirst also considered that the discovery of all these violations was not prompted by any intervention on the part of ReliabilityFirst. ReliabilityFirst encourages such self-assessment and self-disclosure because these behaviors assist ReliabilityFirst in carrying out its mission to preserve and protect the reliability of the BPS. Taking all the facts and circumstances, as well as aggravating and mitigating factors into consideration, ReliabilityFirst determined a zero dollar penalty was appropriate.
2013-01-31 | FERC | NP13-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010776 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-3a R1.5. WECC_URE1 discovered that it had failed to assess available patches as described in CIP-007-3 R3 and required by CIP-005-3a R1.5. The following devices, which encompass the scope of the equipment affected in this violation, were located in two of WECC_URE1's control centers: 1) Three servers which are authentication devices used for access, control and monitoring (ACM); 2) Three RSA SecurID two factor authentication (RSA) appliances used for ACM; and 3) Four firewalls access points used for ACM. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 assessed the potential impact to the BPS as minimal because all network devices in scope are protected from unauthorized physical access behind Physical Security Perimeters and unauthorized access attempts would have triggered alarms alerting personnel. Authorized access to these devices is limited to a very small group comprised of five individuals who all completed Personnel Risk Assessments and CIP training. Also, all electronic access was controlled, logged and monitored. In addition, out of 25 requirements, WECC_URE1 only failed to meet one. All other CIP requirements were met for these devices. | when WECC_URE1 should have begun assessing the devices in scope for available patches | Mitigation Plan completion | 10000 | Self-Report | In accordance with its Mitigation Plan, a WECC_URE1 team assessed posted security patches for the network devices that were in production within the Energy Management System environment, as well as the RSA and server devices located in the energy network. Once the assessments were complete, the team began upgrading the control center devices first, with new security patches where applicable. Once that was complete, WECC_URE1's Information Technology security scanned each device to document its security posture. The same process was applied to the other control center devices at issue. WECC_URE1 also conducted training for all applicable personnel to reinforce familiarity with its patch management process. | 2012-08-31 | 2012-10-08 | Does Not Contest | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it a mitigating factor during the penalty determination.
2013-01-31 | FERC | NP13-23-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102933 | Settlement Agreement | WECC conducted a Compliance Audit of WECC_URE2. WECC determined that WECC_URE2 was in violation of CIP-002-3 R1 because its Critical Asset identification methodology (Methodology) did not include a risk-based assessment component. WECC_URE2 created the Methodology and associated documentation, which included a statement that WECC_URE2 subject matter experts (SMEs) would apply the Methodology to WECC_URE2's list of assets. WECC_URE2 created this Methodology based on threshold values drawn from CIP-002-4 and NERC's Security Guideline for the Electricity Sector on Identifying Critical Assets (dated November 19, 2009). However, WECC determined that WECC_URE2's Methodology did not identify the specific factors that WECC_URE2's SMEs should consider as they applied the criteria set forth in the Methodology. WECC_URE2's previous asset identification methodology demonstrated compliance with CIP-002 R1. | CIP-002-3 | R1; R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE2's noncompliance could have resulted in misidentified or unidentified Critical Assets and over-reporting, under-reporting, or misreporting of associated Critical Cyber Assets (CCAs). Furthermore, given the cross-cutting nature of networked technology, malicious attack or intentional or unintentional misuse may impact multiple assets at once. Therefore, failure to identify, protect, and secure CCAs and Critical Assets may pose a risk and jeopardize BPS reliability by rendering one or a number of Critical Assets vulnerable to misuse or malicious attack. However, WECC_URE2's corporate security policy provides protections that constitute compensating measures, thereby reducing the risk to the BPS. WECC_URE2's corporate security program includes maintaining security staff, overseeing physical facility protections, and responding to alarms. Additionally, the risk was mitigated by the fact that WECC_URE2 based its Methodology on criteria developed in support of Version 4 of the CIP Reliability Standards (i.e., expertise on the Standards drafting team and vetted and pooled industry comment and knowledge), and approved by both NERC and FERC. Furthermore, although application of WECC_URE2's Methodology ultimately reduced WECC_URE2's list of Critical Assets and list of associated CCAs, WECC_URE2 did not remove existing CIP-003 through CIP-009 protections from the assets that were not identified by application of the Methodology. Finally, WECC_URE2's Methodology explicitly states that WECC_URE2 SMEs are to apply WECC_URE2's criteria to WECC_URE2's asset lists. In practice, WECC_URE2 accomplishes this by reviewing its assets and criteria in meetings with SMEs responsible for and knowledgeable about WECC_URE2's system. | when WECC_URE2 modified its Methodology in a manner that did not comply with CIP-002-3 R1.1 | Mitigation Plan completion | 15000 | Compliance Audit | To mitigate this violation, WECC_URE2 updated its risk-based assessment methodology to include clearer, more specific documentation requirements for its annual execution and update. | 2012-09-04 | 2012-10-05 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP), which was in place at the time of the violation, and determined it to be a mitigating factor in the penalty determination.
2013-01-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100435 | Settlement Agreement | FRCC_URE1 self-reported that it had failed to identify the workstations configured for security badging as physical access control systems. This failure was a violation of CIP-006-1 R1.8, which requires a Responsible Entity to apply protective measures of various CIP-002 through CIP-009 requirements to Cyber Assets. These workstations included a device that is used to access the physical access control server and monitor physical access control activities. | CIP-006-1 | R1.8 | Lower | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Even though the systems were not identified, FRCC_URE1 maintained hardened systems that were maintained with updated security patches, protected access to only required personnel and included malware protection. All of these systems were physically protected for unauthorized access as they were in the security control center that is manned 24 hours a day, seven days a week. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Self-Report | FRCC_URE1 has completed a Mitigation Plan by updating the physical access control system list, reviewing the implementation of thick client, updating the physical security plan and verifying compliance for CIP-006 R1.8. | 2011-09-09 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty. FRCC determined that FRCC_URE1's compliance history should not serve as a basis for aggravating the penalty.
2013-01-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100436 | Settlement Agreement | FRCC_URE1 self-reported that it had failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) only enabled ports and services required for normal and emergency operations. FRCC_URE1's specific workstations, listed/identified as Cyber Assets within the ESP with connectivity to production servers, did not restrict all ports to only those required for normal or emergency operations, as required by CIP-007-1 R2. Further, sampled workstations had services enabled that were not required for normal operations of the subject Cyber Asset. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the workstations for which the required ports were not identified are Cyber Assets that reside within the ESP, the virtual local area network (VLAN) configurations limited the exposure from internet or other untrusted sources. FRCC_URE1's VLAN configuration limited access between the identified workstations and the servers and further, the servers were allowed to communicate with the production server for application upgrades only and no client communication was allowed to production servers from the subject environment. Further, the entity had blocked all interactive ports, thereby limiting any outside exposure from untrusted sources. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Self-Report | FRCC_URE1 completed a Mitigation Plan including documentation of required ports and services for each Cyber Asset and disabled all ports and services that were not required for normal and emergency operations. | 2012-07-31 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty. FRCC determined that FRCC_URE1's compliance history should not serve as a basis for aggravating the penalty.
2013-01-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007516 | Settlement Agreement | During a NERC CIP Compliance Audit, it was determined that FRCC_URE1 failed to demonstrate it had only enabled the ports and services required for operations and for access control and monitoring of the Electronic Security Perimeter (ESP). FRCC_URE1 enabled web services on its access points to the ESP when it was not operationally required. FRCC_URE1 did not limit only ports required by Cyber Assets that communicate outside the ESP. All of these assets communicate to trusted devices outside the ESP, but configuration does not specify only the required ports (R2.2). Further, FRCC_URE1 neither implemented strong authentication controls at the access points (R2.4) nor documented the content of the banner that was implemented at the access points for all remote interactive access. All access points had banners implemented, but the banner content was different from the content that was documented by the entity (R2.6). | CIP-005-1 | R2; R2.2; R2.4; R2.6 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the services were enabled on the access points allowing possible access to protocol configuration services, such access was limited to certain devices for which addresses were specified, and remote access was limited and controlled using a jump-host implemented in the perimeter network. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Compliance Audit | FRCC_URE1 completed a Mitigation Plan including: steps for reviewing required ports; disabling a certain software service on the access points; review of ports/services on covered assets; validation of permitted ports/services on covered assets; implementation of recommended process changes to ports/services review process; deployment of two-factor authentication for remote logical access and documentation; and implementation of standardized banner content in FRCC_URE1's cybersecurity policy. | 2012-07-31 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2013-01-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007518 | Settlement Agreement | During a NERC CIP Compliance Audit, it was determined that FRCC_URE1 failed to demonstrate that its cyber vulnerability assessment (CVA) included an assessment to review that only ports and services required for operations at the access points were enabled (R4.2). Further, the assessment did not document the discovery of all access points to all Electronic Security Perimeters (ESPs) (R4.3), and the vulnerability assessment did not document the review of controls for default accounts, passwords, and network management community strings (R4.4). | CIP-005-1 | R4; R4.2; R4.3; R4.4 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Completing the vulnerability assessment would assist the entity in minimizing the impact of open vulnerabilities. The risk was not serious or substantial because FRCC_URE1 completed a CVA but only failed to document the results in a manner that would demonstrate compliance with all the subrequirements. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Compliance Audit | FRCC_URE1 completed a Mitigation Plan including steps for updating the CVA process and scope to include steps for verification of compliance with all the subrequirements. FRCC_URE1 conducted a fresh CVA and verified that all CVA requirements are met and documented in the reports, including the action plan and status for the identified vulnerabilities. | 2011-11-04 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2013-01-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007519 | Settlement Agreement | During a NERC CIP Compliance Audit, it was determined that FRCC_URE1 failed to demonstrate that FRCC_URE1 reviewed, at least annually, all its user accounts to verify that access privileges are in accordance with Standard CIP-003-3 R5 and Standard CIP-004-3 R4 (R5.1.3). FRCC also determined that FRCC_URE1's documents were insufficient to demonstrate it had identified those individuals with access to all the shared accounts for the Cyber Assets within the Electronic Security Perimeter. FRCC_URE1 first created the list 10 months after the mandatory and enforceable compliant date for this requirement. FRCC_URE1 submitted subsequent versions which were incomplete and needed to include all shared user accounts and individual with access to these shared accounts, including those that are used by third-party applications (5.2.2). | CIP-007-1 | R5; R5.1.3; R5.2.2 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because while FRCC_URE1 has access provisioning controls for individual access, not all shared and administrative accounts were documented. Annual review did include all of the accounts, and only specific account privileges were not verified. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Compliance Audit | FRCC_URE1 completed a Mitigation Plan by updating the access administration procedure to represent changes in process related to shared accounts, validated that all shared accounts are documented, created representative security groups for all shared accounts, and performed automated attestation of shared accounts in its identity management system. | 2011-09-30 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty. FRCC determined that FRCC_URE1's compliance history should not serve as a basis for aggravating the penalty.
2012-12-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007523 | Settlement Agreement | FRCC_URE1 self-reported that it failed to establish, document and implement a security patch management program for tracking, evaluating, testing, and installing of some third-party applications installed on many of the Cyber Assets within the Electronic Security Perimeters (ESPs). | CIP-007-1 | R3; R3.1 | Lower | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the Cyber Assets were within the ESP and protected by strong controls of the ESP and patches for very few applications were not tracked in the patch management program. All critical security patches were covered under the program. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Self-Report | FRCC_URE1 completed a Mitigation Plan that included steps for validation of all applications on covered Cyber Assets and reviewed patches for all applications identified for covered assets. FRCC_URE1 also updated the process to ensure that patch review documentation includes: patch identification, release date, assessment date, applicability, scheduled installation date, install date, alternate security measures, and date of application of alternate security. | 2011-10-14 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty. FRCC determined that FRCC_URE1's compliance history should serve as an aggravating factor in the penalty assessment.
2012-12-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007515 | Settlement Agreement | During a FRCC CIP Compliance Audit it was determined that FRCC_URE1 did not document all Critical Cyber Assets (CCA) within the Electronic Security Perimeter (ESP), even though all the CCAs were protected within the ESP. FRCC_URE1's ESP logical drawings did not identify and document all access points to the ESP. FRCC_URE1 documented all access points, but two access points were not marked or identified as access points on the logical drawings. These Cyber Assets were listed as CCAs in the CCA list since the compliance enforcement date. Further, FRCC_URE1 did not document its ESP and associated access points until the following year. Also, the entity did not include a virtual local area network (LAN) in the ESP drawings until two years later. Though the LAN was configured and protected as part of the ESP, the ESP drawing's representation was not accurate, and the devices were shown outside the ESP. All of these documentation corrections were completed a few weeks after the Audit. | CIP-005-1 | R1 | Medium | Severe | FRCC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the CCAs were protected within the ESP and the access points were for downstream communication and not outside-facing. FRCC_URE1 failed to document the access points appropriately on the logical drawing. These assets were listed as CCAs in the official CCA list. Further, the access point was protected and allowed communication to certain devices only as explicit permissions were specified in the Energy Management System (EMS). Even though the access point allowed asynchronous serial communication, the master-slave control was in place as all these devices were mapped one to one with EMS serial control points. All CCAs were protected within the ESP and the official CCA list identified all individual CCAs and their IP addresses. The LAN was protected within the ESP, and the discrepancy was strictly on the drawing documentation only. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Compliance Audit | FRCC_URE1 completed a Mitigation Plan including steps to identify and document two additional access points that use serial communication to communicate outside the ESP and update the logical ESP drawings to indicate the LAN is inside the ESP. | 2012-04-09 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2012-12-31 | FERC | NP13-12-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007517 | Settlement Agreement | During a FRCC CIP Compliance Audit it was determined that FRCC_URE1 implemented all but one of the security monitoring processes (logs and alert configurations) that alerted for attempts at or actual unauthorized access. FRCC_URE1 did not configure alerts for failed or denied attempts to the Electronic Security Perimeter (ESP) at the access point, resulting in the violation of CIP-005 R3.2. FRCC_URE1 maintained all the logs including those for denials and had all other proper alerts configured such as failed authentication, denied access, brute force access attempts and alerts for other threat provisions such as probing and scanning by unauthorized parties from outside the ESP. The deny attempts were a result of a misconfigured server in the ESP for which the IP addresses were changed but remote devices outside the ESP were not updated to communicate to the new IP address. | CIP-005-1 | R3; R3.2 | Medium | Severe | FRCC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All access rule sets were configured appropriately at the access points, any unauthorized accessing party would have been denied access, and any ingress would have been detected by other enforced alert criteria (authentication and threat) set at the access point and the Critical Cyber Assets. Any security risk was further limited as the firewall was configured to restrict all untrusted traffic, and intrusion detection system monitoring was enabled for the subject access point. The subject access point was configured for complete information logging, and all activities including denials and successful connection were logged. Risk was reduced because the successive denials resulted from the entity's own misconfigured database system which was trying to connect to a system in the ESP that was replaced. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Milestone that brought FRCC_URE1 into compliance | $33,000 (for FRCC201100435, FRCC201100436, FRCC2011007516, FRCC2011007518, FRCC2011007519, FRCC2011007523, FRCC2011007515, and FRCC2011007517) | Compliance Audit | FRCC_URE1 completed a Mitigation Plan including steps to create additional correlation rules within the security monitoring application to alert on the identified deny access log events, identify the minimum security monitoring alerting criteria and validate that the identified minimum security alert criteria are implemented and functional. FRCC_URE1 also conducted monthly reviews of firewall access logs to review for attempts at or actual unauthorized access to the ESP that the system failed to alert prior to the configuration changes to the security events monitoring system and no such events were identified and all other alert criteria were implemented and active. | 2011-09-09 | 2012-09-12 | Neither Admits nor Denies | FRCC considered FRCC_URE1's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2012-12-31 | FERC | NP13-12-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100395 | Notice of Confirmed Violation | MRO_URE1 self-reported noncompliance with CIP-007-3 R3 because it failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades. MRO_URE1 uses two secure access devices for the access control and monitoring of its Electronic Security Perimeters (ESPs). These devices are not Critical Cyber Assets (CCAs), although they are Cyber Assets (CAs) used in the access control and monitoring of the ESP, under CIP-005-3 R1.5. Therefore protective measures of CIP-007-3 R3.1 are given to the two devices. The vendor released a technical bulletin related to a vulnerability in the accessibility of information on certain devices. These devices are used by MRO_URE1 for remote access to the ESP. A user first accesses the devices to establish a tunnel, and then must pass through a firewall before being granted access to the ESP. This bulletin was not assessed within the required 30-day window. This oversight was detected 131 days after the bulletin was released, during a meeting to review security patches on the CAs. The review was initiated to provide an additional layer of oversight into existing process to ensure compliance with this NERC Reliability Standard Requirement. | CIP-007-3 | R3; R3.1 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risks from CIP-007-3 R3.1 were limited by electronic security measures which were in place during the pendency of the violation. To gain access to MRO_URE1's ESPs, an individual must go through a firewall after obtaining access to the identified devices. The entity's firewalls are configured per CIP-005 to prevent unauthorized access and are also configured to only allow access from specific authorized hosts (IP addresses). Furthermore, dating back to five months before the violation, MRO_URE1 had correctly assessed 10 of 11 patches made available by the vendor, with this being the only patch missed. MRO_URE1 did not experience a cyber incident during this period. | when MRO_URE1 was required to document the assessment of the security patch per the Standard | during the security patch meeting when the assessment was documented | $20,000 (for MRO201100395, MRO2012010185, and MRO2012009816) | Self-Report | MRO_URE1 completed the following mitigation activities: (1) MRO_URE1 implemented process improvements for assessing security patches and upgrades for all CCAs and other energy management system assets. (2) MRO_URE1 verified that more than one system administrator receives e-mail alerts and has access to vendor technical support, security patches and upgrades for all MRO_URE1 CAs whose security patching or upgrading process relies on e-mail alerts. (3) MRO_URE1 reviewed the current software version on the devices and compared it against all security patches and upgrades that have been made available since five months before the violation. (4) MRO_URE1 executed any security patches or upgrades that were determined to be required in the assessment described above. (5) MRO_URE1 formalized monthly security patch and upgrade meetings as an additional layer of review for discovering, assessing, applying and tracking security patches and upgrades. | 2011-11-21 | 2012-07-03 | Admits | MRO considered the violation history to be an aggravating factor in the penalty determination. MRO considered MRO_URE1's compliance program as a mitigating factor.
2012-12-31 | FERC | NP13-12-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009816 | Notice of Confirmed Violation | MRO_URE1 self-certified noncompliance with CIP-007-3 R6.4 because it failed to retain 90 calendar days of cyber security logs pertaining to monitoring system events. While conducting a quarterly review of individual user account access activity and security events, MRO_URE1 discovered that five workstations, Critical Cyber Assets (CCAs) which log user access and security events, had corrupted event logs. The corruptions occurred the day after the completion of the last quarterly review. As a result, there were no user activity or security logs for that 90-day period. The corruptions were caused by an issue with the operating system installed on the workstations. MRO_URE1 tried to recover the corrupted event logs using the instructions from the software vendor, but they were unrecoverable. | CIP-007-3 | R6; R6.4 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All five of the CCAs are within MRO_URE1's Electronic Security Perimeter (ESP), which are secured per CIP requirements. MRO_URE1 also has an intrusion detection system which alerts personnel of any attempted compromise of the ESP. Furthermore, all five of the devices were current with security patches. MRO_URE1 discovered all five of the CCAs that were found to have an issue within 90 days. As a result, MRO_URE1 had strong internal controls for performing manual checks of its automated process and other electronic security measures in place during the pendency of the violation. | the first day MRO_URE1 did not have historical logs for the CAs at issue | Mitigation Plan completion | $20,000 (for MRO201100395, MRO2012010185, and MRO2012009816) | Self-Certification | MRO_URE1 completed the following mitigating activities: (1) MRO_URE1 reset the logs on the CCAs and verified that they were collecting data. (2) MRO_URE1 investigated possible causes and resolutions for the malfunction using several methods, including Internet searches and software vendor support. The search included identification of any patches that limit reoccurrence (none were found that had not already been applied). (3) MRO_URE1's energy management system support group completed cutover to a new version. (4) MRO_URE1 disconnected the old assets, which concluded the upgrade process and removed from service assets running the identified operating system. | 2012-10-31 | 2012-11-14 | Admits | MRO did not consider the violation history to be an aggravating factor in its penalty determination. MRO considered MRO_URE1's compliance program as a mitigating factor.
2012-12-31 | FERC | NP13-12-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010185 | Notice of Confirmed Violation | MRO_URE1 self-certified noncompliance with CIP-004-2 R3.1 because it identified 9% of its contractors and 1% of its employees that had authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCA) without proper identity verification. MRO_URE1 failed to have the proper identity verification in the personnel risk assessments (PRAs) for approximately 10% of personnel subject to CIP-004-2. | CIP-004-2 | R3; R3.1 | Lower | High | MRO determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A total of 10% subject to CIP-004-2 did not have proper identify verification included as part of their PRAs. While the majority of the contractors had an I-9 verification performed at some time in the past, some had no identity verification. The contractors did not have any identity verification performed by either MRO_URE1 personnel or an independent third party. Additionally, an individual was granted unescorted Physical Security Perimeter (PSP) access as early as 14 months before the issue was identified; therefore, it went undetected for over fourteen months. However, MRO_URE1 confirmed, after it completed the requisite identity and background checks, that there were no issues with the personnel that had not been properly screened during the period at issue. | when the first individual was granted access to the PSP without proper identity verification | when the identity verifications were completed | $20,000 (for MRO201100395, MRO2012010185, and MRO2012009816) | Self-Certification | MRO_URE1 completed the following mitigating activities: (1) Following the identification of this issue, MRO_URE1's security department met with the Human Resources department for employee training and reviewed the requirement for a proper PRA for all contract workers with access to MRO_URE1's PSPs. (2) MRO_URE1 modified the contract worker background check form to include checkboxes to ensure that both the criminal background check and the identity verification are completed. (3) MRO_URE1 reviewed the missing criminal background checks and completed an identity verification for each individual; (4) Following the discovery of the missing identity verification by the internal audit department, MRO_URE1 reviewed PRA documentation for all employees and contractors with current or previous access to its PSPs. (5) MRO_URE1 modified its contractor safety and policies orientation manual to include the following statement regarding the requirement to perform a Social Security number (SSN) verification of their employees before they work at an MRO_URE1 facility. | 2011-10-18 | 2012-07-03 | Admits | MRO considered the violation history to be an aggravating factor in its penalty determination. MRO considered MRO_URE1's compliance program as a mitigating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100885 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-005-1 R1.5 to RF. During an internal review, RFC_URE1 discovered that six servers used in the access control and monitoring of the Electronic Security Perimeter (ESP), were not receiving the protective measures specified in CIP-007-1 R4.2, as required by CIP-005-1 R1.5. Specifically, RFC_URE1 discovered that the servers were not communicating with the device responsible for deploying malware prevention signatures (Signatures) to the servers, and thus the servers were prevented from receiving Signature updates for an 11-month period, when the issue was identified. RFC_URE1 determined the lack of communication between the servers and the device responsible for deploying Signatures was attributable to a defect in the anti-malware product. This defect presents when a certain version of the anti-malware is run on a certain operating system. That defect prevented the servers from receiving current Signatures. RFC_URE1's internal process for updating Signatures requires that RFC_URE1 distribute and activate Signatures within ten days of their release from the vendor. RFC_URE1 self-reported, through its Mitigation Plan, an additional instance of noncompliance with CIP-005-1 R1.5. RFC_URE1 discovered that some of its Cyber Assets used in the access control and monitoring of the ESP (ACM Devices) were not included in its annual cyber vulnerability assessment (Assessment) as specified in CIP-007-1 R8 and required pursuant to CIP-005-1 R1.5. RFC_URE1 provided RF with a complete list of the ACM Devices that were not included in its annual Assessment. | CIP-005-1 | R1; R1.5 | Medium | Moderate | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS because the risk to the BPS of the servers not communicating with the anti-malware product was mitigated by the following factors. RFC_URE1 had earlier versions of Signatures continually operating on the servers during the duration of the violation. Additionally, the servers are protected by firewalls that limit access and do not allow connections to the internet. The servers also sit outside RFC_URE1's ESP, and therefore RFC_URE1's energy control system, the Critical Asset at issue, was at limited risk. Although outside the ESP, the servers reside within a Physical Security Perimeter (PSP). RFC_URE1 limited access to the PSP to RFC_URE1 personnel who have completed CIP training and personnel risk assessments. RFC_URE1 also prohibits the use of removable media, such as flash drives, within its PSP. Also, RFC_URE1 detected no malware on the servers when its personnel uploaded current Signatures. The risk to the reliability of the BPS of RFC_URE1 not including ACM Devices in its annual Assessment was mitigated by the following factors which reduced vulnerabilities to Critical Cyber Assets (CCAs) within the ESP. First, RFC_URE1 included its firewalls in the annual Assessment. Additionally, RFC_URE1's intrusion detection system was in place during the duration of this violation. RFC_URE1 keeps logs for 90 days including, but not limited to, operating system audit logs, application logs, system logs, virtual PC security events, system alerts, and anti-virus/malware detection alerts. Moreover, there is no direct Internet access to the ACM Devices, and these devices continued to perform their functions, including logging and alerting, over the duration of the violation. | when RFC_URE1 failed to implement its process for updating Signatures | when RFC_URE1 conducted an interim Assessment for its ACM Devices | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) updated Signatures on the servers; (2) assigned an additional individual to its information security team to perform weekly reviews to ensure all CCAs, ACM Devices, physical access control and monitoring devices, and interactive access point devices are operating with current Signatures; (3) instituted a weekly process to restart the anti-malware product on the servers to ensure that the servers receive new Signature updates in a timely manner as they are released; (4) conducted an interim Assessment for its ACM Devices; (5) revised the statement of work within its contract with the third-party vendor hired to conduct the next annual Assessment to include ACM Devices; and (6) provided oversight to ensure that all of its ACM Devices were included in the next annual Assessment conducted. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100887 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-007-3 R1 to RF. RFC_URE1 discovered that a repair to a printer, an existing Cyber Asset within the Electronic Security Perimeter (ESP), went unrecognized as a significant change warranting testing of the printer's security controls. RFC_URE1 did not recognize the replacement of a formatter board on the printer within the ESP as a significant change pursuant to CIP-007-3 R1. As a result, RFC_URE1 did not ensure that the replacement did not adversely affect the printer's existing cyber security controls. In fact, the replacement of the formatter board resulted in the reset of the printer's security configurations back to factory default settings. | CIP-007-3 | R1 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. The printer at issue remained within an intact Physical Security Perimeter (PSP) and ESP during the duration of the violation. Additionally, the network firewalls surrounding the ESP during the duration of the violation were working, and there was no indication or alert of any breach of the ESP. | when RFC_URE1 replaced the printer formatter board | when RFC_URE1 removed the printer from the ESP | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) took the printer at issue out of service and reinstated the security settings; (2) held a meeting with its information technology personnel involved in the violation to emphasize the need to perform security control testing when RFC_URE1 makes a modification to printers within the ESP; and (3) removed the printer at issue, as well as all other printers, from the ESP. Therefore, RFC_URE1 no longer classifies the printer at issue as a Cyber Asset within the ESP. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100888 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-007-3 R2 to RF. RFC_URE1 replaced the formatter board on a printer, an existing Cyber Asset within the Electronic Security Perimeter (ESP), which resulted in the reset of the printer's security configurations back to factory default settings. RFC_URE1 determined that the reset of the printer's security settings to factory default settings resulted in the enabling of previously disabled logical ports. While these enabled ports were not used during the duration of the violation, the enabling of these ports is contrary to the requirements of CIP-007-3 R2.1. | CIP-007-3 | R2; R2.1 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. The printer at issue remained within an intact Physical Security Perimeter (PSP) and ESP during the duration of the violation. Additionally, the network firewalls surrounding the ESP during the duration of the violation were working, and there was no indication or alert of any breach of the ESP. | when RFC_URE1 replaced the printer formatter board | when RFC_URE1 removed the printer from the ESP | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) took the printer at issue out of service and reinstated the security settings; (2) held a meeting with its information technology personnel involved in the violation to emphasize the need to perform security control testing when RFC_URE1 makes a modification to printers within the ESP; and (3) removed the printer at issue, as well as all other printers, from the ESP. Therefore, RFC_URE1 no longer classifies the printer at issue as a Cyber Asset within the ESP. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001206 | Settlement Agreement | RFC_URE1 self-reported through its Mitigation Plan a violation of CIP-006-1 R1.8 to RF. RFC_URE1 discovered that some of its physical access control and monitoring (PACM) devices were not included in its annual cyber vulnerability assessment (Assessment), as specified in CIP-007-1 R8 and required pursuant to CIP-006-1 R1.8. RFC_URE1 provided RF with a complete list of the PACM devices that were not included in its annual Assessment. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE1's intrusion detection system was in place during the duration of the violation. Additionally, RFC_URE1 keeps logs for 90 days and includes operating system audit logs, application logs, system logs, virtual PC security events, system alerts, and anti-virus and malware detection alerts. | when CIP-006-1 became mandatory and enforceable to RFC_URE1 | when RFC_URE1 performed an interim Assessment on its PACM devices | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) conducted an interim Assessment for its PACM devices; (2) revised the statement of work within its contract with the third-party vendor hired to conduct the next annual Assessment to include PACM devices; and (3) provided oversight to ensure that all of its PACM devices were included in the next annual Assessment conducted. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001207 | Settlement Agreement | RFC_URE1 self-reported through its Mitigation Plan a violation of CIP-007-1 R3 to RF. After discovering the facts underlying RFC201100885, described above, RFC_URE1 further discovered that 139 patches for a certain operating system running on certain servers were not assessed for applicability for a 16-month period. While the tool RFC_URE1 used for all security patch tracking was correctly configured, the security patch tracking tool did not operate as expected and failed to identify the missed patches. Additionally, for a four-month period, after RFC_URE1 replaced the security patch tracking tool with a more robust primary security patch tracking tool, RFC_URE1 identified 24 applicable security patches released by the vendor that were not assessed within the 30 calendar day required time frame. The delay in assessment was the result of RFC_URE1's implementation of the new tool, as well as the increased volume of potential vulnerability alerts that the information security team had to review in order to identify security patches applicable to the RFC_URE1 system. | CIP-007-1 | R3 | Lower | High | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the fact that RFC_URE1 had an established and documented patch management program during the duration of the violation. Also, the assets in question do not have direct Internet access. Moreover, the assets were servers which log, but have no direct correlation to BPS controls. | when RFC_URE1 should have assessed a certain operating system patches for applicability | when RFC_URE1 assessed the subsequent 24 patches | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) Upon the discovery that the security patch tracking tool was not functioning properly, RFC_URE1 assessed all security patches, of a certain operating system, released to that point for applicability; (2) RFC_URE1 purchased and implemented a new tool to act as its primary security patch tracking tool; (3) Having since scheduled the 24 missed patches for implementation, RFC_URE1 improved its use of the new tool by (a) implementing an additional process to collect and review all patch information directly from the operating system site, and (b) applying a filter to the new tool to isolate and allow for prioritization of security patch assessments specific to the RFC_URE1 CIP environment; and (4) RFC_URE1 implemented a process to continue to review and improve its existing security patch tracking tools. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001208 | Settlement Agreement | RFC_URE1 self-reported through its Mitigation Plan a violation of CIP-007-3 R4.2 to RF. Pursuant to its internal malware management procedure (Procedure), RFC_URE1 tests all of its specific signature files in a production-simulated environment before using such files on Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). These signature files are virus definition files that contain up-to-date virus signatures and other information which anti-virus products use to protect against viruses in circulation. Out-of-date signature files will not allow anti-virus products to recognize the most recent virus signatures and will leave a system vulnerable to possible infection. RFC_URE1 discovered that, for a six-day period, it installed signature files into the production environment without prior testing or evaluation contrary to its Procedure. RFC_URE1 determined that the signature files were installed into the production environment without testing due to configurations changes RFC_URE1 made during a separate project. Additionally, RFC_URE1 discovered that while it corrected the configuration which caused the violation 10 days later, it had failed to re-enable the signature file update process. Therefore, for a two-day period, RFC_URE1 did not deploy updated signature files into the production environment. When RFC_URE1 discovered the violation, it immediately restored the signature files update functionality. | CIP-007-3 | R4; R4.2 | Medium | High | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE1 had a documented procedure in place during the duration of the violation. Moreover, the CCAs in the ESP are protected by firewalls that limit access and do not allow connections to the Internet, thereby reducing the likelihood of anti-virus and malware infection. | when RFC_URE1 installed the specific signature files into the production environment without prior testing and evaluation | when RFC_URE1 re-enabled the signature file process to deploy signature files updates into the production environment after testing and evaluation | $10,000 (for RFC201100885; RFC201100887; RFC201100888; RFC2011001206; RFC2011001207; and RFC2011001208) | Self-Report | RFC_URE1 completed the following mitigation activities: (1) corrected the errors associated with the specific signature file update process; (2) initiated a daily review of all released signature files related to CCAs in the ESP to ensure all are addressed and none are missed; and (3) developed a tool to detect abnormalities in the signature file update process to ensure the signature files are properly tested prior to introduction in the production environment. | 2012-02-17 | 2012-06-26 | Neither Admits nor Denies | RF considered certain aspects of RFC_URE1's compliance program, in place at the time of the violations, to be mitigating factors in the penalty determination. RF considers the fact that RFC_URE1 self-reported all of the violations to be a mitigating factor. RF also considered RFC_URE1's commitment to compliance and reliability as a mitigating factor. RF did not consider RFC_URE1's compliance history to be an aggravating factor.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000657 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to include certain Cyber Assets that use a protocol to communicate outside the Electronic Security Perimeter (ESP) within its list of Critical Cyber Assets (CCAs). RFC_URE2 utilizes computers to remotely operate certain operator consoles. The computers communicate outside of an ESP using a protocol, but RFC_URE2 does not classify these Cyber Assets as CCAs. | CIP-002-1 | R3.1 | Lower | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because remote access into the ESP was protected with two levels of authentication: (1) through two-factor authentication based on a password known to the user combined with an authenticator or key fob; and (2) through a program, which sends an alert to energy management system/supervisory control and data acquisition personnel upon a user's failure to authenticate. As a result, RFC_URE2 had mechanisms in place to guard against unauthorized access. | when RFC_URE2 was found to have failed to include certain Cyber Assets within its CCA list | Mitigation Plan completion | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 reconfigured the operator consoles and disabled remote access control functionality to these consoles. RFC_URE2 now permits view-only access to the energy management system/supervisory control and data acquisition system through remote support, and has disabled all remote access capability for its interface system. The computers are currently not classified as CCAs since their access is now limited to monitoring functions and is therefore not “essential to the operation of the Critical Asset.” | 2010-12-17 | 2011-05-31 | Neither Admits nor Denies | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000444 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to maintain documentation of all Cyber Assets within its Electronic Security Perimeter (ESP). RFC_URE2 failed to document a device that was connected as a Cyber Asset within an ESP. | CIP-005-1 | R1.6 | Lower | High | ReliabilityFirst determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the device does not transmit any data back to the energy management system (EMS). Additionally, RFC_URE2 reconfigured the device outside the ESP because the device was not an asset requiring the protection of an ESP. Furthermore, the device was located within an ESP and within a Physical Security Perimeter and therefore had the protections of each of these security perimeters. | when the Standard became mandatory and enforceable to RFC_URE2 | when RFC_URE2 relocated the device outside the ESP | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 reconfigured the device connection so that it is outside the ESP. In order to prevent the reoccurrence of this issue, RFC_URE2 revised its cyber security test procedures and the associated cyber security test form to include steps for updating documentation, drawings, and diagrams. RFC_URE2 additionally performed a review to verify that no unexpected devices were connected inside the ESP and modified its procedures to include this review on an annual basis. | 2011-01-27 | 2011-03-28 | Admits | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000445 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to ensure that it enabled only those ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP), at all access points to the ESP. ReliabilityFirst examined the lists RFC_URE2 provided as documentation of the ports and services enabled at the access points to the ESP and determined that the lists did not demonstrate that RFC_URE2 enabled only those ports and services that are required for operations and for monitoring Cyber Assets within the ESP. Specifically, RFC_URE2 did not include a description for all ports and services within the lists of enabled ports and services. Additionally, the descriptions of ports and services that RFC_URE2 did include did not provide the operational purpose of the ports and services, which is necessary to demonstrate that the port or service is required for operations. Furthermore, RFC_URE2 did not provide any alternative documentation to demonstrate that RFC_URE2 only enabled ports and services required for operations and for monitoring Cyber Assets within the ESP. | CIP-005-1 | R2.2 | Medium | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE2's systems that reside within an ESP have limited connectivity to outside networks and firewalls that restrict network traffic are in place. RFC_URE2 implemented security services, such as intrusion detection systems and virus scanning, on the ESP network to detect unusual activities. Network traffic monitoring is also in place and sends alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, RFC_URE2 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. | when the Standard became mandatory and enforceable to RFC_URE2 | Mitigation Plan completion | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 revised the ports and services lists, including the descriptions of these ports and services where needed, to ensure that it defined the purpose of each port and service. | 2011-02-18 | 2011-08-12 | Admits | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000446 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to include a review in its cyber vulnerability assessment to verify that RFC_URE2 enabled only ports and services required for operations at access points to the Electronic Security Perimeter (ESP). The evidence provided by RFC_URE2 did not demonstrate that RFC_URE2 included a review within its vulnerability assessment to verify that only ports and services required for operations at access points to the ESP were enabled. Specifically, RFC_URE2 failed to review the configuration of its entire access control device during its cyber vulnerability assessment, and instead only reviewed one portion of its access control device. A review of the configuration of the entire access control device is necessary to verify that only those ports and services required for operations are enabled. | CIP-005-1 | R4.2 | Medium | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE2's systems that reside in an ESP have limited connectivity to outside networks. RFC_URE2 implemented security services, such as intrusion detection systems and virus scanning, on the ESP network to detect unusual activities. Additionally, network traffic monitoring is in place to send alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, RFC_URE2 has monitoring processes in place that provide protection to the ESP by detecting and alerting for unauthorized access. | when the Standard became mandatory and enforceable to RFC_URE2 | Mitigation Plan completion | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 performed a cyber vulnerability assessment, including verification that only ports and services required for operations at access points are enabled. RFC_URE2 modified its cyber vulnerability assessment procedure to include this step for subsequent cyber vulnerability assessments. | 2011-01-27 | 2011-08-16 | Admits | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000447 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to ensure that it enabled only those ports and services required for normal and emergency operations. ReliabilityFirst examined lists that RFC_URE2 provided as documentation of the ports and services that RFC_URE2 enabled on four sample systems, and determined that the lists did not demonstrate that RFC_URE2 enabled only those ports and services required for normal and emergency operations. Specifically, RFC_URE2 did not include a description for all enabled ports and services, which is necessary to demonstrate that the port or service is required for normal or emergency operations. Those descriptions that RFC_URE2 provided did not provide the operational purpose of the ports and services to demonstrate that they are required for operations. Furthermore, RFC_URE2 could not demonstrate that only ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2.1 | Medium | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NERC, based on evaluation of the facts and circumstances of this violation and similar violations from other regions, determined that this violation posed a minimal risk to the reliability of the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE2's systems that reside in an ESP have limited connectivity to outside networks and firewalls that restrict network traffic are in place. RFC_URE2 implemented security services, such as intrusion detection systems and virus scanning, on the ESP network to detect unusual activities. Additionally, network traffic monitoring is in place to send alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, RFC_URE2 has monitoring processes in place that provide protection to the ESP by detecting and alerting for unauthorized access. | when the Standard became mandatory and enforceable to RFC_URE2 | Mitigation Plan completion | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 revised the ports and services lists and revised the descriptions of ports and services where needed, to ensure that the purpose of each port and service was defined. | 2011-02-18 | 2011-08-12 | Admits | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination. ReliabilityFirst determined that violation history should not serve as a basis for aggravating the penalty.
2012-12-31 | FERC | NP13-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000448 | Settlement Agreement | ReliabilityFirst conducted a CIP Compliance Audit of RFC_URE2 and found that RFC_URE2 had failed to include a complete review in its cyber vulnerability assessment to verify that it enabled only ports and services required for operation of Cyber Assets within the Electronic Security Perimeter (ESP). ReliabilityFirst discovered ports and services documented in RFC_URE2's cyber vulnerability assessment that RFC_URE2 did not list on the required ports and services list. Additionally, RFC_URE2 did not include sufficient documentation in its cyber vulnerability assessment to demonstrate that it conducted a complete review to verify that it enabled only ports and services required for operation of Cyber Assets within the ESP. | CIP-007-1 | R8.2 | Lower | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NERC, based on evaluation of the facts and circumstances of this violation and similar violations from other regions, determined that this violation posed a minimal risk to the reliability of the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because RFC_URE2's systems that reside in an ESP have limited connectivity to outside networks and firewalls that restrict network traffic are in place. RFC_URE2 implemented security services, such as intrusion detection systems and virus scanning, on the ESP network to detect unusual activities. Additionally, network traffic monitoring is in place to send alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, RFC_URE2 has monitoring processes in place that provide protection to the ESP by detecting and alerting for unauthorized access. | when the Standard became mandatory and enforceable to RFC_URE2 | Mitigation Plan completion | $65,000 (for RFC201000444, RFC201000445, RFC201000446, RFC201000447, RFC201000448, and RFC201000657) | Compliance Audit | RFC_URE2 previously allowed managers to use different reporting forms to document their individual system assessments regarding enabled ports and services. As part of its mitigating activities, RFC_URE2 standardized the format for documenting that only ports and services required for operation of Cyber Assets within the ESP are enabled. RFC_URE2 then performed a review of the list to ensure that it only enabled necessary ports and services. RFC_URE2 subsequently performed a cyber vulnerability assessment that verified that RFC_URE2 enabled only those ports and services needed for operation of Cyber Assets within the ESP and documented the successful outcome of the cyber vulnerability assessment in the new format. | 2010-10-05 | 2011-08-16 | Admits | ReliabilityFirst commends certain aspects of RFC_URE2’s compliance program and considered them mitigating factors in the penalty determination. ReliabilityFirst noted RFC_URE2's cooperation during the Compliance Audit and throughout the subsequent enforcement activities related to the violation and considered it a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000317 | Settlement Agreement | During a CIP Spot Check, SPP RE found that SPPRE_URE1, had a violation of CIP-002-1 R3. Specifically, switches essential to the reliable operation of SPPRE_URE1’s control center were not identified as Critical Cyber Assets (CCAs) and not included in SPPRE_URE1's list of CCAs. The switches that were not identified utilize a protocol within the control center and therefore, pursuant to CIP-002-1 R3, should be considered CCAs. | CIP-002-1 | R3 | High | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). Although the switches at issue were not identified as CCAs, they were located within both the Electronic Security Perimeter and Physical Security Perimeter of SPPRE_URE1’s primary control center and were protected against potential cyber attack. Further, SPPRE_URE1 had properly identified its remaining CCAs. NERC, based on the evaluation of facts and circumstances of this violation and similar violations from other Regional Entities, determined that this violation posed a moderate risk to the reliability of the BPS. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | To mitigate its violation, SPPRE_URE1 conducted a review of its critical facilities and associated CCAs, and updated its CCA identification list to include the switches. | 2010-11-04 | 2010-11-08 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000318 | Settlement Agreement | During a CIP Spot Check, SPP RE discovered that SPPRE_URE1's cyber security policy (Policy) did not address all the requirements of CIP-002 through CIP-009, as required by CIP-003-1 R1.1. Specifically, SPPRE_URE1’s Policy did not address CIP-006-1 R1.1 for a failure to ensure the Cyber Assets within its Electronic Security Perimeter (ESP) resided within an enclosed six-wall Physical Security Perimeter (PSP). Also, SPPRE_URE1 did not have a prescriptive user password policy, as required by CIP-007-1 R5.3. In addition, the senior manager appointed pursuant to CIP-003-1 R2 had failed to approve and annually review SPPRE_URE1's Policy, as required by CIP-003-1 R1.3. However, the senior manager had delegated approval authority for the Policy documents to subordinate managers according to their assigned areas of responsibility and the delegates' managers did perform the required reviews and approvals. | CIP-003-1 | R1.1; R1.3 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE1’s Policy was not signed by the senior manager, it was reviewed and approved by a delegate that was assigned by the senior manager. Although SPPRE_URE1's password management policy was not thoroughly referenced in its Policy, SPPRE_URE1 employees were familiar with the password management policy for compliance with other CIP standards. Finally, SPP RE determined that the Cyber Assets within the ESP resided within an enclosed six-wall PSP, although SPPRE_URE1's policy did not address this Requirement. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | To mitigate its violation, SPPRE_URE1 revised its Policy to address the requirements in Standards CIP-002 through CIP-009. SPPRE_URE1 added in its Policy a specific language addressing the six-wall border that protects its Cyber Security Assets. SPPRE_URE1 also required its senior manager designated in CIP-003-1 R2 to annually review its Policy. SPPRE_URE1 amended its Policy to properly reference its password management policy and changed the appropriate reporting dates for CIP-008 and CIP-009 from 90 days to 30 days. | 2010-12-31 | 2011-01-19 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000319 | Settlement Agreement | During a CIP Spot Check, SPP RE found a violation of CIP-004-1 R2.1, CIP-004-1 R2.2.1 and CIP-004-1 R2.3. SPP RE found SPPRE_URE1 was noncompliant with CIP-004-1 R2.1 because SPPRE_URE1 did not train one employee with unescorted physical access to Critical Cyber Assets (CCAs) within 90 days of the initial access to the CCAs in accordance with Version 1 of CIP-004, or within 30 days in accordance with Version 2 of CIP-004. SPP RE found SPPRE_URE1 was noncompliant with CIP-004-1 (and Version 2) R2.2.1 because SPPRE_URE1’s training program for vendors and contractors did not include instruction on the proper use of SPPRE_URE1’s CCAs. SPP RE found SPPRE_URE1 was noncompliant with CIP-004-1 R2.3 because 2 randomly sampled personnel with authorized electronic and/or authorized, unescorted physical access to CCAs had not completed the required annual cyber security training. The two individuals at issue were SPPRE_URE1 contractors. Further, SPPRE_URE1 did not provide evidence to show that an additional employee received annual recurring training, although SPPRE_URE1 did provide evidence that this employee had received the training, leaving a 19-month gap between training sessions. | CIP-004-1 | R2.1; R2.2.1; R2.3 | Medium | High | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). One employee never received training on the use of its CCAs, which accounts for less than 1% of the SPPRE_URE1 staff. The one employee with the 19-month gap in training had received training covering both years surrounding the gap in training. Although two contractors had not completed the required annual cyber security training, they did receive training covering where SPPRE_URE1’s CCAs were located. In addition, the contractors had completed personnel risk assessments. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | To mitigate its violation, SPPRE_URE1 updated its contractor and vendor cybersecurity training program to include instruction related to proper use of CCAs for individuals who have authorized cyber access or authorized unescorted physical access to SPPRE_URE1’s CCAs. SPPRE_URE1 also conducted training on its program and documented attendance of the training for all SPPRE_URE1 employees. | 2010-11-08 | 2010-11-08 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000322 | Settlement Agreement | During a CIP Spot Check, SPP RE discovered that SPPRE_URE1 failed to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cybersecurity controls. Specifically, SPPRE_URE1 did not have documented evidence to demonstrate that its cybersecurity controls were being tested. | CIP-007-1 | R1 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE1's procedures related to its security controls were in place but SPPRE_URE1 lacked adequate documentation of the process, as required by R1. At the Spot Check, SPPRE_URE1 provided evidence that its security controls were tested. Further, no occurrences on the cybersecurity controls occurred between the time the Standard became mandatory and enforceable through the violation end date. In addition, SPPRE_URE1 had operating system updates that were performed on its energy management system. | when the Standard became mandatory and enforceable for SPPRE_URE1 | when the documentation for testing was created | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | The documentation for the testing of cybersecurity controls were presented at the Spot Check. SPP RE determined that the documentation addressed the requirements of this Standard. | 2010-06-08 | 2010-11-08 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000323 | Settlement Agreement | During a CIP Spot Check, SPP RE found that SPPRE_URE1’s cyber security incident response plan (Plan) had not been tested at least annually, in violation of CIP-008-1 R1. SPPRE_URE1 could not demonstrate that it had properly classified scenario incidents as reportable, or that it had tested its simulation of communications and responses at least annually. SPPRE_URE1's first scenario incident was conducted on 17 months after the Standard became mandatory and enforceable to SPPRE_URE1. | CIP-008-1 | R1 | Lower | Moderate | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE1 had documentation to demonstrate that training on the Plan had been conducted and that the Plan had been tested. The Plan included response actions, including roles and responsibilities of SPPRE_URE1's cyber security incident response teams, cyber security incident handling procedures, communication plans, and process for reporting cyber security incidents, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | To mitigate its violation, SPPRE_URE1 developed a cyber security incident response plan that addresses the following: 1) procedures to characterize and classify events as reportable cyber security incidents; 2) response actions, including roles and responsibilities of SPPRE_URE1 employees; and 3) a Critical Cyber Asset cyber incident handling checklist to give employees a guideline of how to conduct testing of the Plan. | 2010-09-20 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000324 | Settlement Agreement | During a CIP Spot Check, SPP RE found that SPPRE_URE1 did not have evidence that it had properly tested its recovery plan for Critical Cyber Assets (CCAs), as required by CIP-009-1 R2. Specifically, SPPRE_URE1’s tabletop exercises of its Recovery Plan did not include steps to recover and restore the failed CCAs to normal operation. | CIP-009-1 | R2 | Lower | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE1 provided evidence to demonstrate that it had a Recovery Plan in place during the pendency of the violation. SPPRE_URE1 also provided evidence to demonstrate that training on the Recovery Plan had been conducted on an annual basis by providing agendas, sign-in sheets, and incident recovery procedures. SPPRE_URE1 discussed the Recovery Plan with relevant employees and asserts it had performed table top exercises during the pendency of the violation. | when the Standard became mandatory and enforceable for SPPRE_URE1 | Mitigation Plan completion | $15,000 (for SPP201000317, SPP201000318, SPP201000319, SPP201000322, SPP201000323 and SPP201000324) | Spot Check | To mitigate its violation, SPPRE_URE1 developed and implemented a checklist that will serve to verify testing of the Recovery Plan. | 2010-09-20 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had a written internal compliance program (ICP) at the time the violation occurred but it was considered a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000140 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE stating that it failed to provide documentation to demonstrate that cyber security training (CST) had occurred for affected personnel as required by CIP-004-2 R2. 30.2% of the training issues were for a lack of training documentation that showed timely training and 2.0% lacked any training documentation. Texas RE_URE1 determined during a self assessment of its compliance with NERC Reliability Standards that it did not have documentation to show timely completion of training for 32.2% of its affected personnel. | CIP-004-2 | R2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation of this Standard is associated with CST documentation rather than actual performance of the NERC CIP requirements. The majority of the personnel with training issues that had a lack of timely documentation had access granted prior to the enforceability date of this Standard and had completed the required CST training in accordance with Texas RE_URE1’s Human Resources (HR) procedures. Upon discovery of the lack of documentation, all personnel with insufficient training documentation were trained and the training was documented within four months. Additionally, Texas RE_URE1 had HR procedures that required all affected personnel to have personnel risk assessments (PRAs) and various security controls including card key access, security guards and video surveillance, in place at the time of the violation. The combination of Texas RE_URE1’s access granting procedures that required personnel training, PRAs, management approval, documentation, periodic review of granted access, the documentation deficiency being self-discovered, and employee orientation training received by personnel reduced the risk to the BPS. | the first date that Texas RE_URE1 was in violation of CIP-004-2 R2 | when training was conducted and documented for all affected personnel | $51,000 (for TRE201000140, TRE201000141, TRE201000143, TRE201000144 and TRE201000146) | Self-Report | In accordance with its Mitigation Plan, Texas RE_URE1 completed the following activities: 1) Conducted and documented CST training for all affected personnel; 2) Reviewed compliance activities performed by other utilities to determine best practices and compared them to Texas RE_URE1 processes; 3) Revised Texas RE_URE1 policies to develop robust CIP-004 procedures to ensure compliance; 4) Developed an on-boarding/off-boarding handbook for affected operational organizations; 5) Improved and completed training for affected operational organizations; and 6) Performed periodic spot checks of compliance to ensure all affected operational organizations are using the new processes and successfully complying with the NERC CIP Reliability Standards. | 2011-10-07 | 2012-08-23 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. Texas RE also considered Texas RE_URE1's compliance history and determined it to be a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000141 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE stating that it failed to provide documentation to demonstrate it conducted personnel risk assessments (PRAs) for affected personnel as required by CIP-004-1 R3. As a result of an internal investigation, Texas RE_URE1 determined that it did not have documentation to show timely completion of PRAs for 35.8% of its affected personnel. | CIP-004-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation of this Standard is associated with documentation of the PRAs rather than actual performance of the NERC CIP requirements. The majority of the affected personnel that Texas RE_URE1 failed to document per the requirement had access granted prior to the enforceability date of this Standard and had completed PRAs in accordance with Texas RE_URE1’s Human Resources (HR) procedures. Upon discovery of the lack of documentation for these personnel with insufficient PRAs, the PRAs were conducted and documented within a month. The remaining were completed within four months of discovery. Additionally, Texas RE_URE1 had various security controls including card key access, security guards and video surveillance, in place at the time of the violation. The combination of Texas RE_URE1’s access granting procedures that required personnel training, PRAs, management approval, documentation, and periodic review of granted access and the documentation deficiency being self-discovered reduced the risk to the BPS. | the first date that Texas RE_URE1 was in violation of CIP-004-1 R3 | when PRAs were conducted and documented for all affected personnel | $51,000 (for TRE201000140, TRE201000141, TRE201000143, TRE201000144 and TRE201000146) | Self-Report | In accordance with its Mitigation Plan, Texas RE_URE1 completed the following activities: 1) Conducted and documented PRAs for all affected personnel; 2) Reviewed compliance activities performed by other utilities to determine best practices and compared to Texas RE_URE1 processes; 3) Revised Texas RE_URE1 policies and developed new CIP-004 procedures to ensure compliance; 4) Developed an on-boarding/off-boarding handbook for affected operational organizations; 5) Improved and completed training for affected operational organizations; and 6) Performed periodic spot checks of compliance to ensure all affected operational organizations are using the new processes and successfully complying with the NERC CIP Reliability Standards. | 2011-10-07 | 2012-08-23 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount. Texas RE also considered Texas RE_URE1's compliance history and determined it to be a neutral factor in the penalty determination.
2012-12-31 | FERC | NP13-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000144 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE stating that it had discovered two Physical Security Perimeters (PSPs) with ‘drop-down’ ceilings that did not meet the criteria as a completely enclosed (six-wall) border as required by CIP-006-2 R1.1. Texas RE_URE1 had originally self-reported this as a CIP-006-2 R3 noncompliance, but Texas RE found that CIP-006-2 R1.1 was the Reliability Standard that applied because CIP-006-2 R1.1 relates to the lack of the six-wall enclosure. The two PSPs contained Electronic Security Perimeters (ESPs) with ESP access points and access control/monitoring devices. | CIP-006-2 | R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Though lacking suitable ceilings (Texas RE_URE1 had drop-down types) Texas RE_URE1's equipment rooms had door card key access systems and were in a building that likewise had card key access systems and other security controls such as security guards and video surveillance. The containment of the equipment rooms within a security controlled building reduced the risk to the BPS. | first date that Texas RE_URE1 was in violation of CIP-006-2 R1.1 | Mitigation Plan Completion | $51,000 (for TRE201000140, TRE201000141, TRE201000143, TRE201000144 and TRE201000146) | Self-Report | In accordance with its Mitigation Plan, Texas RE_URE1 moved the Cyber Assets in question into one room and completed the six-wall enclosing of that room. | 2010-10-01 | 2012-08-23 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-12-31 | FERC | NP13-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000143 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE stating that it was in violation of CIP-006-1 R1.8. Texas RE_URE1’s card-key system is housed at the data center of a third-party vendor. That vendor did not afford, as required in CIP-006-2 R2, the protective measures specified in CIP-003, CIP-005, CIP-007 and CIP-009 to the Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s) (PSPs), exclusive of hardware at the PSP access point such as electronic control mechanisms and badge readers. | CIP-006-2 | R2 | Medium | Severe | This violation posed moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the devices did not receive all of the specific protections required in CIP-003, CIP-005, CIP-007 and CIP-009, the assets were located inside a secured PSP with guards, and these devices were within an Electronic Security Perimeter (ESP) and could not be remotely accessed via unauthorized means because of implemented software and hardware. | first date that Texas RE_URE1 was in violation of CIP-006-2 R2 | when vendor was compliant with CIP-006 | $51,000 (for TRE201000140, TRE201000141, TRE201000143, TRE201000144 and TRE201000146) | Self-Report | In accordance with its Mitigation Plan, Texas RE_URE1 completed the following activities: 1) Assisted the vendor in developing and implementing necessary processes for compliance; and 2) Performed spot checks to verify vendor compliance. | 2011-07-28 | 2012-08-23 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-12-31 | FERC | NP13-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000146 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE stating that its disaster recovery plan for Critical Cyber Assets (CCAs) did not specify the required actions in response to events or conditions of varying duration and severity, as required by CIP-009-1 R1.1. | CIP-009-1 | R1.1 | Medium | High | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While Texas RE_URE1’s disaster recovery plan was not specific about the required actions in response to events or conditions of varying duration and severity as required by R1.1, it did have defined roles and responsibilities of responders for the recovery of CCAs. Texas RE_URE1 has quadruple redundancy on its control systems which, if needed, would be able to failover to its back-up control center and continue to run until such time as the primary site could be restored. The defined roles and responsibilities, along with Texas RE_URE1's redundancy and ability to failover to a back-up site and servers reduced the risk to the BPS. | when the Standard became mandatory and enforceable for Texas RE_URE1 | when training and procedure were completed | $51,000 (for TRE201000140, TRE201000141, TRE201000143, TRE201000144 and TRE201000146) | Self-Report | In accordance with its Mitigation Plan, Texas RE_URE1 completed the following activities: 1) Created a disaster recovery plan to cover all requirements set forth in CIP-009; 2) Provided training to appropriate personnel on the new plans; and 3) Performed periodic spot checks to ensure operational organizations follow the disaster recovery plan requirements. | 2011-06-13 | 2012-08-23 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-12-31 | FERC | NP13-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010392 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-003-3 R6 for failure to follow its change control and configuration management process. Specifically, a member of WECC_URE1's information technology (IT) department created a change ticket in WECC_URE1's change management system to perform patching to energy management system (EMS) workstations. The employee failed to obtain the appropriate approvals prior to implementing the change to the devices, as required under WECC_URE1's CIP change control and configuration management procedures. WECC reviewed the Self-Report and contacted WECC_URE1 to request additional information. WECC_URE1 reported that during the course of mitigation, it discovered additional instances in which WECC_URE1 employees did not follow its change control and configuration management process. WECC_URE1 discovered that individuals in WECC_URE1's IT department had not been using the CIP change management checklist, as required under the most recent WECC_URE1 CIP change management program. There were 13 change control efforts in scope. Additionally, an individual on WECC_URE1's network team removed a router classified as a Critical Cyber Asset (CCA) and replaced it without following the CIP change management program document. This change was identified as a break/fix scenario that met the qualifications of an emergency fix under WECC_URE1's CIP change management program. However, documentation was not updated, and CIP controls were not performed within the prescribed 30-day time parameter for an emergency fix, as required by the program. WECC_URE1 reported that it failed to follow its change control and configuration management process on 14 instances for CCAs and Cyber Assets associated with its control center and back-up control center. WECC, therefore, determined that WECC_URE1 was in violation of CIP-003-3 R6 for failure to follow its change control management process on 14 instances, during a two-month period. | CIP-003-3 | R6 | Lower | Severe | WECC determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to follow a change control and configuration management process could introduce potential security vulnerabilities to CCAs. The risk, however, was limited because all CCAs were located within Electronic Security Perimeters where logging was controlled and monitored. Furthermore, all CCAs were physically secured within a Physical Security Perimeter where physical access was controlled and monitored. WECC_URE1 did have a CIP change management program document in place and, in many instances, WECC_URE1 employees adhered to that program. All other controls related to patching on the workstations were performed appropriately, and the individual with access to the workstations had a personnel risk assessment and CIP training. | first instance of failure to follow the CIP change control and configuration management process | last instance of failure to follow the CIP change control and configuration management process | 5000 | Self-Report | WECC_URE1 submitted a Mitigation Plan addressing noncompliance with CIP-003-3 R6. WECC reviewed the plan and issued a Notice of Mitigation Plan Rejection. WECC_URE1 revised the plan and resubmitted it two months later. The following activities were completed in accordance with the Mitigation Plan: 1) WECC_URE1 management trained the affected employees on the proper procedures for CIP change control and configuration management to include all necessary steps to ensure that all CIP controls are met within all applicable timing requirements; and 2) WECC_URE1 completed the CIP change management checklist and ensured that all CIP controls were implemented appropriately, as applicable to each change effort. | 2012-09-28 | 2012-12-06 | Does Not Contest | WECC applied the following mitigating factors when determining the penalty amount: 1) WECC_URE1 self-reported the violation. 2) WECC_URE1 had an internal compliance program (ICP) at the time of the violation.
2012-12-31 | FERC | NP13-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010516 | Settlement Agreement | WECC conducted a joint CIP audit of WECC_URE2 and an affiliate's facilities. WECC_URE2 did develop a list of Critical Assets; however, while preparing for its audit, WECC_URE2 determined that six Critical Cyber Assets (CCAs) were not on WECC_URE2's official list of Critical Assets. The list was updated in anticipation of the audit. WECC reviewed the list and determined that only four of the devices qualified for inclusion on WECC_URE2's list of CCAs essential to the operation of its Critical Assets. Four of the devices were CCAs, while the other two were access points. Therefore, it was determined that WECC_URE2 failed to identify four Cyber Assets on its list of CCAs. WECC determined that WECC_URE2 violated CIP-002-1 R3 for failing to develop a complete list of CCAs essential to the operation of its Critical Assets. | CIP-002-1 | R3 | High | High | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, evidence gathered at the audit confirmed that each device received the following protections even though not on the CCA list: an original port scan; enabling of only necessary ports and services; a vulnerability assessment; user authentication using strong passwords; appropriate use banner; antivirus protection; location within an electronic security perimeter and within a physical security perimeter with no external electrical connectivity beyond the access points; and appropriate access requirements (including business need for access, annual CIP training and up-to-date Personnel Risk Assessments) met for all individuals with access to these devices. | when the Standard became mandatory and enforceable for WECC_URE2 | when WECC_URE2 updated its official hardware inventory list to include the four CCAs) | 15000 | Audit | WECC_URE2 updated and corrected its list of CCAs to include the four CCAs. In addition, WECC_URE2 conducted a comprehensive review and update of its energy management system (EMS) Cyber Assets inventory, including both critical and non-critical assets. WECC_URE2 held a meeting with appropriate staff to review the CIP CCA Methodology and WECC_URE2 inventory list. WECC_URE2 updated its EMS hardware inventory. Lastly, WECC_URE2 documented the review and update of the EMS Cyber Assets inventory work in a service ticket. | 2012-06-28 | 2012-10-26 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2012-12-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007407 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-002-2 R1.2 for a failure to include a documented evaluation criterion associated with the seven types of assets specified in R1.2 of the corporate documented risk-based assessment methodology (RBAM) used to identify Critical Assets (CAs). NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-002-2 R1.2. | CIP-002-2 | R1.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the absence of written language specifically documenting the evaluation criterion could have resulted in improper identification of CAs or some CAs not being identified at all. The risk was mitigated by the fact that NPCC_URE1 attested that it was using CA evaluation criterion in verbal discussions and reviews of the outcomes of engineering studies. Also, the addition of the evaluation criterion to the RBAM did not change the list of facilities or equipment that was previously identified as CAs. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its RBAM and added the required evaluation criteria into the document and communicated the RBAM revisions to the relevant staff; 2. Conducted a review to determine which assets should be on the CA list based on the revised RBAM; 3. Established a team to review the necessary components that need to be specifically documented as evaluation criteria; and 4. Drafted and obtained approval for the documented evaluation criterion. | 2011-04-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-12-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007408 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-003-2 R5 for a failure to develop a program that fully addressed the management of access to protected Critical Cyber Asset (CCA) information. Specifically, NPCC_URE1 neglected to document the process for gaining access (physical and logical) to protected CCA information. As a result, the list required in R5.1 was not kept, the annual review required by R5.2 was not performed, and the annual assessment required by R5.3 was not performed. NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-003-2 R5. | CIP-003-2 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because failure to manage the access to CCAs information could lead to security gaps and unauthorized individuals gaining access to this information. The risk was mitigated by the fact that the CCA information was securely stored, and only personnel with authorized physical or logical access were able to access the information. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Documented a list of managers who are responsible for authorizing access to protected information for NPCC_URE1's employees and contractors; 2. Made a revision to the procedure that documents the process for the designated managers to authorize access to protected information for NPCC_URE1's employees and contractors; 3. Provided cybersecurity training to the employees and contractors that have access to CCA information; and 4. Communicated the revision of the NPCC_URE1 procedure that documents the requirements for authorizing access to protected CCA information to all relevant personnel. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-12-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007409 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-004-2 R4 for a failure to maintain a list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). NPCC_URE1 discovered the violation during an internal review. The review revealed that NPCC_URE1's facility quarterly access reports were not consistent from quarter to quarter but did not contain an explanation of the changes. In addition, NPCC_URE1's access reports did not contain detailed electronic rights, as required by this Standard. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-004-2 R4. | CIP-004-2 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to maintain a list of personnel with access to CCAs could lead to security gaps and unauthorized individuals gaining access to CCAs. The risk was further mitigated by the fact that NPCC_URE1 had physical access control, electronic access control, and electronic alerting procedures already in place. Also, all individuals at issue had completed cybersecurity training and had a personnel risk assessment. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Performed a detailed review of individual physical access rights and individual electronic access rights; 2. Created and revised an access tracking matrix. Also, an access authorization form was created to be used by management in assigning physical and electronic access and ensure uniformity and consistency; 3. Revised the corporate document that describes how physical and electronic rights will be granted and tracked. The corporate document refers to the revised access authorization form as an appendix; and 4. Communicated to all relevant personnel the revised corporate procedure and expected actions. | 2011-09-30 | 2012-02-17 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-12-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007410 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-005-2 R1.5 for a failure to protect fully a Cyber Asset (CA) used in the access control and/or monitoring of a Electronic Security Perimeter (ESP), as required in R1.5. The CA was a remote server that monitored electronic access. NPCC_URE1 discovered the violation during an internal review. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-005-2 R1.5. | CIP-005-2 | R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to afford all required protective measures to the CAs could lead to security gaps and unauthorized individuals gaining access to the CAs and ESPs. The risk was mitigated by the fact that the devices at issue were located on a secure network logically protected by strict firewall access control lists. Further, physical access to the CAs was restricted with key card access though the Physical Security Perimeter (PSP). | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Removed from service and replaced the not fully protected remote server that monitored electronic access with a server that is within the ESP and within a defined PSP; 2. Made a revision to its procedures to include assets involved in access control and/or monitoring in its cyber program; and 3. Reviewed its risk-based assessment methodology list which resulted in the removal of the CA from the list that was the subject of this violation. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-12-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007411 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R1 for a failure to create, implement, and maintain cybersecurity test procedures to perform testing for any of its Critical Cyber Assets (CCAs), its access control and monitoring devices, or its Cyber Assets (CAs). Although changes were tested using a test environment, they were not part of a documented process, and a "before and after" snapshot was not compared after the updates were put into production. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R1. | CIP-007-2a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to have documented procedure for testing its cybersecurity devices could lead to inconsistent testing and potential vulnerabilities of NPCC_URE1's system. The risk was mitigated by the fact that actual testing via the corporate change management procedure was being performed before and after CCA changes were made even without the existence of a written CCA testing process and written guidance on CCA records retention. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Established a series of actions for testing of security controls specific to categories of CAs; 2. Documented the security test procedure for each set of category of CAs; and 3. Communicated new security category specific security test procedures to all relevant staff. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007412 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R3 for a failure to track, evaluate, test and install applicable cybersecurity software patches to its CCAs, access control monitoring devices and other non-critical Cyber Assets devices within the Electronic Security Perimeter (ESP). Security patch activity and review had taken place only for the ESP access points. This violation was discovered during an internal audit. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R3. | CIP-007-2a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a failure to track, evaluate, test and install security patches could lead to cyber vulnerability of the devices at issue. The risk was mitigated by the fact that the devices were located within the ESP. Further, intrusion detection and security logging measures were already in place for all assets. Finally, patches of a certain type have been evaluated as part of a general practice for NPCC_URE1. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Determined which equipment within the ESP needed security patch testing and determined whether there were patches available for installation on this equipment; 2. Performed testing on the patches for installation; 3. Installed the security patches after testing was completed; 4. Updated all relevant documentation to address the requirements of this Standard; and 5. Communicated updates to all relevant staff. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007413 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R4.2 for the failure to document and implement a process for the update of anti-virus and malware prevention “signatures,” along with failing to address testing and installing the signatures. Additionally, the signature files associated with anti-virus/ malware updates were not tested prior to installation on Cyber Assets within the Electronic Security Perimeter (ESP). After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R4. | CIP-007-2a | R4.2 | Medium | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because a possible errant signature update could potentially cause a system to behave abnormally or have serious availability issues. The risk was mitigated by the fact that NPCC_URE1 had implemented intrusion detection systems, security logging, cyber and physical access control and a defense-in-depth network design. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Determined the environment needed to test signature files prior to installation of equipment in ESPs; 2. Built the environment where anti-virus software and malware prevention updates could be tested; 3. Updated the documentation relevant to this Standard; and 4. Notified staff engaged in managing Cyber Assets within the ESP of the changes and made them aware of the requirements. | 2012-05-25 | 2012-06-21 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007414 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-007-2a R5 for a failure to establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity. Specifically, NPCC_URE1 failed to implement its own documented password policy. NPCC_URE1 did not follow its own documented password management policy, which stated that passwords should be changed every 90 days. During an internal review, NPCC_URE1 discovered that passwords do not automatically expire and have not been changed since the Standard became mandatory and enforceable. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-007-2a R5. | CIP-007-2a | R5 | Lower | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1's process requiring password changes every 90 days was more strict than the NERC CIP requirement calling for a password change once a year. NPCC_URE1 changed its password within one calendar year, thereby reducing the risk to the BPS to minimal. In addition, NPCC_URE1 had a written password policy, required appropriate password complexity, and its system locked accounts out after invalid login attempts. | 90 days after this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its account management procedure to document its password management process to state that it must be done annually as required by R5; 2. Verified that all passwords associated with network equipment and Critical Cyber Assets were reset; and 3. Communicated the revisions to the password management process to relevant staff. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007417 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R1 for a failure to ensure that its physical security plan addressed at a minimum the requirements detailed in R1.1 through R1.8. NPCC_URE1 reported that the plan was not drafted to fully address the physical security practices NPCC_URE1 had implemented. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R1. | CIP-006-2 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 had the required physical security controls in place but failed to properly document these controls as required by CIP-006-2 R1. NPCC_URE1 had all Physical Security Perimeter (PSP) entry points documented and had measures to control access at these points (personnel risk assessments, cybersecurity training for the personnel with access, swipe card). Further, alarms were installed to facilitate monitoring the PSPs. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. Revised its corporate physical security procedure to address CIP-006 R1.1 through R1.8; and 2. Trained all personnel on the procedure changes. | 2011-09-22 | 2011-10-14 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered the lateness of the Mitigation Plan completion as an aggravating factor in the penalty determination. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007427 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R3 by not having a remote server associated with the monitoring of electronic access to Critical Assets (CAs) inside of a defined Physical Security Perimeter (PSP). After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R3. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because there were existing physical access control procedures in place at the NPCC_URE1 facility that housed the server at issue. These control procedures included: physical access control procedure at the corporate building, personnel risk assessment and cybersecurity training completed for personnel, swipe cards required to gain access to the server that resided within the PSP. Furthermore, the server was used for monitoring electronic access only, not granting or changing access, which further reduced the risk to the BPS. | when the server at issue was moved from a secure PSP at another company site and became unsecure at this point | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. The remote server that monitored electronic access was removed from service and replaced with a local server that monitors electronic access at the CA; 2. The new server is within the Electronic Security Perimeter (ESP) of the CA and within a defined PSP; and 3. All documentation relevant to this Standard was updated, and the staff engaged in managing Cyber Assets within the PSP was notified of the changes and made aware of the requirements. | 2011-11-30 | 2012-02-17 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007428 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it violated CIP-006-2 R8 by not having a written maintenance and testing program to ensure that all physical security systems under Standard CIP-006-1 R4, R5 and R6, function properly. After reviewing the Self-Report and supporting documentation, NPCC determined that NPCC_URE1 was in violation of CIP-006-2 R8. | CIP-006-2 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because under NPCC_URE1's vendor's recommendations, NPCC_URE1 would not have been required to perform testing and maintenance of all physical security mechanisms during the pendency of the violation. NPCC_URE1's vendor has recommended a three-year cycle of maintenance from the date of NPCC_URE1's registration. NPCC_URE1 discovered the violation and completed all mitigating activities within three years and eleven days, thereby reducing the risk to the BPS to minimal. | when this Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan completion | $40,000 (for NPCC2011007407, NPCC2011007408, NPCC2011007409, NPCC2011007410, NPCC2011007411, NPCC2011007412, NPCC2011007413, NPCC2011007414; NPCC2011007417, NPCC2011007427, and NPCC2011007428) | Self-Report | According to its Mitigation Plan, NPCC_URE1 took the following actions: 1. The recommended maintenance and testing protocols were obtained from the security system vendor; 2. The existing physical security procedure was revised to include the maintenance and testing protocols received from the security system vendor; and 3. Communicated to relevant staff the revisions of the physical security procedure. | 2011-06-30 | 2011-09-19 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP) to be a neutral factor in determining the penalty amount. NPCC considered as a mitigating factor that NPCC_URE1 self-reported all of the instant violations. In addition, NPCC considered the violation history.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000367 | Settlement Agreement | RFC_URE1 self-reported to RF noncompliance with CIP-006-1 R1.1. Within the Self-Report, RFC_URE1 identified 11 user interfaces listed on its Critical Cyber Asset (CCA) list that were not designated as being located in a Physical Security Perimeter (PSP) in the physical security plan. These 11 CCAs were completely enclosed in a “six-wall” border; however, RFC_URE1 did not identify this area as a PSP in its physical security plan. Therefore, RF determined that RFC_URE1 failed to document in the physical security plan that all Cyber Assets within an Electronic Security Perimeter (ESP) also reside within an identified PSP, as required by CIP-006-1 R1.1. | CIP-006-1 | R1.1 | Medium | High | RF determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The 11 identified CCAs were in a completely enclosed “six-wall” border. In addition, the 11 CCAs were physically located on the ground floor of RFC_URE1’s control center and in an ESP. Physical access to the control center was restricted by badge card readers, monitored by cameras and logged. Cyber events on the identified user interfaces were monitored by a security information and event management software and the CCAs were monitored for unauthorized changes. Visitors to the control center were logged and escorted. Finally, physical access to these devices was restricted to only those personnel who had undergone required personnel risk assessments (PRAs) and received appropriate security training. Therefore, RFC_URE1 had other mechanisms in place to provide physical protection to Cyber Assets, particularly the 11 user interfaces. | when RFC_URE1 was required to comply with CIP-006-1 R1.1 | Mitigation Plan completion | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) relocated the 11 CCAs to a defined PSP; (b) reviewed the physical security plan; (c) implemented a process for ensuring new Cyber Assets within the ESPs are also within PSPs; and (d) trained relevant personnel on these changes. | 2010-09-30 | 2011-01-18 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000624 | Settlement Agreement | RFC_URE1 self-reported to RF noncompliance with CIP-004-1 R3.2. RFC_URE1 reported that it had not completed a personnel risk assessment (PRA) for two individuals within seven years of each individual’s previous PRA. Specifically, RFC_URE1 discovered that it calculated the interval for completing the seven-year PRA based on each individual’s hire date, rather than calculating the interval based upon the prior PRA completion date. Therefore, individuals completing their PRA before their date of hire did not undergo the seven-year updated PRA on time. As a result, RFC_URE1 did not update PRAs at least every seven years after the initial PRA for two individuals. This violation involves two instances and therefore the duration of the violation spans two periods of time. | CIP-004-1 | R3.2 | Lower | Moderate | RF determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Both individuals had previously undergone initial PRAs and had received annual security training. Supervisors and critical area owners recertified the access possessed by both individuals quarterly. Finally, RFC_URE1 completed the PRAs for both individuals shortly after their expiration and those PRAs resulted in no negative findings. The foregoing circumstances therefore reduced the potential risk from unauthorized personnel access to Critical Cyber Assets (CCAs). | 1st instance: when a PRA was due for the first individual 2nd instance: when a PRA was due for the second individual | 1st instance: when RFC_URE1 completed the first individual's PRA 2nd instance: when RFC_URE1 completed the second individual's PRA | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) completed the seven-year PRAs for the two identified individuals; (b) completed a review of all individuals with PRAs conducted during or before 2003; (c) updated the PRA tracking system; (d) revised internal processes for tracking and maintaining PRAs; (e) provided training on the revised CIP-004 PRA processes, policies and procedures to Human Resources (HR) staff; and (f) hired an outside consultant for an independent review of HR processes related to NERC CIP Standards. | 2011-04-29 | 2012-06-26 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as an aggravating factor.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100747 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-004-3 R2.1. RFC_URE1 identified three individuals, all of whom were contractors, who received physical access to two of RFC_URE1’s Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs) without first completing security training. | CIP-004-3 | R2.1 | Medium | Severe | RF determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The three individuals had personnel risk assessments (PRAs) completed prior to RFC_URE1 granting access, with no negative findings. Video cameras were present, operational and monitored at the two PSPs in question. Furthermore, two of the identified individuals only used their physical access badges at common areas. The third individual was never on-site at RFC_URE1, and therefore, never received his physical access badge and never entered a PSP. The foregoing circumstances therefore reduced the potential risk from unauthorized personnel access to CCAs. | when physical access was granted to all three individuals | when RFC_URE1 disabled this physical access for all three individuals | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) disabled the PSP access granted to the three identified individuals; (b) modified the operating procedure for account authorization to require security training prior to granting access to CCAs; (c) evaluated contractors to whom RFC_URE1 granted physical access in order to ensure that no additional contractors received PSP access without having completed all requirements; and (d) updated RFC_URE1’s physical security documentation. | 2011-02-28 | 2011-05-06 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as an aggravating factor.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100780 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-007-2a R3.1. RFC_URE1 reported that it had not documented the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades for three security patches and one security upgrade. Specifically, RFC_URE1 did not timely assess three security patches for one non-Critical Cyber Asset residing in one of RFC_URE1’s identified Electronic Security Perimeters (ESPs). Once assessed in accordance with RFC_URE1’s policy, RFC_URE1 determined two of those security patches to be applicable. In addition, RFC_URE1 did not timely assess one security upgrade for a storage device residing on RFC_URE1’s servers within RFC_URE1s ESP. These servers are non-Critical Cyber Assets within the ESP. This violation involves two instances and therefore the duration of the violation spans two periods of time. | CIP-007-2a | R3.1 | Lower | Severe | RF determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. All relevant assessments, while not conducted within the thirty days specified by the Standard, were conducted within a very short timeframe after they were due. Both the security patches and security upgrade were applicable to non-Critical Assets. Regarding the security patches, in the event of an attack, the attacker could only impact the one identified Cyber Asset by manipulating the operating system’s memory to affect the Cyber Asset’s performance and availability. The vulnerability could not be exploited to reach other Cyber Assets within the ESP. Therefore, the function of the identified Cyber Asset reduced the risk of vulnerabilities resulting from RFC_URE1’s failure to implement its process for security patch management. Further, the security upgrade for the storage device was assigned an internal residual risk rating of “low” by RFC_URE1’s assessment team and was designed to remediate a vulnerability that could only be exploited from within the RFC_URE1 network. The term “residual risk rating” refers to a rating assigned by RFC_URE1 security and technology subject matter experts. If the patch or upgrade is designated as applicable, RFC_URE1 assigns a risk rating of “high,” “medium” or “low,” depending on the circumstances. The vendor rating and the associated criteria used to develop this rating for each patch or upgrade is used as the starting point for determining the internal risk rating for RFC_URE1. Based on the results of the discussion, the RFC_URE1 assigns an internal risk rating for each security patch or security upgrade. In addition, the vulnerabilities remediated by the security upgrade could only be exploited from within the RFC_URE1 network by individuals who had access to the servers on which the software resided. All such individuals had authorized cyber access along with the appropriate personnel risk assessments, training and security awareness as prescribed by the requirements of CIP-004. The identified Cyber Asset was only available to personnel with appropriate clearance. As a result, the foregoing circumstances reduced the risk from potential exploitation of the Cyber Asset. | 1st instance: when the first security patch was due for assessment 2nd instance: when the upgrade was due for assessment | 1st instance: when RFC_URE1 completed the assessment of all three security patches 2nd instance: when RFC_URE1 completed the upgrade assessment | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) completed a documented assessment of the three security patches and one security upgrade; (b) removed the non-Critical Cyber Asset from the ESP; and (c) established, documented, implemented and communicated a procedural control to verify that all security patches and security upgrades have been identified for assessment. | 2011-07-29 | 2012-08-20 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as a neutral factor.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100822 | Settlement Agreement | RFC_URE1 self-reported noncompliance with CIP-005-1 R1. RFC_URE1 connected a dial-up modem to a Critical Cyber Asset (CCAs) residing in an Electronic Security Perimeter (ESP). The dial-up modem permits a hardware vendor to remotely access the hardware management console of this CCA. The CCA was an enterprise storage device used by two other CCAs. The hardware management console was used to perform system administration tasks for the enterprise storage device. The dial-up modem was configured for both dial-in and dial-out capability. The dial-out capability was used to communicate component failure and system degradation of the enterprise storage device to the hardware vendor, who would replace components and address degradation. The dial-in capability was used by the hardware vendor’s support team, who would remotely perform troubleshooting activities. RFC_URE1 did not document the dial-up modem as an access point to the ESP, as required by CIP-005-1 R1.1. | CIP-005-1 | R1 | Medium | Lower | RF determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The identified device was specifically designed for a third-party vendor’s remote access to the ESP. RF did, however, consider that RFC_URE1 was unaware of this access point. The databases stored on the identified CCA are associated with the economic dispatch of the generation resources. If either or both databases are lost, then the economic dispatching of the generation could be compromised. However, this would not impact RFC_URE1’s ability to dispatch generation to support reliability of the transmission system. The risk to the reliability of the BPS was further mitigated by the controls in place to minimize remote access through the modem. As noted above, the modem allowed a hardware vendor to gain access to the hardware management console of one storage device. In order to utilize the dial-up modem for remote access, an individual requires an account, password, and unique key. A unique key is generated for each hardware management console and is stored in a secure database at the hardware vendor’s site. There are three accounts with varying levels of access that can be used to gain remote access. The passwords for these accounts are unique to each hardware management console and are changed every twenty-four hours. Data that is not stored on any enterprise storage device is not accessible via any of these accounts. RF further considered that while RFC_URE1 data residing on the identified CCA is not accessible via these accounts, two of the accounts have the ability to affect the availability of the data hosted on this CCA. | when RFC_URE1 was required to comply with CIP-005-1 R1 | when the dial-up modem was documented as an access point to the ESP | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) documented the modem as an ESP access point; (b) reconfigured the modem to remove dial-up capability; (c) confirmed that there are no dial-up accessible Cyber Assets within existing ESPs; (d) implemented a procedural control to validate new Cyber Assets being added to the ESP are not dial-up accessible; and (e) reviewed and updated the quarterly modem discovery scan process. | 2011-06-09 | 2012-08-27 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100864 | Settlement Agreement | RFC_URE1 submitted a Self-Certification identifying noncompliance with CIP-007-3 R2. RFC_URE1 established and documented multiple processes to ensure this requirement is met for the different types of Cyber Assets that reside within its Electronic Security Perimeters (ESPs). However, RFC_URE1 discovered that it did not implement certain components of its process for those Cyber Assets running a RFC_URE1 installation of two operating systems and those Cyber Assets categorized as storage devices. Thus, RFC_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled. | CIP-007-2a | R2 | Medium | Severe | RF determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Using a thorough review process, RFC_URE1 determined that the potential for a cyber attack via the identified ports and services was low given the security controls in place at the time of the violation. In particular, all of the ports and services disabled subsequent to the review could not have been accessed from outside of the ESP. In addition, immediately after discovery of this issue, RFC_URE1 performed a review of all ports and services enabled on those Cyber Assets within RFC_URE1’s ESPs running a RFC_URE1 installation of the two identified operating systems and those Cyber Assets categorized as storage devices. Ports and services not required for normal and emergency operations were disabled. | when RFC_URE1 was required to comply with CIP-007-2a R2 | when RFC_URE1 established, documented and implemented new processes for ensuring that only those ports and services required for normal and emergency operations are enabled | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Certification | RFC_URE1 performed a comprehensive review of all Cyber Assets, and disabled all ports and services that were not needed for normal or emergency operations. In addition, RFC_URE1 updated and published new procedures that govern the ports and services of the assets in question, and implemented more robust detection mechanisms to provide visibility into the status of the entire range where ports may be allocated. Last, training on the new procedures was completed. | 2011-08-19 | 2012-08-27 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as a neutral factor.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100865 | Settlement Agreement | RFC_URE1 submitted a Self-Certification, identifying noncompliance with CIP-007-1 R6. The following month, RFC_URE1 submitted additional information regarding this violation of CIP-007-1 R6. Specifically, RFC_URE1 utilizes a security information and event management software, to comply with CIP-007-1R6. This software stores security audit log data from systems that are properly connected and provides alerting and monitoring capabilities to help identify unauthorized activity on RFC_URE1’s devices. RFC_URE1 identified Cyber Assets within its Electronic Security Perimeters (ESPs) that were not configured to send log data to the security information and event management software. These Cyber Assets provide the infrastructure data storage used by other Cyber Assets within RFC_URE1’s ESPs. As a result of RFC_URE1’s failure to configure these devices to send log data, these Cyber Assets did not have automated tools or organizational process controls to monitor system events related to cyber security. The violation involved 7.2% of the total assets at RFC_URE1. | CIP-007-1 | R6 | Lower | Moderate | RF determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Although RFC_URE1 had limited visibility to security incidents that may have occurred on these identified Cyber Assets, RFC_URE1’s infrastructure had additional layers of defense that provided some security and made these Cyber Assets visible to the security information and event management software for monitoring through other means. For example, RFC_URE1’s firewalls and other network devices send data to the security information and event management software, which monitors the network activity related to these Cyber Assets and sends alerts of suspicious events. In addition, RFC_URE1’s intrusion detection systems monitor network activity for these Cyber Assets and alert on suspicious events. Therefore, RFC_URE1 had other mechanisms in place to monitor system events that are related to cyber security, thereby reducing the risk to the BPS to moderate. | when RFC_URE1 was required to comply with CIP-007-1 | when RFC_URE1 ensured that all Assets within the ESPs were correctly configured and were sending data | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Certification | RFC_URE1 initially performed a reconciliation of its ESP Cyber Assets and the security information and event management software to determine Cyber Assets that were not sending audit log data. Based upon the results of that reconciliation, RFC_URE1 then correctly configured Cyber Assets that had been identified as not sending audit log data. Moreover, RFC_URE1 had previously created procedures to ensure that audit logging is implemented for deploying new Cyber Assets into ESPs and verified that appropriate procedures were in place to ensure that audit logging would be completed prospectively. RFC_URE1 also revalidated that all Cyber Assets were reporting to the software and implemented a monthly process to reconcile the list of Cyber Assets with those being monitored. Last, RFC_URE1 reviewed its need to document Technical Feasibility Exceptions for those Cyber Assets that remained in the ESP for which audit logs cannot be sent to the software, and found none. | 2011-12-15 | 2012-08-27 | Neither Admits nor Denies | RF considered RFC_URE1's established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as a neutral factor.
2012-10-31 | FERC | NP13-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100942 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-007-1 R5. RFC_URE1 identified five Cyber Assets residing within RFC_URE1’s Electronic Security Perimeters (ESPs) for which RFC_URE1 did not enforce the password criteria specified in CIP-007-1 R5.3. The Cyber Assets were storage devices, which are appliances that contain redundant and highly available sets of disks that are portioned out to various host operating systems. Each appliance has local accounts used to manage the appliance. Each appliance contains local user accounts: 50% are system administrator accounts for RFC_URE1 staff, and 50% are default or system/service accounts. Specifically, for two default system accounts on each of the five Cyber Assets (for a total of ten accounts), RFC_URE1 did not enforce the minimum password length of six characters, as required by CIP-007-1 R5.3.1. For all accounts on each of the five identified Cyber Assets, RFC_URE1 did not require that each password consist of a combination of alpha, numeric and “special” characters, as required by CIP-007-1 R5.3.2. | CIP-007-1 | R5.3 | Lower | Moderate | RF determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the bulk power system was mitigated by the following factors. The appliances impacted one of RFC_URE1’s systems which governs the economic dispatch of generation resources. Reliability impacts that could have resulted from the misuse of the system would have been mitigated by an operator’s ability to utilize its manual dispatch capabilities in response to any perceived data anomalies. Moreover, RFC_URE1 reviewed all of its emergency service tickets during the period of the violation to determine whether there was an adverse impact to the availability of these systems. These types of tickets are opened when an ongoing operational issue is identified and occurs for more than 30 minutes. RFC_URE1 determined that one ticket was created for the identified system; however, upon in-depth review, it was determined that this identified issue was not related to the storage appliance. | when the devices were added to the ESP | when RFC_URE1 enforced the password composition criteria of CIP-007-3-1 R5.3 for each of the Cyber Assets residing within RFC_URE1's ESPs | $30,000 (for RFC201000367, RFC201000624, RFC201100747, RFC201100780, RFC201100822, RFC201100864, RFC201100865, and RFC201100942) | Self-Report | RFC_URE1 (a) enforced the password composition criteria of CIP-007 R5.3; (b) implemented a procedural control to verify compliance; (c) performed a compliance review of all storage devices within the ESP to verify compliance with CIP-0070 R5.3; (d) reviewed and updated documentation to include the new procedural control; and (e) communicated the new procedural control to relevant staff. | 2011-06-29 | 2012-06-26 | Neither Admits nor Denies | RF considered RFC_URE1’s established, formal internal compliance program (ICP) as a mitigating factor. RF also considered the fact that RFC_URE1 self-reported the violation and applied mitigating credit. RF considered the violation history of RFC_URE1 as a neutral factor.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000376 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-003-1 R5. SPPRE_URE1 failed to document and implement a program for managing access to protected Critical Cyber Asset (CCA) information until 17 months after the compliance enforcement date of the Standard. Although SPPRE_URE1 did have some documented procedures for managing access to CCA information, its procedures did not address all the requirements of this Standard. Specifically, SPPRE_URE1 did have documented procedures to limit access to CCAs and CCA information to those with cleared background checks and did review the access list quarterly. SPPRE_URE1’s cybersecurity policies did address information owners and made them responsible for protecting that information. It also stated that access to information must be made in accordance with job responsibilities. As part of the annual review of the cybersecurity plan documents, this information protection section would have also been reviewed. However, SPPRE_URE1 failed to maintain a list of designated personnel consistent with the requirements of R5.1, as well as failed to confirm that access privileges were correct and that they corresponded with SPPRE_URE1's needs and appropriate personnel roles and responsibilities, as required by R.5.2. In addition, SPPRE_URE1 had protective measures in place to protect CCA information from unauthorized access, but SPPRE_URE1 did not assess and document at least annually the processes for controlling access privileges to protected information, as required by R5.3. | CIP-003-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1 did have documented procedures to identify and classify CCAs, although SPPRE_URE1 did not address all the requirements of the Standard. SPPRE_URE1 stored CCA information on a restricted site and limited access file shares. SPPRE_URE1 had some documented procedures to manage access to the CCA information, including limiting access to CCAs and CCA information to only those with cleared background checks and quarterly reviews of access lists. Moreover, SPPRE_URE1 had protective measures to protect CCA information from unauthorized access, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | when SPPRE_URE1 documented and implemented its CCA information protection program | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 documented and implemented a CCA information protection program. Additionally, SPPRE_URE1 trained affected personnel on the program. As part of the program, SPPRE_URE1 implemented steps to identify, classify and protect information associated with CCAs. SPPRE_URE1 implemented a program for its document management site security and permission management for protected information. | 2011-02-25 | 2011-03-22 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000378 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-005-1 R3. SPPRE_URE1 failed to implement and document an electronic or manual process for monitoring and logging access at access points to the Electronic Security Perimeter (ESP) twenty-four hours a day, seven days a week. Specifically, at the time of the violation, all devices defined as access points to SPPRE_URE1’s ESP were configured to log security-related events to a central logging tool. While SPPRE_URE1’s security monitoring system was incapable of alerting for attempts at or actual unauthorized accesses, SPPRE_URE1 periodically (at least monthly) manually monitored for unauthorized access attempts. However, because the logs were backed up on tapes, the logs were not easily retrievable; therefore, not all relevant historical logs were reviewed at least every ninety calendar days. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because failure to implement an electronic or manual process for monitoring and logging access at access points presented a risk of SPPRE_URE1 not being aware of unauthorized attempts and/or access into SPPRE_URE1’s ESP. SPPRE_URE1 did, however, have protective measures in place to protect Critical Cyber Assets (CCAs), including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | when SPPRE_URE1 implemented and documented its process for monitoring and logging access at access points to its ESP | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 implemented and documented an electronic process for monitoring and logging access at access points to its ESP twenty-four hours a day, seven days a week. SPPRE_URE1 also installed and tested firewalls at all access points to its ESP; the firewall configurations were hardened to strengthen the security of its servers. Additionally, SPPRE_URE1 configured the firewalls to monitor and log all access points to the ESP twenty-four hours a day, seven days a week, and verified that the monitoring system is capable of detecting and alerting attempts at or actual unauthorized access to the appropriate designated response personnel. | 2011-06-30 | 2011-11-15 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000379 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-005-1 R4. Although SPPRE_URE1 had a documented process for performing cyber vulnerability assessments (CVAs) of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), it did not have a documented process for performing CVAs of access points to the ESP, as required by CIP-005-1 R4.1. Additionally, because no baseline of its ports and services had been conducted, SPPRE_URE1 was unable to ensure that only ports and services required for operations at access points to the ESP were enabled, as required by R4.2. Further, while SPPRE_URE1 conducted CVAs, SPPRE_URE1 did not have a documented process for discovering all access points to the ESP, as required by R4.3. Lastly, although action plans to remediate vulnerabilities identified in the assessment were created, SPPRE_URE1 was unable to provide documentation that such remediation had been executed, as required by R4.5. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1's failure to have a sufficient process for conducting CVAs of access points to the ESP could have led to unauthorized access. This risk was mitigated by the fact that although the required documented review process was not in place, SPPRE_URE1 did conduct CVAs. Additionally, the affected CAs and Critical Cyber Assets (CCAs) were within SPPRE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 performed its annual CVA of the access points to its ESP and developed an action plan to remediate the vulnerabilities found. Additionally, SPPRE_URE1 developed a comprehensive CVA process, which requires an annual review of ports and services required for operations at access points to the ESP; a review of ports and services required for operations of access points; discovery of all access points to the ESP; and a review of controls for default accounts, passwords and network management community strings. The CVA process requires documentation of the results of the assessments, remediation plans to address vulnerabilities discovered in the assessments and execution status of the plans. To prevent recurrence of the violation, SPPRE_URE1 installed firewalls at access points to the ESP to reduce the risk of vulnerabilities to CAs within the ESP. Moreover, SPPRE_URE1 installed into the firewalls an advanced inspection and prevention security services card and an intrusion protection and intrusion prevention system card to further reduce the risk of vulnerabilities. | 2011-08-31 | 2011-11-15 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000383 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R2. SPPRE_URE1 did not establish a documented process for ensuring that only those ports and services required for normal and emergency operations were enabled, as required by R2. Although SPPRE_URE1 conducted a baseline for some devices, it did not conduct a baseline of ports and services to ensure that only ports and services required for normal and emergency operations were enabled, as required by R2.1. Further, SPPRE_URE1 was unable to provide documentation that it disabled other ports and services not required for normal and emergency operations prior to production use of all Cyber Assets (CAs) inside the Electronic Security Perimeter (ESP), as required by R2.2. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because undocumented port configurations presented a risk of incorrect configurations and port vulnerability, port failure, or port inaccessibility in certain situations. Failure to ensure properly designated ports and services were disabled prior to production use of Critical Cyber Assets (CCAs) within the ESP could have led to ports or services failure and/or unauthorized access to CCAs. Failure to review baseline documents resulted in a failure to ensure their continued integrity. However, the risk posed by SPPRE_URE1’s noncompliance was lessened because the affected CAs and CCAs were within SPPRE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 implemented a documented process to ensure that only ports and services required for normal and emergency operations are enabled. SPPRE_URE1 also purchased a quality assurance system for the new software system to provide a test environment to determine a baseline for ports and services within the system’s environment. SPPRE_URE1 performed vulnerability assessments and ran port scans on workstations to develop a baseline and compare the baseline to scans after system changes. SPPRE_URE1 replaced the previous access points, which were switches, with firewalls and hardened the configuration of those firewalls to only enable the required ports and services. SPPRE_URE1 installed new software into the firewalls to further protect its CAs within the ESP. The software’s intrusion prevention capabilities significantly enhance firewall protection by blocking threats and network attacks including worms, Trojans, viruses, and attacks against operating system and application vulnerabilities. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000384 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R3. SPPRE_URE1 failed to implement a documented security patch management program for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). Additionally, although SPPRE_URE1 documented that it tracked, assessed and implemented security patches and upgrades to some of its servers within its ESP, SPPRE_URE1 was unable to provide such documentation for all servers within the ESP. Further, some of the security patches and upgrades that were tracked and evaluated were not done within thirty calendar days of their availability, as required by R3.1. Moreover, SPPRE_URE1’s documentation indicated that a few evaluated security patches were not installed and the documentation did not include compensating measures applied to mitigate risk exposure or an acceptance of risk, as required by R3.2. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to test and implement all available security patches or updates for CAs within the ESP presented a risk that out-of-date security patches could allow unauthorized electronic access and potential compromise to Critical Cyber Assets (CCAs) that support BPS reliability. However, SPPRE_URE1 did evaluate and implement some security patches and updates to some of its CAs within its ESP. Additionally, the risk posed by SPPRE_URE1’s noncompliance was lessened because the affected CAs and CCAs were within SPPRE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 implemented a documented security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches and upgrades for all CAs within its ESP. SPPRE_URE1 also replaced the previous access points (i.e., switches) to its ESP with firewalls. SPPRE_URE1 purchased and is using a quality assurance system and software to ensure testing and assessment of patches and upgrades prior to installation and to create applicable reports and assessments. SPPRE_URE1 also installed new software into the firewalls to further protect its CAs within the ESP. For instance, the software’s intrusion prevention capabilities greatly enhance firewall protection by blocking threats and network attacks including worms, Trojans, viruses, and attacks against operating system and application vulnerabilities. SPPRE_URE1 is now documenting all of its assessment of security patches and upgrades for applicability within thirty calendar days of their availability and has a documented process for situations in which patches were not installed for documenting compensating measures applied to mitigate risk exposure or an acceptance of risk. | 3/38/2011 | 2011-05-03 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000385 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R6. SPPRE_URE1 failed to implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), as required by R6.1. Additionally, not all CAs (e.g., servers, remote terminal units) within SPPRE_URE1’s ESP were capable of issuing automated or manual alerts for detected Cyber Security Incidents, as required by R6.2. | CIP-007-1 | R6; R6.1; R6.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to have processes to monitor system events related to cybersecurity presented a risk that SPPRE_URE1 would not have the ability to respond to critical security events, thereby placing Critical Cyber Assets (CCAs) at risk of being compromised. Although there was not a formal process in place, some of SPPRE_URE1’s CAs were being monitored, such as SCADA production workstations, including servers and remote terminal units. A system was used to monitor user log-on/off, success/failures and system errors for corporate servers and firewalls. It also monitored normal logs like sessions being built/torn down on the firewalls. SPPRE_URE1 also had protective measures in place to protect CAs and CCAs within its ESP, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 implemented and documented formal organizational processes and technical and procedural mechanisms for monitoring security events on all CAs within the ESP. SPPRE_URE1 worked with its energy management system (EMS)/SCADA vendor and installed a new security and compliance management automation system to monitor and alert cybersecurity events within the EMS environment twenty-four hours a day, seven days a week. SPPRE_URE1 also set up the new automated system into its quality assurance system so that testing of various configuration changes to the automated system can be made without impacting the EMS environment. All CAs within SPPRE_URE1’s ESP are now capable of issuing automated alerts for detected cybersecurity incidents. | 2011-06-30 | 2011-07-22 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000386 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R7. SPPRE_URE1 failed to establish formal methods, processes and procedures for both disposal and redeployment of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). | CIP-007-1 | R7 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because any obsolete or out-of-service CAs were stored securely within the ESP. If any CAs would have needed to be disposed of or redeployed during the violation, device drives would have been removed and set aside in a secure environment to be wiped at a later date in bulk. SPPRE_URE1 has been removing drives from its computers since at least before the Standard became mandatory and enforceable, and wiping them using software rated for use by the Department of Defense, simply as good practice. Additionally, the affected CAs were within SPPRE_URE1’s ESP and were afforded some of the measures to protect Critical Cyber Assets (CCAs), including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 developed and formalized methods, processes and procedures for disposal and redeployment of CAs within its ESP to prevent unauthorized retrieval of sensitive cybersecurity or reliability data contained on media used within its ESP. All affected personnel have been trained on all such methods, processes and procedures. | 2010-10-08 | 2011-01-13 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000387 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R8. SPPRE_URE1 had a documented process for its cyber vulnerability assessments (CVAs) of Cyber Assets (CAs) within its Electronic Security Perimeter (ESP), as required by R8.1; however, the process did not address all the requirements of the Standard. First, the documented process did not require the CVA to be performed annually, as required by R8. Additionally, although SPPRE_URE1 conducted CVAs of CAs within its ESP, SPPRE_URE1 did not have a test environment, and its documented process did not include a review and verification process to ensure that only ports and services required for operation of CAs within the ESP were enabled, as required by R8.2. SPPRE_URE1 did not conduct a baseline of ports and services to determine which ports and services needed to be enabled for operations of CAs within its ESP. Further, while reviews of controls for default accounts were conducted, SPPRE_URE1 failed to include these reviews in its documented CVA process, as required by R8.3. In addition, SPPRE_URE1 confirmed that its CVAs may not have identified all vulnerabilities of such default accounts. Although remediation plans to address discovered vulnerabilities from the assessments were created, SPPRE_URE1 was unable to produce documentation to show that it executed the remediation plans, as required by R8.4, since its documented CVA process did not include a process for doing so. | CIP-007-1 | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to perform complete CVAs may have led to a failure to identify all systems or components at risk and mitigation of any known vulnerabilities, which could have placed CAs within the ESP and the BPS at risk. Although not all of the required documented review processes were in place, SPPRE_URE1 did conduct CVAs. Additionally, the affected CAs were within SPPRE_URE1’s ESP and were afforded some protective measures, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 developed a comprehensive CVA process, including an annual policy review provision and performed a CVA using the new procedures. The policy now requires a baseline of ports and services; a review to ensure that only ports and services required for operations of CAs within the ESP are enabled; a review of controls for default accounts; documentation of the results of the CVAs; remediation plans to address vulnerabilities discovered in the assessments; and execution status of the plans. To prevent recurrence of the violation and to further reduce the risk of vulnerabilities, SPPRE_URE1 installed firewalls at access points to the ESP. SPPRE_URE1 also installed into the firewalls an advanced inspection and prevention security services card and an intrusion protection and intrusion prevention system card. SPPRE_URE1 provided documentation demonstrating adherence to its implemented CVA process. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000388 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-007-1 R9. SPPRE_URE1 failed to conduct an annual review of the documents and procedures it maintains pursuant to CIP-007. Additionally, SPPRE_URE1 failed to document changes resulting from modifications to the systems or controls within 90 days of such changes. | CIP-007-1 | R9 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to conduct the required documentation review and maintenance presented a risk that SPPRE_URE1 would not sufficiently assess vulnerabilities to Critical Cyber Assets (CCAs) and Cyber Assets (CAs) within its Electronic Security Perimeter (ESP). However, SPPRE_URE1 did have documented and informal procedures for compliance with some of CIP-007. For example, SPPRE_URE1 conducted baseline testing of ports and services for some of its devices; documented, tracked, assessed, and implemented security patches and upgrades to some of its servers within the ESP; and had a documented process for its cyber vulnerability assessments, even though it did not address all of the requirements of the Standard. Additionally, SPPRE_URE1 had protective measures in place to protect CAs and CCAs, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 revised its cyber security policy to include a provision specifically addressing CIP-007 R9 with language noting that SPPRE_URE1 will: (1) review and update the documentation specified in CIP-007 at least annually; and (2) document any changes resulting from modifications to the systems or controls within thirty calendar days from the date of such changes. SPPRE_URE1 also developed, documented and implemented a CIP-007 systems management process manual, which requires an annual review of the manual and provides specific procedures for documenting changes resulting from modifications to its systems or controls. Additionally, SPPRE_URE1 revised its vulnerability assessment process to provide more detailed procedures for conducting, reviewing, and documenting remediation and changes made to systems or controls. Lastly, SPPRE_URE1 provided attestations from all affected personnel that they are aware of and understand the new CIP-007 R9 policies and procedures. | 2011-09-30 | 2011-10-14 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000389 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that was in violation of CIP-009-1 R4. Although SPPRE_URE1 had a recovery plan, its plan did not include processes and procedures for the backup and storage of information required to successfully restore its Critical Cyber Assets (CCAs). | CIP-009-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 failed to implement documented procedures, in practice, it was backing up and storing information that could successfully restore all of its CCAs. For instance, SPPRE_URE1's SCADA software automatically ran backups of its CCAs, and reports of such backups were regularly reviewed to ensure the backups were running as scheduled and that no errors were reported. Further, SPPRE_URE1 did have protective measures in place to protect CCAs, including permissions providing access control for files and folders; permissions controlling access to network resources based on job functions; a program to protect, analyze and control the user accounts of its document management environment; card swipes and bio readers for sensitive areas; locking drawers; video surveillance; port security to protect devices from viruses and security breaches; password and lockout policies; and personnel physical and cyber access reviews and control processes. Additionally, SPPRE_URE1’s network is isolated without Internet connectivity. Lastly, according to SPPRE_URE1, there have been no incidents requiring recovery of CCAs from a backup. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 revised its recovery plan processes and procedures to include the backup and storage of information required to successfully restore its CCAs. All affected personnel have been trained on the new processes and procedures. | 2011-02-23 | 2011-06-29 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100520 | Settlement Agreement | Pursuant to a Self-Certification by SPPRE_URE1, SPP RE determined that SPPRE_URE1 was in violation of CIP-006-1 R3. SPPRE_URE1 failed to fully implement its documented procedures to monitor physical access points to its Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. Specifically, SPPRE_URE1’s physical access security policies and procedures provide for camera observation of all access points to Critical Cyber Assets (CCAs), twenty-four hours a day, seven days a week. The policies and procedures also provide that SPPRE_URE1’s security system will monitor all access points to its PSP, twenty-four hours a day, seven days a week, and is capable of issuing an alarm, as well as an alarm summary report via security system consoles, to security department personnel for unauthorized access or access attempts of any access point to the PSP. Additionally, the policies and procedures require the security department personnel to review all alarms and alarm summary reports as part of their daily duties. Although camera surveillance was being conducted and SPPRE_URE1’s security system was capable of issuing alarms and alarm reports twenty-four hours a day, seven days a week to security department personnel for unauthorized access or access attempts at access points to the PSP, such human observation and notifications would be observed and immediately investigated only when security department personnel were on-site. Security department personnel were on-site during normal business hours and outside normal business hours. Consequently, SPPRE_URE1 did not fully implement its documented physical security policies and procedures to ensure that immediate notification of unauthorized access or access attempts was given to personnel responsible for investigating and responding to such security breaches, as required by CIP-006-1 R3. | CIP-006-1 | R3; R3.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 failed to fully implement its procedure as required, physical access points to its PSP were being monitored on a daily basis, and there were multiple layers of security measures in place to prevent unauthorized access to the PSP. During normal business hours, SPPRE_URE1’s CCAs had two layers of protection. For instance, once inside SPPRE_URE1’s main lobby, a badge was required to gain access to any area outside the lobby, which included all doors and hallways that led to access points to the PSP. If an intruder somehow had gotten past the first layer of protection, a badge and biometrics were required to gain access to the PSP. Thus, had there been a break-in during normal business hours, SPPRE_URE1 operators, who worked throughout areas beyond the lobby and within the PSP on a daily basis, most likely would have seen the intruder and would have investigated and/or called SPPRE_URE1’s security department prompting an immediate investigation. Even if an intruder had not been seen by an operator, the break-in would have triggered an alarm alerting SPPRE_URE1’s security department of an unauthorized access or access attempt, prompting an immediate investigation. Additionally, all access points to SPPRE_URE1’s PSP were under camera observation, which was recorded twenty-four hours a day, seven days a week, and monitored during normal business hours. Consequently, any malicious activity conducted during that time period would have been seen and immediately investigated by security department personnel. Outside normal business hours, the CCAs were protected by three layers of protection. For example, a badge and biometrics were required to gain access into the facility. Once inside the facility, the same two layers of protection indicated during normal business hours were in place to gain access to any of SPPRE_URE1’s CCAs. Furthermore, if an intruder somehow had gotten through all three layers of protection at times in which SPPRE_URE1 security department personnel were on-site after hours, the break-in would have triggered an alarm alerting them of an unauthorized access or access attempt, prompting an immediate investigation. Also, the security cameras were under human observation; therefore, any malicious activity conducted during that time period would have been seen and immediately investigated by security department personnel. Lastly, during the time period of the violation, there were no known break-ins into any of SPPRE_URE1’s PSPs. | when the Standard became mandatory and enforceable on SPPRE_URE1 | Mitigation Plan completion | $25,000 (for SPP201000376, SPP201000378, SPP201000379, SPP201000383, SPP201000384, SPP201000385, SPP201000386, SPP201000387, SPP201000388, SPP201000389, and SPP201100520) | Self-Certification | To mitigate this violation, SPPRE_URE1 hired additional personnel to fully implement its documented physical access policies and procedures to ensure immediate review and response to unauthorized access or access attempts at all access points to its PSP. SPPRE_URE1 also revised its physical security policies and procedures to make it more clear as to what steps are to be taken and specific contact information should an issue arise. All affected personnel were trained on the revised policies and procedures. | 2011-09-29 | 2011-11-09 | Neither Admits nor Denies | SPPRE_URE1 has a documented internal compliance program (ICP) and SPP RE considered SPPRE_URE1's ICP to be a mitigating factor in the penalty determination.
2012-10-31 | FERC | NP13-5-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100264 | Settlement Agreement | During a Compliance Audit, Texas RE found that Texas RE_URE1 was in violation of CIP-007-1 R2 because Texas RE_URE1's annual cyber vulnerability assessment (CVA) showed multiple logical ports/services that were enabled on Cyber Assets and printers within the Electronic Security Perimeter (ESP); however, these ports/services were not required for normal or emergency operations. The ports identified represent 0.3% of all ports identified during the CVA. The majority of the ports were associated with a message application running on a workstation that no longer was used to process, aggregate, or store messages. The remainder unnecessary port was associated with a system service that Texas RE_URE1 does not need for normal or emergency operations. | CIP-007-1 | R2; R2.1 | Medium | Lower | Texas RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had risk mitigating controls, policies, and procedures in place during the pendency of the violation, as follows: (a) A search of the National Vulnerability Database for vulnerabilities related to the services using the open ports revealed no reported vulnerabilities; (b) Texas RE_URE1 utilizes firewalls to filter incoming network traffic. Logs are reviewed weekly, at which time the unusual activity would have been noted and further investigated; (c) In addition to the network-based defenses of the firewalls and intrusion protection system (IPS), Texas RE_URE1 uses other defense-in-depth measures to protect assets from both known and undiscovered vulnerabilities. Texas RE_URE1 uses a white-listing anti-virus application on all servers and workstations that prevents the execution of applications that have not been previously authorized. It also detects when modified or unauthorized libraries are in-use in memory and blocks their execution. Daily scans of system files and configurations for changes help to detect both authorized and unauthorized system modifications. Also, network traffic from Texas RE_URE1 ESPs is not routable to the internet or on the private supervisory control and data acquisition (SCADA) network. Physical access to Texas RE_URE1 ESPs is protected by secured areas with limited access to reduce the number of personnel who have the opportunity to access devices; (d) Texas RE_URE1 uses a network IPS to monitor traffic entering the ESP and traffic within the ESP. The IPS vendor develops rules to detect the exploitation through network traffic of vulnerabilities that have been reported. Where vulnerabilities have been discovered, the new rules would have been imported during Texas RE_URE1's monthly signature update; (e) For the ports associated with the message application, any exploitation of unknown vulnerabilities (which would have needed to be performed from inside a Texas RE_URE1 ESP due to firewall rules) would most likely have affected only the unused application or, in the worst case, availability of the workstation running the software. Because the workstation running the application was designated for use in system support and not for system operations, even unexpected impacts to host availability would not have affected the BPS; (f) The last unnecessary port was associated with a system service that Texas RE_URE1 does not require for normal or emergency operations. Because Texas RE_URE1 applies patches monthly beginning nine days after the patch was released, any discovered vulnerabilities in the service using that port would have been patched shortly after being publicly acknowledged. The servers which are used for processing SCADA data and controls were not utilizing this unnecessary port, nor were the workstations used for monitoring and control of Texas RE_URE1 field assets; and (g) No breaches or other intrusions into Cyber Assets within Texas RE_URE1 ESPs have been identified during the time the undocumented and unnecessary ports were open. Similarly, no breaches or other intrusions were identified during the period the printer ports may have been open. | when the Standard became mandatory and enforceable for Texas RE_URE1 | when Texas RE_URE1 disabled the last unnecessary port | $17,000 (for TRE201100264 and TRE201100265) | Compliance Audit | Texas RE_URE1 updated its documentation to indicate that Technical Feasibility Exceptions (TFEs) must be filed when ports or services cannot be disabled. Texas RE_URE1 completed its action plan for the annual CVA. Upon completion, Texas RE_URE1 identified the ports required for normal/emergency operation, as well as the open ports that were not necessary for such operations. Texas RE_URE1 disabled the unnecessary ports/services. Texas RE_URE1 amended its procedures to include both stricter controls and assessments when determining which ports/services should be enabled. Texas RE_URE1’s change control process includes performing a full port scan on a representative of each asset class impacted by the change. With the change to the process to require association of dynamic port utilization discovered during the scan with a specific, authorized process, it is more likely changes adding new ports will be discovered during the testing of the change and evaluated before implementation of the change in the production environment. Texas RE_URE1 also configured change monitoring software to scan servers and workstations for additions, deletions, or modifications of services or their properties. This practice helps to support the change management process by easily identifying how changes being tested impact services and to identify when a host in production has changed. | 2012-01-26 | 2012-06-22 | Neither Admits nor Denies | Texas RE considered the presence and the quality of Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100265 | Settlement Agreement | During a Compliance Audit, Texas RE found that Texas RE_URE1 was in violation of CIP-007-2a R3 because seven of the security patches evaluated during the audit period, and deemed required by Texas RE_URE1, had not been implemented in the production environment within 30 calendar days. Texas RE_URE1 also had not documented compensating measures for the security patches that had not been installed. | CIP-007-2a | R3; R3.1 and R3.2 | Lower | Severe | Texas RE determined that the violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had risk mitigating controls, policies, and procedures in place during the pendency of the violation, as follows: (a) Texas RE_URE1 receives indirect protection from its standard defense-in-depth security measures. Firewall rules deny traffic that does not meet predefined source, destination, and port criteria. Texas RE_URE1 uses a network intrusion protection system (IPS) to inspect traffic within the Electronic Security Perimeter (ESP) and from sources external to the ESP which can detect attempted exploitation of vulnerabilities from remote sources. White-list anti-virus software installed on servers and workstations prevents the modification of existing applications and libraries and prevents the execution of files not previously approved for use. The anti-virus software also can detect execution of unauthorized or modified libraries in memory and block their execution. Daily scans of system files and configurations for changes help to detect both authorized and unauthorized system modifications; (b) Also, network traffic from Texas RE_URE1 ESPs is not routable to the internet or corporate network, so communication with Texas RE_URE1 ESPs must be performed from within the ESP or on the private supervisory control and data acquisition network. Physical access to Texas RE_URE1 ESPs is protected by secured areas with limited access to reduce the number of personnel who have the opportunity to access devices; and (c) Of the seven outstanding security patches identified by Texas RE, one was determined not to be associated with security on further evaluation. A second patch did not provide release notes, making it difficult to determine if the patch was security-related. A search of the National Vulnerability Database revealed no known vulnerabilities, indicating the patch was likely not security-related. Of the remaining five patches known to affect security, two had vulnerability-specific mitigations in place that were documented by Texas RE_URE1 as general security protections. The remaining three patches that did not have complete vulnerability-specific mitigations in place were applicable to applications installed only on workstations, limiting the scope of potential impact. | the evaluation date of the oldest required security patch | Texas RE_URE1 documented compensating measures for all outstanding security patches | $17,000 (for TRE201100264 and TRE201100265) | Compliance Audit | Texas RE_URE1 installed the patches identified during the Compliance Audit. Texas RE_URE1 also documented mitigating measures on all other security patches that were not installed. Finally, Texas RE_URE1 revised its policies/procedures to reflect that, if for any reason, existing mitigating measures cannot be found for a security patch, either the patch or relevant risk mitigation measures should be implemented promptly. | 2011-11-04 | 2012-06-07 | Neither Admits nor Denies | Texas RE considered the presence and the quality of Texas RE_URE1's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102850 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R2.1. Specifically, WECC_URE1 reported that several individuals did not have Critical Infrastructure Protection (CIP) training prior to being granted access to Critical Cyber Assets (CCAs). In addition, a number of employees had not received annual CIP training within the required timeframe, in violation of R2.3. WECC_URE1 utilizes a system to monitor and track physical access to all of its facilities, including its Physical Security Perimeters (PSPs). There are two root causes that have been identified with regard to this violation. The first root cause is a lack of in-house technical expertise with regard to the reporting features of the physical access control system. The second root cause is human error. Specifically, the physical access and cyber access lists are maintained by a manual process that includes the transferring of data from a source document to the lists which has resulted in data being entered incorrectly. WECC determined that WECC_URE1 is in violation of CIP-004-1 R2.1 and R2.3 for failing to administer CIP training to individuals within ninety days of being granted access to WECC_URE1's CCAs, and for failing to ensure that its employees received annual CIP training within the required time frame. | CIP-004-1 | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and PSPs. The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty-four hours a day, seven days a week, thereby reducing the risk to the BPS. | 90 days after the WECC_URE1 compliance date for this Standard, when CIP training should have been completed for personnel with access to CCAs | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Retained a technical expert from the physical access control system vendor who developed: a) A standard physical access control system report that will be used to consistently extract the physical access data from that system; b) An exception report to report out any missing data inconsistencies in dates and other such information so that data being entered into the physical access control system can be validated and tracked; and c) Procedures for WECC_URE1 personnel to follow when adding or removing access information into the physical access control system to ensure that continuous physical access dates can be determined. 2. Removed then reinstated, as appropriate, physical access for all PSP access points for all employees and contractors to reset the physical access dates for authorized employees identified. WECC_URE1 also validated the relationship between the physical access date and the training date for all employees and contractors to ensure compliance with the CIP-004-1 R2.3; and 3. Researched industry best practices with regard to the maintenance of the physical access and cyber access lists and developed procedures around those best practices to ensure compliance with this Standard. | 2011-02-26 | 2012-04-27 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002790 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that WECC_URE1 was in violation of CIP-004-1 R3. Specifically, WECC_URE1 reported that 1.56% of the total individuals with authorized logical and/or physical access to Critical Cyber Assets (CCAs) did not have personnel risk assessments (PRAs) that were completed within 30 days of being granted access to CCAs in accordance with WECC_URE1's policy requirements. WECC determined that WECC_URE1 was in violation of CIP-004-1 R3 because it did not conduct PRAs for individuals within 30 days of granting those individuals access to WECC_URE1's CCAs. | CIP-004-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the PRAs should have been completed for the individuals in scope | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Appointed a new subject matter expert and responsible employee to maintain the master CCA access lists and to oversee compliance with CIP-004-1 R3; 2. Verified the dates of completion of PRAs for employees, vendors and contract personnel with unescorted physical and/or cyber access to a CCA and revised the quarterly master access list using source documentation from a vendor utilized to conduct background checks; and 3. Documented a new PRA process in the WECC_URE1 policy document addressing CIP 004 R3. The new process document requires that the source files containing the PRAs will be used to verify the completion and dates of PRAs rather than tracking the information contained in the source files in a spreadsheet to help avoid incorrect data and human error in entering and/or extracting the data. | 2010-07-30 | 2012-04-27 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002791 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R3. Specifically, WECC_URE1 reported that 30.7% of the total individuals having access to Critical Cyber Assets (CCAs) were not properly documented on WECC_URE1's CCAs access list. The categorical breakdown of the individuals is as follows: 1) 9.5% of the individuals either were not updated on the CCA access list or did not have their access removed within seven days of CCA access being revoked; 2) 74.5% of the individuals had incorrect dates listed on the CCA access list for access; 3) 16% of the individuals were not on the CCAs access list when they should have been because they had access to CCAs; and 4) In addition, WECC_URE1 self-certified noncompliant with CIP-004 R4 stating that additional individuals had been discovered that had access to Critical Cyber Assets but were not properly documented on the CCA access list. WECC concluded that WECC_URE1 was in violation of CIP-004-1 R4 for failing to properly document WECC_URE1's CCAs access list for 31.3% of the total individuals who had access to WECC_URE1's CCAs. | CIP-004-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The CCAs in scope were located in Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The PSPs consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Assigned different personnel to maintain the (1) physical access list and (2) cyber access list, who have more extensive auditing and tracking backgrounds; 2. Developed new processes for auditing the physical access list and cyber access list that requires the use of source files containing access requests and approvals to verify the date of any access approval and the type of access approved for any particular individual. Additionally the source documentation was used to verify when access to any PSP or CCA was granting or removed for any particular individual; 3. Removed all information pertaining to access to sites that did not need to be included on the physical access list; and 4. Discontinued use of a single master access list to reduce manual entry of dates to that single file and to the physical access list and cyber access list which reduced the risk and opportunity for human error. | 2011-12-28 | 2012-07-18 | Agrees/Stipulates | WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102793 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1.5. Specifically, WECC_URE1 failed to provide multiple protections for certain of its access control and monitoring (ACM) Cyber Assets that are associated with Electronic Security Perimeters (ESPs) for WECC_URE1. The protections in scope are as follows: 1) CIP-007 R3: For an 18-month period, WECC_URE1 did not assess security patches for three electronic ACM Cyber Assets as required by its program, which was developed to comply with CIP-007 R3. Additionally, WECC_URE1 reported that one security patch and one service pack were installed into production without testing on a server with an identical operating system. The server on which the patches were tested was running an older version of the operating system. The server on which the patches were tested was running an older version of the operating system. 2) CIP-004 R3: 107 individuals who had access to electronic ACM Cyber Assets did not have personnel risk assessments (PRAs). 3) CIP-005 R2.5.3: During two consecutive quarters, quarterly master access lists were not signed as required by WECC_URE1's internal process for three ACM Cyber Assets. 4) CIP-005 R2.4: On two occasions during a three-month period, two individuals were given permission to log into an ESP device without using two-factor authentication as required by WECC_URE1's cyber security policy. The device accessed was WECC_URE1's firewall management control device. WECC Enforcement determined that WECC_URE1 is in violation of CIP-005-1 R1 for failing to afford the required protections to its ACM Cyber Assets as required by the Standard. | CIP-005-1 | R1 | Medium | High | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The Cyber Assets in scope are located in ESPs and a Physical Security Perimeter (PSP). The PSP consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Evaluated, tested and installed all missing cyber security software patches on each of the servers (CIP-007 R3). 2. Implemented a comprehensive patch management process to ensure ongoing tracking, evaluating, testing and implementation of cyber security software patches on all servers in the ESPs. This process includes regular coordination meetings to ensure ongoing compliance with CIP-007 R3. 3. CIP-004 R3: Person in scope had access removed, a PRA was performed and access was granted. 4. CIP-005 R2.5.3: Verified current access was correct, revised policy on how reviews are performed, and CIP-004 R4 and CIP-007 R5 workflow document was implemented for access verification. | 2011-07-20 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount. WECC determined that this violation constituted that same action behind the CIP-005-1 and CIP-005-2 violations, WECC201102794 and WECC201102428, contained within this Notice of Penalty. As a result, WECC did not issue a separate penalty for this violation.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002794 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2. Specifically, on two occasions during a three-month period, contrary to WECC_URE1's cyber security policy, two individuals within were permitted to log into an Electronic Security Perimeter (ESP) device for firewall management control without using two-factor authentication. Therefore, WECC determined that WECC_URE1 had not implemented strong procedural and technical controls to ensure authenticity of the accessing party, where technically feasible, at access points to the ESP where external interactive access was enabled in accordance with CIP-005-1 R2.4. When reviewing WECC_URE1's CIP-005-1 R2 violation, WECC also concluded that WECC_URE1 violated CIP-005-1 R2.5.3 because it did not sign quarterly master access lists during two consecutive quarters per its CIP-004-1 R4 review. WECC concluded that WECC_URE1 was in violation of CIP-005-1 R2.4 because it did not implement its policy regarding the use of two-factor authentication, and CIP-005-1 R2.5.3 because it did not follow its review process for authorization rights in accordance with CIP-004-1 R4. | CIP-005-1 | R2; R2.4; R2.5.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place during the time of the violation. The firewall management control room is in a Physical Security Perimeter (PSP) that requires card reader access. The PSP consist of multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. In addition, the facilities in scope are subject to logging and monitoring twenty four hours a day, 7 days a week. In addition, both individuals in scope had current personnel risk assessments and cyber security training, and were authorized to access this ESP device for firewall management control. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 completed the following actions: 1. Updated its two-factor authentication service to further limit unauthorized access into the ESP and PSP devices; and 2. Implemented a process to ensure management communicates with its staff the expectations regarding policies and procedures when accessing NERC CIP covered systems and to use the formal exception process when necessary. | 2010-04-30 | 2012-04-27 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102428 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-2 R5 because it failed to update documentation within 90 days of modification and change of its network. WECC_URE1 decided to remove the server running the an application and reuse that server for another purpose because the application was no longer being used. The application and the server were turned off, and power as well as network access were removed from the server. However, WECC_URE1 did not update its Electronic Security Perimeter (ESP) architecture diagram to delete the server until five months later, which was more than 90 days after the removal of the server from the ESP. WECC determined that WECC_URE1 is in violation of CIP-005-2 R5.2 for failing to update its documentation within 90 days of a modification and change to its network. | CIP-005-2 | R5; R5.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the Cyber Asset in scope was not being used prior to being removed from the ESP. | 90 days after the date that the relevant device was removed | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 updated its information system architecture diagram to reflect the removal of the server from the ESP and Physical Security Perimeter. Additionally, WECC_URE1 made changes to its change management process document and implemented a checklist for completion of change activities. | 2011-01-04 | 2012-04-27 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002792 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because certain Cyber Assets were not inside a Physical Security Perimeter (PSP) in accordance with CIP-006-1 R1. In addition, WECC_URE1 stated that it did not follow procedures for reviewing access authorization requests and revocation of access authorization in accordance with CIP-004 R4, as required by CIP-006 R1.5. Further, WECC_URE1 also stated that it did not provide multiple protections for its physical access control system, which controls physical access to all of its PSPs, as required by R1.8. The five protections that were not provided by WECC_URE1 are as follows: 1) CIP-005-1 R2.3: WECC_URE1 stated that it did not sign quarterly master access lists during two consecutive quarters in accordance with its internal process for maintaining lists of individuals with cyber and/or physical access to Critical Cyber Assets (CCAs) and PSPs. 2) CIP-005-1 R2.4: WECC_URE1 stated that on two occasions during a three-month period, two individuals were given permission to log into a WECC_URE1 IT management Electronic Security Perimeter (ESP) device without using two-factor authentication as required by WECC_URE1's cyber security policy. The device accessed was WECC_URE1's firewall management control device. 3) CIP-004-1 R3: WECC_URE1 stated that one individual, who had access to WECC_URE1's physical access control system, did not have a personnel risk assessment (PRA). 4) CIP-007-1 R5: WECC_URE1 stated that, although its cyber security policy prohibits the use of shared accounts, WECC_URE1 allowed the use of read-only access shared accounts to view information within the system used in the physical access control and monitoring (ACM) of PSPs. | CIP-006-1 | R1; R1.5; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because compensating measures were in place. The room where the firewall management control device and the two-factor authentication server in scope reside requires card reader access. This room is within multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. Also, the supervisory control and data acquisition workstation in scope resides in the backup control center in a room that requires card reader access and that is inside an ESP. Additionally, the physical access control system device, used in the ACM of CSU's PSPs, is located inside an ESP and PSP, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Report | In accordance with its Mitigation Plan, WECC_URE1 relocated the two systems associated with firewall management access control and two-factor authentication access control to a locked server rack which is a six-wall configuration. WECC_URE1 revised its CIP-004 personnel and training process document for maintaining lists of individuals with cyber and/or physical access to CCAs and PSPs. The revised process document no longer required that quarterly master access lists be signed. WECC_URE1 updated the two-factor authentication service to further limit unauthorized access into the ESP and PSP devices. Server administration staff and information security personnel were instructed to follow process and procedures strictly when accessing NERC CIP covered systems, and to use the formal exception process when necessary. WECC_URE1 removed access rights to the physical access control system, conducted a PRA and then reset the access rights for all individuals in scope. The shared account access used by the contracted security officers was removed and individual user accounts and passwords were established for each security officer to access the physical access control system. WECC_URE1 created a repeating calendar entry for the server administration staff to log into the server once a week to manually copy the security event log to a specified location on the server. WECC_URE1 collaborated with its software provider’s technical support desk for assistance to correct the workflow anomaly that had occurred. WECC_URE1worked with technical support to permanently fix the issues with the system. The system has been monitored and tested to reestablish confidence in its ability. | 2011-12-29 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102788 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-2a R3 and R3.1. Specifically, WECC_URE1 failed to implement its patch management program and to assess patches within 30 days of availability for two electronic access control and monitoring (ACM) devices and one physical ACM device that are all within WECC_URE1's Electronic Security Perimeter (ESP). In addition, WECC_URE1 provided information that patches were not assessed on three additional devices within 30 days. The three devices had been removed from the ESP before it was determined that patches needed to be assessed, and because the three devices had already been removed from the ESP at the time of discovery, patches were not implemented as required by WECC_URE1's cyber security policy. WECC determined that WECC_URE1 is in violation of CIP-007-2a R3.1 for failing to assess its security patches within 30 days and for failing to implement the patches after performing an assessment. | CIP-007-2a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the room in which the devices in scope reside requires card reader access. This room is within multiple secure rooms surrounded by a secure campus, all of which required card reader access. Each layer of card reader access is progressively limited to a smaller number of employees. Also, the facility in scope has twenty-four hour a day logging and monitoring and the devices in scope reside within an ESP. | 30 days after the first patch was available | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 evaluated, tested and implemented all missing cyber security software patches. WECC_URE1 further implemented a revised cyber security patch management process to ensure the ongoing tracking, evaluating, testing and implementing of cyber security software patches. This process includes regular coordination meetings to ensure ongoing compliance with CIP-007 R3. | 2011-01-31 | 2012-06-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102795 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5. Specifically, WECC_URE1 reported that its contracted security officer personnel used read-only access shared accounts to access WECC_URE1's application which controls access to WECC_URE1's Physical Security Perimeters (PSPs), although WECC_URE1's account management policy prohibits the use of shared accounts. In this case, there were two shared read-only access accounts at locations that contained Critical Cyber Assets (CCAs). The first location was WECC_URE1's service center where several security guards had read-only shared access. The second location was at WECC_URE1's plant where several security officers had read-only shared access. At both locations, the shared read-only access accounts limited the capability of the security officers to monitor (viewing, panning, tilting, scanning, and zooming) the display of live surveillance videos at the respective locations. The read-only shared access accounts did not allow any type of modification to the CCAs' physical access data housed in WECC_URE1's physical access control system. WECC determined that WECC_URE1 is in violation of CIP-007-1 R5 for failing to implement WECC_URE1's account management policy, which prohibits the use of shared accounts. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as a compensating measure, WECC_URE1 stated that the shared accounts in scope were used by personnel who had current training and personnel risk assessments. Additionally, the shared accounts provided read-only access to the physical access control system and account usage was monitored. Further, the read-only shared access accounts did not allow any type of modification to the CCAs' physical access data housed in WECC_URE1's physical access control system. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 removed shared account access used by the contracted security officers and established individual user accounts and passwords for each security officer to access the physical access control system. | 2010-11-21 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102439 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-2a R5 for failing to establish and implement formal methods, processes, and procedures for disposal of or redeployment of Cyber Assets within the Electronic Security Perimeter (ESP). Specifically, WECC_URE1 failed to redeploy a Cyber Asset as a like-kind Cyber Asset in accordance with its policy. An application and server were turned off, and power as well as network access were removed from the server. One month later, the server was removed from the Physical Security Perimeter (PSP) and the hard drives were redeployed for use. WECC_URE1 stated that the hard drives from the server were reformatted, as required by CIP-007-2a R7.2, prior to redeployment. However, WECC_URE1's change management process document further required that the hard drives be degaussed, and another section of that same policy document required that the hard drives be redeployed in a like-kind asset within the ESP. Therefore, WECC determined that WECC_URE1 is in violation of CIP-007-2a R7.2 for failing to redeploy the Cyber Asset as a like-kind Cyber Asset in accordance with its policy. | CIP-007-2a | R7; R7.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE1's hard drives were reformatted using a deep-level format. Additionally, the hard drives were used in a secure building on the corporate network. | when the server was removed from the PSP | Mitigation Plan completion | $50,000 (for WECC201102850, WECC201002790, WECC201002791, WECC201102793, WECC201002794, WECC201102428, WECC201002792, WECC201102788, WECC201102795, WECC201102439) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE1 removed, degaussed and destroyed the server hard drives involved. Additionally, employees were provided training and given a NERC CIP change checklist, which includes steps for decommissioning applications and servers. The checklist was added to WECC_URE1's updated change management process document which outlines procedures for changing information technology in the organization. The process document was revised and approved. | 2011-01-11 | 2012-07-18 | Agrees/Stipulates | WECC noted that upon undertaking the actions outlined in the Mitigation Plan, WECC_URE1 took voluntary corrective action to remediate violations. WECC did not review an internal compliance program for WECC_URE1 and therefore did not award any mitigating credit when determining the penalty amount. WECC_URE1 was cooperative throughout the process and WECC_URE1 did not fail to complete any applicable compliance directives. WECC has determined that this violation is classified as a Self-Certification because WECC_URE1 filed its Self-Report during the Self-Certification submittal period. Therefore, WECC did not apply self-reporting credit in determining the penalty amount.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009023 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-004-1 R4. WECC_URE2 failed to properly maintain its Critical Cyber Asset (CCA) access list for a number of individuals (16% of the total with access) for one CCA. The CCA involved is used as a server to provide the correct time for CCAs located inside a WECC_URE2 Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). Although this CCA was properly included on the CIP-002 CCA list, it was not listed on the CIP-004 R4 access list. These employees did not have access listed for the device in scope. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE2 did maintain a physical access list of the personnel having access to the server and did maintain which users had logical access in its CIP-007 R5 users list. Additionally, the device at issue resides in an ESP and PSP with twenty-four hours a day, seven days a week logging and monitoring of physical and logical access. In addition, this device is in a separate locked cabinet within the PSP to which a smaller subset of personnel has access. Although the CCA was not listed on the CIP-004 R4 access list, the individuals who had access to the device had received the appropriate NERC CIP training. | when the Standard became mandatory and enforceable as to WECC_URE2 | when WECC_URE2 completed the quarterly review of the access list of its personnel who have such access to CCAs | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | WECC_URE2 completed the following mitigating activities: 1) Established a practice and process to reference only the CIP-002 CCA list for developing and maintaining CIP-004 access lists; 2) Reviewed the CIP-002 CCA list to ensure all applicable devices are listed on the CIP-004 access lists; 3) Reviewed and updated the CIP-004 list maintenance procedure; 4) Monitored and validated the process; and 5) Reviewed the roles and responsibilities under the CIP-004 list maintenance procedure. | 2012-03-30 | 2012-07-25 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009024 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R3. WECC_URE2 failed to assess all security patches and security upgrades within 30 days of those patches being available on several of its Critical Cyber Assets (CCAs). WECC_URE2 did perform some of the required security patch assessments and security patch upgrades on the CCAs involved, but failed to complete all of the security patch upgrades for all CCAs. The CCAs involved are located inside an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). In this instance, since the Standard became mandatory and enforceable, WECC_URE2 failed to assess security patches and upgrades for a number of CCAs within 30 days of their availability. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because failure to assess security patches for CCAs within an ESP could result in unaddressed security vulnerabilities for an extended period of time, increasing the risk of a successful cyber attack against CCAs essential to the operation of the BPS. As compensating measures, WECC_URE2 did assess security patches and security upgrades for the operating system for the devices in scope, but failed to complete all of the security patch upgrades for all Cyber Assets. In addition, the devices involved are located in an ESP and PSP and protected by firewalls, anti-virus software, and are checked daily for changes to their configuration. | when the Standard became mandatory and enforceable as to WECC_URE2 | Mitigation Plan completion | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | WECC_URE2 completed the following mitigating activities: 1) Identified roles and responsibilities related to checking and reviewing security patch releases for software applications; 2) Completed security patch evaluations; 3) Updated and reviewed WECC_URE2's CIP-007 R3 security patch management procedure; and 4) Monitored and validated its process to ensure effectiveness. | 2012-03-30 | 2012-07-27 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009025 | Settlement Agreement | WECC_URE2 self-reported a violation of EOP-001-0 R6. WECC_URE2 failed to annually review, update, and provide a copy of its emergency operations planning procedure to a neighboring Balancing Authority (BA), a neighboring TOP, and the Reliability Coordinator (RC), for a single calendar year. WECC_URE2 did provide evidence that it fulfilled the requirements of the Standard for the following calendar year. WECC determined that WECC_URE2 is in violation of EOP-001-0 R6 for failing to review, update, and provide a copy of its emergency operations planning procedure to the neighboring BA, TOP and RC for one calendar year. | EOP-001-0 | R6 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because as compensating measures, WECC_URE2 developed its emergency operations planning procedure and distributed it to BPA. In addition, WECC_URE2 did fulfill the requirements of the Standard in the following calendar year. In addition, WECC_URE2 made only minor changes to its emergency response procedures the previous year. | when WECC_URE2 should have reviewed, updated and provided its emergency operations planning procedure to the neighboring BA, TOP and RC for the missing calendar year | Mitigation Plan completion | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | To mitigate the violation, WECC_URE2 reviewed and revised its procedure and distributed an updated emergency operations procedure to the neighboring BA, TOP and RC. WECC reviewed the updated emergency operations planning procedure document and determined that the revised document included procedures for distributing an emergency operations procedure on an annual basis to its neighboring BA and TOP. | 2011-10-07 | 2012-05-07 | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009026 | Settlement Agreement | WECC_URE2 self-reported a violation of PRC-005-1 R2. When WECC_URE2 assumed functional compliance responsibility for compliance obligations associated with a facility. WECC_URE2 failed to test the following Protection System devices within their 48-month interval: relays (0.2%), current transformers and potential transformers (19.8%), communications devices (2.0%), and DC circuitry (2.5%). All batteries were maintained and tested within the defined interval. | PRC-005-1 | R2 | High | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 maintained and tested these devices every four years and performed quarterly inspections of the stations in which they were housed. Failures of instrument transformers would have been discovered during WECC_URE2's quarterly station inspection, which were performed on schedule. | when WECC_URE2 should have performed the maintenance and testing | present | $54,000 (for WECC2011009023, WECC2011009024, WECC2011009025, and WECC2011009026) | Self-Report | To mitigate the violation, WECC_URE2 will: (1) Install test switches and complete relay testing; (2) Implement instrument transformer verification for neutral relays; (3) Complete its instrument transformer verification testing; (4) Provide a status update to WECC; and (5) Design, install and test bus lockout test switch. | 5/31/2013 (approved completion date) | TBD | Agrees/Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009976 | Settlement Agreement | WECC determined that WECC_URE3 had a violation of CIP-005-1 R3.2 because WECC_URE3 failed to implement controls to ensure that access points to WECC_URE3's system control center and backup control center Electronic Security Perimeters (ESPs) were configured to alert appropriate personnel to unauthorized ESP access attempts or unauthorized ESP access. Several ESP access points to ESPs were not configured in accordance with CIP-005-1 R3.2. WECC determined that WECC_URE3 was in violation of CIP-005-1 R3.2 as of the effective compliance enforcement date of the Standard. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because compensating measures were in place during the violation period. WECC_URE3 has an in-depth defense structure to ensure electronic security. This includes network segmentation within ESPs. All personnel with access to each of the three devices have completed cybersecurity training and personnel risk assessments (PRAs). All the devices are password-protected, Cyber Assets and Critical Cyber Assets are secured behind firewalls, and access is controlled, logged, and monitored. | when the Standard became mandatory and enforceable to WECC_URE3 | Mitigation Plan completion | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 completed the following mitigation activities: 1) Identified and documented all electronic access control devices which may be interactively accessed. 2) Configured every device identified in step 1 so that unauthorized access attempt events are sent as syslog events to security information and event management software. | 2012-07-11 | 2012-08-21 | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor. WECC_URE3 was cooperative throughout the process.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009938 | Settlement Agreement | WECC determined that WECC_URE3 had a violation of CIP-006-1 R3 because WECC_URE3 failed to document and implement operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. WECC determined that WECC_URE3 failed to implement controls for immediately reviewing unauthorized access attempts to several PSP access points through several PSPs at multiple locations; that WECC_URE3 did not implement technical or procedural controls for immediately reviewing unauthorized access attempts at a certain type of PSPs; that WECC_URE3 did not implement procedural or technical controls for immediately reviewing unauthorized physical access attempts at access points to PSPs at the backup control center; and, that WECC_URE3 did not monitor physical access to access points to a PSP at the system control center, during normal business hours. | CIP-006-1 | R3 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE3 had compensating measures in place during the pendency of the violation. WECC_URE3 reviews access logs weekly. Access points at the PSPs at issue are locked and monitored twenty-four hours a day, seven days a week. An access point to the PSP at the system control center is locked and monitored during normal business hours. Certain identified assets are located within cabinets identified as separate PSPs within a larger PSP. All individuals with access to Critical Cyber Assets and Cyber Assets within a PSP completed cybersecurity training and personnel risk assessments (PRAs). | the first day following Certification of Mitigation Plan Completion for a prior CIP violation | present | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 will complete the following mitigation activities: 1) WECC_URE3 will identify all physical access points to the backup control center and system control center. 2) WECC_URE3 will configure unauthorized access attempt alarms for all physical access points to the backup control center and system control center. 3) WECC_URE3 will identify the appropriate staff to notify and respond to alarms. 4) WECC_URE3 will configure a method of notifying appropriate staff of unauthorized access alarms. 5) WECC_URE3 will install a video camera to monitor the roof hatch. 6) WECC_URE3 will correct network problems to enable review of the backup control center video recorder at the system control center. 7) WECC_URE3 will train operators to review video, acknowledge alarms, respond to alarms, and document alarm response. | 12/31/2012 (approved completion date) | TBD | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE3's violation history.
2012-10-31 | FERC | NP13-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009939 | Settlement Agreement | WECC determined that WECC_URE3 was in violation of CIP-006-1 R4 because WECC_URE3 failed to implement technical or procedural controls to ensure logging physical access at all access points to the Physical Security Perimeter (PSP) using a logging method listed in the Requirement or their equivalent. WECC_URE3 failed to implement controls that logged physical access for a roof hatch identified as an access point to the system control center PSP. | CIP-006-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE3 had implemented other security measures to protect the PSP. The roof hatch access point was in a garage and pad-locked from the inside. There were no Critical Cyber Assets (CCAs) in the garage. Access to CCAs within the system control center via entry through the roof hatch would require passage through two card-access restricted doors, which are logged and monitored via cameras twenty-four hours a day, seven days a week. | when the Standard became mandatory and enforceable to WECC_URE3 | Mitigation Plan completion | $24,000 (for WECC2012009976, WECC2012009938, and WECC2012009939) | Compliance Audit | WECC_URE3 completed the following mitigation activities: 1) WECC_URE3 placed visitor log books at roof hatch, at the West entrance, between the garage overhead door and garage man door; 2) WECC_URE3 changed the physical security plan to require visitors to sign out on the appropriate log book when leaving the PSP instead of at the main entrance; 3) WECC_URE3 changed the physical security plan to require the escort to return the visitor badge to the front desk and to add a note to the main entrance log book describing from which access point the visitor exited the PSP. | 2012-06-29 | 2012-08-21 | Does Not Contest | WECC considered WECC_URE3's internal compliance program (ICP) as a mitigating factor. WECC_URE3 was cooperative throughout the process.
2012-10-31 | FERC | NP12-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012001322 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF, identifying a violation of CIP-007-1 R4. RFC_URE1 has documented and implemented a process for the update of anti-virus and malware prevention signatures which addresses testing and installing the signatures. Pursuant to that process, RFC_URE1 installed all required signatures. However, RFC_URE1 failed to implement testing of the signatures on certain Cyber Assets when RFC_URE1 tested and installed a new anti-virus product. Specifically, RFC_URE1 failed to implement a testing schedule for signature updates on the Critical Cyber Assets and non-critical Cyber Assets located in its energy control system and backup energy control system Electronic Security Perimeters (ESPs), as required by CIP-007-1 R4.2. As a result, RF determined that RFC_URE1 failed to implement testing of anti-virus and malware prevention signatures for these Cyber Assets pursuant to its anti-virus and malware prevention signature update process. | CIP-007-1 | R4.2 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors. RFC_URE1 had in place, at the time of the violation, a process for the update of anti-virus and malware prevention signatures that addressed testing and installing the signatures. RFC_URE1 installed the requisite signatures pursuant to that process on all of its Cyber Assets. Furthermore, RFC_URE1 has not experienced adverse functionality of any Cyber Asset related to its failure to perform signature testing. | when the Standard became mandatory and enforceable for RFC_URE1 | Mitigation Plan completion | $12,000 (for RFC2012001322, RFC2012010114, RFC2012009872, and RFC2012009871) | Self-Report | RFC_URE1 submitted to RF a mitigation plan to address the violation of CIP-007-1, R4. In this mitigation plan, RFC_URE1 took certain actions to mitigate the alleged violation. In accordance with its Mitigation Plan, RFC_URE1 revised its implemented procedure for testing signature updates on the Cyber Assets at issue, including the Critical Cyber Assets, the Cyber Assets within the ESP, and the Cyber Assets that authorize and/or log access to the Physical Security Perimeter. RFC_URE1 put into place a procedure for local testing of signature updates for the Cyber Assets that uses anti-virus/malware protection. RFC_URE1 contacted its vendor to find an acceptable solution for testing anti-virus/malware signature updates in the system. RFC_URE1 system administrators planned to commence using these enhancements once accepted. RFC_URE1 also trained the appropriate employees on the procedure document. | 2012-05-01 | 2012-07-19 | Admits | RF considered certain aspects of RFC_URE1's internal compliance program (ICP) as mitigating factors in the penalty determination. RF also considered as a mitigating factor the fact that RFC_URE1 discovered the violation through Self-Report. RF considered as a mitigating factor the positive degree and quality of RFC_URE1's cooperation and remedial action during the enforcement process. RFC_URE1 was cooperative throughout its interaction with RF in connection with the violation and promptly submitted an effective Mitigation Plan to remediate the violation.
2012-10-31 | FERC | NP12-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010114 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a violation of CIP-006-1 R1.8. RFC_URE1 has documented and implemented a process for the update of anti-virus and malware prevention signatures which addresses testing and installing the signatures. Pursuant to that process, RFC_URE1 installed all required signatures. However, RFC_URE1 failed to implement testing of the signatures on certain Cyber Assets when RFC_URE1 tested and installed a new anti-virus product. In addition, RFC_URE1 failed to implement a testing schedule for signature updates for its Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP), as required by CIP-007-1 R4. As a result, RF determined that RFC_URE1 was in violation of CIP-006-1 R1.8, which requires RFC_URE1 to afford the protective measures of CIP-007-1 R4 to all Cyber Assets within its ESPs. | CIP-006-1 | R1.8 | Lower | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was mitigated by the following factors. RFC_URE1 had in place, at the time of the violation, a process for the update of anti-virus and malware prevention signatures that addressed testing and installing the signatures. RFC_URE1 installed the requisite signatures pursuant to that process on all of its Cyber Assets. Furthermore, RFC_URE1 has not experienced adverse functionality of any Cyber Asset related to its failure to perform signature testing. | when the Standard became mandatory and enforceable for RFC_URE1 | Mitigation Plan completion | $12,000 (for RFC2012001322, RFC2012010114, RFC2012009872, and RFC2012009871) | Self-Report | RFC_URE1 did not submit a formal Mitigation Plan for this violation as the mitigation activities detailed in the Mitigation Plan, which was submitted to address its violation of CIP-007-1 R4.2 (RFC2012001322, above), were sufficient to bring it into compliance with CIP-006-1 R1.8. as well. RFC_URE1's certification and verification documents pertaining to RFC2012001322 cover the instant violation as well. In accordance with its Mitigation Plan, RFC_URE1 revised its implemented procedure for testing signature updates on the Cyber Assets at issue, including the Critical Cyber Assets, the Cyber Assets within the ESP, and the Cyber Assets that authorize and/or log access to the Physical Security Perimeter. RFC_URE1 put into place a procedure for local testing of signature updates for the Cyber Assets that use anti-virus/malware protection. RFC_URE1 contacted its vendor to find an acceptable solution for testing anti-virus/malware signature updates in the system. RFC_URE1 system administrators planned to commence using these enhancements once accepted. RFC_URE1 also trained the appropriate employees on the procedure document. | 2012-05-01 | 2012-07-19 | Admits | RF considered certain aspects of RFC_URE1's internal compliance program (ICP) as mitigating factors in the penalty determination. RF also considered as a mitigating factor the fact that RFC_URE1 discovered the violation through Self-Report. RF considered as a mitigating factor the positive degree and quality of RFC_URE1's cooperation and remedial action during the enforcement process. RFC_URE1 was cooperative throughout its interaction with RF in connection with the violation and promptly submitted an effective Mitigation Plan to remediate the violation.
2012-10-31 | FERC | NP12-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012009872 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF, identifying a violation of CIP-007-1 R8. For three years RFC_URE1 utilized an outside managed security services provider (the contractor) to conduct its cyber vulnerability assessments of all Cyber Assets within the Electronic Security Perimeter (ESP). However, after a third party performed a gap analysis for RFC_URE1's CIP compliance program, RFC_URE1 discovered that, in violation of the contract between RFC_URE1 and the contractor, the contractor had not performed cyber vulnerability assessments in accordance with CIP-007-1 R8. Specifically, the cyber vulnerability assessments of Cyber Assets within the ESP did not include: a document identifying the vulnerability assessment process (R8.1); a review to verify that only ports and services required for operation of the Cyber Assets within the ESP are enabled (R8.2); a review of controls for default accounts (R8.3); and documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that plan (R8.4). As a result, RF determined that RFC_URE1 was in violation of CIP-007-1 R8. | CIP-007-1 | R8 | Lower | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the violation increased the risk that RFC_URE1 may have non-required open ports and services or deficient account administration controls, the risk was mitigated by the following factors. While RFC_URE1 was not conducting cyber vulnerability assessments pursuant to CIP-007-1 R8, it was performing cyber vulnerability assessments that were based on information technology practices. RFC_URE1's cyber vulnerability assessments documented the open ports on each system and attempted to identify the actual service and version behind each open port. Based upon the service and version, the cyber vulnerability assessment categorized the known vulnerabilities according to severity. In addition, although the cyber vulnerability assessments did not include a review of controls for default accounts, in the event of a failure of the servers or guard workstations, RFC_URE1's physical card access system would still control access to the Physical Security Perimeters and record events, including alarms. Furthermore, RFC_URE1 had multiple additional security measures in place including firewalls, anti-virus protection, and intrusion prevention systems. For example, RFC_URE1 installed anti-virus with updated signatures on all systems. Additionally, RFC_URE1 deploys intrusion prevention systems to protect the network where the physical card access system resides. | when the Standard became mandatory and enforceable for RFC_URE1 | present | $12,000 (for RFC2012001322, RFC2012010114, RFC2012009872, and RFC2012009871) | Self-Report | In accordance with its Mitigation Plan, RFC_URE1 committed to develop documentation of the vulnerability assessment process. Within this document, RFC_URE1 will describe its method for performing ports and services scans of the access points and reviewing such scans against its baseline of ports and services. RFC_URE1 will document the results of the identification process, ports and services scans, the baseline for comparison, and any discrepancies. In addition, RFC_URE1 committed to describe how it will complete the enumeration of default accounts, and once completed, RFC_URE1 will determine, validate, review, and document the controls in place for these accounts. RFC_URE1 will then create an action plan and schedule to follow in order to remediate or mitigate any discovered vulnerabilities or discrepancies. Furthermore, RFC_URE1 will update the vulnerability assessment process documentation to reflect its findings and any necessary changes to its cyber vulnerability assessment process. | approved Mitigation Completion date | TBD | Admits | RF considered certain aspects of RFC_URE1's internal compliance program (ICP) as mitigating factors in the penalty determination. RF also considered as a mitigating factor the fact that RFC_URE1 discovered the violation through Self-Report.
2012-10-31 | FERC | NP12-47-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012009871 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF, identifying a violation of CIP-005-1 R4. For three years RFC_URE1 utilized an outside managed security services provider (the contractor) to conduct its cyber vulnerability assessments of the electronic access points to the Electronic Security Perimeter (ESP). However, after a third party performed a gap analysis for RFC_URE1's CIP compliance program, IPL discovered that, in violation of the contract between RFC_URE1 and the contractor, the contractor had only performed cyber vulnerability assessment activities pursuant to regular IT practices, and not in accordance with CIP-005-1 R4. Specifically, the cyber vulnerability assessments of the electronic access points to the ESP did not include: a document identifying the vulnerability assessment process (R4.1); a review to verify that only ports and services required for operations at these access points are enabled (R4.2); the discovery of all access points to the ESP (R4.3); a review of controls for default accounts, passwords, and network management community strings (R4.4); and documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that plan (R4.5). As a result, RF determined that RFC_URE1 was in violation of CIP-005-1 R4. | CIP-005-1 | R4 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the violation increased the risk that RFC_URE1 may have non-required open ports and services and deficient account administration controls or network management community strings, the risk was mitigated by the following factors. While RFC_URE1 was not conducting cyber vulnerability assessments pursuant to CIP-005-1 R4, it was performing cyber vulnerability assessments that were based on information technology practices. RFC_URE1's cyber vulnerability assessments documented the open ports on each system and attempted to identify the actual service and version behind each open port. Based upon the service and version, the cyber vulnerability assessment categorized the known vulnerabilities according to severity. In addition, RFC_URE1 had multiple additional security measures in place including firewalls, anti-virus protection, and intrusion prevention systems. For example, RFC_URE1 installed anti-virus with updated signatures on all systems, as technically feasible. Additionally, RFC_URE1 deploys intrusion prevention systems so that for each control center data center, an intrusion prevention system monitors and protects each access point interface (except between redundant firewalls). This monitoring occurs on all traffic in and out on all interfaces (except between redundant firewalls). | when the Standard became mandatory and enforceable for RFC_URE1 | present | $12,000 (for RFC2012001322, RFC2012010114, RFC2012009872, and RFC2012009871) | Self-Report | In accordance with its Mitigation Plan, RFC_URE1 committed to develop documentation of its vulnerability assessment process. Within this document, RFC_URE1 will describe its method for identifying all access points to the ESP and its method for performing ports and service scans of the access points and reviewing such scans against its baseline of ports and services. RFC_URE1 will document the results of the identification process, ports and services scans, the baseline for comparison, and any discrepancies. In addition, RFC_URE1 committed to describe how it will complete the enumeration of default accounts, passwords, and network management community strings, and once completed, RFC_URE1 will determine, validate, review, and document the controls in place for accounts, passwords, and strings. RFC_URE1 will then create an action plan and schedule to follow in order to remediate or mitigate any discovered vulnerabilities or discrepancies. Furthermore, RFC_URE1 will update the vulnerability assessment process documentation to reflect its findings and any necessary changes to its cyber vulnerability assessment process. | approved Mitigation Completion date | TBD | Admits | RF considered certain aspects of RFC_URE1's internal compliance program (ICP) as mitigating factors in the penalty determination. RF also considered as a mitigating factor the fact that RFC_URE1 discovered the violation through Self-Report.
2012-10-31 | FERC | NP12-47-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000299 | Notice of Confirmed Violation | During a SPP RE CIP Spot Check of SPPRE_URE1, SPP RE discovered a violation of CIP-002-1 R2. SPP RE determined that SPPRE_URE1 improperly applied its risk-based assessment methodology (RBAM) by failing to identify a substation as a Critical Asset. The SPPRE_URE1 system includes facilities for operating an interconnected electric energy transmission network and a generating facility needed to maintain transmission system reliability, and therefore is part of the bulk power system (BPS). SPPRE_URE1's RBAM did not consider restoration of the SPPRE_URE1 transmission system to be critical to the function of the BPS. The criteria found in SPPRE_URE1's RBAM used to identify Critical Assets based on criticality to BPS restoration states that elements critical to BPS restoration as documented in the Regional restoration plan developed pursuant to standards, unless specifically excluded by engineering assessment, are to be classified as Critical Assets. SPP RE determined that since the substation at issue was essential for the restoration of SPPRE_URE1's system pursuant to a restoration plan, a proper application of SPPRE_URE1's RBAM would have identified the substation as a Critical Asset. Because the substation is a transmission substation relied upon for initial restoration of the SPPRE_URE1 system, the failure to include the substation as a Critical Asset resulted in a violation of CIP-002-1 R2. | CIP-002-1 | R2 | High | High | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the BPS because the SPPRE_URE1 transmission system resides within a larger loop providing multiple ties to the Eastern Interconnect. The number of surrounding ties decreases the likelihood that power could not be restored to the SPPRE_URE1 system if the substation were unavailable. Additionally, SPPRE_URE1 evaluated the substation in a power flow analysis and determined that the substation is not critical to BPS reliability beyond restoration of the SPPRE_URE1 system. Therefore, the risk to the BPS is the possibility the substation would be unavailable at the time of a blackout, potentially causing a delay in the restoration of the SPPRE_URE1 system. | when the Standard became mandatory and enforceable for SPPRE_URE1 | present | 5500 | Spot Check | In order to mitigate this violation, SPPRE_URE1 will: (1) conduct a thorough review of its RBAM and the plans to restore SPPRE_URE1's system; (2) run the Risk Based Assessment while considering the most current plans to restore SPPRE_URE1's system; and (3) coordinate the plans to restore SPPRE_URE1's system with appropriate entities. | 12/28/2012 (approved completion date) | TBD | Does Not Contest | SPP RE considered SPPRE_URE1's internal compliance program (ICP) and SPPRE_URE1's efforts to improve it to be a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000223 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report identifying nine of its energy management system (EMS) servers and two additional servers, documented as Critical Cyber Assets (CCAs) that did not have anti-virus software or other malicious software (malware) prevention tools installed by the effective date of CIP-007-1 R4. | CIP-007-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because numerous compensating measures had been implemented by Texas RE_URE1 to protect the system assets prior to the enforcement date of the Standard. These measures included implementation of an intrusion prevention system, isolation from the internet and the Texas RE_URE1 corporate network, the addition of firewalls, application of a routed network, the disabling of all unused ports and placement of layer 2 switch security. In addition, Texas RE_URE1 deployed a RSA Sys Log Server, further enhancing security of the assets. Although no Technical Feasibility Exception (TFE) request was submitted by Texas RE_URE1, these measures were undertaken based upon Texas RE_URE1's belief that actual installation of anti-virus/anti-malware software was either not technically feasible and/or imprudent, based on vendor recommendations that they not install antivirus or other software on it's EMS machines, as the machines were Linux-based, and did not require it by nature. Texas RE_URE1 also considered the lack of supported anti-virus/anti-malware for the Unix-based servers, and the cumulative protections Texas RE_URE1 put in place. Texas RE’s determinations are further supported by Texas RE_URE1's modest size, interconnection configuration with neighboring utilities, and isolated location within ERCOT, of which Texas RE_URE1's load amounts to a fraction of one percent. | when the Requirement became effective for Texas RE_URE1 | Mitigation Plan completion date | $13,500 (for TRE201000223 and TRE2012010051) | Self-Report | In accordance with its mitigation plan, Texas RE_URE1 installed anti-virus software on all of the capable equipment within its Electronic Security Perimeter (ESP) that was identified in the Self-Report. Prior to full implementation of the software, Texas RE_URE1 installed anti-malware and anti-virus protection into an offline and isolated EMS server as a testing platform. Texas RE_URE1 proceeded to work out the issues on the isolated server and allowed the anti-malware and anti-virus programs to run 24 hours before proceeding to implement the programs on the remaining EMS servers. This exercise confirmed the technical feasibility of the solution. Texas RE_URE1 reviewed the best practices recommendations by the certification team. | 2010-09-09 | 2012-01-10 | Neither Admits nor Denies | TRE considered Texas RE_URE1's compliance program as a mitigating factor during penalty determination.
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010051 | Settlement Agreement | Texas RE conducted an Audit and found that Texas RE_URE1 had 27 additional CCAs (servers, switches, routers, modems, firewalls, etc.) that did not have anti-virus software or other malware prevention tools installed by the effective date of CIP-007-1. During the Audit, the Audit Team also found that Texas RE_URE1 did not have a process or procedure in place to address the updating, testing, or installing of anti-virus and malware prevention signatures between the effective date of CIP-007-1 and the date its procedure was updated. | CIP-007-1 | R4; R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because numerous compensating measures had been implemented by Texas RE_URE1 to protect the system assets prior to the enforcement date of the Standard. These measures included implementation of an intrusion prevention system, isolation from the internet and the Texas RE_URE1 corporate network, the addition of firewalls, application of a routed network, the disabling of all unused ports and placement of layer 2 switch security. In addition, Texas RE_URE1 deployed a RSA Sys Log Server, further enhancing security of the assets. These measures were undertaken based upon Texas RE_URE1's belief that actual installation of anti-virus/anti-malware software was either not technically feasible and/or imprudent, given vendor recommendations, a lack of supported anti-virus/anti-malware for the Unix-based servers utilized, and the cumulative protections provided. Texas RE’s determinations are further supported by Texas RE_URE1's modest size, interconnection configuration with neighboring utilities, and isolated location within ERCOT, of which Texas RE_URE1's load amounts to a fraction of one percent. | when the Requirement became effective for Texas RE_URE1 | Mitigation Plan completion date | $13,500 (for TRE201000223 and TRE2012010051) | Audit | In accordance with its mitigation plan, the Supervisory Control and Data Acquisition (SCADA) & energy management system (EMS) Critical Cyber Asset policies for Texas RE_URE1 were supplemented (The Procedure). The Procedure contains additional details regarding anti-virus and malware prevention tools, and establishes full compliance with CIP-007-1 R4.1 and 4.2. As a result, Texas RE_URE1 has documented and implemented anti-virus and malware prevention tools on the assets in question and, where not feasible to do so, implemented compensating measures. Texas RE_URE1 also documented and implemented a process for the update of anti-virus and malware prevention signatures, including the testing and installing of signatures. Lastly, Texas RE_URE1 submitted Technical Feasibility Exceptions (TFEs) in reference to devices that have attributes that prevent the feasible application of anti-virus and malware prevention tools. | 2012-02-29 | 2012-06-06 | Neither Admits nor Denies | TRE considered Texas RE_URE1's compliance program as a mitigating factor during penalty determination.
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000247 | Settlement Agreement | Texas RE_URE2 self-reported that it had failed in four instances to conduct required testing to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. Instance #1: An intrusion prevention systems patch was installed on PCs at four CIP locations without first conducting required testing of the upgrade to ensure significant changes to existing Cyber Assets within the ESP did not adversely affect existing cyber security controls. Required testing and documentation was completed the same day. Instance #2: An update was inadvertently pushed to production machines within the ESP without first conducting required testing of the update to ensure significant changes to existing Cyber Assets within the ESP did not adversely affect existing cyber security controls. Required testing and documentation was promptly completed the next day. Instance #3: Texas RE_URE2 updated the firmware of 12 switches without conducting required testing of the upgrade to ensure significant changes to existing Cyber Assets within the ESP did not adversely affect existing cyber security controls. Texas RE_URE2 completed the cyber vulnerability assessment on the updated firmware 45 days later. Instance #4: A detailed review was conducted where it was discovered that one Cyber Asset, a storage management software, was upgraded on four dates. These significant changes were made to Cyber Assets used in access control and monitoring of the ESP without conducting required testing of the changes to ensure significant changes to existing Cyber Assets within the ESP did not adversely affect existing cyber security controls. Texas RE_URE2 completed the cyber vulnerability assessment on the upgraded software 93 days after the first upgrade date. | CIP-007-1 | R1 | Medium | Severe | Texas RE has determined that Texas RE_URE2’s violation of CIP-007-1 R1 posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk introduced by the failure to test was mitigated by the in-depth layered defense Texas RE_URE2 had implemented during the violation period. For instance, Texas RE_URE2 utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. | the date when the first patch was installed without testing | Mitigation Plan completion | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Upon discovery of the patch process error, the immediate risk was addressed quickly by completion of the required testing. The testing confirmed that the patch did not affect any existing cyber security controls. Texas RE_URE2 also performed a system impact assessment to evaluate impact to the system; 2) Added a new process for deployment of patch updates that includes additional approvals in the process. Texas RE_URE2 also added the required additional approval process before final installation; 3) Created queries to validate patch sequences/ processes; 4) Implemented controls to review changes to Cyber Assets before implementation; 5) Revised and published the data services process documentation governing test procedures; 6) Revised and published a change management standard to include content governing NERC changes; 7) Revised and published the process documentation governing test procedures; and 8) Provided awareness training to personnel responsible for maintaining data storage infrastructure. | 2011-11-15 | 2012-06-18 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100335 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that two employees with unescorted access privileges entered a Physical Security Perimeter (PSP). Later that day, one of the employees granted and logged access for a visitor, a different employee supporting protection system testing, but who did not have unescorted access privileges. The visitor left that day with both of the employees, without logging out. Although the visitor was logged in and always escorted, the logs did not reflect that the visitor ever logged out of the PSP. | CIP-006-3a | R6 | Lower | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system. First, while the visitor never logged out of the PSP, the visitor was never unescorted. Second, all persons involved had taken security training. Third, all persons involved cleared background checks. Although the employees followed the CIP-006 R6 requirement and Texas RE_URE2 physical security policy by logging the visitor in, the employees with access did not require the visitor to log out. | when the visitor failed to log out when leaving the PSP | Mitigation Plan completion | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Modified the security operations center script to emphasize the need for escorts to report to the security operations center every visitor entry and exit; 2) Modified the issues management process to include supervision of personnel involved in logging incidents to increase awareness and accountability; 3) Improved awareness and communicated visitor logging process among impacted business units. Created a presentation focused on the proper methods for visitor logging for use in staff meetings of all personnel who access critical facilities as part of their normal job functions. Performed this presentation at numerous management meetings and incorporated core messages into other communications. Prepared and published an article describing proper methods of visitor logging; 4) Converted from the use of manual/paper logging at select (e.g., non-staffed) locations to calling the security operations center to help ensure that logging is complete and accurate; 5) Modified policies/procedures to clarify that visitor logging must be performed with each entry and exit into and out of the PSP; 6) Distributed the education/awareness presentation. Disseminated the presentation created to all personnel with authorized unescorted access to Critical Cyber Assets across the company; 7) Created a corporate-wide template for standardized paper log sheets that designates what is minimally required for paper log sheets for use across all lines of business within one of Texas RE_URE2's parent companies (at locations that utilize manual logging); and 8) Enhanced annual CIP web-based training to focus specifically on addressing past issues regarding visitor logging. | 2012-01-01 | 2012-05-10 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100343 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that Texas RE_URE2 discovered that a Cyber Asset, specifically a server, was installed within a transmission substation Electronic Security Perimeter (ESP) without being identified as a Critical Cyber Asset (CCA) or non-CCA within the ESP. This device was not previously identified because of an incorrectly configured gateway router setting. The IP configuration was correct such that the device was within the ESP; however, without the proper gateway router setting, it could not communicate outside the ESP and was, therefore, not recognized. Texas RE_URE2’s engineering group identified this cyber device by performing device scans from within the ESP locally or by reviewing tables. | CIP-005-1 | R1; R1.6 | Lower | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system because the CCA was installed within Texas RE_URE2’s ESP and could not communicate outside the ESP. Texas RE_URE2 had access control measures in place at both the ESP and the Physical Security Perimeter levels. The device in question is used and documented in a similar manner throughout the station network. | when the device was installed without being documented | Mitigation Plan completion | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Increased awareness of the issue to personnel involved with configurations; 2) Conducted a system-wide scan and assess the existing similar devices configuration. Identified and corrected related erroneous configuration; 3) Evaluated alternatives to automate the process to detect device misconfigurations. Evaluated other available IP configuration scan tools and develop practical improvement options; 4) Tested and piloted preferred alternative(s); and 5) Implemented solution. | 2012-02-29 | 2012-06-18 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100345 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that it had failed to maintain records documenting its review of security logs. Texas RE_URE2's log management and incident alerting system (System) is managed by Texas RE_URE2's cyber security team. Texas RE_URE2's System is designed to receive system events captured in local system logs, but the System requires effective business process controls and communications between the cyber security analysis team and the Texas RE_URE2 business units. Texas RE_URE2 failed to implement some of these business process controls and communications, and as a result, local security logs were not sent to the System for log management and incident alerting. Because Texas RE_URE2 did not receive security logs in its System, it did not process the security logs, and therefore Texas RE_URE2 also failed to maintain records documenting its review of security logs. | CIP-007-1 | R6 | Lower | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS by the foregoing facts and circumstances was mitigated by the following several factors. Texas RE_URE2’s current implementation of firewalls, network-based intrusion and detection systems, and anti-virus solutions helps to mitigate the risk exposed by the problems in security logging. All security threats detected by these measures are monitored by Texas RE_URE2’s security operations center twenty-four hours a day, seven days a week. | when the Standard became mandatory and enforceable for Texas RE_URE2 | Mitigation Plan completion | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 and one of its parent companies completed the following activities to mitigate the violation: 1) reviewed the existing process and procedure documents to identify opportunities for improvement; 2) identified the scope of Cyber Assets and developed a high-level project plan that addressed how each category of assets will be brought into strict compliance with each of the sub-requirements, as technically feasible; 3) revised the existing process and procedure documents; 4) enabled alerting on all of the Cyber Assets that are currently reporting logs into the log management system; 5) remediated all remaining Cyber Assets not reporting their logs into the log management system; and 6) enabled alerting on the remaining Cyber Assets. | 2012-06-19 | 2012-08-09 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100359 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that Texas RE_URE2 failed to monitor two firewalls that serve as access points to Cyber Assets that authorize or log access to Physical Security Perimeters (PSPs). Texas RE_URE2 failed to identify the two firewalls as subject to the requirements of CIP-005-1 R3. Texas RE_URE2 did collect and retain firewall logs for the two firewalls for at least 90 days, but it did not perform monitoring and alerting on the two firewalls as required by CIP-005-1 R3. | CIP-006-1 | R1; R1.8 | Medium | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE2 would not have been alerted to potential attacks to the badging system. However, the firewalls which provide the badging system protection would still be in place and the BPS would not be directly affected if the badging system were being attacked. The risk introduced by the failure to monitor was mitigated by the in-depth layered defense Texas RE_URE2 had implemented during the violation period. For instance, Texas RE_URE2 utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. | when the Standard became mandatory and enforceable for Texas RE_URE2 | when monitoring and alerting was enabled on two firewalls | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Enabled alerting on the firewalls; 2) Reviewed the relevant process documents and identified the required changes; and 3) Revised one of Texas RE_URE2's parent companies' document describing the process for monitoring and logging of access points to the ESP (CIP-005 R3.2) to include explicitly those firewalls used to control the electronic access to Cyber Assets that authorize and/or log access to its PSPs. | 2011-09-30 | 2012-05-10 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100360 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that Texas RE_URE2 failed to perform annual cyber vulnerability assessments (Assessments) on certain Cyber Assets. Specifically, Texas RE_URE2 failed to perform annual Assessments of ports, services, or default accounts on servers where host applications are used for physical security and port scanning, to support file transfers between applications, and to provide domain authentication services. Texas RE_URE2 also stated that baseline assessments were performed for ports and services, but lacked evidence to prove that it reviewed the baseline assessments annually. | CIP-007-1 | R8 | Lower | Severe | Texas RE has determined that this violation posed a minimal and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the following factors. Although Texas RE_URE2 failed to perform annual assessments, Texas RE_URE2 performed an initial, baseline cyber vulnerability assessment on all affected assets. Additionally, Texas RE_URE2 protects against cyber attacks through multiple layers of physical and electronic security. Texas RE_URE2 has redundancy on its server and workstation environments that would require potential attackers to bypass multiple layers of control, including human observation. | when the Standard became mandatory and enforceable for Texas RE_URE2 | when the required assessments were completed | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Completed the required cyber vulnerability assessments on the affected Cyber Assets; 2) Reviewed existing management controls to identify potential improvements in the processes governing the cyber vulnerability assessment process and associated documentation required for evidence of compliance; 3) Implemented improvements to the cyber vulnerability assessment processes as required; and 4) Communicated process changes and evidence requirements to appropriate personnel. | 2011-12-12 | 2012-05-14 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100380 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that Texas RE_URE2 failed to remove a contractor's electronic access to Critical Cyber Assets (CCAs) within seven calendar days after the contractor resigned from his position. | CIP-004-3 | R4; R4.2 | Lower | Moderate | Texas RE has determined that this violation posed a minimal and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS by the foregoing facts and circumstances was mitigated by the following factors. Texas RE_URE2 revoked the contractor's access 19 days after he resigned and less fewer than two weeks from the seven-day deadline imposed by CIP-004-3 R4.2. Additionally, the contractor did not have physical access to CCAs, and could not electronically access any CCAs because Texas RE_URE2 collected his network identification token, laptop and company identification upon his resignation. | seven days after the contractor resigned | the date access was removed | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) Upon discovery of the access removal issue, the issue was remediated by removing the employee's electronic access; 2) A communication to managers with employees or contractors who have NERC CIP electronic or unescorted physical access privileges (NERC CIP access) was issued on the NERC CIP Standard and Requirements regarding terminating access, process for terminating individuals with access, and the importance of the urgency to revoking access; and 3) Issued quarterly manager reminders of responsibilities for terminations for managers responsible for managing employees or contractors with NERC CIP access. | 2011-10-21 | 2012-05-14 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100398 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that during a review of personnel risk assessments (PRAs) on file, one of Texas RE_URE2's parent companies' Human Resources group determined that one Texas RE_URE2 employee that had access to Critical Cyber Assets (CCAs) had PRAs that did not conform to the PRA program. Specifically, a seven-year criminal check had not been performed. Texas RE_URE2 uses an automated process to process background check reports that it receives from a third-party vendor. The automated process was designed with an assumption that reports from the vendor would reflect full background checks, but the vendor returned only partial background check data for one employee at issue. In this case, Texas RE_URE2 erroneously recorded the background check as complete. | CIP-004-1 | R3; R3.1 | Lower | High | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system because only one employee with access to CCAs was affected by the issue in the PRA program. The individual involved had an updated, compliant background check performed immediately upon discovery. No issues were uncovered after such check or a subsequent PRA. Additionally, the individual in question began employment with Texas RE_URE2 about 30 years ago and was in good standing. | when the Standard became mandatory and enforceable for Texas RE_URE2 | the date the entity reviewed the background checks | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 completed the following activities to mitigate the violation: 1) All background checks for affected personnel were reviewed and new checks ordered where required. All background checks for personnel newly designated as requiring them are being reviewed manually; and 2) The software program that processes inbound background check data was modified to check for and confirm that all parts of a background check necessary for a CIP-004 compliant PRA be completed before updating the personnel record. | 2011-09-30 | 2012-05-17 | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100517 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that during a Multi-Region CIP Audit, of one of Texas RE_URE2's parent companies that acts as a service provider on Texas RE_URE2's behalf, failed to provide evidence that it enabled only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP). The violation discovered applies to Texas RE_URE2 in Texas RE's region. Although Texas RE_URE2 conducts an annual review of all ports and services, it did not maintain a baseline record of required ports and services. Since Texas RE_URE2 did not conduct its annual review of ports and services using a baseline record, it therefore could not determine a history of modifications to the ports and services in order to verify their configurations. Additionally, Texas RE_URE2 did not provide a list of ports and services and the reason that they are open, and Texas RE_URE2 failed to maintain a document identifying the content of all its required appropriate use banners. | CIP-005-1 | R2 | Medium | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system. Texas RE_URE2 represented that Texas RE_URE2 performs an annual review of each Cyber Asset and documents the process for each Cyber Asset to ensure that it enables only ports and services required for operations and monitoring of Cyber Assets within the ESP. During this annual review, Texas RE_URE2 subject matter experts look for unneeded ports or anomalous entries. Texas RE_URE2 documents the results of this review. Texas RE_URE2 also implemented appropriate use banners on all its access control devices, but failed only to document the content of all such banners. | when the Standard became mandatory and enforceable for Texas RE_URE2 | Present | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 and one of its parent companies will complete the following activities to mitigate the violation: 1) form a cross-functional team of subject matter experts that will perform a comprehensive review and analysis of the audit findings. The team will evaluate multiple options for modifying processes and creating additional documentation to demonstrate compliance. The cross-functional team will make recommendations to one of the parent companies' senior management for remediation strategies, including additional processes or technology required to create the documentation required to demonstrate compliance; 2) approve an action plan for additional process or technology to create the documentation. For banners, this will include verification that documentation exists showing the administrative interface for each ESP access point has either a configured and documented banner, or a Technical Feasibility Exception; 3) design a phased plan to implement the approved action(s) for ports and services and ESP access points; 4) implement Phase 1 of remediation as defined in the approved action plan and design; 5) implement the second phase of remediation, which may include modifications or improvements based on discoveries during implementation, Phase 1; and 6) complete implementation of the approved remediation for all regions and business units. Upon full implementation, for each asset, a comparison of the current ports and services identified in the cyber devices used for the monitoring and control of the access points to the ESP to those ports and services required for operation at the access points will be provided. At the ESP access points, technical programs at all sites, complete baselines to determine if any of the Cyber Assets are connected to other networks outside of the ESP and conduct ongoing data collection will be provided. | Approved completion date of 11/30/2012 | TBD | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100518 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that during a Multi-Region CIP Audit, of one of Texas RE_URE2's parent companies that acts as a service provider on Texas RE_URE2's behalf, failed to provide a list of ports and services that are required for operation. The violation discovered applies to Texas RE_URE2 in Texas RE's region. Texas RE_URE2 provided documentation of an annual review of ports and services and documentation of the function for each port and service, including initial configurations, but did not provide documentation of which ports and services are required for operation, as required by CIP-005-1 R4.2. Texas RE_URE2 also failed to discover all access points to its Electronic Security Perimeter (ESP) as part of its cyber vulnerability assessment, as required by CIP-005-1 R4.3. Texas RE_URE2 conducts a scan to discover all Cyber Assets connected to a network from within the ESP. While this method is effective in finding Cyber Assets within the ESP, it is not effective in determining the access points to the ESP. To summarize, Texas RE has determined that Texas RE_URE2 violated CIP-005-1 R4 by failing to verify that it only enabled those ports and services required for operations at access points to its ESP, and failing to discover all access points to its ESP. | CIP-005-1 | R4 | Medium | Severe | Texas RE has determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system. Texas RE_URE2 performs a comprehensive annual review of all devices, and documents the process with the required level of detail for each individual device, to ensure that only ports and services required for operations and monitoring of Cyber Assets within the ESP are enabled. During this annual review, Texas RE_URE2 subject matter experts seek to identify unneeded ports or anomalous entries, and Texas RE_URE2 documents the results of this review. Regarding CIP-005 R4.3, Texas RE_URE2 conducts an annual discovery scan to identify all Cyber Assets within a specific ESP. Texas RE_URE2 compares the results of this scan to a list of known devices, and then identifies and confirms access points, as applicable. Texas RE_URE2 represents that it has properly identified all the access points to the ESP. Therefore, although Texas RE_URE2 did not conduct a scan that would discover all possible access points to its ESP, Texas RE_URE2 did conduct an annual scan that discovered all Cyber Assets connected to a network with the ESP. | when the Standard became mandatory and enforceable for Texas RE_URE2 | Present | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 and one of its parent companies will complete the following activities to mitigate the violation: 1) form a cross-functional team of subject matter experts that will perform a comprehensive review and analysis of the audit findings. The team will evaluate multiple options for modifying processes and creating additional documentation to demonstrate compliance. The cross-functional team will make recommendations to one of the parent companies' senior management for remediation strategies, including additional processes or technology required to create the documentation required to demonstrate compliance; 2) approve an action plan for additional process or technology to create the documentation. For banners, this will include verification that documentation exists showing the administrative interface for each ESP access point has either a configured and documented banner, or a Technical Feasibility Exception; 3) design a phased plan to implement the approved action(s) for ports and services and ESP access points; 4) implement Phase 1 of remediation as defined in the approved action plan and design; 5) implement the second phase of remediation, which may include modifications or improvements based on discoveries during implementation, Phase 1; and 6) complete implementation of the approved remediation for all regions and business units. Upon full implementation, for each asset, a comparison of the current ports and services identified in the cyber devices used for the monitoring and control of the access points to the ESP to those ports and services required for operation at the access points will be provided. At the ESP access points, technical programs at all sites, complete baselines to determine if any of the Cyber Assets are connected to other networks outside of the ESP and conduct ongoing data collection will be provided. | Approved completion date of 11/30/2012 | TBD | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100519 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that during a Multi-Region CIP Audit, of one of Texas RE_URE2's parent companies that acts as a service provider on Texas RE_URE2's behalf, implemented a process to ensure that it enables only required ports and services, but did not include a type of protocol ports in its system scans that it uses in this process. The violation discovered applies to Texas RE_URE2 in Texas RE's region. As a result, Texas RE_URE2 did not effectively ensure that it only enables those ports and services required for normal and emergency operations. | CIP-007-1 | R2 | Medium | Severe | Texas RE has determined this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS of failing to implement a process to ensure that a type of protocol ports were included its system scans was mitigated by the following facts. Texas RE_URE2 uses network security controls such as a network intrusion detection and prevention system, which analyzes network traffic for known and suspect malicious activity. This system considers threats affecting ports. Lastly, Texas RE_URE2's Electronic Security Perimeter (ESP) firewalls are specifically configured to only allow traffic using specific protocols to enter the network. This configuration prevents unsolicited traffic from passing into the networks segregated by ESPs. | when the Standard became mandatory and enforceable for Texas RE_URE2 | Present | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 and one of its parent companies will complete the following activities to mitigate the violation: 1) form a cross-functional team of subject matter experts that will perform a comprehensive review and analysis of the audit findings. The team will evaluate multiple options for modifying processes and creating additional documentation to demonstrate compliance. The cross-functional team will make recommendations to one of the parent companies' senior management for remediation strategies, including additional processes or technology required to create the documentation required to demonstrate compliance; 2) approve an action plan for additional process or technology to create the documentation. For banners, this will include verification that documentation exists showing the administrative interface for each ESP access point has either a configured and documented banner, or a Technical Feasibility Exception; 3) design a phased plan to implement the approved action(s) for ports and services and ESP access points; 4) implement Phase 1 of remediation as defined in the approved action plan and design; 5) implement the second phase of remediation, which may include modifications or improvements based on discoveries during implementation, Phase 1; and 6) complete implementation of the approved remediation for all regions and business units. Upon full implementation, for each asset, a comparison of the current ports and services identified in the cyber devices used for the monitoring and control of the access points to the ESP to those ports and services required for operation at the access points will be provided. At the ESP access points, technical programs at all sites, complete baselines to determine if any of the Cyber Assets are connected to other networks outside of the ESP and conduct ongoing data collection will be provided. | Approved completion date of 11/30/2012 | TBD | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100520 | Settlement Agreement | Texas RE_URE2 submitted a Self-Report to Texas RE stating that during a Multi-Region CIP Audit, of one of Texas RE_URE2's parent companies that acts as a service provider on Texas RE_URE2's behalf, experienced an outage of a third-party software application that included a patch management feature that Texas RE_URE2 uses to implement CIP-007 processes. The violation discovered applies to Texas RE_URE2 in Texas RE's region. During the time period that this application malfunctioned, Texas RE_URE2 failed to assess the applicability of patches for its third-party software applications. Texas RE_URE2 did not have a backup method in place for identifying or assessing security patches and upgrades. Additionally, Texas RE_URE2 asserted that it automatically deems all security patches to be applicable and therefore did not maintain documentation of the assessment of security patches and upgrades for applicability. | CIP-007-1 | R3; R3.1 | Lower | Severe | Texas RE has determined that this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed to the BPS by the foregoing facts and circumstances was mitigated by the following factors. Texas RE_URE2 represents that it installed all applicable security patches, although it did not document this policy in Texas RE_URE2’s patch management program. Additionally, Texas RE_URE2 applies “defense-in-depth” strategies, with multiple layers of network security including multiple “demilitarized zones” (DMZs) and firewalls, multifactor authentication into each DMZ, and network intrusion detection and prevention systems. Moreover, Texas RE_URE2 protects the systems in question by requiring authentication, which also employs anti-virus protection and host intrusion prevention software. | when the Standard became mandatory and enforceable for Texas RE_URE2 | Present | $0 (for TRE201000247, TRE201100335, TRE201100343, TRE201100345, TRE201100359, TRE201100360, TRE201100380, TRE201100398, TRE201100517, TRE201100518, TRE201100519, and TRE201100520) | Self-Report | Texas RE_URE2 and one of its parent companies will complete the following activities to mitigate the violation: 1) form a cross-functional team of subject matter experts that will perform a comprehensive review and analysis of the audit findings. The team will evaluate multiple options for modifying processes and creating additional documentation to demonstrate compliance. The cross-functional team will make recommendations to one of the parent companies' senior management for remediation strategies, including additional processes or technology required to create the documentation required to demonstrate compliance; 2) approve an action plan for additional process or technology to create the documentation. For banners, this will include verification that documentation exists showing the administrative interface for each ESP access point has either a configured and documented banner, or a Technical Feasibility Exception; 3) design a phased plan to implement the approved action(s) for ports and services and ESP access points; 4) implement Phase 1 of remediation as defined in the approved action plan and design; 5) implement the second phase of remediation, which may include modifications or improvements based on discoveries during implementation, Phase 1; and 6) complete implementation of the approved remediation for all regions and business units. Upon full implementation, for each asset, a comparison of the current ports and services identified in the cyber devices used for the monitoring and control of the access points to the ESP to those ports and services required for operation at the access points will be provided. At the ESP access points, technical programs at all sites, complete baselines to determine if any of the Cyber Assets are connected to other networks outside of the ESP and conduct ongoing data collection will be provided. | Approved completion date of 11/30/2012 | TBD | Neither Admits nor Denies
2012-09-28 | FERC | NP12-47-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201100475 | Settlement Agreement | Texas RE_URE3 submitted a Self-Report to Texas RE stating that Texas RE_URE3 did not properly implement automated tools and organizational process controls to monitor system events that are related to cyber security for a period of approximately six months for 49 total Critical Cyber Assets (CCAs) relating to two Critical Assets (CAs). At the first CA, the violation included 12% of the total CCAs. At the second CA, the violation included 19.7% of the total CCAs. Credentials were not configured properly on Texas RE_URE3's central logging solution, which led to the inability of Texas RE_URE3's system central log collection solution to communicate with the 49 CCAs. The logs were being appropriately generated and stored on 19.7% of the CCAs, at the second CA, within scope of the violation, but were not being sent to the central monitoring solution. This resulted in a failure to review the logs for these 19.7% of the CCAs as required. Additionally, the ability to generate logs of sufficient detail for system events related to cyber security was impacted for 12% of the CCAs, at the first CA, for which appropriate logging policies were active, but logs could not be stored due to the CCAs' Event Logs reaching maximum capacity. This terminated log storage on the 12% of the affected CCAs at the first CA. The log storage was terminated for the 12% of the CCAs. Logging resumed when the issue was noticed and corrected immediately. | CIP-007-1 | R6 | Lower | Severe | This violation posed a moderate and not serious or substantial risk to the bulk power system (BPS) because Texas RE_URE3 had improperly implemented automated tools and organizational process controls to monitor system events that are related to cyber security which resulted in a loss of reporting on the central system. There are several mitigating factors that help decrease the likelihood that these CCAs could have been compromised and negatively impacted the two Critical Assets’ reliability. External interactive access to the Cyber Assets is controlled by a redundant firewall pair at the Critical Assets that implements two-factor authentication, as well as the network infrastructure for Texas RE_URE3, which provides defense in depth. The affected CCAs were protected by anti-virus/malware software, which would have prevented the introduction of virus or malware software. The anti-virus system is wholly separate and distinct from the centralized logging system and remained unaffected during the time period. The anti-virus system provides alerts directly to a user on the control system, as well as sends an alert to the anti-virus system console, which shows up in reports run by the administrator. The in-scope CCAs are physically secured and completely enclosed within a (six-wall) border. Physical access is controlled and monitored using electronic locks and video recording. The physical access controls limit physical access to the cyber assets that are within the Electronic Security Perimeter (ESP). Finally, the event was discovered during a password review and immediately mitigated through proper configuration. | when the Standard became mandatory and enforceable for Texas RE_URE3 | when the centralized monitoring solution was configured with the proper credentials to establish communications and the Event Log was set to the appropriate settings | 7000 | Self-Report | Texas RE_URE3 completed the following activities to mitigate the violation: (1) Based upon review of all Central Monitoring at the two affected sites, Texas RE_URE3 developed and distributed the appropriate configuration settings for all potentially impacted sites detailing the proper configuration for the central logging solution to the appropriate personnel responsible for execution and sustainability of compliance to the CIP-007-3 R6 requirements; (2) Based upon review of all Event Logs at the two affected sites, Texas RE_URE3 developed and distributed a set of the appropriate configurations settings for the Event Log to all of Texas RE_URE3's affected sites to ensure that appropriate configurations for the Event Log are known and implemented by all applicable responsible personnel; (3) Texas RE_URE3 modified existing monitoring controls to use a special purpose account, specifically configured for the monitoring system. This account is monitored separately from normal user and shared accounts, and will only be used to allow the centralized monitoring application access to the individual systems. The account has a reduced permission set; (4) Texas RE_URE3 reviewed the configurations for all applicable sites to ensure that the configurations were correctly established and that all Central Monitoring and Event Log functionality is operating correctly; (5) Texas RE_URE3 modified existing monitoring controls to break down logging review activities on a per-CCA basis to allow monitoring of specific CCAs. Per-CCA basis monitoring allows identification of similar log loss issues by comparing current log volume with baseline log volume, and allowing for identification of volumes that fall outside of baseline values; (6) Texas RE_URE3 designed a bi-weekly monitoring status report that can be used by responsible personnel to verify that the monitoring equipment is in good working order and is receiving logs appropriately. Bi-weekly is chosen as it is within the local buffering period of logs. (i.e., Logs are buffered locally for two weeks and may be recovered for this time period). Implementation of this mitigating action includes appropriate updates to procedures; (7) Texas RE_URE3 created and conducted training on basic monitoring techniques for responsible personnel that demonstrated the actions necessary to determine that CCAs are logging and are generating logs that fall within historical baselines, as well as how to correct issues associated with CCAs not logging; and (8) Texas RE_URE3 implemented monitoring technology within the central logging solution to alert responsible personnel via email when conditions which precede these logging issues occur so Texas RE_URE3 personnel can take proactive action to prevent the reoccurrence of these issues. This monitoring would act as a technical control, alerting responsible personnel in the event that CCAs are not providing logs as anticipated and required. | 2012-03-31 | 2012-06-25 | Admits | Texas RE_URE3 has an internal compliance program (ICP) which was in place at the time of the violation and Texas RE considered it to be a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102731 | Settlement Agreement | WECC_URE1 self-reported a violation of VAR-002-1 R3. WECC_URE1 determined in an internal investigation that the automatic voltage regulators (AVRs) for four generating units were inadvertently being switched out of voltage control mode when the generator operator selected the VAR control mode. WECC_URE1 determined the cause to be a malfunction with the AVR's control system program which was intended to force the voltage control mode if the generator operator selected the VAR control mode. The malfunction with the control system program resulted in the generator operators unknowingly switching the AVRs out of voltage control mode. Because WECC_URE1's generator operators did not know that the AVR was switched out of voltage control mode, WECC_URE1 failed to notify its Transmission Operator (TOP) of the change in AVR status. WECC determined that WECC_URE1 had not notified its (TOP) of the change in status in accordance with the requirement. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 generators were operating the generating units according to the TOP's voltage schedule. WECC_URE1 system studies have shown that the transmission system in the location of these generators is not voltage constrained or close to voltage instability. System studies have also shown that the system voltage in this area usually runs high, not low, due to the interconnection with another entity. | when WECC_URE1's automatic voltage control was first switched out of voltage control mode and it did not notify its TOP | when WECC_URE1 remedied the AVR control system programming issue | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Self-Report | WECC_URE1 switched its AVR back into voltage control mode, notified its TOP of the status change, and provided training and guidance to its operators. WECC_URE1 also disabled the VAR setting in the AVR software, thereby disabling the VAR controller. In addition, WECC_URE1 installed jumpers on the AVRs for the affected generating units, physically disabling the VAR control mode of the AVRs. | 2011-03-29 | 2012-04-06 | Neither Admits nor Denies | WECC_URE1 was awarded self-report credit. WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE1's violation history as an aggravating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002817 | Settlement Agreement | WECC determined that WECC_URE1 had a violation of CIP-007-2a R7.1 because WECC_URE1 returned a hard drive disk, a Critical Cyber Asset (CCA), to the hardware vendor without deleting sensitive data contained on the hard drive. | CIP-007-2a | R7; R7.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the incident was due to human error, and WECC_URE1 provided evidence that there were no other instances where WECC_URE1 failed to erase or destroy sensitive cyber security or reliability data prior to disposal or redeployment of Cyber Assets. Further, the disk was unreadable when it was returned to the hardware vendor and a representative provided verbal confirmation that it is had a policy to destroy devices that are returned. | when WECC_URE1 returned the CCA to the hardware vendor without deleting sensitive material | when WECC_URE1 modified its vendor support agreement permitting WECC_URE1 to retain defective media | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 amended its vendor support contract to include a defective media retention option. This option allows WECC_URE1 to destroy defective media rather than returning it to the vendor and is renewed annually with the vendor support contract. | 2010-11-01 | 2012-07-10 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002816 | Settlement Agreement | WECC determined that WECC_URE1 had a violation of CIP-006-1 R3 because it did not implement procedural controls for monitoring physical access at all points on its Physical Security Perimeter (PSP). Specifically, WECC_URE1's PSP access control and monitoring devices did not provide visual or audible alerting upon entry to the facility. WECC concluded that the position of transmission operators is such that the personnel cannot visually verify entry through the PSP until an individual is already present on the transmission operating floor. WECC_URE1 also did not put in place alarms that provide for immediate notification or human observation responsible for controlling physical access as prescribed in CIP-006-1 R3. | CIP-006-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 did task its operating personnel with the dual role of operating the transmission system, as well as monitoring physical access. WECC_URE1 also provided the operating personnel with tools to visually inspect entry as needed. These measures provided some protection against an unauthorized individual gaining access to the PSP. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 completed the following mitigating activities: (1) installed alarms that provide for immediate visual and audible notification to the system operators of all primary system operations control center PSP door openings; (2) deployed additional video cameras and video display equipment such that the system operators can visually verify entries at each entry door of the system operations control center PSP; and (3) disabled entry capability for any doors for which visual and audible alerting and visual entry observation capabilities cannot be provided. | 2012-06-29 | 2012-07-25 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002814 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-006-1 R1, because WECC_URE1 failed to ensure that its Physical Security Perimeter (PSP) at its backup control center was completely enclosed in a "six-wall" border. The WECC Audit Team identified Critical Cyber Assets located at two of its Critical Asset facilities, a primary control center and a backup control center. The WECC Audit Team performed a walkthrough at the two facilities. During the walkthrough, the WECC Audit Team lifted ceiling tiles at both facilities and discovered that the entire length of the north wall of the backup control center did not have sheet rock that extended to the top of the ceiling. According to WECC Audit Team, this created an opening two feet high, which would allow a person access to the PSP. In addition, the WECC Audit Team found that WECC_URE1 failed to provide any documentation that it had performed testing procedures, applied security patches, deployed anti-virus and malware tools, or had created recovery plans for PSP access control and monitoring devices. WECC_URE1 failed to provide the necessary protective measures for its PSP access control and monitoring (ACM) devices in violation of CIP-006-1 R1.8. WECC Enforcement determined that WECC_URE1 had a violation of CIP-006-1 R1.1 for failing to ensure that the PSP at its backup control center was completely enclosed. WECC Enforcement also determined that WECC_URE1 had a violation of CIP-006-1 R1.8 for failing to afford its ACM Cyber Assets the protections in CIP-007-3 R1 (test procedures), CIP-007-3 R3 (security patches), CIP-007-3 R4 (anti-virus and malware tools); and CIP-009-3 R1 (recovery plans). | CIP-006-1 | R1; R1.1, R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the PSP resides in an area of controlled access. Because the PSP resides within an area of controlled access, the ability of unauthorized personnel gaining access to the PSP is limited. The PSP at issue resides within an WECC_URE1-operated controlled access area, where WECC_URE1 had protective measures prescribed by the Standard. WECC_URE1 had physical access controls, monitored physical access, logged physical access, retained access logs, and had a maintenance and testing program. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 completely enclosed the PSP at its backup control center; applied testing procedures for PSP ACM devices; created recovery plans for PSP ACM devices; modified its cyber security program and policy documents, where necessary, to explicitly address the requirements of CIP-006-1 R1.8 for PSP ACM devices; applied security patches for PSP ACM devices; and deployed anti-virus and malware tools for PSP ACM devices. | 2012-05-15 | 2012-07-18 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002813 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-004-1 R4 because WECC_URE1 did not have documentation that it had performed quarterly reviews of its personnel with access to the Critical Cyber Assets (CCAs). Although WECC_URE1 did perform some level of review, WECC_URE1 was unable to provide dates, times and signatures indicating how the lists were reviewed. | CIP-004-1 | R4; R4.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 provided some level of review but did not have evidence of dates, times, and signatures indicating how the lists were reviewed. Any time an individual's physical access was granted or modified in the system, the entire access list was reviewed and verified. In addition, during the violation period, the list was reviewed more frequently than quarterly because requests to grant or remove access occurred more frequently during this period. | when the Standard became mandatory and enforceable for WECC_URE1 | when the required quarterly review was completed | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | For quarterly reviews, WECC_URE1 utilizes a form that lists personnel with access to CCAs. This form is documented in WECC_URE1’s critical infrastructure cyber security program and records the date of review, location of review, the reviewer’s name, type of access that is being reviewed, and the access lists being reviewed. Copies of the access lists being reviewed are attached to the completed forms along with any required access changes as a result of the review. | 2009-06-29 | 2011-09-13 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002812 | Settlement Agreement | WECC determined that WECC_URE1 had a violation of CIP-003-1 R4 because WECC_URE1 failed to include the Critical Asset list, as required by Standard CIP-002-2, in its protected Critical Cyber Asset information program. | CIP-003-1 | R4; R4.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because not properly protecting a list of Critical Assets could expose the BPS to a cyber security attack. If unauthorized individuals gained access to this information, they could use it to perform malicious acts to the BPS. The risk to the BPS was mitigated by the following factors. WECC_URE1's Critical Asset list did not contain any Critical Cyber Asset information. In addition, although WECC_URE1 had not included the Critical Asset list, WECC_URE1 did have an information protection program in place during the duration of the violation. | when the Standard became mandatory and enforceable for WECC_URE1 | when WECC_URE1 modified its Critical Cyber Asset information protection program to include the Critical Asset list | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 modified its CIP compliance program document for CIP-003 R4 to explicitly classify the Critical Asset list as protected information. WECC_URE1 also modified its CIP-003 R4 compliance program document to explicitly classify floor plans which contain Critical Cyber Asset information as protected information. | 2011-07-20 | 2012-05-18 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002810 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-002-1 R3 because three switches should have been identified as Critical Cyber Assets (CCAs). These switches should have been identified as CCAs because they directly support WECC_URE1's primary control center. WECC concluded that three switches used in the access control and monitoring of one of WECC_URE1's Electronic Security Perimeters were not identified as CCAs as required by CIP-002-1 R3. WECC concluded that the three switches were CCAs because they were used to configure, provide access to, and monitor the primary control center, which is an identified WECC_URE1 Critical Asset. | CIP-002-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 provided some level of protection to these three switches as they are co-located and co-managed with WECC_URE1's other primary control center CCAs. The PSP at issue resides within an WECC_URE1-operated controlled access area, where WECC_URE1 had protective measures prescribed by the Standard. WECC_URE1 had physical access controls, monitored physical access, logged physical access, retained access logs, and had a maintenance and testing program. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 performed configuration changes in the network switches at issue to remove the internet protocol (IP)-based management capability, thus making them no longer CCAs. | 2010-10-15 | 2011-10-04 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002267 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of IRO-STD-006-0 WR1 because WECC_URE1 failed to respond to a schedule curtailment request for 29 minutes. WECC_URE1's Transfer Distribution Factor matrix document indicated that WECC_URE1 did not respond to a schedule curtailment request of contributed 1.4 MW to a Qualified Path for 29 minutes. Pursuant to the Sanction Table appended to the Standard, this violation represents one occurrence at Level One of Noncompliance. | IRO-STD-006-0 | WR1 | N/A | N/A | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The identified Qualified Path was rated at approximately 500 MW at the time and was flowing at less than the rate of the Qualified Path, accommodating 100 MW of unscheduled flow. WECC_URE1's curtailment obligation amounted to 0.28% of the flow on the path. The required schedule relief in the curtailment request was 1.4 MW and the duration lasted 29 minutes. | when WECC_URE1 did not respond to a schedule curtailment request | when WECC_URE1 responded | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 initiated regular reviews of standard operating procedures (SOPs) by its system operators will help prevent future violations of this Standard. WECC_URE1 also initiated a tool to notify its operators of curtailments associated with the WECC Unscheduled Flow Mitigation Plan. WECC_URE1 also instituted a SOP to explain the use of the tool and associated transmission curtailments. All system operators have reviewed the SOP associated with Unscheduled Flow Curtailments. | 2007-09-30 | 2012-05-07 | Neither Admits nor Denies | Pursuant to the Sanction Table appended to the Regional Standard, this violation represents one occurrence at Level One of Noncompliance. The Sanctions Table for this Standard state that the following sanction should be assessed "Letter to Responsible Entity's Chief Executive Officer informing the Responsible Entity of noncompliance with copies to NERC, WECC Member Representative, and WECC Operating Committee Representative." The level of noncompliance in this case is 1 because the required relief was 1.4 MW, which is less than the 5 MW thresholds for Level 1 noncompliance as prescribed by the Standard. WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002266 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of EOP-005-1 R1 because its restoration plan did not include necessary operating instructions and procedures to cover the loss of vital telecommunications channels as required by the Standard. Although WECC_URE1 stated that loss of vital telecommunications channels is addressed in the design requirements of the WECC_URE1 telecommunication infrastructure, no commercial power or third-party telecommunications facilities are required at any point from the blackstart unit to load centers at the two pertinent substations. The telecommunications infrastructure is designed with the requirement that remote switching and supervisory control will be necessary to restore the WECC_URE1 system. WECC_URE1 also stated that its restoration plan includes a backup plan if anything in the proposed plan fails. WECC determined that this was insufficient to address the loss of vital telecommunications channels because WECC_URE1 was relying on the design requirement of WECC_URE1's own telecommunication equipment to be reliable and remain in service to address the loss of vital communications channels. | EOP-005-1 | R1 | Medium | Lower | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 had a plan in place to connect directly with another entity to cover emergency conditions. Furthermore, WECC_URE1's system operators demonstrated during Audit interviews that they are well-trained to man critical facilities when necessary. | the first day following Certification of Mitigation Plan Completion for WECC_URE1's prior EOP-005-1 R1 violation | when WECC_URE1 revised its restoration plan to further address the loss of vital telecommunications systems | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 revised its system restoration plan to address the loss of vital telecommunications during a system restoration event. The revision directs the system operator to utilize the WECC_URE1 radio system to establish necessary communications and also dispatch personnel to the appropriate sites. | 2011-01-21 | 2012-03-15 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE1's violation history as an aggravating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002265 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of COM-001-1 R5 because WECC_URE1 did not have in place operating procedures and instructions that directed WECC_URE1 personnel to man substations in the event of a loss of communications and, therefore, WECC_URE1 did not have in place operating procedures and instructions to enable continued operations of its system during the loss of its telecommunications equipment. WECC reviewed three of WECC_URE1's standard operating procedure (SOP) documents. Although WECC previously determined that these documents adequately described the actions to be taken during a loss of telecommunications facilities, these documents were superseded by WECC_URE1's new SOP. WECC determined that the new SOP did not contain written operations and procedures to enable continued operations of its system in the event that WECC_URE1's telecommunications facilities are inoperable. | COM-001-1 | R5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 had procedures in one of its SOP document to implement fully redundant communications facilities at its backup control center, and had provisions for training its system operators. In addition, although not explicitly documented, WECC_URE1 demonstrated, through interviews with the WECC Audit Team, that its system operators are well-trained to man substations when necessary. | when WECC_URE1's new SOP policy was established | when WECC_URE1 reinstated the previously retired SOP | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 updated and reinstated its previously retired SOP document and provided training. The SOP document provides written operating procedures and instructions to enable continued operation of its system during the loss of voice and data communications. | 2011-01-21 | 2012-03-21 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002400 | Settlement Agreement | WECC sent WECC_URE1 a Notice of On-Site Compliance Audit. WECC_URE1 self-reported a violation of CIP-004-1 R2. WECC conducted an Audit of WECC_URE1's compliance with, among other Reliability Standards, CIP-004-1 R2. Because WECC_URE1 had previously self-reported a violation of CIP-004-1 R2, the WECC Audit Team reviewed WECC_URE1's Self-Report at the Audit. The WECC Audit Team concluded that, consistent with WECC_URE1's Self-Report, four WECC_URE1 contractors had not received training as required by CIP-004-1 R2.1. WECC Enforcement reviewed WECC Audit Team findings and determined that WECC_URE1 had a violation of CIP-004-1 R2.1 for failing to train four of its contractors prior to granting them access to Critical Cyber Assets (CCAs). | CIP-004-1 | R2; R2.1 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the subject individuals are employees of an WECC_URE1 contractor that has been providing monitoring and optimization of the generation control software on WECC_URE1's supervisory control and data acquisition (SCADA) system since several years before the Reliability Standards became mandatory and enforceable. The affected individuals perform similar services for other NERC-registered entities and receive ongoing cyber security training from these entities. Personnel risk assessments were conducted on the affected individuals per CIP-004 R3, and were verified by WECC_URE1 personnel prior to adding the subject individuals to the approved CCA access list. For these contractors, cyber access to WECC_URE1's SCADA system requires two levels of authentication: (1) authentication at the corporate firewall VPN, and (2) authentication at the CIP access point firewall. The ability for a contractor to connect through the two access points is normally disabled. The contractor must specifically request access from SCADA support personnel and be authorized prior to gaining access. Access to WECC_URE1's SCADA system by the subject individuals is not continuous and is granted for short durations a few times per year. | when the Standard became mandatory and enforceable for WECC_URE1 | when the four individuals had their access revoked | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Self-Report | Upon discovery of the violation, WECC_URE1 revoked access authorizations for the individuals involved. On the next day, WECC_URE1 provided them cyber security training specific to their role and added their names to the list of individuals requiring annual cyber security training and quarterly awareness programs. WECC_URE1 also verified that its training and access lists were current and correct. | 2011-08-20 | 2011-12-28 | Neither Admits nor Denies | WECC_URE1 was awarded credit for supplying additional useful information in its Self-Report. WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE1's violation history as an aggravating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009304 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Certification to WECC stating it was in violation of CIP-007-1 R6. WECC_URE2 reported that after it completed its internal documentation sufficiency review, it recognized that some of its generation devices were not sending system event logs to its centralized logging server. Specifically, 52.8% of Critical Cyber Assets (CCAs) and Critical Assets (CAs) within the Electronic Security Perimeter (ESP) failed to log cyber security events to the centralized logging server system. WECC_URE2 stated that since its compliance enforcement date for the Standard it failed to ensure 52.8% of the devices within the ESP were logging cyber security events to its centralized logging system. WECC_URE2 stated further that 28 of the CCAs in scope are part of the operation of its Energy Management System (EMS), and the remaining 10 CAs are network devices (routers and switches) within the WECC_URE2 generating sites ESPs and PSPs . WECC_URE2 noted that the 52.8% devices in scope were unable to send cyber security system events to its centralized logging server system because of incorrect system configurations that did not allow the devices to log or monitor events. WECC determined that WECC_URE2 violated CIP-007-1 R6 for a failure to ensure that all CAs within the ESP implement automated tools or organizational process controls to monitor system events that are related to cyber security. Specifically, WECC_URE2 failed to implement and document organizational processes and technical and procedural mechanisms for monitoring for security events on 52.8% devices. | CIP-007-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the 52.8% devices in scope were located at WECC_URE2's generation sites within the ESPs and Physical Security Perimeters (PSPs), thereby reducing the risk related to cyber security events. As compensating measures, the ESPs at issue are equipped with intrusion detection systems and access point protections, including externally-connected communication end points, which allow for monitoring of security events. Additionally, the devices in scope have only necessary ports and services enabled and anti-virus and anti-malware software installed, further reducing the risk to the BPS related to cyber security events. For these reasons, WECC determined this violation posed moderate risk to the reliability of the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | 17400 | Self-Certification | In accordance with WECC_URE2's Mitigation Plan, WECC_URE2 completed the following activities: (1) Implemented a new system to improve the technical control for log management; (2) Improved ability to automatically identify when systems stop logging; (3) Increased the reliability to automatically track log activities and alerts; (4) Stated generating of automatic dashboards for real-time status reports of logging; (5) Established dedicated personnel to review, track, escalate, fix and monitor status on logging issues; (6) Established that the Information Technology (IT) department provides regular status reports to an Operations and IT Management confirming all CCA and CA devices are logging; (7) Updated IT procedural documentation for management of logging; (8) Established that an Operations department reviews and updates its procedure for ensuring that new assets are configured to log by default prior to deployment; and (9) Established that an Operations department reviews and updates its notification procedure to IT for all new or changed assets or for planned maintenance where logging and system events related to Cyber Security are required. | 2012-06-22 | 2012-09-25 | Agrees and Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP), which was in effect at the time of the violation, and considered it a mitigating factor in determining the penalty amount.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000409 | Settlement Agreement | FRCC_URE1 self-reported that it did not ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) had the proper controls in place to monitor system events that are related to cybersecurity, as required by CIP-007-1 R6. FRCC_URE1 did not ensure that logs were properly maintained for the required duration. FRCC determined that the violation involved a number of individual devices: 15% were Cyber Assets not configured for logging system events; 24% were switches, where logs were not generated due to configuration issues resulting from remote authentication protocol and other upgrades; and 61% were Cyber Assets experiencing a four-day outage of a server and were unable to capture the logs related to cybersecurity. | CIP-007-1 | R6 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the devices in scope were within identified and protected ESPs with protected access points. FRCC determined that the violation posed a moderate risk because lack of monitoring and logging for these assets could have resulted in an opportunity for internal compromise and weakened the defense in depth for the ESP. However, the risk was limited because logging at the access points was effectively implemented and remote access well-controlled. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) improved the Cyber Assets test procedure to require testing of monitoring and logging functions; (2) configured device log storage space; (3) required appropriate configuration of remote authentication protocol and other devices; (4) configured switches with correct log server configuration; (5) reviewed and reconciled all log activity to confirm the results of implementation; (6) locked the console ports for NERC-defined switches; (7) disabled remote access for switches which require physical access to apply changes through the local console port; and (8) trained staff on the new testing and verification process. | 2011-07-19 | 2012-05-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007926 | Settlement Agreement | FRCC_URE1 self-reported that it failed to fully establish, document, and implement a process for ensuring that only ports and services required for normal and emergency operation were enabled. FRCC_URE1 secured most ports and services, but since it did not update documentation for each individual device, but rather created its baseline by device type, it was not possible for FRCC_URE1 to demonstrate compliance with CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE1's evidence demonstrated that all Cyber Assets within an Electronic Security Perimeter were well-hardened and known vulnerabilities were patched and addressed. However, FRCC determined that the violation posed a moderate risk because failure to document the required ports and services can result in unknown ports being left open for attack from sources with malicious intent. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a review of Cyber Assets including software inventory; (2) research and design procedures for ports and services monitoring solution; (3) complete a ports and services evaluation and create a baseline for each asset type; (4) implement ports and services monitoring solution; (5) update ports and services documentation; (6) train and communicate changes to personnel; and (7) request any required Technical Feasibility Exceptions where disabling ports and services is not technically feasible. | 1/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007927 | Settlement Agreement | FRCC_URE1 self-reported that it failed to perform a cyber vulnerability assessment (CVA) in accordance with the requirements of CIP-007-1 R8. FRCC_URE1 does have a documented process document and did complete the CVAs for the previous years, but these CVAs did not meet all of the requirements of the Standard. FRCC_URE1 conducted CVAs which included scans of ports and services for only some Cyber Assets, in violation of R8.2. The CVAs included a review of controls for default accounts, but did not include all Cyber Assets within the Electronic Security Perimeter (ESP). FRCC_URE1's CVA also included a review of configurations for patches and updates of known vulnerabilities. FRCC_URE1 did not create an action plan that included the status to remediate known vulnerabilities identified during the CVA, in violation of R8.4. | CIP-007-1 | R8 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all devices were afforded protection of the ESP. FRCC determined that the violation posed a moderate risk because lack of performing a complete CVA can result in vulnerabilities in the system that would not be discovered or mitigated. While FRCC_URE1 failed to conduct and document the CVA results in the required manner, evidence demonstrated that all Cyber Assets within an ESP were well-hardened and known vulnerabilities were addressed. | when FRCC_URE1 failed to complete a CVA which was in accordance with the Standard | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a vulnerability scan that includes; review of default controls for passwords, review of ports and services, and update of the vulnerability assessment procedure; (2) document the results of the scan; and (3) create an action plan for remediating the identified vulnerabilities. | 1/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007928 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-007-1 R5. Specifically, user account passwords for one local account on a number of workstations and several accounts on one server were not changed at least annually, as required by the Standard. Further, FRCC_URE1 could not demonstrate the following: that logging for all accounts was enabled, as required by R5.1.2; that a policy was implemented to minimize the usage of admin and shared accounts, as required by R5.2; that default account passwords were changed prior to putting systems in service, as required by R5.2.1; that required audit trails were maintained for all user accounts, as required by R5.2.3; and that passwords had the complexity required by R5.3.2. | CIP-007-1 | R5 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE1 did not document a policy to limit use of shared accounts and lacked documentation of all the accounts and users who have access to such accounts. FRCC determined this violation posed a moderate risk because lack of this documentation could limit FRCC_URE1's control and accountability for use of shared and administrative accounts. The risk from this violation was limited because all users with such access were well-trained and maintained control and accountability which included not sharing passwords for shared and administrative accounts, minimizing the use (using only when required), utilizing individual accounts for routine applications and changing passwords when users with access were relocated or transferred. Further, in any condition when a user did not require access as a result of change in status, his or her access was revoked immediately. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) change and update password controls to correct gaps in the account management process; (2) communicated the required password change to procedures for the addition of users in the card key system to ensure that new users are set up with the requirement for their passwords to expire at least annually; (3) document the change and train key individuals on the revised procedure to set up interactive card key user accounts in the card key system; (4) perform a complete review of CIP-007 R5 compliance and document and report the findings to FRCC; and (5) complete a comprehensive training and awareness workshop to incorporate all the lessons learned and introduce newly implemented procedure required to maintain compliance with CIP-007 R5. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007930 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-005-1 R1. FRCC_URE1 failed to identify and document its serially connected communication end points as access points to the Electronic Security Perimeter (ESP), as required by the Standard. Even though the devices are using serial communication protocols, configuration requires use of network switches and host subnet that uses routable protocol; therefore, the devices should have been identified and documented. The devices were protected within the Physical Security Perimeter (PSP) but not identified or documented on any of FRCC_URE1's CIP-005 evidence documentation. | CIP-005-1 | R1 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the devices used serial, non-routable protocol and were protected within the PSP. FRCC determined that the violation posed a moderate risk because even though the access points were protected, devices connected to the access points were not completely protected and provided means of unauthorized access and misconfiguration. The risk was limited because the end points were protected with the termination of FRCC_URE1's fiber network and were only accessible to personnel who were thoroughly vetted and with direct responsibility for support and operation. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) update access points and the Critical Cyber Asset (CCA) documentation for newly identified access points: (2) create or update appropriate processes and procedures: (3) complete review of all Cyber Assets associated with Critical Assets to identify any additional access points using expanded interpretation; (4) determine and implement required controls for newly-identified access points including any required Technical Feasibility Exception requests, and report the findings to FRCC; (5) reduce access points by redesigning network and reconfiguring existing access point devices; and (6) relocate access points to new network segments and protect as per CIP requirements. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit. FRCC considered FRCC_URE1's prior violation history.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007931 | Settlement Agreement | FRCC_URE1 self-reported that its cyber vulnerability assessments (CVAs) of the electronic access points to the Electronic Security Perimeter (ESP) did not comply with all requirements of CIP-005-1 R4. FRCC_URE1's documentation was not complete and could not demonstrate compliance with the requirements. The CVAs did include discovery of access points but did not include review of ports and services, review of default community strings, and a documented action plan for remediation of identified vulnerabilities. As part of its CVA, FRCC_URE1 performed a comprehensive scan with all results documented but did not complete all activities to comply with CIP-005-1 R4.2, R4.3 and R4.5. | CIP-005-1 | R4 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all devices were afforded the protections of the ESP. FRCC determined that the violation posed moderate risk because failure to perform a complete CVA can result in vulnerabilities in the system that would not be discovered or mitigated. While FRCC_URE1 failed to conduct and document the CVA results in the required manner, evidence demonstrated that all ESP access points were well-configured and only trusted network devices were allowed to communicate within the ESP. Further, known vulnerabilities and password controls were effectively addressed. | when FRCC_URE1 failed to complete a CVA which was in accordance with all requirements of the Standard | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a vulnerability scan that includes discovery of all access points; (2) review default controls for accounts, passwords and community strings; (3) review ports and services; (4) update the vulnerability assessment procedure; and (5) document the results and create an action plan for remediating any identified vulnerabilities. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007969 | Settlement Agreement | FRCC_URE1 self-reported that it failed to fully establish and implement a security patch management program for tracking, evaluating, testing, and installing applicable cybersecurity software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). FRCC_URE1 did not complete the assessment and installation of all patches that were of lower risk. Further, some third-party applications were not included in the patch management program. | CIP-007-1 | R3 | Lower | Severe | FRCC determined that the violation posed a minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system (BPS) because a patch management program did exist to apply high and critical security patches to Critical Cyber Assets and Cyber Assets, and the Cyber Assets reside within the Electronic and Physical Security Perimeter (PSP) and are thus provided several layers of ESP and PSP protections. Further, no unauthorized use or breach occurred during the period of the violation. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) conduct a complete review of Cyber Assets including software inventory; (2) research and define requirement for patching solutions for all applications; (3) install and implement patching solution(s) infrastructure and rollout to all Cyber Assets; and (4) train and communicate changes to personnel and issue any required Technical Feasibility Exception requests. | 2/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007972 | Settlement Agreement | FRCC_URE1 self-reported that it did not identify three virtual servers and three workstations as Critical Cyber Assets (CCAs), as required by CIP-002-1 R3. | CIP-002-1 | R3 | High | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because these assets were protected within the Electronic Security Perimeter (ESP) and a Physical Security Perimeter (PSP). FRCC determined that the violation posed a moderate risk because failure to identify CCAs properly could jeopardize compliance with other CIP Standards. While these CCAs lacked some security controls, FRCC determined that none of the gaps posed a serious or substantial risk because all these systems were within the protected ESP and PSP, and security controls for access control, change management, testing, account management, and strong configuration were effectively applied to the subject Cyber Assets. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) completed a review of its CCA identification process(es) to include an expanded interpretation of virtual system hosts and classification based upon functional capability; (2) designed and implemented necessary environment changes; (3) updated the required documentation for newly-identified Cyber Assets; and (4) filed any required Technical Feasibility Exceptions (TFEs). | 2012-03-08 | 2012-08-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007970 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-004-3 R4. FRCC_URE1 failed to revoke access to Critical Cyber Assets (CCAs) for four employees within seven calendar days from the date when access was no longer required, as required by the Standard. Access was revoked as provided below: Employee 1 - Access was revoked more than 5 months after the required by date. This 11-year employee only had password change and report creation access. Employee 2 - Access was revoked less than 3 weeks after the required by date. This 14-year employee had physical access to all areas of the subject generation plant. Employee 3 - Access was revoked less than 3 weeks after the required by date. This 40-year employee had cyber access. Employee 4 - Access was revoked less than 1 week after the required by date. This 3-month intern-contractor had physical access to the subject generation plant. All four employees had completed a successful personnel risk assessment (PRA) and cybersecurity training prior to being granted access. | CIP-004-3 | R4.2 | Lower | Moderate | FRCC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the subject individuals were trusted employees who were thoroughly vetted by FRCC_URE1's PRA process and were appropriately trained as per CIP-004. These individuals were transferred or retired from service and none of the instances were for cause. None of the individuals accessed the systems after the status change. | when access should have been revoked for the first employee | when access was revoked for the fourth employee | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) completed a review of all NERC CCA access removal requests to identify all instances where access was not timely revoked and revoke any unnecessary access. No additional instances of failure to timely revoke access were discovered; (2) updated its termination documentation to clarify accounts being removed, deleted, or disabled; and (3) trained IT security team members on the access removal process. | 2011-12-08 | 2012-05-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008231 | Settlement Agreement | During an Audit, FRCC discovered that FRCC_URE1 was in violation of CIP-005-1 R2.2. FRCC_URE1 did not ensure that, for one of its access points to the Electronic Security Perimeter (ESP), only ports required for operations and monitoring were enabled. It did allow certain networks to communicate to the assets within the ESP, but did not specify the ports. Additionally, FRCC_URE1 did not implement strong procedural or technical controls for remote interactive access, in violation of CIP-005-1 R2.4. FRCC_URE1 was using a login process which was repeated on two different systems but was not sufficient to demonstrate that the control addressed authenticity of the accessing party. | CIP-005-1 | R2; R2.2; R2.4 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the ports that were open but not required for operations and monitoring were limited to trusted networks also controlled and maintained by FRCC_URE1. FRCC determined that the violation posed a moderate risk because ports and services that are not required for normal operations can be exploited in cyber attacks and lack of strong authentication at the access points may allow an unauthorized remote interactive access to the ESP. The risk was limited because for all interactive remote access, FRCC_URE1 implemented a secured jump host that limited direct access to the ESP and only provided access to limited applications and control functions. Lastly, FRCC_URE1 has limited risk from remote access by use of encryption and digital certificates when such remote access is initiated over the internet. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Compliance Audit | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) review the complete firewall configuration and review use of ports for all Cyber Asset configuration; (2) create ports and services baseline identification; (3) update action plan; (4) reconcile ports and services with approved baselines; and (5) submit Technical Feasibility Exception requests as necessary. | 6/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1), a subsidiary of Unidentified Registered Entity (RFC_URE) | NCRXXXXX | RFC2011001265 | Settlement Agreement | RFC_URE1 notified ReliabilityFirst by telephone of a violation of CIP-004-3 R3.1. RFC_URE1 submitted a written Self-Report to ReliabilityFirst. RFC_URE's subsidiary, on behalf of RFC_URE1, contracted with another entity to provide security services, including security officers and, for part of the relevant period, seven-year criminal checks for certain of those security officers. A RFC_URE corporate security employee was asked by a RFC_URE employee to look into what investigation is conducted for persons who have only recently arrived in the United States. Based upon that inquiry, the RFC_URE corporate security employee brought the concern to the attention of a supervisor. As a result of that inquiry, RFC_URE discovered that for two other entity contract security officers to whom RFC_URE1 granted authorized unescorted physical access to Critical Cyber Assets (CCAs), the other entity had not performed full seven-year criminal checks despite certifying that seven-year criminal checks were conducted. Instead, the other entity only conducted a criminal check for the time period the contract security officers resided in the United States. One contract security officer resided in the United States for two months before beginning work at RFC_URE, and the other contract security officer resided in the United States for three months before beginning work at RFC_URE. When RFC_URE discovered this issue, RFC_URE sought to determine whether other entity employees working at RFC_URE1 had similarly deficient personnel risk assessments (PRAs). RFC_URE discovered that four additional other entity employees currently working at RFC_URE1 with authorized unescorted physical access to CCAs had criminal checks for less than seven years. One of these employees had not been over eighteen years old for seven years, two of these employees had not resided in the United States for seven years, and one of these employees had resided in the United States for seven years. In addition, RFC_URE discovered that two other entity employees no longer working at RFC_URE facilities had criminal checks for less than seven years while working at RFC_URE1. All security officers at issue were assigned to the general RFC_URE office, where they could provide services for either RFC_URE1 or its affiliate RFC_URE2. The PRAs for these six individuals occurred in preparation for mandatory enforcement of the CIP Standards. A RFC_URE service provider conducted these PRAs of the other entity employees. While RFC_URE1 personnel performed a manual review of these PRAs provided by the vendor, RFC_URE1 was unaware of the lack of full seven-year criminal checks for these six individuals for a twenty-two month period. | CIP-004-3 | R3.1 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The facts and circumstances of this violation are confined to the PRAs conducted for the security officers for another entity, and do not evidence a systematic issue with RFC_URE1's PRA program. RFC_URE1's PRA program included the background check requirement. Also, the seven-year background check requirement was included in RFC_URE1's contract for security services with the other entity. Importantly, RFC_URE and RFC_URE1 discovered this issue when a RFC_URE corporate security employee recognized that it would be difficult to obtain a seven-year criminal check for an individual who had only been in the United States for a few months and brought the issue to the attention of a supervisor. RFC_URE corporate security employee’s conduct evidences an institutional awareness of the CIP Standards. In addition, RFC_URE1 terminated the contract security officers’ authorized unescorted physical access to CCAs promptly upon learning that a seven-year criminal check was not conducted. RFC_URE1 then conducted a PRA with a complete seven-year criminal check and subsequently re-issued authorized unescorted physical access to Critical Cyber Assets to the six contract security officers still working at RFC_URE1. When RFC_URE1 conducted the seven-year criminal checks for the six individuals who had physical access, they discovered no disqualifying adverse information regarding these six individuals. In addition to reviewing the PRAs for all other entity contract employees, RFC_URE corporate security conducted an audit of a sample of PRAs for the RFC_URE population of individuals working at RFC_URE for seven years or less with authorized unescorted physical access to CCAs, including both employees and contractors. RFC_URE chose a random sample of 74 background checks, reviewed those background checks, and found no errors. | the date RFC_URE1 was required to comply with CIP-004 | the date RFC_URE1 revoked authorized unescorted physical access from the affected individuals still working at RFC_URE1 | 0 | Self-Report | RFC_URE1 took the following actions to mitigate the violation: (a) removed authorized unescorted physical access from the six affected individuals; (b) rescreened the individuals; (c) updated and distributed the list of contractors from which RFC_URE will accept PRAs to remove the other entity; (d) updated the internal job aid documents to reinforce the review of the Social Security Number trace report and another document to ensure the identification of seven years of residences and the implementation of seven-year criminal checks; (e) revised the hard copy of its documentation to include a request for the applicant to provide his or her past seven years of residences (the on-line version already included such a request); (f) conducted a random sample of 74 background checks using RFC_URE corporate audit services’ data sampling tool; and (g) provided a notification reminding all contractors that provide PRA background checks to RFC_URE of their obligation to complete full seven-year criminal checks. | 2012-02-29 | 2012-06-14 | Admits | ReliabilityFirst considered certain aspects of RFC_URE’s compliance program as mitigating factors. ReliabilityFirst considered that it discovered the violation through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered as mitigating factors the degree and quality of RFC_URE1’s cooperation and remedial action during the enforcement processes. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constituted repetitive infractions. RFC_URE’s internal controls and institutional awareness of the CIP Standards is evident based upon RFC_URE’s conduct in this matter. RFC_URE discovered the issue due to the diligence of an employee. RFC_URE acted quickly and thoroughly to remediate the issue, and RFC_URE provided detailed guidance to its peers to promote awareness of the issue.
2012-08-31 | FERC | NP12-44-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2), a subsidiary of Unidentified Registered Entity (RFC_URE) | NCRXXXXX | RFC2011001266 | Settlement Agreement | RFC_URE2 notified ReliabilityFirst by telephone of a violation of CIP-004-3 R3. RFC_URE2 submitted a written Self-Report to ReliabilityFirst. RFC_URE's subsidiary, on behalf of RFC_URE2, contracted with another entity to provide security services, including security officers and, for part of the relevant period, seven-year criminal checks for certain of those security officers. A RFC_URE corporate security employee was asked by a RFC_URE employee to look into what investigation is conducted for persons who have only recently arrived in the United States. Based upon that inquiry, the RFC_URE corporate security employee brought the concern to the attention of a supervisor. As a result of that inquiry, RFC_URE discovered that for two other entity contract security officers to whom RFC_URE2 granted authorized unescorted physical access to Critical Cyber Assets (CCAs), the other entity had not performed full seven-year criminal checks despite certifying that seven-year criminal checks were conducted. Instead, the other entity only conducted a criminal check for the time period the contract security officers resided in the United States. One contract security officer resided in the United States for two months before beginning work at RFC_URE, and the other contract security officer resided in the United States for three months before beginning work at RFC_URE. When RFC_URE discovered this issue, RFC_URE sought to determine whether other entity employees working at RFC_URE2 had similarly deficient personnel risk assessments (PRAs). RFC_URE discovered that four additional other entity employees currently working at RFC_URE2 with authorized unescorted physical access to CCAs had criminal checks for less than seven years. One of these employees had not been over eighteen years old for seven years, two of these employees had not resided in the United States for seven years, and one of these employees had resided in the United States for seven years. In addition, RFC_URE discovered that two other entity employees no longer working at RFC_URE facilities had criminal checks for less than seven years while working at RFC_URE2. All security officers at issue were assigned to the general RFC_URE office, where they could provide services for either RFC_URE2 or its affiliate RFC_URE1. The PRAs for these six individuals occurred in preparation for mandatory enforcement of the CIP Standards. A RFC_URE service provider conducted these PRAs of the other entity employees. While RFC_URE2 personnel performed a manual review of these PRAs provided by the vendor, RFC_URE2 was unaware of the lack of full seven-year criminal checks for these six individuals for a twenty-two month period. | CIP-004-3 | R3.1 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The facts and circumstances of this violation are confined to the PRAs conducted for the security officers for another entity, and do not evidence a systematic issue with RFC_URE2's PRA program. RFC_URE2's PRA program included the background check requirement. Also, the seven-year background check requirement was included in RFC_URE2's contract for security services with the other entity. Importantly, RFC_URE and RFC_URE2 discovered this issue when a RFC_URE corporate security employee recognized that it would be difficult to obtain a seven-year criminal check for an individual who had only been in the United States for a few months and brought the issue to the attention of a supervisor. The RFC_URE corporate security employee’s conduct evidences an institutional awareness of the CIP Standards. In addition, RFC_URE2 terminated the contract security officers’ authorized unescorted physical access to CCAs promptly upon learning that a seven-year criminal check was not conducted. RFC_URE2 then conducted a PRA with a complete seven-year criminal check and subsequently re-issued authorized unescorted physical access to CCAs to the six contract security officers still working at RFC_URE2. When RFC_URE2 conducted the seven-year criminal checks for the six individuals who had physical access, they discovered no disqualifying adverse information regarding these six individuals. In addition to reviewing the PRAs for all other entity contract employees, RFC_URE corporate security conducted an audit of a sample of PRAs for the RFC_URE population of individuals working at RFC_URE for seven years or less with authorized unescorted physical access to CCAs, including both employees and contractors. RFC_URE chose a random sample of 74 background checks, reviewed those background checks, and found no errors. | the date RFC_URE2 was required to comply with CIP-004 | the date RFC_URE2 revoked authorized unescorted physical access from the affected individuals still working at RFC_URE2 | 0 | Self-Report | RFC_URE2 took the following actions to mitigate the violation: (a) removed authorized unescorted physical access from the six affected individuals; (b) rescreened the individuals; (c) updated and distributed the list of contractors from which RFC_URE will accept PRAs to remove the other entity; (d) updated the internal job aid documents to reinforce the review of the Social Security Number trace report and another document to ensure the identification of seven years of residences and the implementation of seven-year criminal checks; (e) revised the hard copy of its documentation to include a request for the applicant to provide his or her past seven years of residences (the on-line version already included such a request); (f) conducted a random sample of 74 background checks using RFC_URE corporate audit services’ data sampling tool; and (g) provided a notification reminding all contractors that provide PRA background checks to RFC_URE of their obligation to complete full seven-year criminal checks. | 2012-02-29 | 2012-06-14 | Admits | ReliabilityFirst considered certain aspects of RFC_URE’s compliance program as mitigating factors. ReliabilityFirst considered that it discovered the violation through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered as mitigating factors the degree and quality of RFC_URE2’s cooperation and remedial action during the enforcement processes. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constituted repetitive infractions. RFC_URE’s internal controls and institutional awareness of the CIP Standards is evident based upon RFC_URE’s conduct in this matter. RFC_URE discovered the issue due to the diligence of an employee. RFC_URE acted quickly and thoroughly to remediate the issue, and RFC_URE provided detailed guidance to its peers to promote awareness of the issue.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102753 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report to WECC concerning a violation of CIP-004-3 R4 due to WECC_URE1's to revoke access within seven calendar days for personnel who no longer required access to Critical Cyber Assets (CCAs), and failure to identify employees specific access rights to CCAs. Specifically, WECC identified four instances in which WECC_URE1 failed to revoke access to CCAs within seven days for personnel who no longer required such access. In addition, WECC identified two instances in which WECC_URE1 access lists failed to identify specific access rights because two employees with both physical and cyber access to CCAs were listed as only having physical access rights to CCAs. | CIP-004-3 | 4 | Medium | Moderate | WECC determined that the violation posed a minimal risk to the reliability of the bulk power system (BPS) because WECC_URE1 did identify and list all individuals with access to CCAs. In addition, all individuals within the scope of the violation had completed requisite Cyber Security training, and had completed Personnel Risk Assessments (PRAs). Finally, while access was not revoked within seven days after such access was no longer required, WECC_URE1 did revoke the employees’ access to CCAs within eight to sixteen days. Further, all individuals within scope of the violation alleged herein completed requisite Cyber Security training and completed Personnel Risk Assessments. | when WECC_URE1 was required to comply with the Standard | when the Mitigation Plan was completed | $27,800 (Settlement of WECC201102753 and WECC201102407) | Self-Report | WECC_URE1 revoked access to those employees who no longer required access. WECC_URE1 completed a comprehensive quarterly review of the CIP access log. | 2011-02-17 | 2012-08-24 | Does Not Contest | WECC considered as a mitigating factor that WECC_URE1 self-reported the violation of CIP-004-1 R4.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102407 | Notice of Confirmed Violation | WECC notified WECC_URE1 that WECC was initiating the Self-Certification process. WECC_URE1 submitted a Self-Report and a Self-Certification concerning a violation of PRC-005-1 R2.1 due to WECC_URE1's failure to perform pre-operational testing of current transformer (CT)/ potential transformer (PT) devices for two units of the Facility before returning the units to service. WECC determined that pursuant to WECC_URE1's maintenance and testing program (Program), CT/PT testing at the Facility was scheduled. However, the facility and associated protection systems were removed from service six months prior to the scheduled testing. The facility was returned to service after WECC_URE1 completed trip and functional tests. WECC_URE1 reviewed functional and trip test reports for the facility, and determined that pre-operational CT/PT load testing was not performed at the facility. Although WECC_URE1 completed CT/PT load testing, WECC determined that WECC_URE1's failure to complete pre-operational testing before putting the facility into service constitutes a violation of PRC-005-1 R2. | PRC-005-1 | 2 | High | Lower | WECC determined that the violation posed a minimal risk to the reliability of the bulk power system (BPS) because the scope of the violation is limited, in that, WECC_URE1 completed required testing for all other protection systems at the facility. In addition, WECC_URE1's failure to complete CT/PT testing at the facility represents only 8.33% CT/PT protection systems. Finally, when WECC_URE1 completed the required testing, approximately a month after returning the units to service, the protection systems devices were in good working condition. | when WECC_URE1 failed to perform testing of CT/PT devices before returning the units to service | when WECC_URE1 completed testing of the CT/PT devices | $27,800 (Settlement of WECC201102753 and WECC201102407) | Self-Certification | WECC_URE1 instructed one of its divisions not to operate facility until the CT/PT load tests were performed. WECC_URE1 completed the CT/PT load tests for the two units. WECC_URE1 issued a memo which designated a manger in each field division to be responsible for overseeing the protection system testing program for that field division. In addition, WECC_URE1 managers are required to prevent a unit from being operated if the protection system tests have not been completed, documented, and reviewed according to the identified test intervals or after a long outage. WECC_URE1 e-mailed the memo to each of the field division chiefs shared the memo with the appropriate staff. One of WECC_URE1's divisions implemented an order to help prevent this type of occurrence in the future at the field division. The order outlines one of WECC_URE1's divisions acceptance procedures that must be followed before returning a unit to service after the completion of major maintenance activities. On its effective date, this order was added to the division file server and made available to the plant operations personnel. The division chief operator, who was involved in preparing the order, was informed that the order had become effective. Hard copies were distributed a couple of weeks later to other lead and supervisory personnel. | 2010-09-30 | 2011-11-08 | Does Not Contest | WECC considered as aggravating factors that WECC_URE1 had two previous PRC-005-1 R2 violations.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009556 | Settlement Agreement | WECC conducted an on-site compliance audit of WECC_URE2 (Audit) and determined that WECC_URE2 violated CIP-005-1 R2.2 for failing to ensure that only required ports and services for operations and monitoring of Cyber Assets within Electronic Security Perimeters (ESP) were enabled and documented as required by R2.2. At the Audit, WECC reviewed WECC_URE2's document annotating the authorized ports and services baseline for WECC_URE2's security operations control center and backup control center access points. Based on the record, WECC determined that WECC_URE2 failed to document an internet protocol and port as access points to its backup control center ESP. Also, a default password was enabled, thereby potentially allowing an attacker to enumerate critical information about the access point, including the ability to infer information concerning the ESP network topology. WECC_URE2 maintains that its internet protocol service, port, and the password were not enabled, as determined by WECC, because WECC_URE2's internet protocol service was in its default setting, which was precluding access to the ESP. Also, WECC_URE2's firewall was effectively denying access to the internet protocol server and port. However, WECC determined that despite the fact that it was in its default setting, it was still enabled, in violation of R2.2. WECC determined that WECC_URE2 failed to enable only those ports and services required for operations and monitoring of Cyber Assets within the ESP and failed to document an unauthorized service to its access point to its backup control center ESP, in violation of CIP-005-1 R2.2. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE2 did not identify an unauthorized service to its backup control center ESP, WECC_URE2 provided a defense-in-depth architecture, including electronic access controls for authentication and encryption at the ESP. In addition, WECC_URE2 had physical security controls in place at the Physical Security Perimeter (key card readers, locked doors and cameras), thus reducing the likelihood of a successful cyber attack. Further, WECC_URE2's internet protocol software vendor verified that the service was in its default setting, which was set to preclude access and prevent an attacker from enumerating critical information about the access point, including the ability to infer information concerning the ESP network topology, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $30,000 (for WECC2012009556 and WECC2012009557) | Compliance Audit | In accordance with its Mitigation Plan, WECC_URE2 completed the following actions: 1) Contacted its internet protocol software vendor to confirm that the service was not configured, and that in its state, the internet protocol services were not available and a potential cyber attacker could not gain information about WECC_URE2's ESP network topography, or gain access to the ESP; 2) Retained a consultant to verify its vendor's representation of facts by testing the service independently; 3) Disabled the server and in so doing also stopped the server from running on the access point to the ESP; 4) Upgraded its cyber vulnerability assessment procedure to ensure the use of "show run all" to verify the server is not enabled; and 5) Conducted informal meetings to communicate the updated procedures to the appropriate WECC_URE2 subject matter experts. | 2012-01-24 | 2012-06-15 | Agrees/ Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009557 | Settlement Agreement | WECC conducted an on-site compliance audit of WECC_URE2 (Audit) and determined that WECC_URE2 violated CIP-005-1 R4 for failing to perform an accurate cyber vulnerability assessment (CVA) due to inconsistencies found in the CVA results, which did not correlate with the actual access point configurations. During the Audit, WECC determined that the CVA did not detect an internet protocol service running on a port open for an access point to the Electronic Security Perimeters (ESPs) of WECC_URE2's backup control center. WECC_URE2 failed to conduct a review to verify that only ports and services required for the operations of these access points were enabled and did not discover all access points to the backup control center ESP. WECC_URE2 maintains that its internet protocol service and port were not enabled, as determined by WECC, because WECC_URE2's internet protocol service was in its default setting, which was precluding access to the ESP. However, WECC determined that despite the fact that it was in its default setting, it was still enabled. WECC_URE2's firewall was effectively denying access to the internet protocol server and port. WECC determined that WECC_URE2 failed to verify in its CVA that only those ports and services required for operations at its access points were enabled and that it failed to appropriately discover all access points to the ESP, in violation of CIP-005-1 R4. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE2 did not identify an unauthorized service to its backup control center ESP, WECC_URE2 provided a defense-in-depth architecture, including electronic access controls for authentication and encryption at the ESP. In addition, WECC_URE2 had physical security controls in place at the Physical Security Perimeter (key card readers, locked doors and cameras), thus reducing the likelihood of a successful cyber attack. Further, WECC_URE2's internet protocol software vendor verified that the service was in its default setting, which was set to preclude access and prevent an attacker from enumerating critical information about the access point, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $30,000 (for WECC2012009556 and WECC2012009557) | Compliance Audit | In accordance with its Mitigation Plan, WECC_URE2 completed the following actions: 1) Contacted its internet protocol software vendor to confirm that the service was not configured, and that in its state, the internet protocol services were not available and a potential cyber attacker could not gain information about WECC_URE2's ESP network topography, or gain access to the ESP; 2) Retained a consultant to verify its vendor's representation of facts by testing the service independently; 3) Disabled the server and in so doing also stopped the server from running on the access point to the ESP; 4) Upgraded its CVA procedure to ensure the use of "show run all" to verify the server is not enabled; and 5) Conducted informal meetings to communicate the updated procedures to the appropriate WECC_URE2 subject matter experts. | 2012-01-24 | 2012-06-15 | Agrees/ Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103008 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R2 for a failure to file timely Technical Feasibility Exception (TFE) requests for six devices on which it could not disable ports and services that were not used for normal or emergency operations. Approximately two months after the submittal of its Self-Certification, WECC_URE3 submitted a TFE for the six devices in question. WECC_URE3 stated that although the vendor published a configuration command to close ports on these devices, WECC_URE3 has not been able to successfully implement the configuration command and close ports not used for normal or emergency operations. WECC determined that for each of the six devices at issue, WECC_URE3 failed to ensure that all ports and services not required for normal and emergency operations were disabled pursuant to CIP-007-1 R2 by when WECC_URE3 was required to comply with the Standard. Further, WECC determined that the devices fall within the scope of WECC_URE3's TFE request and issued a notice of TFE approval. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, all six devices were physically secured within a Physical Security Perimeter (PSP), thereby limiting physical access to ports and reducing the risk to the BPS. Second, all ports were also secured within an Electronic Security Perimeter (ESP) equipped with an intrusion detection system that monitored traffic on all ports within the ESP. Should access be attempted through any one of the ten ports within scope of the violation, the intrusion detection system is programmed to detect intrusion and to immediately alert the cyber security staff, thereby reducing the risk to the BPS. WECC asserted that it is not aware of any instances of unauthorized access to the PSPs or ESPs during the pendency of this violation. Although WECC_URE3 originally failed to file a timely TFE request, WECC determined that the six devices at issue fell within the scope of WECC_URE3's TFE request, which was approved by WECC. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFE for the six devices | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan, but WECC determined that the Mitigation Plan did not include all mitigating activities undertaken by WECC_URE3 and did not reflect the full scope of these activities. WECC_URE3 submitted a revised Mitigation Plan that included the full scope of the mitigating activities. In accordance with its Mitigation Plan, WECC_URE3 completed the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine where TFEs are required and filed Self-Reports and Mitigation Plans in the instances where TFEs were required; 2) Gathered all vendor and manufacturer documentation supporting its request for a TFE and all documentation describing the compensating measures that were in place on from the day WECC_URE3 was required to comply with this Standard; 3) Submitted all required TFEs to WECC and began a TFE monitoring process; 4) Initiated a change request to replace the switches; 5) Modified its Hardening Checklist to ensure vendor port and services recommendations are reviewed for applicability, and also modified its change management process to incorporate the completion of the Hardening Checklist. WECC_URE3 modified its security training to reinforce the use of the Hardening Checklist in the change management process; and 6) Configured a new switch and replaced four older ones; performed device hardening and security control testing, among other activities designed to ensure compliance with this Standard. | 2012-02-28 | 2012-05-25 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC reviewed WECC_URE3's compliance history and determined it was as an aggravating factor in determining the penalty.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103009 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R4 for a failure to file Technical Feasibility Exceptions (TFEs) for 27 devices on which the use of anti-virus software was not technically feasible. Approximately two weeks after the submittal of WECC_URE3's Self-Certification, WECC_URE3 submitted three TFE requests for 15 devices and amended the requests four days later. WECC confirmed that WECC_URE3 filed TFEs for the remaining 12 devices, thus requesting a TFE for all 27 devices. WECC determined the scope of the violation to include 27 devices associated with two Critical Assets at two of its facilities. WECC determined that WECC_URE3 failed to use anti-virus software and implement malware prevention measures for the twenty-seven (27) devices at issue as of the date it was required to comply with the Standard, in violation of this Standard. Further, WECC determined that the devices at issue fall within the scope of WECC_URE3's TFE requests and issued a notice of approval. | CIP-007-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, all devices were physically secured within a Physical Security Perimeter (PSP), thereby limiting physical access to ports. Further, all devices were logically secured within an Electronic Security Perimeter (ESP) equipped with an Intrusion Detection System that monitored traffic on all ports within the ESP. Finally, although WECC_URE3 failed to file a timely TFE request, WECC determined the 27 devices at issue fell within the scope of WECC_URE3's TFE requests, which were approved by WECC. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE3 took the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine if additional TFEs were required and filed Self-Reports and Mitigation Plans where necessary; 2) Gathered all vendor and manufacturer documentation supporting its request for TFEs; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; and 4) Submitted all required TFEs to WECC and began a TFE monitoring process. | 2011-10-14 | 2012-03-16 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103010 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R5.3 for a failure to ensure that all passwords satisfied the criteria outlined under R5.3. Approximately two weeks after the submittal of WECC_URE3's Self-Certification, WECC_URE3 submitted three Technical Feasibility Exceptions (TFEs) requests for the 13 devices at issue. WECC_URE3 failed to comply with CIP-007-1 R5.3 and its subrequirements for one Cyber Asset, and failed to ensure that passwords were changed annually for 12 Cyber Assets, as required by R5.3.3. WECC determined that WECC_URE3 failed to ensure that the passwords implemented for the 13 Critical Cyber Asset (CCA) devices conformed to the criteria outlined in CIP-007-1 R5.3, in violation of this Standard. Further, WECC determined that the 13 CCAs at issue are within the scope of WECC_URE3's three TFE requests. | CIP-007-1 | R5.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE3 failed to ensure that the 13 CCAs satisfied the password criteria of R5.3.3, the risk was mitigated by the limited scope of the violation and the compensating measures in place during the violation period. The scope was limited because only 13 CCAs were involved in this violation. Also, access to the 13 CCAs was limited to personnel who have received training and had successfully completed Personnel Risk Assessments (PRA). Further, electronic access to these devices was logged and monitored by WECC_URE3. Finally, although the passwords were not fully compliant with the requirements of R5.3.3, WECC determined that some protection was afforded to a number of the devices equipped with passwords. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan, but WECC rejected it. WECC_URE3 submitted a revised Mitigation Plan outlining additional activities to mitigate this violation. WECC Reviewed WECC_URE3's Revised Mitigation Plan and rejected it due to an inconsistent completion date. WECC_URE3 submitted a second Revised Mitigation Plan. WECC reviewed the Revised Mitigation Plan issued Notice of Mitigation Plan Acceptance. In accordance with its Mitigation Plan, WECC_URE3 took the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine if additional TFEs were required and filed Self-Reports and Mitigation Plans where necessary; 2) Gathered all vendor and manufacturer documentation supporting its request for TFEs; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; 4) Submitted all required TFEs to WECC and began a TFE monitoring process; and 5) Opened a change request, assigned resources and developed test cases, performed integrated platform testing, staged changes for implementation; implemented the changes into the production environment and closed the change request. | 2012-03-30 | 2012-05-10 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103011 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R6 for a failure to implement automated tools and organizational process controls to monitor system events that are related to cyber security. WECC determined that WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events for a total of 15 Cyber Assets within two Electronic Security Perimeters (ESPs). The 15 devices at issue include transmitters, Energy Management System (EMS) servers, historian servers, ICCP servers, data storage devices, and Human Machine Interface (HMI) devices. For one device, described as a "time server," implementation of controls was represented to be "technically infeasible" by WECC_URE3. Irrespective of WECC's Technical Feasibility Exceptions (TFEs) review, WECC determined that for the remaining 14 devices, implementation of automated or process controls under CIP-007-1 R6 was technically feasible. WECC, therefore, determined that WECC_URE3 was in violation of CIP-007-1 R6 for its failure to implement CIP-007-1 R6 controls for the 15 devices at issue. WECC_URE3 submitted three TFE filings, for the 15 devices included in the CIP-007-1 R6 noncompliance Self-Certification. WECC approved the TFEs for the 15 devices at issue. WECC determined that WECC_URE3's filing of a TFE for the "time server" may affect the violation period for this device, but did not obviate compliance with CIP-007-1 R6 prior to the TFE filing. WECC also determined that WECC_URE3 failed to implement controls to monitor and log system events for the 14 devices located within two ESPs, in violation of CIP-007-1 R6. | CIP-007-1 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE3 failed to implement automated tools and organizational process controls for 15 devices, the risk to the BPS was mitigated by the measures in place during the violation period. WECC determined that the scope of the violation was limited to 15 devices. Further, all individuals with logical and/or unescorted physical access rights have completed Personnel Risk Assessments (PRA) and Cyber Security training, thereby reducing the risk to the BPS. In addition, all devices within the scope of the violation were contained within a Physical Security Perimeter (PSP) and ESP, whereby access was controlled, logged and monitored. Additionally, any unauthorized access attempts would have triggered alarming. WECC, therefore, determined that WECC_URE3 noncompliance with CIP-007-1 R6 posed a moderate risk to the BPS. | when the Standard became mandatory and enforceable | when WECC_URE3 filed TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan but WECC determined that the Mitigation Plan did not include all mitigating activities undertaken by WECC_URE3 and did not reflect the full scope of these activities. WECC_URE3 submitted a revised Mitigation Plan. In accordance with its Mitigation Plan, WECC_URE3 took the following actions to mitigate the instant violation: 1) Performed a complete analysis of all in-scope Cyber Assets to determine where TFEs are required and filed Self-Reports and Mitigation Plans in the instances where TFEs were required; 2) Gathered all vendor and manufacturer documentation supporting the request for a TFE and all documentation describing the compensating measures that were in place from the day WECC_URE3 was required to comply with this Standard; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; 4) Submitted all required TFEs to WECC and began a TFE monitoring process; and 5) Opened a change request, assigned resources and developed test cases, performed integrated platform testing, staged changes for implementation; implemented the changes into the production environment and closed the change request. | 2012-03-30 | 2012-05-25 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009702 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1.8 for failing to afford Cyber Assets used in the access control and monitoring of three Physical Security Perimeters (PSPs) protective measures, as specified in CIP-007-1 R5. Consequently, default accounts on nine physical access control panels were not disabled when installed. This failure to remove, disable or rename default accounts as required under CIP-007-1 R5 for nine physical access control panels used in the access control and monitoring of three PSPs resulted in a violation of CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1's physical access control panels were all located within PSPs with no direct external physical or cyber access. Also, only one default account was active per panel. In addition, WECC_URE1 failed to afford Cyber Assets protective measures specified in only CIP-007-1 R5.2.1 (the specific protective measure that was not afforded) and all the other protective measures were afforded. | when the Standard became mandatory and enforceable to WECC_URE1 | Mitigation Plan completion | 7500 | Self-Report | WECC_URE1 completed the following mitigation activities: 1) Followed its disciplinary procedure towards the employee who did not follow the associated change control program procedures for the installation of new assets; 2) Removed all default accounts from the physical access control panels; 3) Performed refresher training by reiterating to the physical security staff the importance of following WECC_URE1's change control program for new assets; 4) Created an electronic calendar reminder task for a manager to periodically spot check panel configurations; and 5) Submitted a Technical Feasibility Exception (TFE) for the physical access control panels. | 2012-02-27 | 2012-05-10 | Agrees/ Stipulates | WECC_URE1's internal compliance program (ICP) was a mitigating factor in the penalty determination. WECC applied cooperation credit for reporting this violation because WECC_URE1 submitted the Self-Report after WECC notified WECC_URE1 of its upcoming audit. WECC determined that no adjustments to the penalty were warranted because all milestones were completed by the approved completion date, except for submitting a TFE for the physical access control panels. The TFE submittal did not increase the risk to the BPS, albeit it did extend the completion date.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008699 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-005-1 R2. WECC_URE2 failed to fully document, individually or by specific groups, the configuration of the ports and services at all Electronic Security Perimeter (ESP) access points. WECC determined that WECC_URE2 did enable only those ports and services required for operations and for monitoring Cyber Assets within the ESP, but failed to document, individually or by specified grouping, the configuration of those ports and services, in violation of CIP-005-1 R2.2 | CIP-005-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to fully document the configuration of the ports and services in question, WECC_URE2 fully documented a process addressing services and addressing one category of ports. In addition, WECC determined that WECC_URE2 implemented processes and mechanisms used in ESP access controls. Finally, WECC determined that this violation presented a documentation issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Modified its CIP-005-3a R2 Electronic access controls procedure; 3) Developed of a new report to provide evidence for all access points; 4) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP- 005 R2.2, in accordance with the WECC_URE2's internal compliance program (ICP); and 5) Conducted staff meetings and training to ensure that WECC_URE2's personnel understood the new procedure and followed all processes necessary to ensure complete and consistent evidence for all ports and services. | 2011-11-30 | 2012-05-31 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009701 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-005-1 R1.5. Based on the Self-Report, WECC determined that WECC_URE2 failed to fully document the configuration of ports and services for Cyber Assets used in the Electronic Security Perimeter (ESP) access control and monitoring, as described in CIP-005-1 R2.2 and required by CIP-005-1 R1.5. | CIP-005-1 | R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to fully document the configuration of the ports and services as described in R2.2, WECC_URE2 fully documented a process addressing services and addressing one category of ports. Also, WECC_URE2 ensured that only the ports and services required for normal operations and monitoring were enabled during the violation period. WECC_URE2 ensured that the Cyber Assets requiring electronic access control and monitoring were afforded 96.6% of the protective measures referenced in R1.5. Finally, WECC determined that this violation presented a documentation issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Modification to CIP-005-3a R2 Electronic access controls procedure; 3) Developed of a new report to provide evidence for all access control and monitoring (ACM); 4) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP-005 R1.5, in accordance with WECC_URE2's internal compliance program (ICP); and 5) Conducted staff meetings and training to ensure that WECC_URE2 personnel understood the new procedure and followed all processes necessary to ensure complete and consistent evidence for all ports and services. | 2011-11-30 | 2012-05-31 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009043 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-006-1 R1 because it failed to secure five Critical Cyber Assets (CCAs) within a Physical Security Perimeter (PSP). Based on the Self-Report, WECC determined that WECC_URE2 failed to secure five CCAs within a PSP, in violation of CIP-006-1 R1.1. | CIP-006-1 | R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to ensure that five CCAs were located within a PSP, the risk was mitigated by several factors. The CCAs were located within a secured generation project with limited access to the site, which was monitored and controlled by WECC_URE2. Also, WECC determined that the scope of the violation was limited because it only involved five CCAs, thus reducing the risk to the BPS. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) WECC_URE2 took immediate steps to increase the physical security measures surrounding these devices; 2) WECC_URE2 completed an inventory of the assets applicable to the CIP standards that are required to be within a PSP and found no additional assets located outside of their defined PSPs; 3) Completed site walkthrough/visits of all PSPs; 4) Completed relocation of the devices to their appropriate identified PSP; and 5) Modified the annual review and approval of the CCA list as required in CIP-002-3 R3 to include a physical inventory of all the devices on the list to verify they are located within the appropriate PSP. | 2012-01-12 | 2012-05-18 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history in determining the penalty amount.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008647 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-007-1 R2. WECC_URE2 failed to fully document a process to ensure that only those ports and services required for the normal and emergency operations were enabled on 63 Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). Based on the Self-Report, WECC determined that although WECC_URE2 did enable only ports and services required for normal and emergency operations on Cyber Assets and CCAs within an ESP, WECC_URE2 failed to fully document the configuration of those ports and services, in violation of CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to failed to document a comprehensive process pursuant to CIP-007-1 R2, WECC_URE2 did document a process addressing services and one category of ports. Also, WECC_URE2 ensured that only ports and services required for normal and emergency operations were enabled on the 63 Cyber Assets. Further, the Cyber Assets were located within the PSP and ESPs, and were afforded the protections required by CIP-005-1 and CIP-006-1, which reduced the risk to the BPS. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Implemented documentation enhancements as follows: Modified its CIP-005-3a R2 Electronic access controls procedure; modified its CIP-007-3 R2 ports and services procedure; and developed new reports; and 3) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP- 007-1 R2, in accordance with the WECC_URE2's internal compliance program (ICP). | 2011-11-30 | 2012-04-11 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102804 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-006-1 R1. Specifically, a WECC_URE3 employee logged onto a physical access control system server located in an Electronic Security Perimeter (ESP) without using two-factor authentication. The individual accessed the server using a tunneling protocol that was used for authentication between the ESP and a directory server. WECC_URE3's process to ensure strong access controls to the server is to implement two-factor authentication. WECC found that WECC_URE3 did not afford the protective measures of CIP-005 R2.4 to the server since the two-factor authentication controls were circumvented. Therefore, WECC determined that WECC_URE3 had a violation of CIP-006-1 R1.8 because it did not apply all the protective measures outlined in R1.8 to Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP), specifically one server. WECC also determined that CIP-005 R2 does not itself apply to the server as it is a server that is a Cyber Asset used in physical access control and monitoring, but is not a Critical Cyber Asset. | CIP-006-1 | R1.8 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, the server for the access control and monitoring was in an ESP and Physical Security Perimeter (PSP). The individual involved was authorized to access it and had current CIP training and a valid personnel risk assessment. Additionally, all devices within the ESP had anti-virus protections installed, only those ports and services necessary were enabled, devices were password protected, the entity had 24 hours a day and 7 days a week electronic monitoring for the ESP in scope, and access was limited to fewer than five WECC_URE3 personnel. | when the Standard became mandatory and enforceable for WECC_URE3 | when WECC_URE3 disabled the tunneling protocol, ensuring the protective measures required by CIP-006-1 R1.8 applied to WECC_URE3's Cyber Assets used in physical access control and monitoring Prior to 4/1/2010, WECC_URE3 was in violation of CIP-006-1 R1.8. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, WECC_URE3 was in violation of CIP-006 R2.2. | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate the violation, WECC_URE3 immediately instructed its personnel to cease all remote access via the tunneling protocol and provided training associated with WECC_URE3's authentication procedures. WECC_URE3 also created an alert and associated escalation process for any protocol access to the Cyber Asset that did not originate from two-factor authentication. Finally, WECC_URE3 disabled the tunneling protocol. | 2011-05-24 | 2012-03-16 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102943 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-007-3 R5. WECC_URE3 uses a single security event monitoring solution to ensure compliance with CIP-007 R5 and R6. The solution requires that a log collector pull system event logs (used for audit trail and security status monitoring) from each Cyber Asset within the Electronic Security Perimeter (ESP). A configuration change to the service account from an administrator account to one with fewer privileges caused WECC_URE3's log collector to not pull logs from 23 Cyber Assets within two ESPs, specifically within WECC_URE3's ESPs at its control centers. WECC determined that WECC_URE3 did not generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days, resulting in a violation of CIP-007-3 R5.1.2. | CIP-007-3 | R5.1.2 | Lower | High | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, for 23 Cyber Assets, WECC_URE3 did not generate logs of sufficient detail to create historical audit trails of individual user account access activity. These assets are located in WECC_URE3's control centers. The risk was mitigated by the fact that WECC_URE3 has intrusion detection and prevention controls in place, including physical and electronic surveillance, for assets within the ESPs, and these controls could reduce or minimize the impact to the BPS. | when WECC_URE3 changed its historical audit trail configuration | when WECC_URE3 reconfigured its system and updated its test plan to ensure it generated applicable logs | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate this violation, WECC_URE3 alerted its administrators to monitor systems that are not logging to further investigate the configuration change and logging issues. WECC_URE3 also ensured that all monitored assets generate appropriate logs. Finally, WECC_URE3 updated its test plan to ensure authentication changes associated with log collection do not disrupt logging capabilities. | 2011-09-30 | 2011-10-31 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102944 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-007-3 R6. WECC_URE3 uses a single security event monitoring solution to ensure compliance with CIP-007 R5 and R6. The solution requires that a log collector pull system event logs (used for audit trail and security status monitoring) from each Cyber Asset within the Electronic Security Perimeter (ESP). A configuration change to the service account from an administrator account to one with fewer privileges caused WECC_URE3's log collector to not pull logs from 23 Cyber Assets within two ESPs, specifically within WECC_URE3's ESPs at its control centers. WECC determined that WECC_URE3 did not maintain logs of security events for a minimum of ninety days, resulting in a violation of CIP-007-3 R6.4. | CIP-007-3 | R6.4 | Lower | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, for 23 Cyber Assets, WECC_URE3 did not maintain logs of security events for a minimum of ninety days. These assets are located in WECC_URE3's control centers. The risk was mitigated by the fact that WECC_URE3 has intrusion detection and prevention controls in place, including physical and electronic surveillance, for assets within the ESPs, and these controls could reduce or minimize the impact to the BPS. | when WECC_URE3 changed its historical audit trail configuration | when WECC_URE3 reconfigured its system and updated its test plan to ensure it generated applicable logs | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate this violation, WECC_URE3 alerted its administrators to monitor systems that are not logging to further investigate the configuration change and logging issues. WECC_URE3 also ensured that all monitored assets generate appropriate logs. Finally, WECC_URE3 updated its test plan to ensure authentication changes associated with log collection do not disrupt logging capabilities. | 2011-09-30 | 2011-10-31 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001884 | Settlement Agreement | WECC reviewed documentation from WECC_URE4 detailing its cyber security policy. WECC found that WECC_URE4’s cyber security policy was divided into two periods. In reviewing these documents, WECC determined WECC_URE4’s cyber security policy in effect for the first twelve months of the enforceable date of the Standard did not establish policies covering all the requirements in Standards CIP-002 through CIP-009, nor did it reference any external documents that provided this policy coverage. Despite WECC_URE4’s claims that its cyber security policy for this period was actually represented by its submitted document, WECC determined this document did not provide coverage for all the requirements in Standards CIP-002 through CIP-009. In addition, WECC determined WECC_URE4 could not establish that all the hyperlinked documents were made readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets (CCAs), as required by R1.2. Finally, WECC determined that WECC_URE4 could not document approval by the senior manager assigned pursuant to R2, as required by R1.3. While the senior manager’s approval of this document was typed in the revision history, this could not be verified by WECC as there was no other documentation of the review. WECC also reviewed the cyber security policy documentation in effect twelve months after the enforceable date of the Standard that was approved by WECC_URE4’s compliance officer, who was not the designated senior manager assigned pursuant to R2. WECC determined that this documentation addressed all the requirements for CIP-002 through CIP-009, except CIP-004-1 R3 dealing with a personnel risk assessment program, which WECC determined was not addressed until the approval of WECC_URE4’s document dated nineteen months after the enforceable date of the Standard. WECC determined that WECC_URE4 had a violation of CIP-003-1 R1 because WECC_URE4’s documentation did not demonstrate, for the duration of the violation period, that WECC_URE4 had a cyber security policy compliant with all the subrequirements of CIP-003-1 R1. | CIP-003-1 | R1; R1.2; R1.3 | Lower | N/A | WECC determined that this violation posed a moderate risk and not serious or substantial risk to the reliability of the bulk power system (BPS). Failure to document and implement a consistent cyber security policy that addresses the requirements of CIP-003-1 R1 may result in security controls required by the CIP Standards not being uniformly or consistently applied across all applicable CCAs, leading to security vulnerabilities for CCAs. In this instance, the entity could not demonstrate the implementation of a cyber security policy that addressed all requirements of CIP-002 through CIP-009 and was approved by the designated senior manager. Although WECC_URE4's policy did not address all of the relevant requirements, for at least a portion of the duration, it addressed most of them. Also, although WECC_URE4 had not accurately designated assigned CIP senior managers in accordance with the requirements of R2.1 and R2.2, for the first twelve months of the enforceable date of the Standard, WECC_URE4 did have CIP senior managers during this period who were implementing WECC_URE4’s CIP program. | when the Standard became mandatory and enforceable for WECC_URE4 | when WECC_URE4 implemented a cyber security policy covering all the requirements in Standards CIP-002 through CIP-009 | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | WECC_URE4 updated its cyber security policy twelve months after the enforceable date of the Standard to include comprehensive mapping of CIP-002 through CIP-009, and the policy was officially reviewed and approved by the designated senior manager. | 2010-04-07 | 2011-05-17 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001885 | Settlement Agreement | WECC reviewed WECC_URE4’s cyber security-related document, which contained a historical list of assigned CIP senior managers. Based on this historical list and other documentation provided by WECC_URE4, WECC determined the documentation provided did not demonstrate the two specified CIP senior managers assigned pursuant to the Standard, for the first twelve months of the enforceable date of the Standard, were designated consistent with the requirements in R2.1 and R2.2. In addition, WECC determined this documentation provided conflicting information as to who the assigned CIP senior manager was during this period. In response to data requests issued to address these findings, WECC_URE4 indicated that the CIP senior manager assigned for the first three months of the enforceable date of the Standard was designated as such in WECC_URE4's other cyber security-related document. Nevertheless, WECC determined that this document did not identify this CIP senior manager by business phone and address as required by R2.1. WECC_URE4 also indicated that its compliance officer was the senior manager for the fourth month through twelfth month of the enforceable date of the Standard, assigned pursuant to the Standard, and that he delegated authority to someone else to act as the assigned CIP senior manager during this period. WECC_URE4 provided meeting minutes, company information pamphlets, and its internal compliance program (ICP) charter to demonstrate this delegation. Nevertheless, WECC determined this documentation did not identify this delegated CIP senior manager and did not designate this delegated CIP senior manager within thirty-calendar days of his designation three months after the enforceable date of the Standard, as required by R2.2. Various documents effective during the period of this violation identified WECC_URE4’s compliance officer as the assigned CIP senior manager. Nevertheless, WECC determined these documents were inconsistent with the other documentation references above and did not serve to identify the compliance officer as the assigned CIP senior manager within the thirty-calendar day time frame required by R2.2. WECC determined that WECC_URE4 had a violation of CIP-003-1 R2 because WECC_URE4’s assigned CIP senior managers were not designated consistent with the requirements in R2.1 and R2.2. Although, after the Spot Check, WECC_URE4 was able to produce documents which showed senior management assignments, these documents were approved by a senior manager who was not designated as the senior manager pursuant to CIP-003-1 R2. The confusion surrounding this issue was further exacerbated by the significant turnover of staff in the period leading up to the Spot Check. | CIP-003-1 | R2; R2.1; R2.2 | Lower | N/A | WECC determined that this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system because, although WECC_URE4 could not prove its senior manager signed off on the security policy, WECC_URE4’s history included documentation of a manager’s approval of the policy. | when the Standard became mandatory and enforceable for WECC_URE4 | when the cyber security policy was approved | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | After the Spot Check, WECC_URE4 submitted a Mitigation Plan stating that it had located the documentation dated two months before and three months after the enforceable date of the Standard designating WECC_URE4’s senior manager for the period of this violation. In addition, 27 months after the enforceable date of the Standard, the cyber security policy was approved by the appropriate manager. | 2010-09-27 | 2011-04-26 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001886 | Settlement Agreement | WECC determined that documentation presented by WECC_URE4 demonstrated that it had cyber security test procedures for new Cyber Assets in effect 38 days after the enforceable date of the Standard. As evidence for cyber security test procedures for new Cyber Assets before that date, WECC_URE4 provided a copy of its test procedures document. WECC determined from this document that WECC_URE4’s materials did not provide a set of procedures that tested the cyber security controls of new assets. In addition, WECC determined that the documentation provided for significant changes to existing Cyber Assets did not demonstrate cyber security controls tests were part of the procedure. WECC_URE4’s documentation focused on functionality and lacked specific tests that would assure the existing security controls were not adversely affected as a result of a significant change. Moreover, WECC discovered that WECC_URE4’s evidence could not demonstrate test results for the following two significant changes to Cyber Assets that took place twelve months after the enforceable date of the Standard: (1) WECC_URE4 submitted a change request for an installation of its firewall service module, and (2) added interfaces and routes to/from its energy management system (EMS) networks, and removed the transparent firewall. WECC determined that WECC_URE4 had a violation of CIP-007-1 R1 because WECC_URE4 did not create, implement and maintain adequate cyber security test procedures as required by R1 and R1.1 and did not document test results for two significant changes to existing Cyber Assets as required by R1.3. | CIP-007-1 | R1; R1.3 | Lower | N/A | WECC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system because although WECC_URE4 could not provide documentation that it tested the security controls for new Cyber Assets, WECC_URE4 could provide documentation that it had cyber security test procedures for its new Cyber Assets. Despite lack of documentation, WECC_URE4 did actually complete the testing of the security controls for new Cyber Assets. | when the Standard became mandatory and enforceable for WECC_URE4 | when WECC_URE4 updated its cyber security test procedures per the requirements of the Standard | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | WECC_URE4 initiated a project, 38 days after the enforceable date of the Standard, to implement change management practices with a goal to achieve and maintain a controlled, consistent, collaborative and confident approach to meeting CIP-007 R1 change management requirements, inclusive of cyber security testing for new Critical Cyber Assets and significant changes to existing critical Cyber Assets. | 2011-01-21 | 2012-07-26 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102894 | Notice of Confirmed Violation | WECC_URE5 self-reported a violation of CIP-004-3 R3.2 for failing to ensure that two employees (less than 1% of the total employees) with authorized unescorted physical access to several of WECC_URE5's Physical Security Perimeters (PSPs) had personnel risk assessments (PRAs) that were updated at least every seven years. WECC_URE5 completed an initial PRA for these two individuals before the Standard became mandatory and enforceable but failed to update the PRAs for these two individuals seven years later. The first employee’s PRA completion date was incorrectly documented within WECC_URE5 corporate security’s records as having been completed three years after the actual date. The discrepancy was discovered four weeks after the actual due date, during an internal review. Consequently the employee did not have a valid PRA but still had had physical access to WECC_URE5’s PSPs for a 28-day period. The second employee’s PRA completion date was incorrectly documented as having been completed six months after the actual date. The discrepancy was discovered three months after the actual due date, during an annual review of the PRA master access list. Consequently, the WECC_URE5 employee did not have a valid PRA but still had physical access to WECC_URE5's PSPs for a 98-day period. WECC determined that WECC_URE5 was in violation of CIP-004-3 R3 for failing to update the PRAs for the two individuals identified above within the seven-year time period as required by the Standard. | CIP-004-3 | R3; R3.2 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the two individuals in scope had initial PRAs and current training as required by CIP-004-3 R2. The individuals posed a lesser risk because they did have initial security threat assessment and were trained to properly handle Critical Cyber Assets. In addition, WECC_URE5 revoked the employees’ access rights immediately upon discovery. | date by which WECC_URE5 was required to update the first individual's PRA | date WECC_URE5 revoked the last affected individual's access rights | $12,600 (for WECC201102894 and WECC201102895) | Self-Report | Upon learning of these incidents WECC_URE5 took the following actions: 1. WECC_URE5 revoked the employees’ access rights immediately upon discovery of the violation instances; 2. The employees’ PRAs were completed; and 3. WECC_URE5 reinstated both employees’ physical access rights after completion of PRAs. | 2011-04-21 | 2012-04-20 | Does Not Contest | WECC reviewed WECC_URE5's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE5's and its affiliates' compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102895 | Notice of Confirmed Violation | WECC_URE5 self-reported a violation of CIP-004-3 R4.2 for failing to revoke an individual’s electronic access to Critical Cyber Assets (CCAs) within seven days of no longer requiring such access. The individual was employed by WECC_URE5's affiliate and no longer required access to WECC_URE5’s CCAs when he retired, but his access was not revoked by the due date. WECC_URE5’s corporate security department revoked the retired employee’s physical access rights before the due date, but the employee's supervisor did not submit a request to WECC_URE5’s Information Technology (IT) department to revoke the retired employee’s electronic access rights until the actual due date. The following day, upon receiving the request, the IT department revoked the retired employee's electronic access rights. | CIP-004-3 | R4 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because WECC_URE5 uses two-factor authentication, has automated and manual logging, and all operator commands issued on the Energy Management System (EMS) are recorded in the event log. Therefore, WECC_URE5 was able to monitor the use of its CCAs and possibly identify malicious conduct. WECC_URE5 also stated the individual in scope had cyber security training and knew how to properly use CCAs and a personnel risk assessment which revealed no security threats. | when WECC_URE5 was required to revoke the employee's access to CCAs | when WECC_URE5 revoked the employee's access to CCAs | $12,600 (for WECC201102894 and WECC201102895) | Self-Report | WECC_URE5 conducted a review of the incident to ensure established procedures were followed. At the completion of the review, it was determined that the current process needed additional enhancements to specifically address employee retirements. Upon learning of these incidents,WECC_URE5 took the following actions: 1. WECC_URE5 confirmed that the employee’s physical access was revoked and the revocation records were retained; 2. WECC_URE5 revoked the employee’s electronic access rights; 3. WECC_URE5's affiliate developed new procedures for NERC CIP electronic and physical access; 4. WECC_URE5's affiliate ensured that WECC_URE5's procedure for requesting and maintaining NERC CIP electronic and physical access was integrated into the affiliate's own procedures; 5. As an enhancement to the developed procedure, on-boarding and off-boarding checklists were developed to ensure that affected managers and supervisors provide all necessary information and notifications to the appropriate groups who provision and de-provision access rights. These checklists became procedural and were formally released to the affected managers and supervisors; 6. Managers and supervisors were briefed and trained on the new procedures during monthly staff meetings; and 7. As on-going reinforcement, reminder notifications have been and will be communicated to WECC_URE5's affiliate managers. | 2011-08-26 | 2012-04-20 | Does Not Contest | WECC reviewed WECC_URE5's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE5's and its affiliates' compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102667 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC stating that it was in violation of CIP-004-3 R2. WECC found that 0.45% of employees with authorized unescorted physical access to 21 Physical Security Perimeters (PSPs) did not receive annual training during the calendar year. The Critical Cyber Assets (CCAs) inside these PSPs include servers, workstations, and networking equipment used in WECC_URE5's Energy Management System. | CIP-004-3 | R2; R2.1 | Medium | Severe | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS) because the 0.45% individuals in scope had a valid Personnel Risk Assessment (PRA) and had completed training the previous year. In addition, all PSPs are monitored twenty-four hours a day, and all CCAs require a username and password before an individual can gain access. | the date by which WECC_URE5 should have performed the required annual training | Mitigation Plan completion | 5000 | Self-Certification | WECC_URE5 implemented the following Mitigation Plan Activities: 1) WECC_URE5 removed access for personnel associated with this violation; 2) WECC_URE5 verified monthly training records; 3) WECC_URE5 implemented manual tracking of training expiration; 4) WECC_URE5 instituted the automated “early warning” notification for pending training expiration. This notice is sent directly to affected personnel and their manager/supervisor prior to the expiration of training; and 5) WECC_URE5 automated the notification of seven-day access revocation upon the expiration of training. Compliance staff from WECC_URE5 and supporting organizations manually verified that all training records for personnel with access to WECC_URE5's Electronic Security Perimeters and PSPs were valid. Confirmation of such manual verification was required in order to ensure data validity and consistent practice of manual verification across WECC_URE5. Manual verifications continue to occur. Automated notifications for upcoming expired training qualifications and revocation of access were implemented by WECC_URE5. | 2011-12-31 | 2012-05-25 | Does Not Contest | WECC considered WECC_URE5's Internal Compliance Program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900347 | Settlement Agreement | The SERC CIP Spot Check team reported a violation of CIP-007-1 R1, because SERC_URE1 was unable to provide evidence that it was testing all significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC found that SERC_URE1 had a test procedure that included testing all cyber security controls for new Cyber Assets brought into the ESP, performing all tests in an appropriate test environment, and documenting all test results; however, this procedure failed to address the testing of all cyber security controls for significant changes to existing Cyber Assets to ensure that those changes would not have an adverse effect upon existing cyber security controls. SERC_URE1 had not considered certain resources, including ports and services, anti-virus software, and malware prevention tools, to be “controls” within the meaning of CIP-007-1 R1, therefore they were not included in the test procedure, as required by the Standard. Instead, these resources were addressed in SERC_URE1's internal procedures associated with other requirements of CIP-007-1. During the time this deficient procedure was in place, it was used to test three significant changes to existing Cyber Assets located within SERC_URE1’s ESP. These three changes were: (1) a software update on all Critical Cyber Assets (CCAs) to prevent the dispatcher training simulator from crashing when a real-time snapshot was taken; (2) a software update on four CCAs to fix discrepancies between the databases among four servers; and (3) a software update on one CCA in order to resolve non-updating communications protocol points. | CIP-007-1 | R1 | Lower | Severe | SERC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because, although SERC_URE1 failed to test in the manner required by the Standard, SERC_URE1 addressed the testing of some cyber security controls, conducted testing in an appropriate test environment, documented the results, and only used the deficient procedure three times. | when the Standard became mandatory and effective for SERC_URE1 | when SERC_URE1 updated its test procedures | 0 | Spot Check | To mitigate this violation, SERC_URE1 updated its test procedures to include the testing of all cyber security controls for significant changes to existing Cyber Assets. SERC_URE1’s test records and associated documentation were re-formatted to explicitly document the checks performed for cyber security controls during installations of new Cyber Assets and significant changes to existing Cyber Assets within the ESP. In addition, SERC_URE1’s test records and associated documentation were re-formatted to explicitly document checks of other systems, such as ports and services, performed during installations of new Cyber Assets and significant changes to existing Cyber Assets. | 2009-11-23 | 2012-02-22 | Neither Admits nor Denies | SERC considered SERC_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, SERC_URE1 was cooperative in helping SERC understand the nature and scope of the violation.
2012-07-31 | FERC | NP12-36-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000348 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE indicating that it was in violation of CIP-006-1 R3. Texas RE_URE1 documented but failed to implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week (24/7) using at least one of the monitoring methods identified in CIP-006-1 R3. Specifically, Texas RE_URE1 failed to implement physical access monitoring at one fire exit door. While the evidence provided by Texas RE_URE1 suggests that video recording started with the surveillance camera installation that occurred four months after the mandatory compliance date, no evidence was provided that proves the video footage was reviewed 24/7. Further, a Texas RE_URE1 manager attested that he reviewed the surveillance videos during an eight week period at his leisure, but not 24/7. Texas RE_URE1 began reviewing the surveillance videos 24/7 8.5 months after the mandatory compliance date. With no 24/7 video surveillance in place prior to then, human observation was Texas RE_URE1’s only monitoring option. Human observation existed, but it was not in place 24/7. | CIP-006-1 | R3 | Medium | High | Texas RE determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because the access point was a fire exit door in the backup control center that was designed to be opened from inside the computer room only. This access point was a door within a defined PSP. Only personnel with authorized physical access are allowed to enter the PSP. Moreover, the fire exit door was secured by a crash bar from inside the computer room. However, without an operative door alarm and adequate physical access monitoring, a person within the control center computer room could open the door and allow an unauthorized person access into the PSP. A Texas RE_URE1 manager did review the surveillance videos, but this was not performed 24/7 in accordance with the Standard for the entire mandatory compliance period. Texas RE_URE1 personnel also attested that video footage from various cameras throughout the Texas RE_URE1 campus is manually cycled across large computer monitors where it is viewed by security personnel. | when the Standard became mandatory and enforceable for Texas RE_URE1 | Mitigation Plan completion Prior to 4/1/2010, Texas RE_URE1 was in violation of CIP-006-1 R3. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, Texas RE_URE1 was in violation of CIP-006 R5. | $8,000 (for TRE201000348 and TRE201000349) | Self-Report | To mitigate this violation, Texas RE_URE1 eliminated the subject computer room exit door by completely drywalling this access point and notifying Texas RE_URE1's internal NERC compliance group of the updated PSP floor plans, reflecting this change. Additionally, Texas RE_URE1 completed the following "above and beyond" measures: (1) Created a 12-month audit strategy for an applicable function, to ensure communication and success which included the following: creation of a formal audit timeline with deadlines to complete documents and evidence; formal meetings to roll out the audit plan to appropriate senior management; incorporation of a review of all CIP programs and evidence; incorporation of a series of mock audits on all CIP programs; and creation of a status tracking report used to update managers and executives at bi-weekly meetings. (2) Added a document control position to the internal compliance team. (3) Researched compliance tracking tools to automate many of the compliance functions and reporting; this included vendors conducting onsite demonstrations. (4) Conducted two self-audits. | 2010-11-02 | 2011-12-22 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, "above and beyond" mitigating measures were considered in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000349 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE indicating that it was in violation of CIP-006-1 R4. Texas RE_URE1 documented but failed to implement the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter (PSP) using one or more of the logging methods identified in CIP-006-1 R4. Specifically, Texas RE_URE1 failed to log physical entry at one fire exit door for a ten-month period. Based on the evidence provided by Texas RE_URE1, no mechanism for logging existed before the video surveillance camera installation for the aforementioned access point was completed four months after the mandatory compliance date. Texas RE_URE1 believes the subject fire exit door should not be classified as an access point. | CIP-006-1 | R4 | Lower | High | Texas RE determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because the access point was a fire exit door in the backup control center that was designed to be opened from inside the computer room only. This access point was a door within another defined PSP. Only personnel with authorized physical access are allowed to enter the PSP. Moreover, the fire exit door was secured by a crash bar from inside the computer room. | when the Standard became mandatory and enforceable for Texas RE_URE1 | Mitigation Plan completion Prior to 4/1/2010, Texas RE_URE1 was in violation of CIP-006-1 R4. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, Texas RE_URE1 was in violation of CIP-006 R6. | $8,000 (for TRE201000348 and TRE201000349) | Self-Report | To mitigate this violation, Texas RE_URE1 eliminated the subject computer room exit door by completely drywalling this access point and notifying Texas RE_URE1's internal NERC compliance group of the updated PSP floor plans, reflecting this change. Additionally, Texas RE_URE1 completed the following "above and beyond" measures: (1) Created a 12-month audit strategy for an applicable function, to ensure communication and success which included the following: creation of a formal audit timeline with deadlines to complete documents and evidence; formal meetings to roll out the audit plan to appropriate senior management; incorporation of a review of all CIP programs and evidence; incorporation of a series of mock audits on all CIP programs; and creation of a status tracking report used to update managers and executives at bi-weekly meetings. (2) Added a document control position to the internal compliance team. (3) Researched compliance tracking tools to automate many of the compliance functions and reporting; this included vendors conducting onsite demonstrations. (4) Conducted two self-audits. | 2010-11-02 | 2011-12-22 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, "above and beyond" mitigating measures were considered in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009825 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R2.1. More specifically, during a periodic spot check, WECC_URE1 discovered that one individual was granted access to a Physical Security Perimeter (PSP) prior to completing required cyber security training. Access was inadvertently granted and taken away three days later when WECC_URE1 recognized the error. Upon discovering the error, WECC_URE1 performed a thorough analysis of the error and determined the individual in scope did not access the PSP at any time during the four days in which access was granted. Further, the individual in scope had a current personnel risk assessment (PRA) on file, and the individual was not aware he had such access. Consequently, WECC determined that WECC_URE1 failed to ensure that all personnel having such access to Critical Cyber Assets (CCAs), including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency, as required by CIP-004-3 R2.1. | CIP-004-3 | R2.1 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the individual had physical access, he did not have account access and could not log on to any of the CCA systems inside of the PSP. The CCAs in the PSP were also physically resistant, meaning there was no way to introduce information to the CCAs by way of any means of hardware communication. The PSP is monitored 24 hours a day, seven days a week via security cameras and security personnel. Lastly, the individual in question had a current PRA, and did not access the PSP while he was granted access to it. | date access to the PSP was granted in error | date access to PSP granted in error was revoked | 7000 | Self-Report | In accordance with the Mitigation Plan submitted by WECC_URE1 to WECC, WECC_URE1 revoked access for the individual who had inadvertently been granted access to a PSP prior to having completed the required cyber security training. WECC_URE1 completed a review of all provisioned physical and cyber access and determined that no other errors in training validation for any access afforded existed. In consideration of the need for further protections against human error, WECC_URE1 updated its procedure for access implementation. The procedure now includes steps for validating training records, including a peer review prior to approving the training completion part of the access request workflow. In addition, WECC_URE1 trained its personnel on the new procedure. | 2012-02-22 | 2012-06-05 | Does Not Contest | WECC considered WECC_URE1's internal compliance program and compliance history.
2012-07-31 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102926 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC indicating that it was in violation of CIP-005-1 R2. In its Self-Report, WECC_URE2 stated that it performed an incomplete review of its ports and services. WECC_URE2 stated that for six access points on its Electronic Security Perimeters (ESPs), it failed to ensure that only those ports and services required for normal operations were enabled. The access points WECC_URE2 identified are firewalls that control all of its ESPs. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system because, as a compensating measure, controls were in place during the duration of the violation, to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed 24 hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became mandatory and enforceable for WECC_URE2 | when WECC_URE2 conducted the required revisions and performed the training | $12,000 (for WECC201102926 and WECC201102927) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. Per its Mitigation Plan, WECC_URE2 revised its critical infrastructure protection program procedures for evaluating and assessing its ports and services for firewalls and switches, as well as conducted training on the revised procedures. | 2011-12-31 | 2012-05-07 | Agrees/ Stipulates | WECC considered WECC_URE2's compliance history.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102927 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC indicating that it was in violation of CIP-007-1 R2. In its Self-Report, WECC_URE2 stated that it performed an incomplete review of its ports and services. WECC_URE2 stated that for less than 8% of its total Cyber Assets, WECC_URE2 failed to ensure that only those ports and services required for normal operation were enabled. The Cyber Assets are network switches and workstations used for physical access monitoring. | CIP-007-1 | R2; R.2.1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system because, as a compensating measure, controls were in place during the duration of the violation, to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became mandatory and enforceable for WECC_URE2 | when WECC_URE2 conducted the required revisions and performed the training | $12,000 (for WECC201102926 and WECC201102927) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. Per its Mitigation Plan, WECC_URE2 revised its critical infrastructure protection program procedures for evaluating and assessing its ports and services for firewalls and switches, as well as conducted training on the revised procedures. | 2011-12-31 | 2012-05-07 | Agrees/ Stipulates | WECC considered WECC_URE2's compliance history.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2011008643 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Report addressing noncompliance with CIP-004-3 R4. WECC_URE3 did not timely update its access lists following employee retirement or transfers, including third-party contractors who had been given physical access rights to WECC_URE3 facilities that house Critical Cyber Assets (CCAs). Specifically, WECC_URE3 reported that its access list violation was associated with 11 individuals (three WECC_URE3 employees and eight third-party contractors), which represent less than 5% of WECC_URE3's authorized personnel. WECC_URE3 further determined it updated its access list two days late for a retired employee, 74 days late for a transferred employee, 210 days late for a different transferred employee, two days late for one contractor no longer requiring access, and between 140 and 159 days late for the remaining 7 contractors. During an on-site Compliance Audit, WECC reviewed the Self-Report and determined the individuals associated with the Self-Report initially had physical access to WECC_URE3's control centers. The individuals did not have electronic access to CCAs. WECC determined that WECC_URE3 revoked access for the individuals in question but did not update its authorized access lists. WECC determined that WECC_URE3 violated CIP-004-3 R4.1 for a failure to update its lists of personnel with authorized unescorted physical access to its CCAs. WECC also determined that WECC_URE3 violated CIP-004-3 R4.2 for a failure to revoke physical access to its CCAs within 24 hours for personnel who no longer require such access to CCAs. | CIP-004-3 | R4.1/ R4.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, WECC determined that the violation did not include any issue with unauthorized access to WECC_URE3's CCAs and was limited to WECC_URE3's failure to update its lists of personnel with authorized unescorted physical access to its CCAs. Second, the contractors did not gain access to the CCAs. Third, the CCAs reside in a Physical Security Perimeter (PSP), which is subject to continuous monitoring and logging of both authorized logs and unauthorized access attempts. Also, the CCAs reside within an Electronic Security Perimeter (ESP); however none of the individuals associated with this violation had electronic access to CCAs. Finally, this instance of noncompliance is related to fewer than 5% of authorized WECC_URE3 employees or contractors, thus presenting a very limited risk to the BPS. | the date WECC_URE3 failed to update the access list associated with this violation | Mitigation Plan completion | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Self-Report | WECC_URE3 submitted a Mitigation Plan and completed the following actions to mitigate this violation: WECC_URE3 implemented a revised Access Program and enacted changes to the automated secure access request workflow process. The changes included: (1) Specific attention to third-party contractor authorization/termination of access privileges; (2) The addition of a process step within WECC_URE3's workflow process to route the process back to the authorized approver following the provisioning of authorized unescorted physical or cyber access; (3) Under the revised process, the authorized approver must review and attest that the list was updated; (4) The addition of a new confirmation process. After the authorized approver reviews and attests that the access list has been updated, WECC_URE3's Compliance group confirms the update. | 2012-03-21 | 2012-04-10 | Does Not Contest | WECC considered the internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102449 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Certification addressing possible noncompliance with this requirement. WECC_URE3 indicated on the Self-Certification that two operators did not meet the required training hours for the calendar year, but each operator did compile enough hours to maintain NERC certification and re-certification. WECC_URE3 further determined the two operators did not complete the required training time for system emergencies. WECC_URE3 added that it did not allow the employees to continue operating the WECC_URE3 system beyond the end of the year. Once the calendar year expired and the employees had not reached the minimum training requirements, WECC_URE3 did not allow the employees to operate. Thus, WECC_URE3 ensured that it maintained a staff of operating personnel with five days of emergency training, as required by this Standard. During an on-site Compliance Audit, WECC reviewed the Self-Certification and determined that the noncompliance was related to a single operator, not two operators. WECC determined that one individual received 17 hours of emergency training, approximately 15 hours short of the five days required by the Standard. WECC determined WECC_URE3's failure to provide at least five days per year of training and drills using realistic simulations of system emergencies to the operator resulted in a violation of PER-002-0 R4. | PER-002-0 | R4 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. WECC_URE3's transmission system includes approximately 1,000 miles of 345 kV transmission lines, which increases the risk to the BPS. WECC_URE3 did not allow the employee to operate the system once the training deadline had passed, thus reducing the risk to the BPS. WECC_URE3 made sure that the operator associated with this violation was experienced, was NERC-certified, and maintained his NERC Certification. Also, the operator completed all of the required training in the prior year and 17 hours of training in the next year, the year when the violation occurred. Finally, all other WECC_URE3 operators received the training required by this Standard. | when the operator should have completed the required training | the operator was removed from the operating desk | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Self-Certification | According to its Mitigation Plan, WECC_URE3 took the following actions: (1) Removed the one operator who did not timely complete the requisite training hours from the WECC_URE3 system operations desk. After the end of the year, the employee did not serve in the operator capacity. (2) Ensured that all of its personnel allowed to operate the WECC_URE3 system remained adequately trained pursuant to this Standard. The employee did not return to the system operating desk until the employee completed training for the next calendar year. | 2010-12-31 | 2012-05-25 | Does Not Contest | WECC considered the internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009561 | Settlement Agreement | During an on-site Compliance Audit, WECC discovered that WECC_URE3 violated PER-002-0 R1. WECC's Audit Team determined that one WECC_URE3 operator received 17 hours of emergency training for the calendar year, which was approximately 15 hours fewer than the 32 contact hours required by WECC_URE3's training plan. WECC determined that WECC_URE3 failure to provide at least 32 hours of contact hours per year of training and drills using realistic simulations of system emergencies to the operator resulted in a violation of PER-002-0 R4 (WECC201102449), which was addressed in a separate enforcement action that is concurrently being filed in WECC Violation ID# WECC201102449. WECC also determined based on the same set of facts that WECC_URE3 violated PER-002-0 R1 because the operator did not complete WECC_URE3's training requirement for the calendar year, and thus WECC_URE3 was not staffed with adequately trained operating personnel during the period of the violation. At the time of the violation, WECC_URE3 had 17 operators. | PER-002-0 | R1 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. WECC_URE3's transmission system includes approximately 1,000 miles of 345 kV transmission lines, which increases the risk to the BPS. WECC_URE3 did not allow the employee to operate the system once the training deadline had passed, thus reducing the risk to the BPS. WECC_URE3 made sure that the operator associated with this violation was experienced, was NERC-certified, and maintained his NERC Certification. Also, the operator completed all of the required training in the prior year and 17 hours of training in the next year, the year when the violation occurred. Finally, all other WECC_URE3 operators received the training required by this Standard. | the last date the entity was staffed with adequately trained operator personnel | the operator was removed from the operating desk | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Audit | WECC_URE3 submitted a Mitigation Plan to address its violation of PER-002-0 R4. WECC determined that the instant violation and the violation of PER-002-0 R4 are a result of a single act of noncompliance stemming from WECC_URE3's violation of PER-002-0 R4. As a result, WECC also determined that WECC_URE3's remediating actions associated with the violation of PER-002-0 R4 serve as a remediating actions for the instant violation. According to its Mitigation Plan for PER-002-0 R4, WECC_URE3 took the following actions: (1) Removed the one operator who did not timely complete the requisite training hours from the WECC_URE3 system operations desk. After the end of the year, the employee did not serve in the operator capacity. (2) Ensured that all of its personnel allowed to operate the WECC_URE3 system remained adequately trained pursuant to this Standard. The employee did not return to the system operating desk until the employee completed training for the next calendar year. | 2010-12-31 | 2012-05-27 | Neither Admits nor Denies | WECC imposed a penalty for the related PER-002-0 R4 violation (WECC201102449, see above) and $0 for the instant violation. The PER-002-0 R4 penalty is addressed in a separate enforcement action that is being concurrently filed. WECC determined that no aggravation of the penalty was warranted in this case because the penalty for PER-002-0 R4 is a single penalty representative of the aggregate of the related violations.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002448 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-003-1 R5. WECC_URE4 submitted a Self-Report to WECC stating that it did not review the access privileges to protected information to confirm that the access privileges are correct and that they correspond with WECC_URE4's needs and appropriate personnel roles and responsibilities. Twenty-two WECC_URE4 personnel who previously had physical and/or logical access to protected information, based on job need, were "grandfathered" in as authorized personnel, but were not documented in accordance with procedures. WECC determined WECC_URE4 had a violation of CIP-003-1 R5, specifically R5.2, due to its failure to annually review the access privileges to protected Critical Cyber Asset (CCA) information to confirm that access privileges are correct. Although WECC_URE4 has a process in place for granting access to CCA information, twenty-two individuals who had been granted authorized access prior to the effective date of the standard were "grandfathered" and did not fill out the authorization form. Therefore, WECC_URE4 failed to confirm that, for these individuals, access privileges were correct. | CIP-003-1 | R5 (R5.2) | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The personnel within the scope of the violation had personnel risk assessments and CIP training, and access could be verified using Windows Active Directory. WECC_URE4 also stated its CCAs had updated anti-malware, logging enabled, and tripwire installed. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 reviewed and documented employees with "grandfathered" access to CCA information to ensure their authorized access to protected CCA information is appropriate and necessary and to verify continued compliance with WECC_URE4 procedure(s). | 2010-09-02 | 2011-04-29 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002490 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-003-1 R6. WECC_URE4 submitted a Self-Report to WECC stating that it had not used its own prescribed form for documenting changes to Critical Cyber Asset (CCA) / Critical Asset (CA) hardware and/or software, nor did it use its Change Log, as required by CIP-003-1 R6. WECC determined that WECC_URE4 failed to document WECC_URE4's use of a process of change control and configuration management for adding, modifying, replacing, or removing CCA hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of CCAs pursuant to WECC_URE4's change control process, as required by CIP-003-1 R6. WECC_URE4 failed to complete the documentation specified in its change control and configuration management procedure for six patch cycles for fourteen CCAs. The CCAs in scope were used for Windows Active Directory, Network Time Protocol, and vulnerability scanning. The devices in scope are located in WECC_URE4's Electronic Security Perimeter. | CIP-003-1 | R6 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. At the time of the violation, information similar to that which was missed in the CIP-003-1 R6 documentation was captured in WECC_URE4's CIP-007 R3 documentation. WECC_URE4 also stated tripwire software was recording any changes made to CCAs, and systems were tested before being put into production. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 created, implemented, and maintained a CCA Inventory Worksheet and Change Control Log, as described in WECC_URE4's change control and configuration management procedure, and uses these documents to record configuration changes to CCAs retroactive to when the Standard became mandatory and enforceable. | 2010-09-30 | 2011-05-26 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002447 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-004-1 R4. WECC_URE4 submitted a Self-Report to WECC stating that it did not maintain a list of personnel authorized for cyber access to Critical Cyber Assets (CCAs). WECC_URE4 did not maintain a list of personnel with authorized cyber or authorized unescorted physical access to CCAs, including their specific electronic and physical access rights to CCAs. WECC_URE4 did not have a list of personnel with cyber access to CCAs. At the time of the violation, there were 26 individuals with cyber access to 21 CCAs. WECC found that WECC_URE4 failed to maintain lists of personnel with authorized cyber or authorized unescorted physical access to CCAs for 26 individuals with cyber access to CCAs. These CCAs were located in WECC_URE4's facilities. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because the personnel in scope had Personnel Risk Assessments and CIP Training, and access could be verified using Windows Active Directory. WECC_URE4 also stated the CCAs in scope had updated anti-malware, logging enabled, and tripwire installed. This violation affected 21.14% personnel. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 created a consolidated list of personnel with authorized cyber access to CCAs from existing documentation with relevant information, and maintains the list in accordance with CIP-004-1 R4 and WECC_URE4 procedure(s). | 2011-06-09 | 2011-07-08 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002491 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-005-1 R1. WECC_URE4 submitted a Self-Report to WECC stating that it failed to afford all the required protective measures to the RSA device that collects logs associated with access control and/or monitoring of WECC_URE4's Electronic Security Perimeter (ESP) and Critical Cyber Assets (CCAs). WECC found that WECC_URE4 had a violation of CIP-005-1 R1 for its failure to afford all the required protective measures for its Cyber Assets used in the access control and monitoring of the ESP, as specified in CIP-003, CIP-004 R3, CIP-005 R2 and R3, CIP-006 R2 and R3, CIP-007 R1 and R3 through R9, CIP-008, and CIP-009. The RSA device is used for monitoring the ESP and supporting WECC_URE4's access control and monitoring device. The RSA device is WECC_URE4's centralized logging server and maintains logs relating to log-ins, syslogs, and anomalous traffic. The device also maintains firewall rules and configuration changes made to firewalls. WECC_URE4 failed to provide the following protections for the RSA device. For protections required under CIP-005 R2.5.3, WECC_URE4 did not have a cyber access list, thus authorization rights for the three individuals with cyber access to this device could not be reviewed. For CIP-007 R1, WECC_URE4 failed to ensure one operating system patch for Windows Server 2003 would not adversely affect security controls, and failed to test the installation of anti-virus software prior to the software being put into production. For CIP-007 R4, the device in scope did not have anti-virus or anti-malware software installed. For CIP-007 R8, no cyber vulnerability assessment was performed on the device in scope. For CIP-009 R1 - R4, WECC_URE4 did not create a recovery plan for the device in scope. Following subsequent discussions with WECC_URE4, WECC determined that there were also four switches, externally connected devices with end points terminating within the ESP that were not identified and documented as access points to the ESP, as required by CIP-005 R1. WECC_URE4 stated these switches were classified as CCAs that contained a management port using an IP routable protocol, and the traffic did not route through the identified access points to the ESP. In addition, one Keyboard, Video, Mouse switch, which was not located inside an ESP, is used to provide the functions of a keyboard, monitor (video), and mouse to several servers and therefore allow remote control of the CCAs from outside the ESP. Thus, WECC_URE4 failed to identify and protect this Keyboard, Video, Mouse switch as an access point to the ESP. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Failure to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded the protective measures specified in CIP-005 R1 puts such assets at risk to be manipulated, allowing malicious access to Cyber Assets within the ESP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS, thereby potentially negatively impacting the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because the personnel with access to the devices in scope had Personnel Risk Assessments and CIP training, and access could be verified using Windows Active Directory. WECC_URE4 also stated the RSA device was in a Physical Security Perimeter, and WECC_URE4 was maintaining firewall logs that were reviewed daily during the work week. Alerts for failed log-ins or odd traffic were automated and configured to be sent to the security staff, an intrusion detection system was installed, and logs were reviewed daily during the workweek. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 completed the testing, application and documentation of malicious software prevention software on the RSA device; instituted changes to related work procedures and processes to ensure use and documentation of the appropriate electronic access authorization process; completed a cyber vulnerability assessment on the RSA device, created a recovery plan for the RSA device; determined an acceptable solution to the test environment required by CIP-007 R1.2; defined a course of action toward the RSA device testing environment; implemented a solution to ensure that testing is done in an environment that reflects the RSA device's production environment; reclassified its switches as both CCAs and access control monitoring devices; and replaced remote access Keyboard, Video, Mouse devices with local Keyboard, Video, Mouse. | 2012-01-31 | 2012-06-07 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002492 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-006-1 R1.8. WECC_URE4 submitted a Self-Report to WECC stating that it failed to afford the protective measures specified in the Standard for its access control and/or monitoring (ACM) system for its Physical Security Perimeters (PSPs). The specific device is a WECC_URE4 server. The Standard requires WECC_URE4 to afford the server certain protections. Specifically, for the protections afforded under CIP-005 R2.5.3, WECC_URE4 has not provided the WinPak server the same process and mechanisms for control of electronic access as other critical systems. For CIP-005 R3.2, WECC_URE4 does not have a device in place for cyber access to the server that will monitor and alert of attempts at or actual unauthorized access. For CIP-007 R1, WECC_URE4 does not have test procedures in place as there is no test system available for the server. At the recommendation of its vendor, WECC_URE4 does not make changes/updates to the system due to its obsolescence. For CIP-007 R2, WECC_URE4 has not had a list of ports and services for the server. For CIP-007 R4, WECC_URE4 has not updated its anti-virus and malware prevention tools on the server based on the recommendation of its vendor. For CIP-007 R5, WECC_URE4 has not been following Account Management practices for the server. For CIP-007 R6, WECC_URE4 has not manually or electronically monitored the server operating system events. For CIP-007 R85, WECC_URE4 has not performed cyber vulnerability assessments to the PSP Cyber Assets at the recommendation of its vendor. WECC determined that WECC_URE4 had a violation of CIP-006-1 R1.8, for its failure to afford all the required protective measures of the Standard for its Server used in the access control and monitoring of its PSPs. The server is used for access control and monitoring of the PSPs. | CIP-006-1 | R1 (R1.8) | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Failure to ensure that Cyber Assets used in the access control and monitoring of the PSP are afforded the protective measures specified in CIP-006-1 R1.8 puts such assets at risk to be manipulated, allowing malicious access to Cyber Assets within the PSP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS, thereby potentially negatively impacting the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because the personnel with access to the device in scope had Personnel Risk Assessments and CIP training, and cyber access could be verified using Windows Active Directory. WECC_URE4 also stated the device was in a PSP with firewall logs to its Electronic Security Perimeter. The logs were reviewed daily during the work week and failed logins or odd traffic automated alerting was configured to be sent to the security staff. An intrusion detection system was installed and logs were reviewed daily during weekdays. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | This violation was primarily related to the recommendation by the vendor that the system not be modified or altered given that the system is no longer supported. The corrective action is the replacement of the system with a new ACM. WECC_URE4 reviewed and documented electronic access authorization; commenced account management practices; manually monitored system events; documented on the Cyber Security Exceptions Report these exceptions to requirements to heighten awareness, and prepared for the appropriate management of the new system. | 2011-02-18 | 2011-09-27 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002467 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-007-1 R1. WECC_URE4 submitted a Self-Report to WECC stating that it failed to implement full security testing following routine system patches in accordance with its implementation procedures prior to placing systems in production (testing was limited to operational checks only (R1.1)); failed to have test environments that accurately reflect the environment for three Critical Cyber Assts (CCAs): two Interface Servers and two Archive Servers (R1.2); and failed to document test results in accordance with WECC_URE4 test procedures (R1.3). With respect to R1.1, WECC_URE4 implemented a large number of patches (greater than 300) related to Windows Server 2003, Red Hat Linux 5, Windows XP Workstation, supervisory control and data acquisition (SCADA), and service packs for a back-up client. These patches were not tested as per WECC_URE4's CIP-007 R1 test procedures. WECC_URE4 did not test for security control created and/or modified by these patches, and only tested for operational issues created by the patches. There were 18 CCAs in scope located in an Electronic Security Perimeter (ESP). Examples of the functions performed by these CCAs are Windows Active Directory, Network Time Protocol, and vulnerability scanning. With respect to R1.2, WECC_URE4 has Historian software installed on three CCAs. WECC_URE4 had a test environment in place for the operating system the CCAs were using; however, this test environment did not include the Historian software and, as a result, failed to adequately reflect the production environment. The CCAs in scope are located in the network operations center. These devices are used to store and retrieve archived data from the SCADA system. This data is primarily used for decision-making. A total of 160 (out of the 300 listed in R1.1) operating system patches were applied to these CCAs. These patches were tested on the test environment that did not reflect the production environment. With respect to R 1.3, test results were not adequately documented for the 300 patches listed in R1.1. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. The devices in scope had software that was monitored daily, syslogs with automated alerting, anti-virus/anti-malware, and an Intrusion Detection System which was reviewed at least every three days. WECC_URE4 also stated that, although it did not perform security testing, operational testing was performed on the patches in scope that tested post-update functionality. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 completed the installation of test systems; reviewed and critiqued system security testing procedures; and developed and implemented test procedures to conduct full security testing and document results. | 2010-01-05 | 2011-08-02 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002437 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-007-1 R2. WECC_URE4 submitted a Self-Report to WECC stating that it had identified one required port on a Critical Cyber Asset (CCA) device that was not appropriately documented. Additionally, a required service was not appropriately documented which was running on two CCA devices. According to WECC_URE4 in the Self-Report, these documentation gaps had been corrected. WECC determined that WECC_URE4 had a possible violation of CIP-007-1 R2 for its failure to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled, as required by CIP-007-1 R2. WECC_URE4 failed to follow its process that included documenting all ports and services required for normal or emergency operations. The documentation required by WECC_URE4's CIP-007 R2 process includes the port/service, date of authorization, title of authorizer, and name of authorizer. The two errors were in an Electronic Security Perimeter (ESP). The ports and services were not documented as per WECC_URE4's CIP-007 R2 process. In addition, WECC discussed a potential increase in scope with WECC_URE4. During the interview WECC_URE4 stated that for four switches located in an ESP, it failed to document ports and services required for normal and emergency operations. The CCAs in scope were used for Windows Active Directory, Network Time Protocol, and vulnerability scanning. | CIP-007-1 | R2 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Anti-malware was installed on the devices in scope. The devices were being monitored by software, which would report any changes made to these CCAs. | when the Standard became mandatory and enforceable for WECC_URE4 | the date documentation of ports and services for the switches was completed | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 validated the ports and services on all Cyber Assets within the ESP and completed the correct documentation. | 2011-08-09 | 2011-08-12 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102840 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that its Security Patch Management program was not being applied consistently for four of eighteen Critical Cyber Assets (CCAs); specifically four switches. The cause of this oversight is miscommunication regarding the ownership and responsibility for these devices. Contributing factors include the retirement of a Manager responsible for the assignment of roles and responsibilities, as well as the lack of a documented approach for the assignment of asset ownership and responsibilities. WECC_URE4 had not documented the assessment of security patches and security upgrades for applicability to four CCAs (switches) within thirty calendar days of the availability of the patches or upgrades, in violation of R3.1. With respect to R3.2, in cases where a security patch was not installed, WECC_URE4 did not document the compensating measure(s) applied to mitigate risk exposure or an acceptance of risk associated with available upgrades to four CCAs (switches). Per WECC_URE4 some of the patches were applied, but the implementation was not documented. The four devices in scope are switches located in an Electronic Security Perimeter. WECC determined that WECC_URE4 had a possible violation of CIP-007-1 R3 for its failure to either separately, or as a component of the documented configuration management specified in CIP-003 R6, consistently apply its security patch management for tracking, evaluating, testing, and installing applicable cyber security software patches for all Critical Assets within the Electronic Security Perimeter(s) (ESP). Specifically, for four of eighteen CCAs, WECC_URE4 failed to assess patches within 30 days of availability and failed to document implementation of the patches. | CIP-007-1 | R3 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. The purpose of this Standard is to ensure that WECC_URE4 defines its methods, processes and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the ESPs. WECC_URE4 failed to establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESPs. However, as compensating measures, the devices in scope are located in a Physical Security Perimeter and ESP, and thus afforded the protections specified in CIP-005 and CIP-006. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Report | WECC_URE4 established the CIP compliance responsibilities regarding the four CCA devices to network services personnel; developed a means by which CCA device responsibilities are clearly delineated and communicated to responsible parties; and completed an evaluation of the security patches or other functional or configuration changes to these devices that have been evaluated in accordance with CIP-007 R3. | 2011-06-21 | 2011-11-23 | Agrees/ Stipulates | WECC evaluated WECC_URE's internal compliance program (ICP) and considered it a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102841 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it failed to achieve strict compliance with CIP-009 R1. WECC_URE4 has a documented recovery plan for all Critical Cyber Assets (CCAs), but, according to WECC_URE4 there was a violation of WECC_URE4's implementing procedure that applies to CIP-009 R1 only, with no violation of the sub-elements of CIP-009-1 R1.1 or R1.2. This violation is specific to four CCAs (switches). There was a violation of WECC_URE4's implementing procedure (the Recovery Plan), in that these switches were not referenced in the Recovery Plan. The Recovery Plan specified that each CCA be identified in the Plan. WECC_URE4, however, has restoral procedures for the switches. The recovery plan specifies it will reference all CCAs. However, the recovery plan does not reference four out of eighteen CCAs. These four devices are switches located in an Electronic Security Perimeter (ESP). Although WECC_URE4 states it has a comprehensive recovery plan that references specific CCA recovery procedures, in this instance, the comprehensive recovery plan did not contain any reference to the four devices in scope. | CIP-009-1 | R1 | Medium | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and does not pose a serious or substantial risk to the BPS. The purpose of this Standard is to ensure that WECC_URE4 puts recovery plans in place for Critical Cyber Assets. Although WECC_URE4 failed to create and annually review recovery plans fit its Critical Cyber Assets, as a compensating measure, the devices in scope are redundant pairs and thus there would be no significant impact if one device of the pair failed. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Report | WECC_URE4 revised its implementing procedure, the Recovery Plan, to include the four CCAs (switches). WECC_URE4 also developed a means by which CCA device responsibilities are clearly delineated and communicated to responsible parties. | 2011-06-24 | 2011-11-23 | Agrees/ Stipulates | WECC evaluated WECC_URE's internal compliance program (ICP) and considered it a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2011008663 | Settlement Agreement | WECC_URE5 submitted a Self-Report to WECC citing it was in violation of CIP-007-1 R3. More specifically, WECC_URE5 reported that it failed to document its assessment of certain types of security patches within 30 days of availability for Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). WECC reviewed WECC_URE5's Self-Report and contacted the entity to request additional information. WECC reviewed the additional information and determined that WECC_URE5 failed to document assessments of security patches for 230 devices within 10 ESPs associated with WECC_URE5's control centers. WECC determined that the scope of the violation included all WECC_URE5 CCAs. Compliance with CIP-007-1 R3 requires entities to assess and document all security patches within 30 days of availability. WECC determined that WECC_URE5's failure to document its assessment of certain types of patches for any Cyber Assets within the ESP constitutes a violation of CIP-007-1 R3. | CIP-007-1 | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Report | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-007-1 R3. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009235 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC citing it was in violation of CIP-006-1 R1.8. More specifically, WECC_URE5 reported that it failed to afford all security measures prescribed under CIP-006-1 R1.8 to Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP). WECC reviewed WECC_URE5's Self-Certification and found that WECC_URE5 failed to document its assessment of certain types of security patches and upgrades for Cyber Assets while provisioning its PSP access control and monitoring system within 30 days of availability, as required in CIP-007-1 R3. WECC found WECC_URE5 in violation of CIP-006-1 R1.8 because WECC_URE5 failed to implement the protective measures described under CIP-007-1 R3 to Cyber Assets used in the access control and monitoring of the PSP. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. Lastly, WECC_URE5 failed to implement a single security measure out of 27 required by CIP-006-1 R1.8 by not documenting its assessment of patches. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Certification | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-006-1 R1. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program as a mitigating factor in the penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009233 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC citing it was in violation of CIP-005-1 R1.5. More specifically, WECC_URE5 reported that it failed to afford all security measures prescribed under CIP-005-1 R1.5 to Cyber Assets used in access control and monitoring for the Electronic Security Perimeter (ESP). WECC reviewed the Self-Certification and found that WECC_URE5 failed to document its assessment of certain types of security patches for Cyber Asset provisioning of the access control and monitoring to the ESP, in violation of CIP-005-1 R1.5. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. Lastly, WECC_URE5 failed to implement a single security measure out of 26 required by CIP-005-1 R1.5 by not documenting its assessment of patches. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Certification | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-005-1 R1. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program as a mitigating factor in the penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201000231 | Settlement Agreement | MRO_URE1 self-reported a violation of CIP-006-2 R2 because it failed to retain and review logs for Cyber Assets that authorize and/or log access to the Physical Security Perimeters (PSPs) as required by R2.2 and associated Standards referenced within the Requirement (CIP-007-2 R6.4 and CIP-005-2 R3.2). Additionally, MRO_URE1 reported that it failed to document a change per associated Standard CIP-003-2 R6 to a Cyber Asset that authorizes and/or logs access to PSPs. MRO_URE1 engaged a third-party consultant to conduct a compliance evidence review of its NERC CIP documentation. MRO_URE1 reported that the log retention sub-requirement of CIP-007-2 (R6.4) had not been fully met for the LAN controller at a control center for twenty days. In addition, MRO_URE1's internal investigation found that the log review sub-requirement of CIP-005-2 (R3.2) had not been fully met for the LAN controller at a control center for three and a half months. MRO_URE1 conducted a thorough investigation which verified that logs exist on the device and the log history going back to April 20, 2010 was recovered. As a result, a log review was completed which included the period from when the log history was recovered to when the log review was completed. Additionally, MRO_URE1 re-configured the servers for the LAN controllers that control access to MRO_URE1's PSP. This change involved logically moving the LAN controller that controls access to the PSP at the control center from one server to another server. With this change, the second server now includes all LAN controllers which control access to MRO_URE1's PSPs. During the compliance evidence review conducted with a third-party consultant, MRO_URE1 discovered that this change was not documented in accordance with MRO_URE1's documented change control and configuration management procedure. | CIP-006-2 | R2.2 | Medium | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or the reliability of the bulk power system (BPS) because this violation related to the failure to retain and review certain logs and there were other layered defenses at MRO_URE1's control center that provided security to detect unauthorized access. While the failure to properly test and document a change in the pre-production environment could affect MRO_URE1's physical access control system by allowing unauthorized access or a change to existing cyber security controls on the LAN controller servers, MRO_URE1's control center building is staffed, partially surrounded by a security fence and the entire facility is protected by card readers. The PSP is located inside the alarmed perimeter. Additionally, entry into the control center computer room would have been detected by an active motion detector alarm system in the room. This system is also monitored continuously by MRO_URE1's security. The motion detector alarm system is partitioned separately from that of the building perimeter alarm system. MRO_URE1 took proper corrective actions immediately upon identifying the concern with failure to review logs. While MRO_URE1 did not have logs available for review about twenty days, it was able to identify the logs starting after that and performed reviews per the requirements which did not reveal any unauthorized access attempts. Additionally, MRO_URE1's failure to document the change related to the LAN controller servers’ configurations was a one-time change. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Self Report | 1. MRO_URE1 reconfigured the logging of remote interactive access for the LAN controllers that control access to MRO_URE1's PSPs to take place on the second server. The MRO_URE1 Physical Security Plan was updated to include the quarterly review of the second server logs. 2. Security improvements were made for remote interactive access to the LAN controllers that control access to MRO_URE1's PSP. The firewall that provided access control to the LAN controller at a control center was reconfigured to only allow remote interactive access from the second server. As part of the server login process, the user's login identity is captured and the user is required to explain why they are logging into the system. 3. The event application was reconfigured to provide the reporting function. 4. The security manager met with the IT supervisor for training on the use of the change control and configuration management procedure. | 2011-02-24 | 2011-03-18 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100275 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO determined that while MRO_URE1 had established and documented a change control and configuration management procedure for adding, modifying, replacing, or removing Critical Cyber Asset (CCA) hardware or software, MRO_URE1 was not consistently following its procedure. MRO examined files provided by MRO_URE1 to assess alignment with MRO_URE1's documented change control and configuration management procedure and determined that some change request forms were incomplete, their use was inconsistent, and in some cases the information provided on them lacked the specificity needed to determine compliance. For example, MRO reviewed a change to the inter-control center communications protocol (ICCP) node. The corresponding ticket for this change did not include reference to the ICCP primary node in the hardware listings. Additionally, the ticket showed an implementation date of more than five months after the change was made to the ICCP node. In addition, MRO_URE1's documented procedure requires “sign off” upon implementation of requested changes. MRO observed several instances where “sign off” was not noted, even months after a request was approved. MRO observed that in some instances, the change control request forms included a detailed list of individual CCAs subject to changes, whereas other change control request forms did not identify which individual CCAs were subject to changes. Without the detailed list of individual CCAs subject to changes, it was not possible to determine which among a group of CCAs on a single change request form had undergone a requested change, and which had not. The differences in how the change control request forms were completed were illustrative of internal inconsistencies. In the first instance, where detailed lists were included and individual CCA devices were checked off, the documentation evidences that MRO_URE1's procedures were followed. In the second instance, where the change control request forms did not identify the individual CCAs or indicated “sign off” upon completion of the change, the documentation does not evidence that MRO_URE1's procedures were followed. | CIP-003-1 | R6 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or reliability and operability of the bulk power system (BPS). While the failure to properly manage changes to cyber security controls could possibly render one or many Critical Assets inoperable, in this instance MRO_URE1 had a compliant procedure and was able to evidence that it was following it for some changes to cyber security controls. MRO_URE1 maintained that it followed the procedure, but was not able to provide sufficient documentation to support that the procedure was followed in every instance. MRO_URE1 uses a phased approach in implementing changes on its system to better ensure that changes do not adversely affect the security of the control systems or reliability and operability of the BPS. MRO considered the failure to demonstrate consistent application of its procedure to manage changes to cyber security controls as demonstrating a need for training within MRO_URE1's staff. MRO expedited the mitigation of this violation to address concerns with testing and change management and worked with MRO_URE1 to implement an effective Mitigation Plan to strengthen its internal controls even before the CIP Spot Check report was finalized. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 reviewed and updated the change control and configuration management procedure and supporting documentation. 2. MRO_URE1 trained all applicable staff on the procedure including completeness of forms and log entries, consistent use, and required granularity for content. 3. MRO_URE1 implemented a review process to ensure consistent application of the change control and configuration management procedure. | 2011-09-07 | 2011-09-20 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100276 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain that MRO_URE1 had ensured that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. MRO_URE1's Energy Management System and backup Energy Management System systems security management plan describes the security management plan for Critical Cyber Assets (CCAs). This plan includes required actions to be taken to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter(s) do not adversely affect existing cyber security controls. The Energy Management System support group is responsible for ensuring that the installation of new Cyber Assets and significant changes to existing Energy Management System support group assets do not adversely affect cyber security controls. At a minimum, significant changes include security patches, service packs, vendor releases and version upgrades. While MRO_URE1 had a documented procedure to ensure system cyber security, MRO noted that the evidence to demonstrate that the required testing was conducted was not sufficient. MRO_URE1 maintained that the required testing was conducted according to its documented procedure, but MRO was not able to verify this with the documentation provided. | CIP-007-1 | R1.1 | Medium | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or the reliability and operability of the bulk power system (BPS). In making this determination, MRO considered that MRO_URE1 had a documented procedure and maintained that it was following the procedure when implementing changes. MRO_URE1 was able to provide documentation of changes implemented, but MRO was not able to verify that the required testing was completed upon implementation of changes to CCAs to ensure changes did not adversely affect cyber security controls. However, MRO was not able to verify the extent of this testing based on the provided documentation. MRO expedited the mitigation of this violation to address concerns with testing and change management and worked with MRO_URE1 to implement an effective Mitigation Plan even before the CIP Spot Check report was finalized. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 developed changes to the existing test documentation for CCAs to generate the depth of evidence and test results required for an Audit. 2. MRO_URE1 developed a testing worksheet that provides the tester a means to develop, execute and document a test plan and test results for CCAs. 3. MRO_URE1 tested, approved and implemented the revised test documentation and testing worksheet. 4. MRO_URE1 updated, tested, approved and implemented the revised supporting test documentation. | 2011-08-30 | 2011-09-06 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100278 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain that MRO_URE1 had established, documented and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). MRO_URE1’s Energy Management System and backup Energy Management System systems security management plan describes the security management plans for MRO_URE1's Critical Cyber Assets (CCAs). This plan includes required actions to be taken to ensure that a security patch management program is established, documented and implemented, and that cyber security patches for all Cyber Assets and assets supporting Cyber Assets are tracked, evaluated, tested and installed as applicable. MRO determined that MRO_URE1 relies on its vendor to provide a security patch list on a monthly basis. MRO_URE1's Energy Management System support group reviews each vendor patch for applicability and then determines an implementation plan. The review is conducted within thirty days of receipt of the monthly security patch list from the vendor, and the review is documented in the IT system change log as required in MRO_URE1's security management procedure. MRO determined that for certain applications or systems supported by MRO_URE1, a process was not in place to review security patches within thirty days of availability. | CIP-007-1 | R3.1 | Lower | Severe | MRO determined that the violation posed moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to evaluate patches and apply them in a timely manner to CCAs presents opportunities for exploitation of unpatched vulnerabilities which could render one or many CCAs inoperable. This risk was mitigated by the fact that MRO_URE1 was utilizing a vendor service which identified and evaluated newly available security patches for MRO_URE1's Energy Management System and backup Energy Management System critical and supporting Cyber Assets. Additionally, the service utilized by MRO_URE1 to identify and evaluate newly available security patches covered the majority of software installed on MRO_URE1's CCAs. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 completed inventory of software on all Cyber Assets. 2. MRO_URE1 identified software not covered by the existing security patch management program. 3. MRO_URE1 determined which applications were known to be safe for removal. 4. MRO_URE1 removed identified software from Cyber Assets. 5. MRO_URE1 identified and evaluated security patch availability for remaining software. 6. MRO_URE1 updated, tested, approved and implemented revised security patch management procedures. | 2011-08-15 | 2011-09-08 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100280 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain whether authorized exceptions to MRO_URE1's cyber security policy were reviewed and approved annually by the senior manager or delegate to ensure the exceptions were still required and valid. MRO was not able to determine if exceptions documented in 2008 were terminated or converted to Technical Feasibility Exceptions within a year of approval. The evidence provided to MRO did not demonstrate that documented exceptions from 2008 were closed prior to the annual review or reviewed in 2009 or 2010. | CIP-003-1 | R3.3 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because the violation is an administrative issue, dealing with proper documentation of cyber security policy exceptions and their review. While there was no evidence to demonstrate that documented exceptions had been reviewed, there was no concern with the exceptions or the compensating measures in place for any documented exception. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 re-evaluated documented exceptions. 2. MRO_URE1 received senior manager review and approval of required exceptions or attestation of no exceptions. | 2011-11-30 | 2012-01-16 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100281 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain whether MRO_URE1 conducted a review of access privileges to protected information for two years. MRO reviewed several policy and procedure documents which included entries relating to annual review in the version history section of the documents; however, none of these documents represented the access privileges list. MRO also reviewed notes from several meetings indicating that approvals took place, but it was not clear what exactly was being approved. Based on the information provided, MRO determined that there was not sufficient evidence to demonstrate that MRO_URE1 reviewed access privileges to protected information for two years. | CIP-003-1 | R5.2 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because the violation is an administrative issue, dealing with proper documentation of reviews of access privileges to protected information. MRO_URE1 maintains that the reviews were conducted, and there are several documents referencing annual reviews and access privileges; however, the documentation is not complete and does not expressly indicate that the annual review of access privileges was conducted. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 reviewed and updated the access control program. 2. The MRO_URE1 cyber security team reviewed associated documents. 3. A MRO_URE1 compliance committee reviewed and approved associated documents. 4. MRO_URE1 documented completion of the required annual review. | 2011-12-27 | 2012-01-17 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100282 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO determined that MRO_URE1 failed to demonstrate that a list of sufficient detail is maintained that documents individuals’ specific electronic and physical access rights. MRO determined that only a limited number of MRO_URE1 personnel were aware of what privileges were actually granted through membership in various active directory groups. The privileges assigned to these groups were not clearly documented. Additionally, MRO_URE1 failed to demonstrate that quarterly reviews are sufficient to verify the appropriateness of individuals’ physical and cyber access privileges. | CIP-004-1 | R4.1 | Lower | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while inadequate management of access privileges may result in personnel retaining inappropriate levels of access after a job change or termination, MRO_URE1 had documented procedures in place to ensure that its CIP personnel list was being reviewed and updated as required, and was conducting the reviews. Additionally, the individuals on the list were properly qualified but the list failed to identify specific electronic access rights. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 modified existing procedures used to assign and review electronic access rights, including reviews of active directory accounts, active directory group privileges and verification of information. 2. MRO_URE1 verified privileges, verified the appropriateness of existing active directory group privileges and their membership using modified procedures. 3. MRO_URE1 approved and implemented modified procedures for electronic access rights. | 2012-02-02 | 2012-02-06 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100283 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to determine that MRO_URE1 reviewed, updated, and maintained all documentation to support the annual reviews required by CIP-005-1 R5.1. MRO observed that MRO_URE1 had not ensured that all documentation required by CIP‐005 had been reviewed, updated and maintained on an annual basis. Specifically, MRO identified a document which did not evidence that it had been reviewed annually and did not appear to be subject to versioning controls. Also, a second document did not evidence that it had been reviewed annually and did not appear to be subject to versioning controls. | CIP-005-1 | R5.1 | Lower | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while MRO_URE1 was not able to evidence a small number of documents had been reviewed, evidence was available for the majority of the documents examined. Additionally, the finding is not that any procedures were lacking, but that there was no evidence that a small number of those procedures were being reviewed on an annual basis. This violation is an administrative violation that relates to properly documenting review of policies and procedures. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 formalized the annual documentation review process. 2. MRO_URE1 completed training for all standard owners. 3. MRO_URE1 conducted annual review of all policies referenced in CIP documentation and security management. 4. MRO_URE1 completed annual review for CIP-005 documents. | 2011-09-20 | 2011-09-27 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100284 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO observed that MRO_URE1's Physical Security Plan was not adequately maintained and that not all in‐scope identified Physical Security Perimeters (PSPs) incorporated a completely enclosed six‐wall border as required by CIP-006-1 R1.1. MRO found several inconsistencies in the version of the Physical Security Plan that was in effect at the time of the CIP Spot Check. The text of the document did not accurately reflect the controls that were actually implemented, nor was it internally consistent with other portions of the content. MRO determined that this version of the Physical Security Plan contained errors with regard to a control center. The location of a LAN controller was incorrectly shown on the diagram, and the visitor log book located at the door to the parking lot was not documented. Further, this version of the Physical Security Plan contained errors with regard to a second control center. The diagram for the second control center's computer room and communications room did not identify the two rooms as part of the PSP, nor did the diagram indicate that each room's door had a proximity card reader. The two rooms were misidentified, and there were no indications of where the alarm system components were located. The Physical Security Plan documented the procedures used to log visitor entry and exit. According to the document, visitors to the first control center were required to sign in and out using one of two specific log books. Based on interviews, however, visitors could sign in and out using any one of the log books located at six of the seven designated access points. During a tour of the first control center, it was determined that the seventh access point (parking lot door) also had a visitor log. The plan did not reflect the arrangement of visitor log books at the time of the tour. In the second control room's computer room, a square opening was found. The opening allowed passage from the uninterrupted power supply room to the second control room's computer room, bypassing PSP access controls. The opening was cut for HVAC work. The HVAC work had been suspended on the next day to facilitate the MRO Spot Check and to ensure safety of personnel while onsite. Prior to leaving the site, the contractor failed to properly cover the new duct opening due to miscommunication regarding what type of covering was needed. The contractor had assumed the covering was for dust control, and had not understood the need for a completely enclosed (six-wall) border. Upon identification of the opening during the walkthrough the local contractor was immediately contacted and the opening was properly closed before the MRO auditors left the site. The auditors observed and documented the mitigation. | CIP-006-1 | R1.1 | Medium | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while the unprotected opening in the six-wall perimeter allowed direct access to Critical Cyber Assets (CCAs) and the Electronic Security Perimeter (ESP), there were other mechanisms in place to monitor and limit access. The building is staffed, partially surrounded by a security fence, and the entire facility is protected by card readers. Security records show that the second control center was staffed until 21:06 on the day the HVAC work began at which time the security system was armed. The ESP is located inside the alarmed perimeter. The second control center remained armed and was continuously monitored by MRO_URE1's security department until 06:38 on the next day. MRO_URE1 staff were on-site from that time until the opening was secured. In addition, if, during the period when the building was unstaffed, an individual would have somehow managed to gain access to the building, entry into the second control center's computer room would have been detected by an active motion detector alarm system in the room. This system is also monitored continuously by the MRO_URE1 security department. The motion detector alarm system is partitioned separately from that of the building perimeter alarm system. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. The opening in the wall between the uninterrupted power supply room and the computer room was properly closed on the day the HVAC work was suspended while the MRO Audit staff was onsite. 2. The floor plans in MRO_URE1's Physical Security Plan were updated to reflect accurate representation of where the equipment, logs, and boundaries are located. 3. The Physical Security Plan was reviewed for accuracy, updated to eliminate any inconsistencies, and the plan was reviewed and approved. | 2011-02-24 | 2011-07-22 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102918 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-002-1 R3. In its Self-Report, WECC_URE1 stated that its Critical Cyber Asset (CCA) inventory was incomplete because it did not include primary PC-integrated devices. WECC_URE1 stated that it failed to identify one Cyber Asset, essential to the operation of another Critical Asset, as a CCA. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, the device in scope was located inside of an Electronic Security Perimeter and Physical Security Perimeter (PSP), which was subject to the protections required by CIP-005 and CIP-006. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Mitigation Plan completion | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | A complete review and assessment of the Critical Asset inventory and configuration per CIP-002 R3 was completed and corrected for the WECC_URE1's devices. The missing device was added to the inventory one week after the Self-Report and updated six weeks later. Unique device identifiers have been created for each device in the inventory for ease of tracking in data collection and oversight in the compliance activities. | 2011-08-15 | 2012-05-07 | Agrees
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102919 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-005-1 R2. In its Self-Report, WECC_URE1 stated that it performed an incomplete review of its ports and services. WECC_URE1 stated that for two access points on its Electronic Security Perimeter (ESP), it failed to ensure that only those ports and services required for normal operation were enabled. The access points WECC_URE1 identified are firewalls that control access to two of WECC_URE1's ESPs. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, controls were implemented to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Date of revised procedure and training | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | WECC_URE1 revised its critical infrastructure protection program procedure to evaluate and assess ports and services for firewalls and switches in order to better clarify the process, and training was completed. Unique device identifiers have been created for each device for ease of tracking in data collection. A review of the ports and services for the firewalls in question was also completed. | 2011-12-31 | 2012-05-07 | Agrees
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102920 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-007-1 R2. In its Self-Report, WECC_URE1 stated that it performed an incomplete review of its ports and services. WECC_URE1 stated that for thirteen Cyber Assets, WECC_URE1 failed to ensure that only those ports and services required for normal operation were enabled. The Cyber Assets are network switches and workstations used for physical access monitoring. | CIP-007-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, controls were implemented to log and monitor access to all Cyber Assets within the Electronic Security Perimeter (ESP). Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Date of revised procedure and training | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | WECC_URE1 revised its critical infrastructure protection program procedure to evaluate and assess ports and services for firewalls and switches in order to better clarify the process, and training was completed. Unique device identifiers have been created for each device for ease of tracking in data collection. A review of the ports and services for the switches in question was also completed. The remaining ports and service review for network switches and work stations involved in the violation were performed by scans. | 2011-12-31 | 2012-05-07 | Agrees | WECC considered WECC_URE1's compliance history.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008702 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R5. WECC_URE2 reported that it failed to implement a process consistent with CIP-007-1 R5.2 and failed to identify those individuals with access to shared accounts pursuant to CIP-007-1 R5.2.2. WECC subject matter experts (SMEs) reviewed WECC_URE2's Self-Report and contacted the entity to request additional information. In response to queries from the SMEs, WECC_URE2 provided a list of individuals with electronic access to Critical Cyber Assets (CCAs) and Cyber Assets within the Electronic Security Perimeter (ESP) who had not been previously identified. Based on this information, SMEs found that WECC_URE2 failed to identify three individuals with access to a total of seven shared accounts. Further, the SMEs determined that these shared accounts provided access to approximately 29 Cyber Assets and CCAs associated with two WECC_URE2 Critical Assets, the control center and backup control center. WECC Enforcement determined that WECC_URE2 failed to identify three individuals with access to shared accounts, in violation of CIP-007-1 R5.2.2. | CIP-007-1 | R5; R5.2.2 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given the existing compensating measures in place during the violation period. Each of the three individuals in question had completed training and personnel risk assessments pursuant to CIP-004. Further, such access was necessary for each individual in the course of performing their regular job-related duties. Cyber Assets and CCAs accessed through these seven, shared accounts were all secured with Physical Security Perimeters and ESPs. Lastly, all access to CCAs and Cyber Assets within an ESP through these shared accounts was documented. | when WECC_URE2 failed to identify the individuals with access to the shared accounts | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and of the individuals that have access to the accounts that addresses the requirements of CIP-007 R5.2.2. WECC_URE2 also documented and implemented a new process designed to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process included provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2 process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-04-09 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008703 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-006-1 R1.8. WECC_URE2 reported that it had failed to afford all security measures prescribed under R1.8 to Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP). WECC Subject Matter Experts (SMEs) reviewed WECC_URE2's Self-Report and found that WECC_URE2 failed to identify individuals accessing shared user accounts to Cyber Assets used in PSP access control and monitoring. The SMEs found that WECC_URE2 failed to identify 11 individuals with access to shared accounts. WECC Enforcement determined that WECC_URE2's failure to implement protective measures described under CIP-007-1 R5 to Cyber Assets involved in PSP access control and monitoring, constituted a violation of CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given compensating measures in place during the violation period. Each of the 11 individuals with access to shared accounts completed training and personnel risk assessments described under CIP-004. Further, electronic access to devices using shared accounts was logged and monitored. | date Standard became mandatory and enforceable | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and the individuals that have access to the accounts that addresses the requirements of CIP-007 R5.2.2. WECC_URE2 also documented and implemented a process to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process includes provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2's process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-05-08 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty. Based on the NERC Sanction Guidelines, WECC determined the violations of CIP-006-1 R1 and CIP-007-1 R5 were related to a single act or common incidence of non-compliance for which WECC would assess a single aggregate penalty.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008705 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-005-1 R1. WECC_URE2 reported that it had failed to afford all security measures prescribed under R1.5 to Cyber Assets used in access control and monitoring of the Electronic Security Perimeter (ESP), specifically one security measure per CIP-007-1 R5 that requires entities to identify individuals with access to shared accounts. WECC subject matter experts (SMEs) found that WECC_URE2 failed to identify individuals accessing shared user accounts to Cyber Assets used in ESP access control and monitoring. SMEs determined that three individuals were not identified as having access to shared accounts provisioning access to three ESP access points. WECC Enforcement determined that CIP-005-1 R1.5 incorporates protective measures described in CIP-007-1 R5 by reference. WECC Enforcement determined that WECC_URE2's failure to list individuals with access to shared accounts for ESP devices pursuant to CIP-007-5 R5 constituted a violation of CIP-005-1 R1.5. | CIP-005-1 | R1; R1.5 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given the existing compensating measures in place during the violation period. Each of the three unidentified individuals with access to shared accounts completed a personnel risk assessment and cyber security training under CIP-004. Further, access by these individuals using shared accounts was logged and monitored. All Critical Cyber Assets and Cyber Assets were secured within ESPs and Physical Security Perimeters. | date Standard became mandatory and enforceable | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and the individuals that have access to the accounts that meets CIP-007 R5.2.2. WECC_URE2 also documented and implemented a process to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process includes provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2's process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-05-03 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty. Based on the NERC Sanction Guidelines, WECC determined the violations of CIP-005-1 R1 and CIP-007-1 R5 were related to a single act or common incidence of non-compliance for which WECC would assess a single aggregate penalty.
2012-05-30 | FERC | NP12-26-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100249 | Notice of Confirmed Violation | During a CIP Spot Check, MRO determined that MRO_URE1 failed to provide evidence of recovery plans for every Critical Cyber Asset (CCA), as required by CIP-009-1 R1. MRO_URE1 provided evidence of a general recovery plan for all assets, which included disaster recovery and failover to the backup control center and backup systems, and also transfer to a backup center and recovery of the system in general. However, the plan did not include plans for recovering each CCA. | CIP-009-1 | R1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. Although MRO_URE1's recovery plan did not include documented procedures for recovery of each CCA individually, it did address disaster recovery and transfer to a backup center and recovery system. MRO_URE1 also has a support agreement with an established Energy Management System vendor for recovery support, including device recovery. Additionally, the recovery plan was tested annually via table top exercises. | When the Standard became mandatory and enforceable for MRO_URE1 | When MRO_URE1 completed its mitigation plan | 6000 | Spot Check | MRO_URE1 has completed the following mitigation activities: (1) updated its recovery plan to include procedures for every type of Critical Asset (and each CCA) as required by the Standard; and (2) reviewed, approved, and implemented its recovery procedures. | 2011-09-09 | 2011-10-05 | Admits | MRO considered MRO_URE1's internal compliance program, in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007731 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-2 R3 because it did not perform a manual 90-day review for unauthorized electronic access to the server associated with the physical security system. | CIP-005-2 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the existing physical and electronic controls in place. Specifically, the physical security system server could only be accessed from dedicated physical security control system personal computers that are within the Electronic Security Perimeter and Physical Security Perimeter. Further, a corporate user ID and password is required, and the user must be listed as an active user of the system to have authorization to use the program. There were no instances of unauthorized access in the timeframe of the violation. | When NPCC_URE1 should have reviewed the access logs | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) In the NPCC_URE1 calendar, a monthly pop-up reminder was created to remind administrator and manager to review the monthly server access reports for instances of unauthorized access; and (2) In the NPCC_URE1 calendar, a quarterly pop-up reminder was created to remind a manager, administrator, and appropriate department to perform a quarterly review to ensure that the monthly reviews were completed as described in item (1), above. The quarterly reminder also reminds the recipients to file evidence of the completed quarterly review with the department. | 2011-03-22 | 2011-10-14 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007732 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5 because the passwords associated with several accounts did not meet the requirements of the Standard. Specifically, the NPCC_URE1 physical security system had three shared default accounts associated with IT administration of the physical security system. Each of these three accounts had permissions allowing them to perform any function within the system, in violation of R5.2.1. The passwords associated with each of the accounts were not changed since placing the system into service, in violation of R5.3.3. In addition, the passwords did not meet the strong password requirements of R5.3.2. Further, there were four instances associated with individual IT accounts where the passwords of the users' physical security system were not changed at least annually, in violation of R5.3.3. In two of those instances, the passwords did not consist of a combination of alpha, numeric and special characters, as required by R5.3.2. | CIP-007-1 | R5; R5.2.1; R5.3.2; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the existing electronic access/account controls. Specifically, the user must obtain access to NPCC_URE1's parent company's domain via an active directory account, then must satisfy the requirements of the secure network device (user name, PIN and password) to gain access to the icon associated with the physical security system. The user then clicks on the physical security system icon and enters his or her physical security system user ID and password. There were no instances of unauthorized access associated with the shared accounts in the timeframe of the violation. | When the Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) Disabled two of the three shared accounts previously used by IT administrators. Only one shared account will remain as the hierarchy default account for emergency use; (2) Changed the password associated with the one account to meet strong password requirements. This account will now be used as an emergency administrator account only. A specific manager has the responsibility to ensure that the password associated with the hierarchy account is updated every April. A reminder has been added to the calendar to ensure that this will occur every April and that the appropriate department is notified; and (3) Reset the passwords of the four individual IT accounts, and implemented the functionality of the physical security system to automatically require that passwords associated with individual accounts be changed every 90 days and that the user creates a strong password. | 2011-07-26 | 2011-10-18 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008068 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5 because it failed to properly identify individuals with access to shared accounts. Specifically, the shared account password to operate a certain type of personal computer (PC) at a number of Critical Asset substations was being shared by substation personnel who required the password to perform their job responsibilities. Personnel were obtaining the password from other substation personnel in an informal manner without coordinating this release with the password administrator. This resulted in the Electronic Security Perimeter (ESP) access list for the PCs not being updated as these individuals gained access, as required by R5.2.2. | CIP-007-1 | R5; R5.2.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the individuals that were obtaining the password in the "shared" fashion required the password to perform their normal job duties. Such personnel would have been given the password had the appropriate administrator been contacted, as personnel risk assessments and cyber security training had already been completed on the substation personnel. In addition, the PC is inside of the Physical Security Perimeter at the substation, so only authorized personnel or those with proper escort can gain access. | When the Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) Changed the single password associated with the PC shared account; (2) Re-trained all substation management, operators and technicians on the expectations and proper use of the PC shared password account and overall corporate password policy. The procedure documenting the appropriate use of shared passwords was already in existence prior to this violation; (3) Revised the corporate master access list to include a column associated with the substation PC shared account. This list is used by corporate IT during their monthly corporate access reviews; and (4) Revised the substation master list to include a column associated with the PC access for substation personnel. This list is used by substations to track the types of access to all substation personnel. | 2011-11-17 | 2011-12-08 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007269 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-005-1 R1.5 to NPCC. During an internal audit review of NPCC_URE2’s NERC CIP compliance program conducted, NPCC_URE2 discovered that, due to an oversight, it had not properly identified all Electronic Security Perimeter (ESP) access control and monitoring assets. Specifically, ten devices were not properly classified as access control and/or monitoring devices and therefore were not included in the NERC CIP compliance program. As a result of this identification failure, these assets were not afforded all of the protective measures required by R1.5. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined ESP and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 3) Security event logging and network intrusion detection. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Updated its NERC CIP asset list to include the ESP access control and monitoring assets that were previously missing from the list; 2. Conducted internal analysis to identify the required controls for each asset added to the list; 3. Implemented the required controls on each asset; 4. Tracked the implementation of each control for each asset via a tracking spreadsheet; and 5. Performed a final review of the tracking spreadsheet to ensure that the control for each asset was in fact implemented in the proper fashion. | 2011-11-30 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor. NPCC considered that NPCC_URE2 completed the Mitigation Plan after the approved completion date. NPCC determined that no adjustments to the penalty were warranted because the entity was completing related work under a separate Mitigation Plan that followed a different timeline and NPCC was aware of the revised timeframe.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007270 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R3. During an internal audit review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered that, due to an oversight, it did not include several Cyber Assets in the security patch management program. | CIP-007-1 | R3 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined Electronic Security Perimeter (ESP) and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Anti-virus, where technically feasible; 3) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 4) Security event logging and network intrusion detection. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Removed certain devices from the ESP that were not in the patch management program; 2. Identified additional assets within the ESP to include in the patch management program; 3. Developed a patch management process flow diagram; 4. Developed tracking spreadsheets for additional assets; and 5. Reviewed all previous security patches for the additional assets that were added to the NERC CIP patch management program. | 2011-12-23 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007271 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-006-1 R1.8 to NPCC. During an internal review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered that, due to an oversight, it had not properly identified or included the Cyber Assets associated with the physical access control system on the Critical Cyber Assets (CCA) list. Thus, the physical access control system was not provided all of the protective measures required by R1.8. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined Electronic Security Perimeter (ESP) and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 3) Security event logging. In addition, NPCC_URE2 did not experience any cyber security-related events involving these assets. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Identified nine additional assets that must be included on the CCA list, including the physical access control system server and eight panels; 2. Conducted internal analysis to identify the required controls for each asset and created a tracking spreadsheet to monitor the implementation of the controls; 3. Updated the CCA list; 4. Implemented the required controls on each asset; and 5. Performed a final review of the tracking spreadsheet to ensure that the control for each asset was implemented correctly. | 2011-11-30 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor. NPCC considered that NPCC_URE2 completed the Mitigation Plan after the approved completion date. NPCC determined that no adjustments to the penalty were warranted because the entity was completing related work under a separate Mitigation Plan that followed a different timeline and NPCC was aware of the revised timeframe.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007272 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R1.1 to NPCC. During an internal review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered, due to an oversight, the lack of a documented cyber security testing procedure specific to verifying that changes made to existing Critical Cyber Assets (CCAs) did not adversely affect that same CCAs' security controls. | CIP-007-1 | R1; R1.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 has implemented and adheres to a comprehensive change management procedure that includes extensive testing and validation of changes to the CCAs prior to going into a production environment. NPCC_URE2 had a documented corporate change management procedure in place, while not specific to CCAs, was applied to all assets. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Developed and implemented a cyber security controls testing procedure to validate and document that existing cyber security controls are not adversely impacted when significant changes are made to CCAs, which was shared with all relevant employees; and 2. Provided documented cyber security test results for CCAs. | 2011-12-23 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100854 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF indicating a violation of CIP-009-1 R1. RFC_URE1 did not include 46% of its Critical Cyber Assets (CCAs) in its recovery plan, as required by CIP-009-1 R1.1. RFC_URE1’s recovery plan did not specify events or conditions of varying duration and severity that would activate the recovery plan, pursuant to CIP-009-1 R1.1. Additionally, RFC_URE1’s recovery plan did not define all of the roles and responsibilities of responders, as required by CIP-009-1 R1.2. RF determined that RFC_URE1 violated CIP-009-1 R1 when it did not include all of its CCAs within its recovery plan and did not address the requirements of CIP-009-1 R1.1 and R1.2 within its recovery plan. | CIP-009-1 | R1 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, RFC_URE1 addressed responding to events of varying duration and severity within its CIP-008 Cyber Security Incident response plan. Similarly, RFC_URE1 addressed the roles and responsibilities of responders within its CIP-003 cyber security policy. Additionally, RFC_URE1 represents that the information that was not specifically stated within its recovery plan was readily available to authorized RFC_URE1 personnel responding to an event requiring the recovery of CCAs. | When RFC_URE1 was subject to compliance with CIP-009-1 R1 | When RFC_URE1 revised its recovery plan to comply with CIP-009-1 R1 | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Report | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-009-1 R1. In accordance with the Mitigation Plan, RFC_URE1 revised its recovery plan to specify events or conditions of varying duration and severity that would activate the recovery plan, defined the roles and responsibilities of responders, and included all of RFC_URE1’s CCAs. | 2011-01-28 | 2011-12-27 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount. RF also considered the fact that RFC_URE1 self-reported the violation, as a mitigating factor. Internal controls and Self-Reports of possible violations assist RF’s mission of improving the reliability of the BPS.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100922 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-005-1 R3 with RF. RFC_URE1's security monitoring process to detect and alert for unauthorized access attempts at two firewalls located on an Electronic Security Perimeter (ESP) was not properly configured. Specifically, RFC_URE1's security management software tool was configured to alert RFC_URE1 about unauthorized access attempts based upon a threshold frequency of access denials from a specific IP address. However, RFC_URE1 did not configure its two firewalls to report access denial events to the security management software tool. As a result, RFC_URE1's security logging and alerts would not have functioned correctly if there had been unauthorized access attempts to the firewalls. RF determined that RFC_URE1 violated CIP-005-1 R3.2 when it could not detect and alert for attempts at or actual unauthorized accesses to the ESP. | CIP-005-1 | R3.2 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the several factors. The firewalls on the ESP were configured to deny access by default, and therefore the Critical Cyber Assets (CCAs) within the ESP remained protected from unauthorized access attempts throughout the duration of the violation. Additionally, the security management software tool did log all permitted access attempts and firewall configuration changes. | When RFC_URE1 was subject to compliance with CIP-005-1 R3.2 | Date the firewalls were properly configured to log and report access denial events to the security management software tool | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-005-1 R3.2. In accordance with the Mitigation Plan, the firewalls at RFC_URE1 were properly configured to log and alert for denied unauthorized access attempts. | 2010-10-12 | 2012-02-09 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100923 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-007-1 R2 with RF. A network switch located inside the Electronic Security Perimeter (ESP) had ports and services that were not required for normal or emergency operations, but still enabled, in violation of CIP-007-1 R2. RF determined that RFC_URE1 violated CIP-007-1 R2 when it did not enable only those ports and services required for normal and emergency operations, and failed to disable other ports and services prior to production use of all Cyber Assets inside the ESP. | CIP-007-1 | R2 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the network switch is located behind the ESP firewall and is therefore not accessible from outside the ESP. | When RFC_URE1 was subject to compliance with CIP-007-1 R2 | Date the ports and services on the network switch were disabled | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-007-3 R2. In this Mitigation Plan, RFC_URE1 outlined the actions it took to mitigate the violation. RFC_URE1 disabled the ports and services that were enabled on the network switch. | 2010-11-19 | 2011-12-20 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100924 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-007-1 R5 to RF. RFC_URE1 did not remove or disable factory default accounts on a network switch pursuant to CIP-007-1 R5.2.2 (this network switch is also described in the violation of CIP-007-1 R2). In addition, these factory default accounts did not meet the password requirements of CIP-007-1 R5.3. Specifically, a network switch within the Electronic Security Perimeter (ESP) had factory default accounts that were not removed, disabled, or renamed. Additionally, passwords for the two factory default accounts were not created prior to placing them into service, and the passwords did not conform to the requirements of CIP-007-1 R5.3. RF determined that RFC_URE1 violated CIP-007-1 R5.3 when it did not manage the scope and acceptable use of factory default accounts and when it did not require and use passwords that conform to CIP-007-1 R5.3. | CIP-007-1 | R5; R5.2.2; R5.3 | Lower | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the network switch containing the two factory default accounts is located behind the ESP firewall and is therefore not accessible from outside the ESP. | When RFC_URE1 was subject to compliance with CIP-007-1 R5.3 | Date RFC_URE1 set complex passwords which comply with CIP-007-1 R5.3 for the two factory default accounts on the network switch | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-007-3 R5. In accordance with the Mitigation Plan, RFC_URE1 set complex passwords for the two factory default accounts on the network switch that conform to CIP-007-1 R5. | 2010-11-19 | 2011-12-20 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | SPP201000278 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | RFC201000366 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | TRE201000180 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | SPP200900156 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | RFC200900327 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | TRE201000225 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102977 | Notice of Confirmed Violation | WECC_URE1 self-certified noncompliance with CIP-005-3 R5. WECC_URE1 stated that it was in violation of the Standard because it failed to review the documentation specified in CIP-005-3 R5 in the calendar year. Specifically, WECC_URE1 identified that it failed to review documentation relating to: (1) establishing and maintaining Electronic Security Perimeters; (2) monitoring system events related to Cyber Security; (3) user account access activities; and (4) the manual retrieval of system account logs. | CIP-005-3 | R5 (R5.1.) | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. There were no changes to the four CIP-005 procedures in scope. Also, WECC_URE1 demonstrated that all Critical Cyber Assets (CCAs) are located inside Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs) and are afforded all the protections of CIP-005 and CIP-006. | the date by which WECC_URE1 should have reviewed the documentation) | TBD | $17,300 (for WECC201102977 and WECC201102983) | Self-Certification | WECC_URE1 will review the documents specified in CIP-005-3 R5. In addition, WECC_URE1 will research and implement a more robust NERC compliance administrative task tracking calendar system. | Anticipated 7/1/2012 | TBD | Does Not Contest | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination.
2012-04-30 | FERC | NP12-26-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102983 | Notice of Confirmed Violation | WECC_URE1 self-certified noncompliance with CIP-007-3 R9. WECC_URE1 stated that it was in violation of the Standard because it failed to review the documentation specified in CIP-007-3 in the calendar year. Specifically, WECC_URE1 identified that it failed to review the documentation for 29 CIP-007 procedures, which topics include: (1) change implementation; (2) anti-virus and malware prevention; (3) tests to produce when Cyber Assets are modified; (4) security patches; (5) risk assessment; (6) user account access activities; (7) shared accounts; (8) passwords; (9) asset disposal or redeployment requests; (10) data destruction; (11) security tests; and (12) ports and services. | CIP-007-3 | R9 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. There were no changes to the 29 CIP-007 procedures in scope and all Critical Cyber Assets are located inside Electronic Security Perimeters and Physical Security Perimeters and are afforded all the CIP-005 and CIP-006 protections. | the date by which WECC_URE1 should have reviewed the documentation | TBD | $17,300 (for WECC201102977 and WECC201102983) | Self-Certification | WECC_URE1 will review the documents specified in CIP-007-3 R9. In addition, WECC_URE1 will research and implement a more robust NERC compliance administrative task tracking calendar system. | Anticipated 7/1/2012 | TBD | Does Not Contest | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201000219 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-006-2 R5. NPCC determined that NPCC_URE1 did not implement the technical controls for monitoring physical access at all access points to the Physical Security Perimeter twenty-four hours a day, seven days a week, as required by the Standard. NPCC_URE1 failed to do this for two of its Critical Assets at two of its facilities. | CIP-006-2 | R5 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Moreover, the two assets at issue were in fact determined not to be Critical Assets. NPCC_URE1 completed a risk-based asset management (RBAM) study after having its Mitigation Plan approved and determined the two assets did not need to be part of the Critical Asset list. NPCC Enforcement verified the one-line diagram and agreed with the assessment. Lastly, there were no incidents at NPCC_URE1 facilities related to the lack of proper monitoring of physical access. | when the Standard became mandatory and enforceable to NPCC_URE1 | date Mitigation Plan was completed | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-006-2 R5. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer and plant personnel to better understand the best way to implement the Mitigation Plan; (2) scheduled conference calls with its telecommunications vendor to discuss various options and the expected timeframe for resolution (specifically, NPCC_URE1 attempted to install higher speed lines at each location to provide sufficient bandwidth to allow video and card reader access data combined with generation data); (3) scheduled installation and testing of satellite network, test camera and card reader functionality on the satellite line; (4) monitored continuous operations of alarms for two weeks; and (5) updated all relevant documentation associated with CIP-006 R5 and communicated those updates to all relevant staff. | 2011-04-28 | 2011-10-21 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201000220 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-002-2 R3. NPCC determined that NPCC_URE1 did not include the continuous emissions monitoring system on the list of Critical Cyber Assets (CCA) essential to the operation of the identified Critical Assets, as required by the Standard. The system (used as a means to comply with government air emission standards) is connected to the Critical Asset by serial communications, where a single stream of data is transmitted. NPCC_URE1 determined that due to the remote dial-up connectivity to this system, the asset would be identified as a CCA. | CIP-002-2 | R3 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 had developed a list of associated CCA essential to the operation of the Critical Asset and reviewed this list at least annually, and updated it as necessary. Also, the continuous emissions monitoring system has physical security control to the device and system logical access to the system is maintained, which provides additional security. There were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | when the violation was mitigated by updating all relevant documentation | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-002-2 R3. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) added the continuous emissions monitoring system to the CCA list; (2) interviewed the network engineer and applied the appropriate protective measures to the continuous emissions monitoring system equipment to conform to the CIP requirements; (3) required that all continuous emissions monitoring system equipment be afforded the protective measures required in the remaining CIP requirements; where any of the equipment cannot meet the standard, Technical Feasibility Exceptions will be submitted; (4) completed application of all relevant CIP requirements; (5) updated documentation relevant to CIP-002 R3 to ensure that it is in line with the requirements and establishes the expectations to maintain a state of compliance; and (6) all staff engaged in managing Cyber Assets within the ESP were notified of the changes and made aware of the requirements. | 2011-06-30 | 2011-10-25 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. For the CIP-002-2 R3 violation, mitigation activities were not completed by the approved due date, and no extension was requested. This delay was considered by NPCC to be an aggravating factor in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100247 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-006-2 R2. NPCC determined that NPCC_URE1 did not protect a server, a digital video recorder (DVR) and a personal computer (PC) from unauthorized physical access, as required by the Standard. These devices create badges; therefore they qualify as Cyber Assets that authorize and/or log access to the Physical Security Perimeter, and authorized access is needed for these devices to be considered access control and monitoring assets. | CIP-006-2 | R2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 documents and implements a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. NPCC_URE1 also implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Additionally, there were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | date Mitigation Plan was completed | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-006-2 R2. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer to better understand how best to implement the Mitigation Plan; (2) scheduled the protection of the Cyber Assets in accordance with CIP-006 R2.2; specifically, the server, DVR and PC were afforded all protections required in accordance with the Standard, and in instances where it is not technically feasible the appropriate TFE submittals will be made; (3) updated all documentation relevant to CIP-006 R2.2 to ensure that it is in line with the Standard and establishes the expectations to maintain a state of compliance; and (4) all staff engaged in managing Cyber Assets within the ESP were notified of changes and made aware of the requirements. | 2011-07-29 | 2011-10-25 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. NPCC considered NPCC_URE1's and its affiliates' compliance history.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100248 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-007-1 R2. NPCC determined that NPCC_URE1 did not disable unused ports prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP), as required by the Standard. The cause of the violation was NPCC_URE1's misunderstanding that the unused ports and services needed to be disabled on each Cyber Asset within the ESP. The unused ports were shut down on the firewalls, but not the specific Cyber Assets. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 has processes and procedures for securing those systems determined to be Critical Cyber Assets, as well as the non-critical Cyber Assets within the ESP. NPCC_URE1 also implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Additionally, there were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | when the violation was mitigated by updating all relevant documentation | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-007-1 R2. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer to better understand how best to implement a Mitigation Plan; (2) reviewed each Cyber Asset within the ESP to determine the existing ports and services that are not currently disabled; (3) scheduled the disabling of all unused ports and services; (4) disabled all unused ports and services on each Cyber Asset within the ESP, or, if they could not be disabled for operational reasons, NPCC_URE1 documented the compensating measures applied to each Cyber Asset in order to mitigate the risk; (5) updated all documentation relevant to CIP-007 R2 to ensure that it is in line with the Standard and establishes the expectations to maintain a state of compliance; and (6) all staff engaged in managing Cyber Assets within the ESP were notified of changes and made aware of the requirements. | 2011-05-31 | 2011-10-21 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. NPCC considered NPCC_URE1's and its affiliates' compliance history.
2012-04-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000234 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to identify two substations as Critical Assets. The substations are essential to the regional blackstart cranking path and should have been identified using the criteria set forth in SPPRE_URE1's risk-based assessment methodology (RBAM). The RBAM states that blackstart resources that are in the SPP RE Regional Restoration Plan are to be considered and identifies blackstart assets as critical assets. SPPRE_URE1 correctly identified the combustion turbine, which is connected to one of the substations, as a blackstart generator and therefore a Critical Asset. Also, the transmission line between the two substations was properly identified as the blackstart cranking path and a Critical Asset. As the two substations are essential to energize the transmission line and allow power from the combustion turbine to flow across the cranking path, the two substations should have been deemed Critical Assets. | CIP-002-1 | R2 | High | High | SPP RE determined that SPPRE_URE1's violation of CIP-002-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because, upon adding the two substations to the critical asset list, SPPRE_URE1 determined that the two substations contained no associated Critical Cyber Assets. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 applied the approved methodology to its list of assets, added the two substations to its Critical Asset list, and the Chief Security Officer reviewed and approved the revised list. | 2010-06-14 | 2010-08-18 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000236 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to address, in its cyber security policy (CSP), all of the requirements of CIP-002 through CIP-009 as required by R1.1. Specifically, the following requirements: CIP-003-1 R1.1, 1.2, 1.3, 5.1, 5.1.2, 5.2.; CIP-004-1 R4; CIP-005-1 R1.2, 1.3, 2.3, 2.5, 2.5.1, 2.5.2, 2.5.4, 3, 3.1; CIP-006-1: R1.5, 1.8, 3, 3.1, 4; and CIP-007-1: R2.3, 5.2.2, 6.5. SPPRE_URE1 also did not make the CSP readily available to the supervisory control and data acquisition (SCADA)/Energy Management System (EMS) vendor support personnel with authorized electronic access, as required by R1.2. Further, there was no evidence of an annual review and approval of the CSP during the calendar year, as required by R1.3. | CIP-003-1 | R1 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-003-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had a CSP in place, and although every requirement was not addressed in the consolidated policy document, individual policies addressing the CIP requirements were in place. Although the CSP was not readily available to the SCADA/EMS vendor personnel, no vendor personnel had accessed Critical Cyber Assets since prior to July 1, 2008. Further, the CSP was reviewed in two non-sequential years and only the one review was missed. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 revised its CSP to address all of the requirements from CIP-002 through CIP-009 and obtained Chief Security Officer approval. Also, SPPRE_URE1 made the CSP available to the SCADA/EMS vendor and added review and approval of the CSP to the list of annual reviews necessary under the Standards to ensure that the review is performed every year and is not omitted again. | 2010-10-01 | 2010-11-11 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000238 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1's failed to address, in its cyber security training (CST), proper use of Critical Cyber Assets (CCAs) pursuant to R2.2.1 and did not include recovery procedure training for CCAs pursuant to R2.2.4. Further, SPPRE_URE1 failed to provide documentation demonstrating that the janitorial staff members with authorized, unescorted access were trained pursuant to R2.3. This violation affected three janitorial staff members, SPPRE_URE1 attested that the janitorial staff received training. However, no other documentation supported the referenced attestation. | CIP-004-1 | R2; R2.2.1; R.2.2.4; R2.3 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-004-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the training on CCAs under R2.2 only omitted part R2.2.1 until the 2009 updated annual training. Also, SPPRE_URE1 employees were generally aware of the proper use of the long-standing CCAs. All personnel with CCA access did receive CCA recovery procedure training in the previous year. For R2.3, SPPRE_URE1 provided an attestation that the janitorial staff had received training, although documentation could not be provided. Only three janitors had unescorted access, and they had received Personnel Risk Assessments. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its CST materials to ensure that all required items were covered in the version of the training program. SPPRE_URE1 contracted with a new janitorial services provider, replacing its old provider. The on-site staff of the newly contracted company were provided the proper CST appropriate for their level of access prior to the issuance of such access. | 2010-07-01 | 2010-08-18 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000239 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to sufficiently document the cyber access afforded its supervisory control and data acquisition (SCADA)/Energy Management System (EMS) vendor support personnel via an administratively privileged shared user account. Additionally, SPPRE_URE1 violated R4.2 because it failed to demonstrate that one employee's physical access to Critical Cyber Assets was revoked within seven days of the employee's transfer, after which the employee no longer required such access. | CIP-004-1 | R4; R4.2 | Lower | Moderate | SPP RE determined that SPPRE_URE1's violation of CIP-004-1 R4 posed a minimal risk to the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because no SCADA/EMS vendor personnel had logged in via the shared user account since prior to the Standard became mandatory and enforceable. Further, SPPRE_URE1 utilized a physical safeguard by not maintaining a continuous open line for dial-in to SPPRE_URE1's system. If the vendor were to require access, SPPRE_URE1 would physically plug in a line to allow access and then unplug the line when the vendor was finished. As for R4.2, SPPRE_URE1's badge system showed that the employee's badge access rights were changed the day after the employee was transferred; however, the change could not be tied to the transferred employee because the badge system logged only the fact that a change occurred without indicating which employee's access was changed. Further, access logs demonstrate that subsequent to the employee's transfer, the transferred employee never attempted to gain physical access to the area from which his access was to be revoked. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 developed a written procedure to ensure proper management of the shared vendor account access. To mitigate the R4.2 violation, SPPRE_URE1 implemented a physical access request and revocation procedure. The procedure documents the change request and documents the date and time that the change is made. The procedure will be utilized until such time that SPPRE_URE1 obtains a badge system that will log specific identifying information regarding access changes. | 2010-05-11 | 2010-08-28 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000240 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 could not provide evidence demonstrating that it had compared test data from before and after the introduction of new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter in order to ensure that there were no adverse effects on existing cyber security controls. Specifically, SPPRE_URE1 did not save the results of running the software tool to perform a comparison of the before and after the network statistic tool runs (which SPPRE_URE1 did save), which were performed to test network and internet connections. The software tool comparison produces test results that demonstrate the testing was properly performed. | CIP-007-1 | R1.3 | Lower | Moderate | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R1.3 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because testing was performed before and after the introduction of new Cyber Assets and significant changes to existing Cyber Assets. In order to determine if the changes had an effect on cyber security controls, the results of the before and after tests need to be compared. SPPRE_URE1 performed such comparison as part of its testing procedure and was able to demonstrate the procedure to SPP RE; it had only failed to maintain documentation of having performed the comparison testing. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 amended its cyber security controls testing procedures to require that the results of the before and after comparison testing be saved. | 2010-09-15 | 2010-09-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000241 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 did not change a Windows shared user account password or otherwise secure the account following the retirement of an employee who had access to the shared account. | CIP-007-1 | R5.2 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R5.2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although the entity did not change the Windows account password, each employee has an individual Energy Management System application account that must be used to further authenticate access to the operator console. Additionally, physical access to the operator console and login access to the corporate network was revoked for the retiring employee. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 changed the account password and provided additional steps in its user account policy that specify that when an individual's access to a shared account is revoked, the password to the shared account is to be changed as well. | 2010-08-30 | 2010-09-24 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000242 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 had not changed a Windows shared user account password in over four years. CIP-007-1 R5.3 requires that passwords be changed at least annually. | CIP-007-1 | R5.3 | Lower | Lower | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R5.3 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the shared user account was local to a particular workstation and was only used to logon to the workstation following a reboot. Further, the workstation requires employees of SPPRE_URE1 to have individual Energy Management System application accounts which are changed annually. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 reviewed and ensured that all local and domain accounts had been changed within the required time. SPPRE_URE1 also set its software settings to enforce password changes to meet the requirements of CIP-007-1 R5.3. | 2010-07-31 | 2010-09-24 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000243 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to include in its Cyber Security Incident Response Plan (CSIRP) a defined process to ensure reporting of incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC) pursuant to R1.3. The CSIRP in effect prior to this plan, which was in effect a few years before the Standard became mandatory and enforceable, did not include: sufficient procedures to characterize and classify incidents as being reportable pursuant to R1.1; incident handling procedures pursuant to R1.2; a defined process to ensure reporting to the ES-ISAC pursuant to R1.3; or requirements to update within 90 days of any changes to the response plan pursuant to R1.4. Further, SPPRE_URE1 failed to perform an adequate test of the CSIRP pursuant to R1.6. SPPRE_URE1 had self-reported the violation of R1.6 indicating that it did not perform a test of its incident response plan by the date SPPRE_URE1 was first required to be compliant with CIP-008-1 R1. | CIP-008-1 | R1 | Lower | High | SPP RE has determined that SPPRE_URE1's violation of CIP-008-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the bulk power system. The CSIRP provided that incidents at a certain security level (as defined in the CSIRP) involving Critical Cyber Assets were to be reported to the ES-ISAC. However, the CSIRP provided no ES-ISAC contact information or other details regarding how such reporting was to be accomplished. The omission of this process was the only deficiency found in the CSIRP. The plan, which was in effect prior to the date the Standard became mandatory and enforceable, had other deficiencies that were resolved upon implementation of the revised CSIRP. The prior plan did not include sufficient procedures to characterize and classify events as reportable or sufficient incident handling procedures. However, it did provide some examples of cyber security incidents and provided that in the event of an incident, an operations supervisor should be notified immediately. Had an incident occurred, an operations supervisor would have coordinated the response and handling of the incident. The operations supervisor is an electrical engineer with 20 years of experience in the electric industry, twelve years experience in a supervisory role in operations at SPPRE_URE1, and was responsible for the implementation of SPPRE_URE1's current SCADA/EMS system. Additionally, guidelines were provided in the prior plan to be considered during a cyber attack, although specific incident handling procedures were not provided. As for the violation of R1.6, an initial attempt at a response plan test was made. The test was a continuity of operations test in which the response to a virus taking down the EMS/SCADA server was to evacuate to the backup site and begin manual operations. No formal incident response procedure was followed. Another attempt was made to test the procedure. The documentation of that test provides that a review of the process was performed and general scenarios were tested. However, the scenarios were not documented so as to demonstrate that the plan was actually tested with respect to an incident involving Critical Cyber Assets. A compliant test was performed as part of the mitigation plan and documented. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its CSIRP to include all elements required by CIP-008-1 R1, such as classification of reportable events, incident handling procedures, and detailed steps for reporting an incident to ES-ISAC, along with the requirement to update the plan within 90 days of any changes. SPPRE_URE1 ensured that the annual Incident Response Test fully tested the CSIRP. | 2010-10-28 | 2010-11-11 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor. Although SPPRE_URE1 self-reported part of the violation, the self-reported portion of the violation discovered during the Spot Check was a very small piece of the violation on the whole, so no self-reporting credit was given in the penalty assessment.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000244 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to sufficiently define in its recovery plan the roles and responsibilities of responders. | CIP-009-1 | R1 | Medium | High | SPP RE determined that SPPRE_URE1's violation of CIP-009-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had an otherwise well-defined plan for recovery of CCAs and a small enough staff that failure to fully document roles and responsibilities would not likely hamper the ability to execute the recovery plan when needed. In the event that the recovery plan had needed to be activated, the recovery of CCAs would have been coordinated by an experienced operations supervisor, who is the individual to which cyber incidents were required to be reported. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its recovery plan to define roles and responsibilities based on job title and duties. These definitions are to be included in the updated Cyber Security Training materials. | 2010-10-01 | 2010-11-12 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000259 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to perform an adequate test of its recovery plan. The test, performed was a continuity of operations tabletop exercise that did not include restoration of the failed systems back to normal operation. SPPRE_URE1 had self-reported that it did not perform a test prior to the date SPPRE_URE1 was first required to be compliant with CIP-009-1 R2. | CIP-009-1 | R2 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-009-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had a recovery plan in place, but failed to fully test the plan. SPPRE_URE1 did perform a continuity of operations table top exercise, however, that test did not include restoration of the failed systems back to normal operation. The scenario involved a tornado and the evacuation of operations to a backup location. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 performed and documented a full test of its recovery plan as required by CIP-009-1 R2. | 2010-10-11 | 2010-11-15 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor. Since SPPRE_URE1 self-reported non-compliance with the Standard, SPP RE gave SPPRE_URE1 self-reporting credit.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000345 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R2, more specifically R2.2 and R2.4. SPP RE_URE2 reported that it had not documented the configuration for those ports and services used in accessing its Electronic Security Perimeter (ESP) as required by R2.2. Additionally, SPP RE_URE2 had not documented the process utilized by its information technology administrators to remotely access SPP RE_URE2’s Energy Management System (EMS) through its ESP firewall, nor had SPP RE_URE2 adequately documented the external login process utilized by its read-only EMS users as required by R2.4. | CIP-005-1 | R2; R2.2; R2.4 | Medium | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R2 was documentary in nature and posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because regarding access restriction (R2.4), EMS access was restricted to user access and Cyber Asset administrator access through the ESP’s firewall. EMS users were allowed only read-only access through the firewall to the EMS server. Further, the users were first required to authenticate through the SPP RE_URE2 Physical Security Perimeter, then through the workstation console, and finally into the EMS application. Administrator access was accomplished by the same process but was limited to three individuals at SPP RE_URE2. In addition, SPP RE_URE2 administrators could only obtain configuration level access to the EMS network devices following the submission of a CIP access level request form that allowed administrators access to the “enable” password. Also, an encryption protocol was utilized for gaining access to the EMS server through the devices. These redundant authentication mechanisms helped to insulate the EMS servers from unauthorized access. Regarding ports and services (R2.2), despite the omission from SPP RE_URE2’s CIP-005-1 procedure, SPP RE_URE2 had documented its ports and services for ESP access in two earlier CIP-005 vulnerability assessments. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented its process for controlling access to the EMS web server inside the SPP RE_URE2 ESP. The process explains how a firewall protects the ESP from the corporate network allowing read-only access to the EMS server within the ESP for EMS users and requiring two layers of electronic authentication. In addition, administrators are limited to a subset of EMS network device commands after entering their corporate password. Also, a greater number of commands can only be obtained by submitting a CIP access level request form to gain access to the enable password on the SPP RE_URE2 network devices. SPP RE_URE2 created a procedure documenting its ports and services and provided evidence that the required ports and services were documented in the vulnerability assessments conducted. | 2010-09-17 | 2011-04-01 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000346 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R3 and R3.2. SPP RE_URE2 reported that its policies and procedures lacked specific detail on electronic or manual processes for monitoring and logging access at access points to the Electronic Security Perimeter (ESP) in accordance with R3. Specifically, SPP RE_URE2 failed to identify the order of firewall logging; corporate firewalls log first while Energy Management System (EMS) firewalls log second. SPP RE_URE2 also failed to record or review its firewall access logs. Finally, SPP RE_URE2 failed to document the process to be followed by its IT department in response to a user being locked out of a firewall. | CIP-005-1 | R3; R3.2 | Medium | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R3 and R3.2 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had security measures in place to protect its network against unauthorized access. To provide redundant authentication mechanisms, user and administrator access to the SPP RE_URE2 EMS required two factor authentication through both the workstation and then to the EMS application. To limit administrative configuration access to the network, SPP RE_URE2 limited authorized IT administrator access to three personnel. In addition, it required an additional layer of authentication to achieve full enable level access on its network devices, and utilized an encryption protocol for device communication. SPP RE_URE2 was utilizing a server to support overall network security within the ESP. This particular server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress. Prior to automated alerting being achieved, SPP RE_URE2 was conducting manual reviews of the server logs. Finally, while the logging and review process was not documented during the violation period, no reportable cyber security events occurred. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented and implemented a procedure for the monitoring and logging of all access points to its ESP twenty-four hours a day using a server appliance. Successful/unsuccessful access attempts are captured. Data including, but not limited to: date, time, user ID, device ID and IP address for each access attempt is retained. Logs are collected into a centralized event server and are actively monitored by another server. This other server sends an alert on suspicious activity and also monitors specific ports for unauthorized addresses. Active alerts are reviewed by SPP RE_URE2 personnel. Any identified security incident will be logged into SPP RE_URE2’s ticket tracking system for further investigation. Additionally, SPP RE_URE2 IT personnel have procedures to check access logs each morning, Monday through Friday (excluding holidays). Finally, SPP RE_URE2 updated its processes to provide a process for user recovery of locked accounts following five failed authentication attempts. | 2010-08-31 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000348 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R5 and R5.1. SPP RE_URE2 stated that it did not have documentation to reflect current access point and Cyber Asset configurations, and its processes for access and logging were not sufficiently documented. Additionally, because it did not have all the required documentation, SPP RE_URE2 had not reviewed the documents and procedures referenced in Standard CIP-005 at least annually, as required by the Standard. | CIP-005-1 | R5; R5.1 | Lower | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R5 and R5.1 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because while SPP RE_URE2 had not documented its ports and services in its CIP-005 procedure, SPP RE determined that SPP RE_URE2 did have current and historical documentation of its access points to the Electronic Security Perimeter (ESP) and their configuration. This documentation was contained in two vulnerability assessment reports conducted by its Energy Management System (EMS) vendor. Additionally, the EMS vendor’s two ESP access point reviews served as a review of the SPP RE_URE2 access point configurations. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 EMS and IT staff have reviewed previously existing documents and either created new documents or modified its previously existing documents to provide details on SPP RE_URE2 Cyber Assets and their configurations as well as supporting processes and procedures to ensure compliance with the CIP-005-1 R5. SPP RE_URE2 developed a process to maintain ESP documentation and provided a revised topology map of the ESP identifying all access points to the ESP. Additionally, SPP RE_URE2 developed a process for monitoring and logging access at all access points to the ESP twenty-four hours a day and included evidence of logging processes (in the form of a checklist identified in the monitoring procedure), sample access logs for access control devices at the ESP, and evidence of log reviews. SPP RE_URE2 also provided a screen shot of its newly implemented warning banner. Additionally, SPP RE_URE2 updated its account management procedure for access control, authentication and accountability. Finally, SPP RE_URE2 documented its authorization rights and created a list of access rights mapped to user groups segregated by servers and workstations. | 2011-08-05 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000349 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R1.3. SPP RE_URE2 reported that when changes were made on EMS application servers, performance testing was conducted on non-critical systems using a network security scanner application. At the time of its Self-Report, SPP RE_URE2 indicated that it was utilizing this application to perform security scans of offline workstations and EMS servers in both pre- and post-installation timeframes. Following installation, the application compares the post installation scan to the pre-installation base line scan to determine if any security issues exist. While SPP RE_URE2 was performing the required security scans at the time of its Self-Report, it indicated that it had failed to adequately document and preserve its historical application scans (security test results). | CIP-007-1 | R1.3 | Lower | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R1.3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because SPP RE_URE2 was performing security testing using a network security and vulnerability scanner on Critical Cyber Assets (servers and workstations) within the Electronic Security Perimeter (ESP) after a software/hardware upgrade. Although SPP RE_URE2 failed to save the application monitoring results as evidence of testing, SPP RE_URE2 indicated that it was utilizing the application to perform checks for current security patches, and as of SPP RE_URE2’s earlier vulnerability assessment, all systems within the ESP had current update patches installed. Moreover, SPP RE_URE2 was utilizing a server to analyze event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 was conducting manual reviews of the server logs. There were also no reportable cyber security events during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 configured its network security scanner application to be able to collect and maintain complete system test results on all Cyber Assets (CAs) within the ESP. The information collected is broader than the CIP-007 R1 Standard. SPP RE_URE2 demonstrated that it has the ability to comply with CIP-007 R1 by submitting a sample of the test report for a Critical Asset used in the access control and monitoring of the ESP, a Critical Asset used in the access control and monitoring of the Physical Security Perimeter, and a Critical Cyber Asset within the ESP. An application report will be run on Critical Assets affected by changes or upgrades for purposes of satisfying CIP-007 R1 as part of the change control procedure. | 2011-01-01 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000352 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R4. SPP RE_URE2 reported that it did not have documentation outlining which assets did not have anti-virus software installed and did not monitor the anti-virus management console for virus alerts. Additionally, SPP RE_URE2 was not performing any testing of anti-virus signature files prior to rolling them out onto critical systems within the production environment. SPP RE also discovered that SPP RE_URE2 failed to have anti-virus installed on its Energy Management System (EMS) servers by the Standard's compliance enforcement date. | CIP-007-1 | R4; R4.1; R4.2 | Medium | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R4.1 and R4.2 posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because, notwithstanding SPP RE_URE2’s failure to test anti-virus signatures prior to updating critical systems, the signatures were being pushed to the production system on a regular basis and updated. Additionally, while the failure to install anti-virus software on the EMS servers presents a vulnerability into the EMS environment, the servers' previous operating system was replaced with another operating system and anti-virus software was installed. Further, SPP RE_URE2 was utilizing a server with automated alerting. The server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Finally, for the duration of the violation, no cyber events occurred on its EMS systems. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented and implemented a process for distribution of anti-virus signatures to Critical Assets within the ESP. The anti-virus platform is now configured to distribute anti-virus signatures to a small subset of non-critical computers within the EMS environment for testing prior to deploying updates to critical production systems, similar to the patch management process. Once it has been verified and documented that no issues have been introduced, the signature files are then deployed to the remaining systems. These steps are then documented within the existing logs. SPP RE_URE2 also configured the anti-virus platform to automatically alert EMS engineers for anti-virus events. Further, SPP RE_URE2 replaced its servers' operating system with another operating system, and anti-virus software was installed. SPP RE_URE2 also created a document containing a list of Critical Cyber Assets which do not have anti-virus installed and an explanation of why an anti-virus solution could not be implemented. The devices addressed include printers and network devices. SPP RE_URE2 requested a Technical Feasibility Exception on the remaining devices without anti-virus installation. | 2011-04-06 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000353 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R5. Specifically, SPP RE_URE2 had not performed an in-depth review of the user accounts with access to its Energy Management System (EMS) application. Further, SPP RE_URE2 had not enforced passwords that met the CIP-005-1 R5.3 password requirements. | CIP-007-1 | R5; R5.1.3; R5.3 | Medium | Severe | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R5.1.3 and R5.3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because user access to the EMS application at the time of the violation was a three-step process that began with Physical Security Perimeter authentication, followed by EMS corporate workstation authentication, and finally EMS application authentication. While EMS application passwords were identified as having failed to meet the requirements of CIP-007-1 R5.3, the reliability risk to the BPS was low because redundant authentication procedures were in place for access from the EMS workstation through the ESP to servers hosting EMS applications as stated above. Additionally, user access was limited to read-only access. Further, a redundant application, a server was in place to monitor for “system events” on the local area networks within the ESP. This application monitored event logs to ensure that systems and devices were functioning within defined parameters. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Such redundant network monitoring serves to detect changes made to the network configurations via unauthorized access. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 developed a comprehensive account management process and form to record the user account review. SPP RE_URE2 EMS employees performed a thorough review of EMS user accounts. This review is now performed at least annually as prescribed in the account management process. Additionally, SPP RE_URE2 EMS employees were trained in CIP password requirements and SPP RE_URE2 strengthened its EMS application passwords to meet the CIP-005-1 R5.3 Standard. | 2010-08-24 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000354 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R6. Specifically, SPP RE_URE2 failed to implement a process for monitoring security events on all Critical Assets (CAs) within its ESP as required by R6.1. Additionally, although four Energy Management System (EMS) servers located within its ESP were configured to log all events, SPP RE_URE2 did not have security monitoring controls in place for automated or manual alerts for detected Cyber Security Incidents as required by R6.2. Moreover, the logs were not reviewed on a regular basis as required by R6.5. | CIP-007-1 | R6; R6.1; R6.2; R6.5 | Medium | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R6.1, R6.2 and R6.5 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because SPP RE_URE2 had been logging all events relating to its CA servers within the ESP, and such logs were periodically being reviewed but not on a consistent basis. All CA servers and workstations are located within SPP RE_URE2’s Physical Security Perimeter and are accessible only by personnel with authorized card access privileges. Additionally, SPP RE_URE2 was utilizing a server to monitor its network. The server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Moreover, no reportable Cyber Security Incidents occurred during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 implemented and documented a process to monitor for cyber security events on CAs within the ESP. The process utilizes an event log monitoring, management and archiving application to correlate and alert on events from its particular operating system. Network devices are monitored through a server. Alerts from these CAs are reviewed daily by SPP RE_URE2 personnel. | 2010-08-27 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000441 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-003-1 R3. Specifically, SPP RE_URE2 was unable to institute security monitoring controls capable of issuing automated alerts for detected Cyber Security Incidents as required by SPP RE_URE2’s cyber security policy until 71 days after the Standard became mandatory and enforceable. This instance should have been identified as an exception to SPP RE_URE2’s cyber security policy, and authorized by the senior manager. | CIP-003-1 | R3 | Lower | Severe | SPP RE determined that SPP RE_URE2's violation of CIP-003-1 R3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because when the violation was mitigated, SPP RE_URE2 began utilizing a server to meet the requirement of its cyber security policy. The server analyzes event logs collected from network devices within the Electronic Security Perimeter (ESP) to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Additionally, SPP RE_URE2 attested that there have been no reportable Cyber Security Incidents during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | Since the installed software/hardware used to monitor SPP RE_URE2’s Critical Assets within its ESP was incapable of issuing automated alerts for detected Cyber Security Incidents as intended, until the feasibility of the automation could be completed, SPP RE_URE2 revised its cyber security policy to require manual security monitoring. At that time, SPP RE_URE2 began monitoring logs for security incidents. SPP RE_URE2 began installing updates to its security monitoring controls. SPP RE_URE2 successfully tested its security monitoring controls and began receiving automated alerts for security events. | 2009-09-10 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002076 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating its semi-annual CIP self-certification process. WECC_URE1 self-reported a violation of CIP-006-1 R3 and a couple days later submitted its self-certification for CIP-006-1 R3. WECC_URE1 failed to implement controls to monitor access at access points to a single Physical Security Perimeter (PSP). WECC_URE1 was required by the Standard to implement technical controls to monitor access at all PSP access points. Although access points to the PSP were equipped with card readers, the existing card access system did not provide 24/7 monitoring consistent with CIP-006-1 R3. Further, the card access system did not trigger an alarm in the event of unauthorized access to the PSP. WECC determined that WECC_URE1 was in violation of the Standard for failing to implement technical controls monitoring access at PSP. Specifically, the existing controls did not provide for 24/7 access monitoring and alarming. | CIP-006-1 | R3 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the PSP was afforded, during the violation period, a significant degree of layer security and monitoring. WECC determined access to the PSP required entry through a separate access point that did have 24/7 monitoring. In addition, WECC_URE1 did have a card access system in place that provided monitoring through a shared system on a limited basis and without alarming. | when WECC_URE1 was required to comply with the Standard | date Mitigation Plan was completed | $8,000 (for WECC201002076 and WECC201002138) | Self-Certification | WECC_URE1 submitted a Revised Mitigation Plan outlining the following mitigating actions: 1. Switched card access system from shared system to a standalone system, which provided 24/7 monitoring and unauthorized access alarming capability; 2. The new card access system was secured within the PSP; and 3. Control and Monitoring of the card access system assigned to the Critical Asset for full operability. | 2010-06-29 | 2010-10-13 | Agrees/ Stipulates | Although WECC_URE1 self-reported the CIP-006-1 violation during a self-certification period, WECC applied mitigating credit based on WECC_URE1's attempts to disclose noncompliance prior to when WECC_URE1 was required to comply with the Standard. WECC applied mitigating credit based on evidence of WECC_URE1's attempts to self-disclose the violation prior to receiving notice to self-certify.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002138 | Settlement Agreement | WECC_URE1 self-reported a violation of PRC-023-1 R2. WECC_URE1 failed to obtain agreements from its Planning Coordinator (PC), Transmission Operator (TOP) and Reliability Coordinator (RC), in which parties agree to use the calculated circuit capability as the Facility Rating of the circuit. This violation affected four of WECC_URE1's facilities. While WECC_URE1 did apply the R1.6 criteria to calculate circuit capability with respect to three facilities and the R.1.13 criteria for the fourth facility, WECC_URE1 did not obtain the required agreements with its PC, TOP and RC. In addition, although WECC_URE1 did submit the necessary requests to secure such agreements it had not reached an agreement with any of the other parties. WECC determined that although WECC_URE1 did apply circuit capabilities prescribed under PRC-023-1 R2, WECC_URE1 failed to execute agreements with its PC, TOP and RC pursuant to R2. | PRC-023-1 | R2 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because, although the WECC_URE1 failed to ensure that protective relay settings do not limit transmission loadability and do not interfere with system operators' ability to protect the BPS and failed to secure the necessary agreements from its PC, TOPs, and RC, the Facility Ratings used by all parties were calculated using criteria in accordance with PRC-023-1 R1. | when Standard became mandatory and enforceable | date Mitigation Plan was completed | $8,000 (for WECC201002076 and WECC201002138) | Self-Report | WECC_URE1 identified all parties with which it was required to execute an agreement and entered into agreements with the appropriate entities. | 2011-07-19 | 2011-12-22 | Agrees/ Stipulates | WECC considered that WECC_URE1 submitted a Self-Report for this violation and that WECC_URE1 did not have any repeat violations of this Standard or any relevant negative compliance history.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000306 | Settlement Agreement | FRCC_URE1 determined that a total of 109 changes made to Critical Cyber Assets (CCA) were not controlled or documented properly according to the entity's change control and configuration management process, as required by CIP-003-1 R6. FRCC_URE1 determined that 17 package changes, 83 display changes, 8 code changes and 1 configuration (.rc) file change were not documented due to ineffective implementation and failure to adhere to FRCC_URE1's practice. This violation was self-reported by FRCC_URE1. | CIP-003-1 | R6 | Lower | High | FRCC determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because changes to FRCC_URE1's CCAs were tracked using brief change logs, but no formal documentation was maintained. Out of 109 changes that were not formally tracked during the violation period, most of the changes were day to day routine configuration and update changes. | The date of first change | The completion of MP | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Self-Report | FRCC_URE1 has reviewed and revised its change control practice to ensure that all changes are accompanied with change control/request forms and processes. These processes include an evaluation of new applications to determine whether codes and revisions are stored; peer review is conducted for all the changes including file changes to the Supervisory Data and Acquisition (SCADA) system. All changes were implemented using a newly designed service request form and evaluation of existing security controls for any adverse effect as a result of change. Additionally, FRCC_URE1 provided training to affected employees in the revised change control practice and service request forms. | 2010-05-04 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000307 | Settlement Agreement | During the Spot Check it was discovered that FRCC_URE1 was unable to demonstrate having test procedures for all significant changes to 2 Cyber Assets within the Electronic Security Perimeter (ESP) that minimized adverse effects to the cyber security controls, as required by CIP-007-1 R1. The entity's evidence did not demonstrate that the router test procedure addressed ESP configuration controls, ports and services to maintain the ESP integrity, lockout or change of password for default user access, user access controls, review of physical security for access control, review of banners, or review of modems access for the ESP. Similarly, the testing process for application changes did not address adverse effects to existing security controls. Further, the entity did not document test results as per the entity's own test procedure. | CIP-007-1 | R1/ R1.1; R1.2; R1.3 | Medium | Lower | FRCC determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because during the workstation and router configuration updates the entity used its Supervisory Control and Data Acquisition (SCADA) vendor's approved configurations and performed operational testing only. The application changes (Wave file recorder) for which CIP-007 R1 testing was found deficient are widely used within the control center environment but did not add any new ports and services. Furthermore, the changes were from trusted control system vendors. | The date of first change with limited testing | The completion of MP | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Spot Check | As a part of FRCC_URE1's mitigating activity, FRCC_URE1 re-designed checklists and controls on third-party testing and service request forms of various types. FRCC_URE1 also produced revised testing guidelines for the tests identified as incomplete and corrected any deficiencies. Training was given to all affected personnel including those who implement these changes. Testing was performed to ensure that no additional ports or services were opened as a result of the installation of the “Power Play” software. A command line tool, was used to show all open and listening ports on the client. Ports were translated to processes which were further defined via a task list. As a result of the testing, all ports and services were determined to be legitimate. All findings were documented on a testing worksheet. For the router, security was configured on the router; a port scan performed against the router confirmed that only the required open ports and services were available. All findings and test results were documented on a testing worksheet. | 2010-07-15 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000362 | Settlement Agreement | Four of FRCC_URE1's switches contained within the entity's ESP were not configured for automatic logging of system events as required by CIP-007-1 R6. The configuration had been set to the original EMS vendor specifications as delivered. This was self reported by FRCC_URE1. | CIP-007-1 | R6/ R6.1; R6.3; R6.4 | Medium | Lower | FRCC determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The lack of logging limits the capability of the environment to monitor for possible Cyber Security Incidents and allows for exploitation. While these switches used redundant configurations, they lacked logging which could allow an unauthorized person the opportunity to gain access without detection. The likelihood of these occurrences was reduced substantially because of the switches being located in a secure ESP. | The date Standard became enforceable for FRCC_URE1 | When FRCC_URE1 configured Syslog on the switches; review logs and add to scheduled reporting | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Self-Report | FRCC_URE1 corrected the logging configuration to enable logging of the system events for the concerned switches. FRCC_URE1 also updated hardware and software testing forms to address logging and training of all affected staff responsible for installation of networking devices. Additionally, FRCC_URE1 hired an EMS Administrator to update and revise existing practices and guidelines. | 2010-05-21 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100249 | Settlement Agreement | NPCC_URE1 self-reported a violation of CIP-004-2 R3. NPCC determined that NPCC_URE1 failed to conduct a personnel risk assessment (PRA) for one of its employees. Specifically, a NPCC_URE1 employee was granted authorized unescorted physical access to Critical Cyber Assets (CCAs) at a power station, prior to having a PRA conducted. The mistake was discovered approximately six months later during an internal review of PRA documentation. The manager responsible for granting access had requested a PRA for the employee three months before the required access date but did not confirm that the PRA was completed when access was granted. | CIP-004-2 | R3 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because this involved a single employee. Further, this employee did not access the CCA Physical Security Perimeter during the period of time the PRA was not performed. Also, this employee is required to have government-approved credentials to work at this location and this was completed two years prior to the violation. This check verified his identity, looked at criminal history records, terrorist watch lists and immigration databases. | When the NPCC_URE1 employee at issue was granted access to CCAs | When the PRA was completed | 3800 | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-004-2 R3. In accordance with the Mitigation Plan, NPCC_URE1: (1) completed a PRA for the affected employee; (2) revised the form for approving personnel physical access to CCAs to include the source of the PRA date listed on the form. This change makes the approving manager responsible for confirming that a PRA was in fact completed and logged in the system rather than assuming, in the absence of a report to the contrary, that the PRA was completed before the manager submits the access approval form; (3) conducted critical infrastructure protection awareness training; (4) discussed the incident with the employee directly responsible for granting the access and reinforced the need for compliance. | 2010-11-30 | 2011-08-10 | Does Not Contest | NPCC viewed the compliance program, in effect at the time of the violation, to be a mitigating factor in the penalty determination. NPCC took into consideration NPCC_URE1's violation history.
2012-03-30 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201000190 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R2.1. NPCC_URE2 discovered, during an internal assessment, that all of the ports and services required for normal and emergency operations were not properly documented for a subset of servers and workstations associated with the Energy Management System (EMS). The internal assessment determined that select devices within the Electronic Security Perimeter (ESP) lacked adequate documentation of ports and services. These devices are initially configured to a corporate standard configuration. After initial configuration, additional applications are installed depending upon the function to be performed by the device. Documentation of the initial standard corporate configurations were controlled and documented, but this documentation did not include ports and services information. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because access to the ESP is controlled by a combination of firewall rules and router access control lists. Device cyber access is monitored by an intrusion detection system. Cyber access to the devices is limited to a small number of authorized personnel. Access to the public internet is not possible from inside the ESP. CCA devices are contained within a Physical Security Perimeter which has limited access by authorized personnel. In addition, there were no incidents at NPCC_URE2 related to the lack of proper documentation of the normal and emergency ports and services. | Date the Standard became mandatory and enforceable for the entity | Mitigation Plan Completion | $5,000 (for NPCC201000190 and NPCC201000191) | Self-Report | NPCC_URE2 submitted a Mitigation Plan with the following mitigation activities: 1. Existing configurations of active services and open ports, including those of devices affected by the violation, for each identified Critical Cyber Asset (CCA) were documented; 2. Subject matter experts reviewed and documented the configuration of the standard corporate client and server images on all CCAs to identify required ports and services; 3. Based on the current year's vulnerability assessment results, updates were made to appropriate documentation associated with all applicable CCAs; 4. The standard client and server configurations per the Mitigation Plan were supplemented with services required for specific asset types to create device specific ports and services configurations; 5. Device configurations were modified to conform with the device specific documentation developed per the Mitigation Plan; and 6. A procedure was created for the documentation of ports and services. | 2011-03-01 | 2011-04-19 | Neither Admits nor Denies | NPCC considered certain aspects of NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201000191 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-005-1 R2.2. NPCC_URE2 discovered during an internal assessment that certain baseline ports and services associated with the primary control center firewall had incomplete configuration documentation. NPCC_URE2's assessment of firewall ports determined that a firewall selected for inspection did not have proper documentation of enabled ports. Upon discovery of this violation, NPCC_URE2 reviewed all documentation of ports and services on the rest of its control center firewalls. NPCC_URE2 discovered that the other firewalls had the same documentation issues as the firewall reported in the Self-Report; however, these issues were also resolved through mitigation activities for this violation. | CIP-005-1 | R2; R2.2 | Medium | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE2 had Critical Cyber Asset account management controls, an intrusion detection system and access log review protocols. Access to the NPCC_URE2 Energy Management System (EMS) network is not allowed from the public internet, nor can devices within the EMS and Electronic Security Perimeter reach the public internet directly as the EMS network space utilizes non-routable private addresses to further enhance protection of the environment. In addition, there were no incidents at NPCC_URE2 related to the lack of proper configuration documentation of the primary control center firewall. | Date the Standard became mandatory and enforceable for the entity | Mitigation Plan Completion | $5,000 (for NPCC201000190 and NPCC201000191) | Self-Report | NPCC_URE2 submitted a Mitigation Plan with the following mitigation activities: 1. Port and service documentation for all checkpoint firewalls, including the affected firewall, was reviewed and updated as necessary; 2. Based on the current year's vulnerability assessment results, updates were made to the appropriate documentation associated with all ESP access devices; 3. The access point device configurations were updated as appropriate; and 4. A procedure was created for the documentation of ports and services. | 2011-03-01 | 2011-04-19 | Neither Admits nor Denies | NPCC considered certain aspects of NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100830 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs), and while RFC_URE1 did have lists of personnel with authorized cyber access, it failed to accurately maintain these lists. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training,38.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R2 by failing to implement its annual cyber security training program for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | CIP-004-1 | R2/ R2.1; R2.3 | Medium, Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been brought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two outside independent auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100831 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs) because RFC_URE1 failed to accurately maintain its lists of personnel with authorized cyber access. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training, 38.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R3 by failing to conduct PRAs for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | CIP-004-1 | R3/ R3.1; R3.3 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been bought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two outside auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100832 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs) because RFC_URE1 failed to accurately maintain its lists of personnel with authorized cyber access. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training, 35.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R4 by failing to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to CCAs | CIP-004-1 | R4/ R4.1; R4.2 | Lower, Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been bought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two independent outside auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100833 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-3c R1.6. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to maintain visitor logs to document the entry and exit of visitors at its Physical Security Perimeters (PSPs), as required by CIP-006- 3c R1.6; however, RFC_URE1 did maintain company policies related to visitor control and observation, and did maintain electronic logs of the entry and exit of authorized personnel at its facilities. RF determined that RFC_URE1 violated CIP-006-3c R1.6 by failing to implement a visitor control program for visitors (personnel without authorized unescorted access to a PSP) in its physical security plan. | CIP-006-3c | R1/ R1.6 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-3c R1, the risk to the BPS was mitigated by the fact that, while RFC_URE1 did not implement CIP-006-1 visitor logs at all PSPs, RFC_URE1 trained its employees and contractors in visitor control and monitoring within PSP boundaries, and the visitors posed no actual security risk during the duration of the violation, as there was always an escort present. At no time were unauthorized visitors allowed to access its PSPs without an authorized escort present. | The effective date of Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | The visitor log issue has been corrected. Upon discovery of this issue, RFC_URE1 immediately instituted a new process, whereby escorts at each Critical Area must call a central guard desk, with specific identifying information for all escorts and visitors to Critical Cyber Assets, including the name and company of the visitor, and the purpose of the visit; these visitors are logged going in and out of these facilities, including date and time, and all of the information is maintained in a log at the central guard facility. While it is maintained manually at this point, it is RFC_URE1's intent to develop and implement electronic logging of all visitors. In furtherance of this new process, signs reminding all personnel of this process and its requirements were posted at each Critical Area. Additionally, RFC_URE1 provided a company-wide communication detailing this new process via conference call and email, which included a reminder on visitor escort responsibilities. With respect to all of these issues of non-compliance under CIP-006, the RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the Company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100834 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-1 R2.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to afford all of the protective measures specified in CIP-006-1 R2.2 to two personal computers that had the capability to control access to Physical Security Perimeters (PSPs). Until the time it submitted the Self-Report, RFC_URE1 incorrectly believed that the personal computers did not have capability to control access to PSPs, and as a result, RFC_URE1 did not provide the protective measures specified in ClP-005 R2 and R3 and ClP-007 to those personal computers. RF determined that RFC_URE1 violated ClP-006-1 R2.2 by failing to afford the protective measures specified in ClP-003, CIP-004 R3, ClP-005 R2 and R3, ClP-006 R4 and R5; ClP-007, ClP-008, and CIP-009 to two cyber assets that authorize access to the PSP. | CIP-006-1 | R2/ R2.2 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-1 R2.2, the risk to the BPS was mitigated by the fact that the two computers at issue were both located within secure PSPs, preventing unauthorized physical access. The two computers were also on secure network segments, which provided additional protections against cyber vulnerabilities. Additionally, one of the two computers resided in the main guard facility, which RFC_URE1 staffs and monitors 24 hours per day. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | With respect to the two computers that had physical access control functionality which were not adequately electronically protected under CIP-006 R2.2, this issue was an isolated incident. That said, it was immediately remedied, and the computers were afforded all required electronic protections. A complete review of the operating capabilities of the system hardware components has been performed, and RFC_URE1 has verified there are no other unidentified physical access control devices. With respect to all of these issues of non-compliance under CIP-006, RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the Company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100835 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-1 R5. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to maintain full documentation for all physical security alarms to demonstrate that it reviewed and responded to unauthorized access attempts in accordance with the procedures specified in its physical security plan, pursuant to ClP-006-1 R5. RFC_URE1 investigated all physical security alarms and had documentation of the alarms and who acknowledged them, but failed to generate written documentation of the security reviews and responses for each alarm. RF determined that RFC_URE1 violated ClP-006-1 R5 by failing to document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeters (PSPs) twenty-four hours a day, seven days a week. | CIP-006-1 | R5 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-1 R5, the risk to the BPS was mitigated by the fact that although RFC_URE1 failed to document controls for monitoring physical access to PSPs, its corporate security procedures required the guard on duty to respond to and investigate each event. Additionally, RFC_URE1 has documentation of every alarm received and when the security professional on duty acknowledged each alarm. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | Regarding the documentation of responses to alarm events and unauthorized access attempts, the security guards charged with investigating these alarm alerts are now well versed on the required documentation, and are maintaining evidentiary documentation of each alarm or unauthorized access attempt response. This was instituted shortly after the issue was discovered. With respect to all of these issues of non-compliance under CIP-006, RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100778 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-006-2c R2.2 (the duration of this violation involves versions 2 and 3 of CIP-006. Other than referencing the corresponding version of the CIP Reliability Standards, the text of all applicable versions of CIP-006 R2 and R2.2 are identical). RFC_URE2 determined that it failed to identify three devices as Cyber Assets that authorize access to its Physical Security Perimeter (PSP), and did not afford them the protective measures as specified in CIP-006-2c R2.2. Specifically, RFC_URE2 failed to afford these protective measures to a physical security server, a digital video recorder, and a personal computer (collectively, the Server/DVR/PC), each of which RFC_URE2 used to create access badges and authorize access to the PSP. ReliabilityFirst determined that RFC_URE2 violated CIP-006-2c R2.2 by failing to afford the Server/DVR/PC the protective measures specified in CIP-006-2c R2.2. | CIP-006-2c | R2; R2.2 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 implemented, at all relevant times, separate security mechanisms designed to minimize overall cyber and physical security risks at the facility including intrusion detection, anti-virus, security logging, access control (both cyber and physical), and defense-in-depth network design. These mechanisms help RFC_URE2 to, among other things, detect possible attacks on its system, help prevent virus and malware infection, and limit inbound traffic. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 afforded the protective measures specified in CIP-006-2c R2.2 to the Server/DVR/PC | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Report | RFC_URE2 afforded all the protective measures specified in CIP-006-2c R2.2 to the Server/DVR/PC. RFC_URE2 also updated all relevant documentation associated with the Server/DVR/PC to reflect the protective measures RFC_URE2 afforded to the Server/DVR/PC. These updates were communicated to all relevant staff. | 2011-04-30 | 2011-11-28 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100779 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-2a R2 (the duration of this violation involves version 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R2 are identical). RFC_URE2 determined that it failed to disable its unused ports and services on a single transmission control room personal computer, located within the Electronic Security Perimeter (ESP) pursuant to Reliability Standard CIP-007-2a R2. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2a R2 by failing to implement its established, documented process to ensure it enabled only ports and services used for normal and emergency operations. | CIP-007-2a | R2 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. Although RFC_URE2 did not disable its unused ports and services on one personal computer in the ESP, RFC_URE2 has a documented process to perform such actions, but in this instance failed to implement its process. In addition, RFC_URE2 disabled the unused ports and services on the firewall surrounding the personal computer at issue, thereby minimizing the exposure of Cyber Assets inside the ESP to outside attacks. RFC_URE2 also implements separate security mechanisms designed to minimize overall cyber and physical security risks including intrusion detection, anti-virus, security logging, access control (both cyber and physical), as well as defense-in-depth network design. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 disabled the unused ports and services on the personal computer located within the ESP | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Report | RFC_URE2 disabled the unused ports and services on the transmission control room personal computer within the ESP. RFC_URE2 also updated all relevant documentation associated with CIP-007 R2 and these updates were communicated to all relevant staff. | 2011-04-30 | 2012-02-09 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100913 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-005-2 R1.5 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-005-1 R1 (the duration of this violation involves versions 2 and 3 of CIP-005. Other than referencing the corresponding version of the CIP Reliability Standards, the text of all applicable versions of CIP-005 R1.5 are identical). RFC_URE2 determined it had not afforded certain Cyber Assets used in access control and monitoring of its Electronic Security Perimeter (ESP) all the protective measures described in CIP-005-2 R1.5. Specifically, RFC_URE2 did not afford two servers the protections specified in CIP-007 R4, CIP-005 R2.6 and CIP-007 R2. ReliabilityFirst determined that RFC_URE2 violated CIP-005-2 R1.5 by failing to afford two Cyber Assets used in access control and monitoring of its ESP the protective measures specified in CIP-007 R4, CIP-005 R2.6 and CIP-007 R2. | CIP-005-2 | R1; R1.5 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 was affording its Cyber Assets used in controlling and monitoring its ESP some of the protective measures required by CIP-005-2 R1.5. This included the protective measures found in Reliability Standards CIP-005 R3 and CIP-004 R3. In addition, RFC_URE2 implements separate security mechanisms to minimize overall cyber security risk including intrusion prevention systems, anti-virus software, security logging, and defense-in-depth network design. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 afforded all protective measures included in CIP-005-2 R1.5 to its Cyber Assets used in the access control and monitoring of its ESP) | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 updated all documentation associated with those Cyber Assets to reflect the newly afforded protections, as well as communicated the required protective measures with all relevant staff. | 2011-11-30 | 2012-02-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100915 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-006-2 R3 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-006. The text of versions 2 and 3 of CIP-006 R3 are identical). RFC_URE2 determined that it did not position two servers, both Cyber Assets used in the access control and monitoring of its Electronic Security Perimeter (ESP) (ACM Cyber Assets), within an identified Physical Security Perimeter (PSP). ReliabilityFirst determined that RFC_URE2 violated CIP-006-2 R3 by failing to position the ACM Cyber Assets within an identified PSP. | CIP-006-2 | R3 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. While RFC_URE2 did not locate its ACM Cyber Assets within an identified PSP, it did position the ACM Cyber Assets in a secured room. RFC_URE2 controlled access to the secured room by a badge reader and biometrics, which required fingerprinting, to enter. In order for RFC_URE2 to grant access to the secured room, an individual first had to go through a personnel risk assessment (PRA) and receive CIP training. Additionally, RFC_URE2 monitored the ACM Cyber Assets within the secured room via security camera. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 completed installation of the equipment necessary to create a PSP around the ACM Cyber Assets | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 installed the equipment necessary to create a PSP surrounding ACM Cyber Assets. Additionally, RFC_URE2 updated all relevant documentation associated with CIP-006 R3 and notified all staff engaged in managing Cyber Assets within the PSP of the changes. | 2011-11-30 | 2012-02-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100917 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-006-2 R8 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-006 R8. The duration of this violation involves versions 2 and 3 of CIP-006. The text of all applicable versions of R8 are identical). RFC_URE2 determined that it did not implement a maintenance and testing program to help ensure all its physical security systems under CIP-006 R4, R5 and R6 function properly. ReliabilityFirst determined that RFC_URE2 violated CIP-006-2 R3 by failing to implement its maintenance and testing program to help ensure all its physical security systems under CIP-006 R4 R5 and R6 function properly. | CIP-006-2 | R8 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 tested the physical security systems just prior to its mandatory compliance date. At the time of testing, RFC_URE2's security vendor initially performed a number of tests on the physical security system. These included verifying that: (a) card readers work properly and record logging of entrants; (b) the system creates and maintains a database of entrants; (c) the system denies access to unauthorized cards; (d) the system alarms when a door is forced open or remains open for certain period of time; (e) the security cameras face all points of entry to each PSP and record footage to a DVR server; and (f) the badge creation system ensured that the created badges work and deactivated badges are denied. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 implemented a documented maintenance and testing program to help ensure its physical security systems under CIP-006-2 R4, R5, and R6 function properly | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 obtained a documented maintenance and testing program for the installed security system from its vendor to help ensure that all physical security systems under CIP-006 R4, R5 and R6 function properly. RFC_URE2 also updated all relevant documentation associated with CIP-006 R8 and notified all staff involved in managing Cyber Assets within the ESP of the newly created maintenance and testing program for its physical security systems. | 2011-04-30 | 2011-09-29 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100918 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R1 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R1. ReliabilityFirst determined the violation implicated sub-requirements R1.2 and R1.3. The duration of this violation spans versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R1 and its sub-requirements, other than the reference to the corresponding version of CIP-007, is identical). RFC_URE2 reported that while it has a procedure in place to help ensure new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls, it had no procedures for actual testing of any Critical Cyber Assets (CCAs) or Cyber Assets. Further, ReliabilityFirst determined that RFC_URE2 could not provide evidence that it performed security testing for Cyber Assets within the ESP or the results of the testing. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R1 by failing to document the testing it performed. Additionally, it failed to document the results of that testing, and therefore could not demonstrate that testing was performed in a manner that reflects the production environment or the results of that testing pursuant to CIP-007-2 R1.2 and R1.3. | CIP-007-2 | R1 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that this is the result of a documentation error. It is a documentation error because RFC_URE2 represents it performed testing in a test environment that reflects the production environment to Cyber Assets prior to RFC_URE2 installing any new Cyber Assets or making significant changes to existing Cyber Assets within the ESP. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 established and documented the security testing procedures and manner of testing | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 established and documented the security testing procedures and manner of testing for each category of Cyber Assets within its ESP and communicated the updates to all relevant staff. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100919 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R3 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R3. The duration of this violation involves versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R3 and its sub-requirements, other than the reference to the corresponding version of CIP-003, is identical). RFC_URE2 determined it had not established, documented or implemented a security patch management program for a specific class of Critical Cyber Assets (CCAs), access control and monitoring devices, and other Cyber Assets within its Electronic Security Perimeter (ESP) pursuant to CIP-007-2 R3. RFC_URE2 did not apply security patches to one Cyber Asset within its ESP during the duration of the violation. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R3 by failing to establish, document or implement a security patch management program for its specified class of CCAs, access control and monitoring devices, and other Cyber Assets within its ESP pursuant to CIP-007-2 R3. | CIP-007-2 | R3 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that RFC_URE2 subscribes to multiple security alerts to evaluate, on a monthly basis, if the indentified vulnerabilities are applicable to RFC_URE2's Cyber Assets and the possible level of threat. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 implemented its documented security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP pursuant to CIP-007-2 R3 | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 determined which CCAs within the ESP it must subject to security patch testing and determined whether security patches exist for the identified equipment. RFC_URE2 installed all applicable security patches to CCAs and Cyber Assets within its ESP and documented its security patch management program in accordance with CIP-007-2 R3's requirements. These updates were communicated to all relevant staff. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100920 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R4 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R4. The duration of this violation involves versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R4 and its sub-requirements is identical). RFC_URE2 determined it did not test its malware prevention signatures (Signatures) prior to installing the Signatures on one Cyber Asset, a transmission control room personal computer, within its Electronic Security Perimeter (ESP) (RFC_URE2 has other Cyber Assets within the ESP, however, they were not involved in this violation). RFC_URE2 had set the transmission control room personal computer to automatically update the anti-virus signature files directly from a server without prior testing. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R4 by failing to test its Signatures prior to installing the Signatures on one Cyber Asset within its ESP. | CIP-007-2 | R4 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that RFC_URE2 continued to use network intrusion detection systems, access controls at the firewall and system logging during the duration of the violation. Additionally, the Cyber Assets on which RFC_URE2 failed to test its Signatures prior to installation had no direct Internet access, which reduced the potential for exposure to malware. | Date RFC_URE2 was subject to compliance with the Standard | Date by which RFC_URE2 implemented a process for the update of its Signatures which included testing and installation | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 constructed an environment to test Signatures prior to installing them on assets within the ESP. RFC_URE2 also updated all documentation relevant to CIP-007-2 R4.2 compliance and notified staff engaged in managing Cyber Assets within the ESP of the changes to the documentation. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000302 | Settlement Agreement | SPP RE discovered a violation of CIP-004-1 R2.1 during a Spot Check. SPP RE determined that SPPRE_URE1 was noncompliant with the Standard by failing to train all personnel having authorized access to Critical Cyber Assets within 90 days of such authorization. SPPRE_URE1 had 58 employees that had physical and/or electronic access to Critical Cyber Assets (CCAs) at SPPRE_URE1’s primary control center (CC) and/or backup control center (BCC), but only six had received cyber security training required by CIP-004-1 R2.1 by the end of the year. Such training was provided in the summer of that year, and all of SPPRE_URE1's applicable operators received training on that date. By the end of the following year, seven more employees had been granted access to CCAs at the CC and/or BCC for a total of 65 employees. In spring of that year, the six employees who received training in the prior year were trained again, along with 28 others, leaving 31 employees without training at the end of the year. As of the beginning of the next year, assets beyond the control centers came into scope and 47 additional personnel (employees and contractors) with physical access to non-control center CCAs were required to be trained pursuant to CIP-004-1 R2.1. Thirty-two (32) of these individuals received training in the prior year. The remaining 15 had not received training within 90 days of the beginning of the year. Forty-five (45) individuals were removed from the access list and had their access revoked during the spring, the majority of whom were management personnel who did not require access to CCAs. As of the spring, seven total individuals remained on the access list without having received training; these seven individuals received their training by the end of the summer. | CIP-004-1 | R2.1 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all five energy control system operators completed training. Further, the 45 individuals removed in the spring were in roles that did not require access to CCAs. The access of these individuals was revoked in the spring. After removal of those individuals, only seven remained without training. These individuals were all trained by the end of the summer. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date individuals were trained | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | All individuals with electronic and unescorted physical access to CCAs who had not received the proper cyber security training received such training. A new training procedure was implemented to ensure that new employees and existing employees that are granted access to critical cyber assets receive timely cyber security training. Also, the procedure provides steps to ensure that annual training is timely received. The new program covers all of the requirements included in CIP-004 R2, and access list designees were required to take the new training program. SPPRE_URE1 will enforce revocation of access privileges in the event of expiration of any access designee's CIP-004 R2 training. Similarly, new access shall not be granted until successful completion of CIP-004 R2 online training is verified by the CIP Senior Manager. | 2011-03-28 | 2011-04-14 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000303 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-004-1 R3 during a Spot Check. An SPPRE_URE1 procedure did not provide for conducting background checks on incumbent employees. Although SPPRE_URE1 was required to comply with CIP-004-1 R3 for personnel with authorized access to control center assets, the earliest evidence indicating that SPPRE_URE1 informed the human resources department of the need to conduct background checks was almost a year later. The SPPRE_URE1 procedure was revised to include a provision requiring background checks in order to comply with CIP-004-1 R3. CIP-004-1 R3 allowed for a 30-day window in which Personnel Risk Assessments (PRAs) must be performed after issuance of authorized cyber or authorized unescorted physical access to Critical Cyber Assets. However, the required PRAs were not completed within 30 days of the effective date of the revised policy. There was only one employee who required newly granted access subsequent to when the procedure went into effect. That employee received access almost two months later and then had his access removed about six months later and never received a PRA. Managers and directors that had access to CCAs did not receive PRAs and had their access removed in the spring prior to the Spot Check. | CIP-004-1 | R3 | Medium | High | SPP RE determined that the violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The personnel that had not received PRAs were incumbent employees, many of them long-term SPPRE_URE1 employees. Most of the PRAs were completed within six months of the policy revision, and all were completed within eight months. None of the personnel failed to successfully pass a PRA. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date last affected employee's access was revoked | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 performed a review to ensure that all required PRAs had been conducted. A SPPRE_URE1 manager of Compliance reviewed the personnel and training procedure to ensure its sufficiency and attested that SPPRE_URE1 understands and will ensure that CCA access will not be granted in the future without first conducting a PRA. | 2010-10-01 | 2010-10-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000304 | Settlement Agreement | SPP RE discovered a violation of CIP-004-1 R4 during a Spot Check. A SPPRE_URE1 employee with authorized unescorted physical access to Critical Cyber Assets (CCAs) retired. The retired employee’s name was not removed from the SPPRE_URE1 CCA access list within seven days, as required by CIP-004-1 R4.1. Further, a review and approval of the list was performed almost two weeks after the employee retired, but SPPRE_URE1 failed to remove the retired employee’s name before approving the list. In addition, CIP-004-1 R4.2 requires the actual revocation of access to CCAs to occur within seven days for personnel who no longer require such access. SPP RE was unable to verify that such revocation occurred within seven days. Although SPPRE_URE1 took possession of the employee's access card on the day the employee retired, the employee was not removed from the access list until four months later. | CIP-004-1 | R4 | Medium | Moderate | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the retired employee was not removed from the access list until four months later, SPPRE_URE1 indicated that it in effect revoked access by taking possession of the retired employee's access card on the date of the retirement. The SPP RE spot check team verified that, as of the date of the spot check, the retired employee had been removed from the access control system, but could not verify the date of removal. The employee, who had been employed by SPPRE_URE1 since 1989, retired and was not involuntarily terminated. There was no evidence that the retired employee attempted to gain access subsequent to the date of retirement. Further, the employee had only unescorted physical access, not electronic access. Therefore, had the retired employee successfully gained physical access, he still would not have had a username and password with which to access the Supervisory Control and Data Acquisition System. The size of SPPRE_URE1 reduced the potential impact on the BPS. | The date by which retired employee's access should have been revoked | The date the retired employee was removed from the access list | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 removed the retired employee from the access list. SPPRE_URE1 performed a detailed review of its access list to ensure that the list is accurate and up-to-date. To help ensure future compliance, SPPRE_URE1 managers with duties pursuant to SPPRE_URE1's access control procedure certified that they are aware of their responsibilities under that procedure. | 2010-10-01 | 2010-10-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000305 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-007-1 R1 during a Spot Check. SPPRE_URE1 did not have a procedure per CIP-007-1 R1 for testing to ensure that cyber security controls were not adversely affected by new Cyber Assets introduced into the Electronic Security Perimeter (ESP) or by significant changes that were made to existing Cyber Assets within the ESP. The procedure that was in place prior to the revised procedure only included testing to ensure proper functionality. The testing procedure did not test for adverse effects on security controls. Therefore, security controls testing pursuant to CIP-007-1 R1 was not being performed before that date. | CIP-007-1 | R1 | Medium | Severe | SPP RE determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). At the time of the spot check, SPPRE_URE1 had already implemented a security controls testing procedure per CIP-007-1 R1; however, prior to the revised procedure, SPPRE_URE1's procedures only called for functional testing. As a result, the potential existed for the new assets and changes to existing assets to have an adverse impact on security controls, thereby causing SPPRE_URE1's Critical Cyber Assets to be more vulnerable to attack. Despite this vulnerability, the size of SPPRE_URE1 reduced the impact that potential attacks would have had on the BPS. | When Standard became mandatory and enforceable | The date SPPRE_URE1 implemented a security controls testing procedure per CIP-007-1 R1 | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 submitted its Mitigation Plan as complete because a complete security controls testing procedure has been created. The implementation of testing procedures for Cyber Assets within the ESP address testing of security controls where previous plans did not. | 2010-01-01 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000306 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-008-1 R1.6 during a Spot Check. SPPRE_URE1 tested its incident response plan the two prior years, but the forms documenting the tests do not demonstrate that the plan was fully tested. The documentation shows that for each of the tests a mock cyber incident was considered, the cause was determined, the potential impact was analyzed, and the incident handling steps to be taken were outlined. However, the documentation does not demonstrate that the incident was characterized as reportable and that the incident would have been reported to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC) as required by the incident response plan. Further, the completed forms do not show that all members of the cyber security incident response team were or would have been contacted as required by the plan. | CIP-008-1 | R1.6 | Lower | High | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 did not maintain sufficient documentation to demonstrate that the incident response plan was fully tested the two prior years, tests involving simulated cyber incidents were performed. Performing regular tests helps to ensure that SPPRE_URE1 will rely on and follow its incident response plan in the event of a true cyber incident. The size of SPPRE_URE1, reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 updated its plan and exercise to include the following Spot Check Team recommendations: - Adding alternative contact information to ES-ISAC; - Adding an ES-ISAC checkbox to response documentation; and - Aligning incident response classification and characterization criteria with NERC Incident Reporting Guideline. SPPRE_URE1 also performed a test per CIP-008-1 R1.6 of its incident response. Revisions to the plan went into effect. SPPRE_URE1 initially performed a test that SPP RE deemed to be still not fully in line with the Standard. After review and further discussion with SPPRE_URE1, SPP RE requested and received evidence demonstrating that a test per the Standard was performed. | 2011-01-18 | 2011-02-02 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000307 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-009-1 R1 during a Spot Check. The two prior versions of SPPRE_URE1's recovery plans only covered the restoration of backed-up data and information from tape. The plan did not address the recovery of all Critical Cyber Assets such as remote terminal units, server hardware, and other networking assets. The plans did not address recovery situations involving varying duration and severity as required by R1.1. The revised recovery plan addresses the requirements of the Standard. | CIP-009-1 | R1 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1, in addition to maintaining a backup control center, retains a standby unit for all CCA hardware. In the absence of a recovery plan for a particular asset, SPPRE_URE1 had the option to place the standby unit into service. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 revised its recovery plan to address the recovery of all Critical Cyber Assets such as remote terminal units, server hardware, and other networking assets and address recovery situations involving varying duration and severity. The revised recovery plan was implemented per the Standard. | 2010-05-07 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000308 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-009-1 R2 during a Spot Check. SPPRE_URE1's exercise of its CIP-009-1 recovery plans in the two prior years both involved actual occurrences of hardware failure; however, neither recovery scenario was covered in the existing recovery plans. The two prior versions of the recovery plans were found to be deficient, and a separate violation was found regarding R1 as well. To comply with R2, SPPRE_URE1 needed to test the recovery plan that was in place; it did not, and instead followed undocumented recovery procedures for assets not covered in the recovery plan. | CIP-009-1 | R2 | Lower | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE1's existing recovery plan did not cover the actual occurrences of hardware failure, the two prior versions of the exercises of its recovery plans still applied the framework of its recovery plans in recovering from the loss of a hard drive and the loss of a motherboard. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 developed a new form to better document both Critical Cyber Asset (CCA) recovery exercises and actual incident recovery. In addition, SPPRE_URE1 expanded the scope of its recovery plan to consider CCAs at the component level, allowing for better planning of individual CCA recovery. SPPRE_URE1 performed an exercise of its revised recovery plan per the Standard. | 2010-12-21 | 2011-02-02 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000330 | Settlement Agreement | During a Spot Check, SPP RE determined that SPP RE_URE2 was noncompliant with CIP-007-1 R1 for not adequately testing security controls when performing significant changes to Cyber Assets (CAs) within the Electronic Security Perimeter (ESP). Cyber security controls testing for updates made to existing CAs was not performed until 22 months after the compliance enforcement date. Only application functionality testing was being performed according to the Energy Management System (EMS) staff and confirmed by SPP RE by examining the submitted test results documentation. | CIP-007-1 | R1 | Medium | High | SPP RE determined that SPP RE_URE2’s violation of CIP-007-1 R1 posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had additional cyber security control measures in place that reduced its risk profile, including strict firewall rules and automated security analysis tools monitoring for security threats. Consequently, had there been a successful cyber attack against CAs within SPP RE_URE2's ESP, additional security control measures were in place to detect the event. Due to these factors, SPP RE determined that the risk to the BPS was moderate. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-007-1 R1 and to prevent reoccurrence, SPP RE_URE2 implemented a new procedure for testing cyber security controls. The new procedure utilizes a vulnerability program, which is used to scan SPP RE_URE2's network system, create scan reports, and compare scan reports against one another for potential vulnerabilities and remediation prior to implementing significant changes in SPP RE_URE2’s production systems. | 2010-05-13 | 2010-10-29 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000331 | Settlement Agreement | During a Spot Check, SPP RE determined that SPP RE_URE2 was noncompliant with CIP-008-1 R1.5 and R1.6. Regarding R1.5, although SPP RE_URE2 had an informal process for reviewing its Cyber Security Incident response plan and did conduct a review of the plan 15 months before the Spot Check, a formal process was not included in SPP RE_URE2’s Cyber Security Incident response plan until 3 months after that review or 1 year after the compliance enforcement date. Regarding R1.6, SPP RE_URE2 was required to test its Cyber Security Incident response plan by the date stated in the Implementation Plan for Cyber Security Standards Table; however, the test was not conducted until approximately 9 months after the enforceable date. | CIP-008-1 | R1; R1.5; R1.6 | Lower | High | SPP RE determined that SPP RE_URE2’s violation of CIP-008-1 R1 posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE2 failed to include a formal process in its Cyber Security Incident response plan (Plan) by the mandatory and effective compliance date of the Standard, SPP RE_URE2 did have an informal process for reviewing its Plan and conducted a review of the Plan. SPP RE_URE2 revised its Plan to include a process for an annual review. In addition, the identified incident response team had received comprehensive training on CIP Standards and are very experienced in the support of Critical Cyber Assets and would have reasonably been expected to recognize cyber security events, contain, and ultimately recover from an incident. Moreover, there have been no reported Cyber Security Incidents to date requiring activation of the Plan. Due to these factors, SPP RE determined that the risk to the BPS was minimal. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-008-1 R1 and to prevent reoccurrence, SPP RE_URE2 implemented a process for testing the Plan and began testing the Plan. SPP RE_URE2 revised its Plan to include a formal process to ensure an annual review of the plan. | 2009-03-25 | 2010-10-18 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000332 | Settlement Agreement | During a Spot Check, SPP RE determined SPP RE_URE2 was noncompliant with CIP-009-1 R1. Specifically, although SPP RE_URE2’s Critical Cyber Asset (CCA) recovery plan outlined how operations could be restored, it did not address how CCAs would be recovered from an actual incident. | CIP-009-1 | R1 | Medium | Severe | SPP RE determined that SPP RE_URE2’s violation of CIP-009-1 R1 posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had a recovery plan in place, as well as a business continuity plan, which addressed long-term recovery plans. Additionally, SPP RE_URE2’s backup control center could reasonably be expected to allow operations to continue at length until the primary control center could be recovered. Further, the entity support staff were experienced in the support of CCAs and could have performed the appropriate recovery steps for a wide variety of incidents. Due to these factors, SPP RE determined that the risk to the BPS was minimal. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-009-1 R1 and to prevent reoccurrence, SPP RE_URE2 amended its CCA recovery plan to include the recovery of CCAs. | 2010-10-27 | 2010-12-15 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.