## Public Non-CIP Oct. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA | NCR11171 | NPCC2012009728 | PRC-005-1a | R2; R2.1 | On January 27, 2012, National Grid USA, as a Distribution Provider and Transmission Owner, self-reported an issue with PRC-005-1a R2.1. National Grid USA failed to complete annual communication testing of a three-terminal transmission line within the intervals defined in its Protection System maintenance and testing program because of scheduling problems. The annual communication testing was scheduled to be completed by December 31, 2011 and was actually completed on January 27, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because National Grid USA did perform a non-intrusive inspection of its equipment associated with the transmission line. The risk during the pendency of the issue was mitigated by National Grid USA's inspection and testing on as much of its communications facilities as was possible without participation of the other entities. The system redundancies, system monitoring, and system alarming also mitigated the interim reliability risk. The transmission line is designed with two fully independent high-speed relaying systems for line protection. Neither system experienced any alarm conditions during the period of the issue. System tests were completed 27 days past the expected date with no problems found. NPCC considered the compliance history of affiliates and the fact that they do not share compliance documents or responsibilities, in determining that FFT treatment was warranted. | To mitigate this issue, National Grid USA adjusted its testing schedule so that the annual communication channel test for the transmission line will be scheduled earlier during each calendar year. The earlier scheduled test date will reduce the probability that the test will not be completed during the time period required by the National Grid USA procedure. The 2012 annual telecommunications testing is now scheduled for the beginning of October with a proposed rain date. Confirmation between all interconnected entities for the annual testing have been completed.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2012010199 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Altona Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since August 14, 2009, when Noble Altona Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Altona Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Altona Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Altona Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Altona Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2012010200 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Altona Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since August 14, 2009, when Noble Altona Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Altona Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Altona Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Altona Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Altona Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Altona Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2012010201 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Altona Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since August 14, 2009, when Noble Altona Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Altona Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Altona Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well as response guidelines for reporting those emergencies. Furthermore, Noble Altona Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 97.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Altona Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2012010206 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Bliss Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since October 15, 2008, when Noble Bliss Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Bliss Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Bliss Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Bliss Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Bliss Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2012010207 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Bliss Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since October 15, 2008, when Noble Bliss Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Bliss Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Bliss Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Bliss Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Bliss Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Bliss Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2012010208 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Bliss Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since October 15, 2008, when Noble Bliss Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Bliss Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Bliss Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well as response guidelines for reporting those emergencies. Furthermore, Noble Bliss Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Bliss Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2012010213 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Chateaugay Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since August 14, 2009, when Noble Chateaugay Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Chateaugay Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Chateaugay Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Chateaugay Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Chateaugay Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2012010214 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Chateaugay Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since August 14, 2009, when Noble Chateaugay Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Chateaugay Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Chateaugay Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Chateaugay Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Chateaugay Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Chateaugay Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2012010215 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Chateaugay Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since August 14, 2009, when Noble Chateaugay Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Chateaugay Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Chateaugay Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well as response guidelines for reporting those emergencies. Furthermore, Noble Chateaugay Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 106.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Chateaugay Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2012010192 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Clinton Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since October 15, 2008, when Noble Clinton Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Clinton Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Clinton Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Clinton Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Clinton Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2012010193 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Clinton Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since October 15, 2008, when Noble Clinton Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Clinton Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Clinton Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Clinton Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Clinton Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Clinton Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2012010194 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Clinton Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since October 15, 2008, when Noble Clinton Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Clinton Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Clinton Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well as response guidelines for reporting those emergencies. Furthermore, Noble Clinton Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 100.5 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Clinton Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2012010220 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Ellenburg Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since October 15, 2008, when Noble Ellenburg Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Ellenburg Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Ellenburg Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Ellenburg Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Ellenburg Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2012010221 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Ellenburg Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since October 15, 2008, when Noble Ellenburg Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Ellenburg Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Ellenburg Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Ellenburg Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Ellenburg Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Ellenburg Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2012010222 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Ellenburg Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since October 15, 2008, when Noble Ellenburg Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Ellenburg Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Ellenburg Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well a response guidelines for reporting those emergencies. Furthermore, Noble Ellenburg Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 81 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Ellenburg Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2012010706 | CIP-001-1 | R1 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Wethersfield Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R1 for failing to have a procedure for recognizing and making operating personnel aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. This condition existed since August 14, 2009, when Noble Wethersfield Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Wethersfield Windpark, LLC did not have a procedure for recognizing sabotage and making operating personnel aware of sabotage events on its facilities and multi-sabotage affecting larger portions of the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Wethersfield Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Furthermore, Noble Wethersfield Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Wethersfield Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2012010228 | CIP-001-1 | R2 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Wethersfield Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R2 for failing to have a procedure for communicating information concerning sabotage events to appropriate parties in the Interconnection. This condition existed since August 14, 2009, when Noble Wethersfield Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Wethersfield Windpark, LLC did not have a procedure for recognizing sabotage or communicating information concerning sabotage events to appropriate parties in the Interconnection, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Wethersfield Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage. Noble Wethersfield Windpark, LLC also had an emergency phone list, including the Federal Bureau of Investigation, for making notification of emergency events. Furthermore, Noble Wethersfield Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the Interconnection. | To mitigate the issue, Noble Wethersfield Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, including the communication of information concerning sabotage events to appropriate parties in the Interconnection; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2012010229 | CIP-001-1 | R3 | During an off-site Compliance Audit ending on July 1, 2011, NPCC determined that Noble Wethersfield Windpark, LLC, as a Generator Operator, had an issue with CIP-001-1 R3 for failing to have guidelines for its operating personnel for sabotage events, including all the personnel to contact for reporting disturbance due to sabotage events. This condition existed since August 14, 2009, when Noble Wethersfield Windpark, LLC was registered on the NERC Compliance Registry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Noble Wethersfield Windpark, LLC did not have sabotage response guidelines for reporting disturbances due to sabotage and therefore could not provide such guidelines to its operating personnel, its parent company, Noble Environmental Power, did have an emergency response policy, utilized by its affiliated wind generation units (including Noble Wethersfield Windpark, LLC), that raised awareness for many emergencies, including turbine equipment failure, detection of fires, and other events that would significantly affect the delivery of electricity to the grid and that could occur as a result of sabotage, as well as response guidelines for reporting those emergencies. Furthermore, Noble Wethersfield Windpark, LLC is a wind-powered variable energy facility with a maximum capacity of 126 MW. Its variable output prevents the facility from being dispatched to support base load or being deemed critical generation within the interconnection. | To mitigate the issue, Noble Wethersfield Windpark, LLC: 1. Implemented a written procedure for recognizing and making operating personnel aware of sabotage events, provided its operating personnel with sabotage response guidelines and included personnel to contact for reporting sabotage event disturbances; and 2. Provided sabotage training to site personnel. NPCC has verified completion of the mitigation activities.
ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge II Wind Farm LLC (Fowler Ridge II) | NCR03040 | RFC2012010792 | VAR-002-1.1b | R2 | During a Compliance Audit, conducted from May 2, 2011 to May 17, 2011, ReliabilityFirst discovered that Fowler Ridge III, as a Generator Operator, had an issue with VAR-002-1.1b R2. Fowler Ridge, Fowler Ridge II and Fowler Ridge III (collectively, Fowler Ridge Companies) are affiliates that share metering at their point of interconnection. Subsequently, on May 2, 2011, Fowler Ridge II, as a Generator Operator, self-reported this issue with VAR-002-1.1b R2 based on the same facts discovered at the Fowler Ridge III Compliance Audit. Fowler Ridge III is required to maintain Reactive Power output as defined by its Transmission Operator (TOP). American Electric Power provides criteria for Fowler Ridge III’s Reactive Power output in a power factor schedule within its Interconnection Service Agreement with the Fowler Ridge Companies. Fowler Ridge III’s power factor schedule requires a power factor of 1.00 plus or minus 5.0% at its Dequine 345 kV substation, also the point of interconnection with American Electric Power. On numerous occasions Fowler Ridge III failed to maintain the power factor within the required range. During the Compliance Audit, Fowler Ridge III provided an outdated power factor schedule that contained a narrower range. After the Compliance Audit, Fowler Ridge III provided the correct schedule, which resulted in fewer instances of Fowler Ridge III failing to maintain Reactive Power output. Additionally, because Fowler Ridge III shares metering with Fowler Ridge and Fowler Ridge II at its point of interconnection, it cannot determine which of the excursions were attributable to which affiliate. | ReliabilityFirst determined that this posed a minimal risk to the reliability of the bulk power system (BPS) because although the Fowler Ridge Companies failed to maintain their power factor schedule, the Fowler Ridge Companies maintained voltage at all relevant times and have not been directed to modify voltage since their initial operation. Additionally, all of the power factor excursions occurred when the output of the Fowler Ridge Companies was at or less than 25 percent of nameplate capacity, when the wind farms have limited dynamic reactive control, and would not have been considered excursions under the Fowler Ridge Companies’ power factor scheduled updated in July 2012. Moreover, as small, wind-powered generating facilities, the Fowler Ridge Wind Farm Complex’s generation output is variable by nature and not coincident with peak load. As a result of these inherent characteristics and its limited ability to produce dispatchable power, the Fowler Ridge Wind Farm Complex has a relative lesser impact on the BPS. | The Fowler Ridge Companies took action to mitigate the issue. The Fowler Ridge Companies worked with their TOP to revise their power factor schedule to better reflect design criteria, operating conditions, and characteristics inherent to the limited dynamic reactive control capabilities of wind farms. On July 20, 2012, American Electric Power issued a new power factor schedule that addresses these factors by applying the schedule to the Fowler Ridge Companies only when the units are online and generating greater than or equal to 25 percent of the total wind farm nameplate capacity.
ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge III Wind Farm LLC (Fowler Ridge III) | NCR10308 | RFC201100996 | VAR-002-1.1b | R2 | During a Compliance Audit, conducted from May 2, 2011 to May 17, 2011, ReliabilityFirst discovered that Fowler Ridge III, as a Generator Operator, had an issue with VAR-002-1.1b R2. Fowler Ridge, Fowler Ridge II and Fowler Ridge III (collectively, Fowler Ridge Companies) are affiliates that share metering at their point of interconnection. Fowler Ridge III is required to maintain Reactive Power output as defined by its Transmission Operator (TOP). American Electric Power provides criteria for Fowler Ridge III’s Reactive Power output in a power factor schedule within its Interconnection Service Agreement with the Fowler Ridge Companies. Fowler Ridge III’s power factor schedule requires a power factor of 1.00 plus or minus 5.0% at its Dequine 345 kV substation, also the point of interconnection with American Electric Power. On numerous occasions Fowler Ridge III failed to maintain the power factor within the required range. During the Compliance Audit, Fowler Ridge III provided an outdated power factor schedule that contained a narrower range. After the Compliance Audit, Fowler Ridge III provided the correct schedule, which resulted in fewer instances of Fowler Ridge III failing to maintain Reactive Power output. Additionally, because Fowler Ridge III shares metering with Fowler Ridge and Fowler Ridge II at its point of interconnection, it cannot determine which of the excursions were attributable to which affiliate. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because although the Fowler Ridge Companies failed to maintain their power factor schedule, the Fowler Ridge Companies maintained voltage at all relevant times and have not been directed to modify voltage since their initial operation. Additionally, all of the power factor excursions occurred when the output of the Fowler Ridge Companies was at or less than 25 percent of nameplate capacity, when the wind farms have limited dynamic reactive control, and would not have been considered excursions under the Fowler Ridge Companies’ power factor scheduled updated in July 2012. Moreover, as small, wind-powered generating facilities, the Fowler Ridge Wind Farm Complex’s generation output is variable by nature and not coincident with peak load. As a result of these inherent characteristics and its limited ability to produce dispatchable power, the Fowler Ridge Wind Farm Complex has a relative lesser impact on the BPS. | The Fowler Ridge Companies took action to mitigate the issue. The Fowler Ridge Companies worked with their TOP to revise their power factor schedule to better reflect design criteria, operating conditions, and characteristics inherent to the limited dynamic reactive control capabilities of wind farms. On July 20, 2012, American Electric Power issued a new power factor schedule that addresses these factors by applying the schedule to the Fowler Ridge Companies only when the units are online and generating greater than or equal to 25 percent of the total wind farm nameplate capacity.
ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge Wind Farm LLC (Fowler Ridge) | NCR10307 | RFC2012010791 | VAR-002-1.1b | R2 | During a Compliance Audit, conducted from May 2, 2011 to May 17, 2011, ReliabilityFirst discovered that Fowler Ridge III, as a Generator Operator, had an issue with VAR-002-1.1b R2. Fowler Ridge, Fowler Ridge II and Fowler Ridge III (collectively, Fowler Ridge Companies) are affiliates that share metering at their point of interconnection. Subsequently, on May 2, 2011, Fowler Ridge, as a Generator Operator, self-reported this issue with VAR-002-1.1b R2 based on the same facts discovered at the Fowler Ridge III Compliance Audit. Fowler Ridge III is required to maintain Reactive Power output as defined by its Transmission Operator (TOP). American Electric Power provides criteria for Fowler Ridge III’s Reactive Power output in a power factor schedule within its Interconnection Service Agreement with the Fowler Ridge Companies. Fowler Ridge III’s power factor schedule requires a power factor of 1.00 plus or minus 5.0% at its Dequine 345 kV substation, also the point of interconnection with American Electric Power. On numerous occasions Fowler Ridge III failed to maintain the power factor within the required range. During the Compliance Audit, Fowler Ridge III provided an outdated power factor schedule that contained a narrower range. After the Compliance Audit, Fowler Ridge III provided the correct schedule, which resulted in fewer instances of Fowler Ridge III failing to maintain Reactive Power output. Additionally, because Fowler Ridge III shares metering with Fowler Ridge and Fowler Ridge II at its point of interconnection, it cannot determine which of the excursions were attributable to which affiliate. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because although the Fowler Ridge Companies failed to maintain their power factor schedule, the Fowler Ridge Companies maintained voltage at all relevant times and have not been directed to modify voltage since their initial operation. Additionally, all of the power factor excursions occurred when the output of the Fowler Ridge Companies was at or less than 25 percent of nameplate capacity, when the wind farms have limited dynamic reactive control, and would not have been considered excursions under the Fowler Ridge Companies’ power factor scheduled updated in July 2012. Moreover, as small, wind-powered generating facilities, the Fowler Ridge Wind Farm Complex’s generation output is variable by nature and not coincident with peak load. As a result of these inherent characteristics and its limited ability to produce dispatchable power, the Fowler Ridge Wind Farm Complex has a relative lesser impact on the BPS. | The Fowler Ridge Companies took action to mitigate the issue. The Fowler Ridge Companies worked with their TOP to revise their power factor schedule to better reflect design criteria, operating conditions, and characteristics inherent to the limited dynamic reactive control capabilities of wind farms. On July 20, 2012, American Electric Power issued a new power factor schedule that addresses these factors by applying the schedule to the Fowler Ridge Companies only when the units are online and generating greater than or equal to 25 percent of the total wind farm nameplate capacity.
ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2012010447 | EOP-001-0 | R6 | On May 31, 2012, IPL, as a Balancing Authority (BA) and Transmission Operator, self-reported an issue with EOP-001-0 R6 to ReliabilityFirst. IPL has a Coordinated Functional Registration (CFR) with Midwest Independent Transmission System Operator (MISO) whereby MISO performs certain of IPL’s BA functions. The individual responsible for the Transmission System Emergency Operating Plan that IPL developed pursuant to EOP-001-0 R3.2 mistakenly believed that MISO would complete the annual review of this plan pursuant to the CFR. As a result of this mistake, IPL did not perform an annual review of this plan in 2011. In fact, IPL was required to annually review the Transmission System Emergency Operating Plan, as required by EOP-001-0 R6. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because the only substantial updates to the Transmission System Emergency Operating Plan during the pendency of the issue were organizational name changes and updated distribution lists. In addition, many of the elements of the plan existed within other emergency plans that IPL had properly reviewed and updated annually. | IPL committed to take certain actions to mitigate the issue. IPL reviewed and updated the Transmission System Emergency Operating Plan. In addition, IPL incorporated an electronic reminder to automatically send an alert to the individual responsible for updating the emergency plan.
ReliabilityFirst Corporation (ReliabilityFirst) | InterPower/ Ahlcon Partners, Limited Partnership [GOP] (InterPower) | NCR02604 | RFC2012009867 | VAR-002-1.1b | R2 | From November 7, 2011 through November 12, 2011, ReliabilityFirst conducted a Compliance Audit of InterPower (Audit). During the Audit, ReliabilityFirst discovered that InterPower, as a Generator Operator, had an issue with VAR-002-1.1b R2. InterPower’s voltage schedule for its 110 MW Colver generating plant is 116.5 kV plus or minus 1.5% for normal and light load conditions and 117.5 kV plus or minus 1.5% for heavy load conditions or when requested. On May 18, 2011, May 22, 2011, and September 14, 2011, during light load conditions, InterPower exceeded its voltage schedule by less than 1% of the voltage schedule. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system. The risk to the BPS was mitigated by the following factors. InterPower attested that its Transmission Operator (TOP) relies on the Colver generating plant as a reactive power resource in addition to maintaining the generator voltage schedule. InterPower’s TOP has provided direction to InterPower regarding the Colver plant’s generator voltage or reactive power output throughout both a voltage schedule and the ongoing expectation that InterPower operate the plant as a reactive power resource that results in slightly positive MVARs at the interconnection point. When operating the plant in this manner, system load variations may occasionally cause slight deviations from the voltage schedule. While InterPower did not seek or receive an exemption from its voltage schedule during these events, InterPower believed it was carrying out the directive of its TOP. In addition, the automatic voltage regulator was in automatic voltage control mode during the voltage excursions, and InterPower did not have a voltage excursion greater than 1%. | InterPower committed to take certain actions to mitigate the issue. InterPower worked with Corporate NERC Compliance to identify additional measures to better control the voltage output within the voltage schedule parameters while still responding to the expectation of slightly positive MVARs at the interconnection point as expected by the TOP. Specifically, InterPower posted the voltage schedule in the control room, conducted operator meetings on the use of the voltage schedule, and created voltage alarms in the control system to alert the operator of voltage deviations. In addition, between December 2011 and March 2012, InterPower's Corporate NERC Compliance staff initiated and completed a comprehensive VAR-002 R2 compliance review of its entire NERC-registered generation fleet. This was a review of 23 facilities located across five NERC regions and yielded no additional VAR-002 R2 compliance issues.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2012010014 | EOP-008-0 | R1 | From December 6, 2011 through December 13, 2011, ReliabilityFirst conducted a Compliance Audit of NIPSCO (Audit). During the Audit, ReliabilityFirst discovered that NIPSCO, as a Balancing Authority and Transmission Operator, had an issue with EOP-008-0 R1. ReliabilityFirst determined that NIPSCO’s Operations and Cyber Recovery Plan (Plan) to continue reliability operations if their control center becomes inoperable was not sufficient to demonstrate compliance with EOP-008-0, R1.5 and R1.6. Specifically, in its Plan NIPSCO states, “[t]he Electric Transmission Department is to coordinate tests, at least annually, of this recovery plan. Operating personnel shall review and undergo training at least annually on the procedures and responsibilities contained within this plan.” ReliabilityFirst determined, based on these two sentences, that the Plan lacked procedures and responsibilities for conducting periodic tests, at least annually, or for providing annual training pursuant to EOP-008-0 R1.5 and R1.6. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because it is a documentation issue. Although NIPSCO did not adequately document EOP-008-0 R1.5 and R1.6 in its Plan, NIPSCO conducted annual testing demonstrating the viability of the Plan and provided training to its personnel as part of its annual testing to ensure operating personnel were able to successfully implement the Plan. NIPSCO ensures the viability of the Plan and that operating personnel are able to implement the Plan by performing annual testing in which NIPSCO personnel successfully engage the backup control center and take over the operation of the energy management system to operate in real-time. NIPSCO utilizes various departmental documents, procedures, and checklists which tests the viability of the Plan during this annual exercise. The responsibilities for conducting periodic tests to ensure viability of the Plan are reflected in the various departmental documents, procedures, and checklists. Therefore, although NIPSCO’s Plan did not adequately address EOP-008-0 R1.5 and R1.6, NIPSCO was conducting an annual exercise during which NIPSCO successfully engaged its backup control center. This annual exercise included procedures and responsibilities that ensured the viability of the Plan and NIPSCO operating personnel’s ability to implement the Plan. | NIPSCO created a document on the procedures and responsibilities for conducting periodic tests and included procedures and responsibilities for providing annual training that reflects the practices it is already implementing.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Holtwood, L.L.C. (PPL Holtwood) | NCR00886 | RFC2011001215 | VAR-002-1.1b | R1 | On November 7, 2011, PPL Holtwood, as a Generator Operator, self-reported to ReliabilityFirst an issue with VAR-002-1.1b R1 and R3. On October 3, 2011, after flooding caused by a recent tropical storm, PPL Holtwood operations and maintenance personnel were working to locate and clear electrical grounds on the 125 volt direct current and 125 volt alternating current electrical systems. This work included checking the motor-operated valves on the plant drainage pumps in the operating tunnel and opening a circuit breaker and de-energizing a cabinet that contains plant control equipment. The ongoing work caused PPL Holtwood’s Unit 5 to reduce megawatt output from full output, which is approximately 10 MW. In response to a unit alarm alerting the hydro plant control operator to switch Unit 5’s turbine governor to manual mode, the hydro plant control operator switched Unit 5’s automatic voltage regulator (AVR) from automatic to manual voltage control mode. In response to the megawatt output reduction, the hydro plant control operator attempted to open the gates that control the flow of water supply for a hydroelectric generating unit, but could not do so until the governor was placed into hand control mode. At the time the hydro plant control operator placed the governor switch in hand control mode, the operator also placed the AVR in manual. However, the hydro plant control operator failed to notify the Transmission Operator (TOP) that the Unit 5 AVR was not in automatic voltage control mode, as required by VAR-002-1.1b R1. In addition, the hydro plant control operator failed to notify the TOP within 30 minutes of the status change on the AVR, as required by VAR-002-1.1b R3. The afternoon shift hydro plant control operator noticed that the Unit 5 AVR was operating in manual mode and switched the AVR back to automatic voltage control mode. At this time, PPL Holtwood notified the TOP of the status change on the Unit 5 AVR. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because during the time period of the issue, six generating units at PPL Holtwood were operating with their AVRs in automatic voltage control mode and were therefore able to provide any required voltage or reactive support. In addition, PPL Holtwood maintained its voltage schedule during the time period of the issue. A PJM letter confirming that the PPL Generation entities, which includes PPL Holtwood, "have not caused any reliability concerns on the PJM Bulk Electric System with respect to their operating within the PJM voltage criteria outlined in PJM Manual 14D” provides verification that no adverse system events occurred during the 6.5 hours that the AVR was in manual mode. Finally, the issue implicated one of the generating units, which had a ten MW generating capacity. | PPL Holtwood completed the following mitigating activities: 1) installed visible reminders at each voltage regulator control switch to prompt the operators to contact the individuals who notify the TOP when the AVR status changes; 2) implemented an additional level of monitoring by connecting the AVR status indication to the generation management system; 3) reviewed procedures related to excitation system operation in the various governor modes with the appropriate individuals; and 4) reviewed the NERC Reliability Standard Requirements with the appropriate individuals.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Holtwood, LLC (PPL Holtwood) | NCR00886 | RFC2011001216 | VAR-002-1.1b | R3 | On November 7, 2011, PPL Holtwood, as a Generator Operator, self-reported to ReliabilityFirst an issue with VAR-002-1.1b R1 and R3. On October 3, 2011, after flooding caused by a recent tropical storm, PPL Holtwood operations and maintenance personnel were working to locate and clear electrical grounds on the 125 volt direct current and 125 volt alternating current electrical systems. This work included checking the motor-operated valves on the plant drainage pumps in the operating tunnel and opening a circuit breaker and de-energizing a cabinet that contains plant control equipment. The ongoing work caused PPL Holtwood’s Unit 5 to reduce megawatt output from full output, which is approximately 10 MW. In response to a unit alarm alerting the hydro plant control operator to switch Unit 5’s turbine governor to manual mode, the hydro plant control operator switched Unit 5’s automatic voltage regulator (AVR) from automatic to manual voltage control mode. In response to the megawatt output reduction, the hydro plant control operator attempted to open the gates that control the flow of water supply for a hydroelectric generating unit, but could not do so until the governor was placed into hand control mode. At the time the hydro plant control operator placed the governor switch in hand control mode, the operator also placed the AVR in manual. However, the hydro plant control operator failed to notify the Transmission Operator (TOP) that the Unit 5 AVR was not in automatic voltage control mode, as required by VAR-002-1.1b R1. In addition, the hydro plant control operator failed to notify the TOP within 30 minutes of the status change on the AVR, as required by VAR-002-1.1b R3. The afternoon shift hydro plant control operator noticed that the Unit 5 AVR was operating in manual mode and switched the AVR back to automatic voltage control mode. At this time, PPL Holtwood notified the TOP of the status change on the Unit 5 AVR. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because during the time period of the issue, six generating units at PPL Holtwood were operating with their AVRs in automatic voltage control mode and were therefore able to provide any required voltage or reactive support. In addition, PPL Holtwood maintained its voltage schedule during the time period of the issue. A PJM letter confirming that the PPL Generation entities, which includes PPL Holtwood, "have not caused any reliability concerns on the PJM Bulk Electric System with respect to their operating within the PJM voltage criteria outlined in PJM Manual 14D” provides verification that no adverse system events occurred during the 6.5 hours that the AVR was in manual mode. Finally, the issue implicated one of the generating units, which had a ten MW generating capacity. | PPL Holtwood completed the following mitigating activities: 1) installed visible reminders at each voltage regulator control switch to prompt the operators to contact the individuals who notify the TOP when the AVR status changes; 2) implemented an additional level of monitoring by connecting the AVR status indication to the generation management system; 3) reviewed procedures related to excitation system operation in the various governor modes with the appropriate individuals; and 4) reviewed the NERC Reliability Standard Requirements with the appropriate individuals.
ReliabilityFirst Corporation (ReliabilityFirst) | Whitewater Operating Services, LLC (Whitewater) | NCR10156 | RFC2012010609 | VAR-002-1.1b | R3 | On June 25, 2012, Whitewater, as a Generator Operator, self-reported an issue with VAR-002-1.1b R3 to ReliabilityFirst. On June 10, 2012, Whitewater started its steam turbine generator and synchronized it to the grid at 6:24 a.m. Approximately 14 minutes later, Whitewater noticed the steam turbine generator’s automatic voltage regulator (AVR) was not controlling voltage automatically, at which time Whitewater’s shift operator began to control voltage manually. Whitewater notified its Transmission Operator (TOP), American Transmission Company, of the status change on its AVR 36 minutes after its steam turbine generator was synchronized to the grid. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because the issue was caused by an isolated incident; the Whitewater operator closing a breaker earlier in the generator’s startup procedures than required. The Whitewater operator began manual voltage control within 14 minutes of synchronization to the grid, and Whitewater notified its TOP within 36 minutes of the status change on its AVR. | On June 10, 2012, 36 minutes after the status change on its AVR, Whitewater notified its TOP. By virtue of this notification, Whitewater mitigated this issue.
ReliabilityFirst Corporation (ReliabilityFirst) | Whitewater Operating Services, LLC (Whitewater) | NCR10156 | RFC2012010677 | VAR-002-1.1b | R1 | On June 25, 2012, Whitewater, as a Generator Operator, self-reported an issue with VAR-002-1.1b R3 to ReliabilityFirst. ReliabilityFirst determined that the reported facts also constituted an issue with VAR-002-1.1b R1. On June 10, 2012, Whitewater started its steam turbine generator and synchronized it to the grid at 6:24 a.m. Approximately 14 minutes later, Whitewater noticed the steam turbine generator’s automatic voltage regulator (AVR) was not controlling voltage automatically, at which time Whitewater’s shift operator began to control voltage manually. Whitewater notified its Transmission Operator (TOP), American Transmission Company, of the status change on its AVR 36 minutes after its steam turbine generator was synchronized to the grid. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because the issue was caused by an isolated incident; the Whitewater operator closing a breaker earlier in the generator’s startup procedures than required. The Whitewater operator began manual voltage control within 14 minutes of synchronization to the grid, and Whitewater notified its TOP within 36 minutes of the status change on its AVR. | On June 10, 2012, 36 minutes after the status change on its AVR, Whitewater notified its TOP. By virtue of this notification, Whitewater mitigated this issue.
SERC Reliability Corporation (SERC) | Electric Energy, Inc. (EEI) | NCR01230 | SERC2011007386 | BAL-002-0 | R4 | On June 6, 2011, EEI, as a Balancing Authority (BA), self-reported an issue with BAL-002-0 R4.2, stating that it experienced a Reportable Disturbance in the form of a unit trip that resulted in a drop in the Area Control Error (ACE) greater than 80% of the most severe single contingency. Following that event, EEI did not return ACE to zero within 15 minutes as required by BAL-002-0 R4.2. On June 5, 2011, EEI’s Unit 3 tripped offline, resulting in a drop in the ACE greater than 80% of EEI’s largest single contingency. EEI’s largest single contingency is 167 MW. At the time of the event, Unit 3 was at 170 MW (158 MW net) and ACE was at +3 MW. ACE dropped to -163 MW immediately following the trip. The EEI systems operator contacted Midwest Independent Transmission System Operator, Inc. (MISO) to arrange a 170 MW coordinated adjustment to the interchange schedule. However, the systems supervisor was slow in entering the 10-minute ramped adjustment in supervisory control and data acquisition (SCADA) which caused EEI to exceed the 15 minute limit to restore ACE. EEI returned ACE to zero within 17 minutes of the start of the Reportable Disturbance. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. EEI was two minutes late in returning ACE to zero after the start of the Reportable Disturbance; and 2. MISO had sufficient reserves to cover the Disturbance Control Standard event. Although EEI has violated this Standard previously, the instant remediated issue nonetheless does not represent recurring conduct by EEI. The prior violation occurred in 2008, when EEI failed to achieve a Disturbance Control Standard (DCS) event average recovery of 100% for the third quarter of 2008. Following the prior violation, EEI reviewed the event with EEI system operators to reemphasize the BAL-002-0 requirements, reviewed EEI’s Reserve Policy, and also reviewed appropriate actions including options to utilize during a DCS event. In addition to the actions described in the Mitigation Plan, EEI also applied the appropriate Contingency Reserve Adjustment Factor (CRAF) of 101.75% relative to their single largest contingency of 167 MW, which increased EEI’s Contingency Reserve requirement from 167 MW to 170 MW to help prevent recurrence of a similar violation. The prior violation was considered and distinguished because it occurred approximately three years before the current issue, indicating this was not a problem with recurring conduct by EEI. | SERC verified that EEI has completed the following actions: 1. Conducted a performance improvement discussion with the employees involved in the event; 2. Communicated with the systems operator the importance of being able to curtail interchange schedules quickly in the event of a unit trip; 3. Increased EEI's Contingency Reserve obligation from 167 MW to 189 MW of curtailable interchange schedules; 4. Revised the job task in EEI's Quality Training Database for balancing the loss of a major generation resource by curtailing interchange; and 5. Re-trained each systems supervisor using the revised job task from the database and issued a memo re-emphasizing EEI's Reserve Policy.
SERC Reliability Corporation (SERC) | Electric Energy, Inc. (EEI) | NCR01230 | SERC2011007534 | PRC-005-1 | R2 | On June 28, 2011, EEI, as a Generator Owner (GO) and Transmission Owner (TO), self-reported an issue with PRC-005-1 R2, stating that it did not have evidence that all relays were maintained and tested within the defined intervals of its Protection System maintenance and testing program. SERC reviewed a spreadsheet prepared by EEI that included each of its Protection System devices and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC verified the defined intervals based on a review of EEI’s Protection System maintenance and testing procedures. Based on this review, SERC determined that EEI tested 16 out of 176 protective relays (9.1%) and five out of six batteries (83.3%) outside of their defined intervals. In total, EEI tested 21 out of 556 Protection System devices (3.8%) outside of their defined intervals. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. EEI’s batteries are alarmed with direct current (DC) ground, loss of power, and voltage alarms, which would alert EEI personnel to possible problems and prompt them to investigate; 2. Although EEI conducted the five-year battery load test three to six years outside of the defined interval, it still tested and maintained the batteries according to the monthly, quarterly and annual requirements; and 3. Although the relays were tested two to five years late, EEI’s subsequent testing of the relays was successful and found no problems, suggesting that the relays likely would have performed as intended if called upon to do so. | SERC verified that EEI has completed the following actions: 1. Tested the 16 identified protective relays and documented the test results; 2. Revised its internal procedures such that the system engineer responsible for protective relays will review EEI's list of NERC auditable relays on an annual basis and verify that the list is complete and accurate and that all of the relays on the list are scheduled for regular testing within the defined intervals in the Protection System maintenance and testing procedure. The system engineer is also required to work with the maintenance planning department to ensure that work orders are automatically generating for the testing of each NERC auditable relay and that procedures exist so that testing can be performed. The revised procedure also requires the maintenance supervisor responsible for protective relays to conduct a quarterly review of all work orders related to NERC auditable maintenance and verify that the work orders are issued and executed timely. A list of open NERC auditable work orders is generated and distributed to the group supervisor electrical maintenance and the system engineer; and 3. Revised its internal procedures such that the system engineer responsible for batteries is required to work with the maintenance planning department to ensure that work orders are automatically generating for the testing of each battery set and that procedures exist so that testing can be performed. The revised procedure also requires the maintenance supervisor responsible for batteries to conduct a quarterly review of all work orders related to NERC auditable maintenance and verify that the work orders are issued and executed within the required timeframe. A list of open NERC auditable work orders is generated and distributed to the group supervisor electrical maintenance and the system engineer.
SERC Reliability Corporation (SERC) | Electric Energy, Inc. (EEI) | NCR01230 | SERC2011007876 | FAC-008-1 | R1 | On August 10, 2011, the SERC audit team reported an issue with FAC-008-1 R1, stating that EEI, as a Transmission Owner (TO), did not include series and shunt compensation devices within the scope of its Facility Ratings Methodology (FRM). SERC reviewed EEI’s 2010 version of its FRM and confirmed the audit team’s finding that the FRM did not include series and shunt compensation devices for the TO function. SERC also determined that the FRM failed to address series and shunt compensation devices for the Generator Owner function. SERC reviewed all versions of EEI’s FRM back to June 18, 2007 and confirmed that series and shunt compensation devices were not addressed in any of them. EEI owns a bus tie series reactor and developed a Facility Rating for the series reactor using its nameplate rating. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. EEI considered series and shunt compensation devices despite its failure to document it. EEI owns a bus tie series reactor, which is a series compensation device. EEI developed and used a Facility Rating for the series reactor using its nameplate rating; and 2. After documenting series and shunt compensation devices in its FRM, EEI’s Rating for the series reactor did not change and the most limiting device did not change. | SERC verified that EEI revised its FRM to include a section detailing its rating methodology for series and shunt compensation devices.
SERC Reliability Corporation (SERC) | Gulf Power Company (Gulf) | NCR01252 | SERC2012009778 | PRC-005-1 | R2 | On February 24, 2012, Gulf, as a Generator Owner (GO), self-reported an issue with PRC-005-1 R2, stating that it was unable to establish that eight relay sets associated with a standby spare station service transformer at its Scholz generating plant were tested within the intervals defined in its Protection System maintenance and testing program due to the misclassification of the relays as not subject to the NERC Reliability Standards. While Gulf identified eight relays as noncompliant in its Self-Report, further analysis of the data determined that four of the eight self-reported relays had a 12-year interval and had been maintained and tested within the defined interval. In the course of performing this inventory of Protection System equipment, Gulf determined that two other relays also associated with the standby spare station service transformer connected to Unit 1 of the Scholz generating plant were not accounted for in the original eight relays reported to SERC. SERC reviewed a spreadsheet prepared by Gulf that included each of its Protection System devices and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. Based on this review, SERC determined that Gulf tested five out of 1,160 protective relays (0.4%) approximately two years outside of the defined interval and did not have previous test or maintenance records for one out of 1,160 protective relays (0.1%). In total, Gulf had six out of 2,319 Protection System devices (0.3%) that were tested outside of the defined interval or had missing previous test or maintenance records. SERC staff verified that there were no findings relating to Gulf’s Protection System devices under its Transmission Owner (TO) function. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. Gulf personnel conduct daily rounds through the plant and would have observed relay targets had the six relays operated unexpectedly. Gulf personnel did not observe any such unexpected operation of these relays; 2. Gulf subsequently calibrated the six relays and found no issues, suggesting that the devices likely would have performed as intended; and 3. Unit 1 of Gulf’s Scholz generating plant has a normal generation output of 49 MW, which represents 1.7% of Gulf's total generation capacity. In addition, Unit 1 has had an average capacity factor of 23% since 2007. Although Gulf has violated this Standard previously, the instant remediated issue nonetheless does not represent recurring conduct by Gulf. The prior violation occurred in 2007, in the early stages of mandatory compliance, when Gulf failed to have documentation that its batteries were maintained and tested within the intervals identified in its maintenance and testing program. Following the prior violation, Gulf revised its Preventive Maintenance Plan to specify monthly testing, ensured that the batteries were inspected and tested and documentation was retained, communicated the requirements to appropriate plant maintenance personnel. The prior violation was considered and distinguished because it dealt with the lack of documentation to show that the batteries had been maintained and tested, while the instant issue deals with the misclassification of six relays as not subject to the NERC Reliability Standards. | SERC verified that Gulf has completed the following actions: 1. Calibrated the NERC relay sets associated with the standby spare station service transformer at its Scholz generating plant for which the previous test record (or lack thereof) indicated the prescribed test interval had been exceeded; 2. Ensured that all relays associated with the standby spare station service transformer at its Scholz generating plant are appropriately identified as NERC or non-NERC in its Protection System Equipment Database (PEDS); 3. Reviewed the use of the term “Spare” in the purpose field of the relay record for all relays (both NERC and non-NERC) in PEDS. Gulf also revised the purpose field as appropriate to more clearly specify whether the protective relay is in use or not in use; and 4. Reviewed the use of the attribute “New” in the relay record for all relays (both NERC and non-NERC) in PEDS to ensure appropriate usage.
SERC Reliability Corporation (SERC) | Hopewell Cogeneration Limited Partnership (Hopewell) | NCR01256 | SERC2012010259 | PRC-005-1 | R2 | On May 15, 2012, Hopewell, as a Generator Owner, self-reported an issue with PRC-005-1 R2, stating that during an internal assessment of Hopewell’s Protection System, Hopewell found that the interval for battery load testing had been exceeded and that there was no evidence of testing the DC control circuitry prior to October 2009. SERC reviewed a spreadsheet compiled by Hopewell providing a complete inventory of its Protection System devices and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC verified the assigned intervals based on a review of Hopewell’s Protection System maintenance and testing procedure, ensuring consistency between the listed intervals provided in the spreadsheet. SERC determined that Hopewell tested the following Protection System devices outside of its defined intervals: four out of four station batteries (100%) and four out of four DC control circuitry devices (100%). In total, Hopewell tested eight out of 265 Protection System devices (3.0%) outside of the defined interval. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. Hopewell’s battery charger and DC system has basic alarming in the control system. These alarms are part of a supervisory control and data acquisition (SCADA) system that allows the operators to monitor the alarms continuously which would allow Hopewell personnel to respond to a battery or charger failure; 2. Hopewell missed one monthly maintenance interval in July 2010 for all four batteries and the two-year interval for three out of the four batteries by approximately three years, but otherwise met all maintenance and testing intervals. Hopewell also visually inspected the batteries monthly and annually. Hopewell subsequently conducted load tests on the batteries and replaced faulty cells, but found no other issues; 3. Power flow analysis simulating the loss of Hopewell under peak conditions was performed on August 15, 2012 and demonstrated that the loss of Hopewell would not cause a reliability impact on the transmission system; and 4. Hopewell subsequently tested its DC control circuitry devices and found no issues | SERC verified that Hopewell completed the following actions: 1. Tested its DC control circuitry in 2010 and load tested its batteries in 2011; 2. Entered the tasks associated with these tests into Hopewell's maintenance management system as work orders to prevent missing the defined intervals going forward; and 3. Trained plant personnel on the defined elements and the associated intervals of Hopewell's Protection System maintenance and testing program on July 26, 2012.
SERC Reliability Corporation (SERC) | Hopewell Cogeneration Limited Partnership (Hopewell) | NCR01256 | SERC2012010788 | PRC-005-1 | R1 | On July 25, 2012, Hopewell, as a Generator Owner, self-reported an issue with PRC-005-1 R1, stating that its Protection System maintenance and testing program did not include associated communication system (ACS) devices as required by the Standard. Although Hopewell does not own ACS devices, it failed to include a statement to that effect in its procedure. SERC reviewed Hopewell’s Protection System maintenance and testing procedures and verified that the procedures included protective relays, voltage and current sensing devices, batteries, and DC control circuitry, including the maintenance and testing intervals and their basis, and a summary of maintenance and testing for each of these device types. SERC also verified that the procedure did not address ACS devices. Although Hopewell does not own ACS devices, it failed to include a statement to that effect. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the only omission from Hopewell’s Protection System maintenance and testing procedures was a statement that Hopewell does not own any ACS devices. | SERC verified that Hopewell completed the following actions: 1. Revised its Protection System maintenance and testing procedures on July 27, 2012 to include a statement that Hopewell does not own any ACS devices; and 2. Trained plant personnel on the defined elements and the associated intervals of Hopewell's Protection System maintenance and testing procedures on July 26, 2012.
SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LG&E-KU) | NCR01223 | SERC2012010372 | FAC-009-1 | R1 | On May 31, 2012, LG&E-KU, as a Transmission Owner (TO), self-reported an issue with FAC-009-1 R1, stating that it discovered a Facility Rating that was not in accordance with its Facility Ratings Methodology (FRM). While preparing for 2012 Self-Certifications, LG&E-KU discovered one instance in which it failed to properly apply its FRM. LG&E-KU’s FRM stated that the emergency rating for field verified Facilities should be the lesser of the verified maximum operating temperature or 212 degrees Fahrenheit (°F). LG&E-KU self-reported that the Ghent-Fairview 138 kV line, which was specifically designed to operate at 283°F, had been rated at this field verified 283°F temperature, not at 212°F as required by the FRM. As part of its assessment, SERC reviewed LG&E-KU’s FRM and its Facility Ratings and found that the Ghent-Fairview line identified in the Self-Report was the only Facility that had a Facility Rating that was not consistent with the LG&E-KU FRM. LG&E-KU, as a TO, maintains Facility Ratings for 319 Facilities. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. The line was modeled and operated at its designed rating and therefore operating the line at 283°F would not have damaged the line; and 2. The use of the designed rating meant that the Ghent-Fairview line was not the most limiting element. Although LG&E-KU has violated this Standard previously, the instant remediated issue nonetheless does not represent recurring conduct by LG&E-KU. The prior violation occurred in 2010, when LG&E-KU failed to establish a Facility Rating consistent with its FRM. Following the prior violation, LG&E-KU upgraded its outage request software to include a required field to identify any Facility Ratings impact associated with an outage request, implemented Cascade, a new software tool to replace LG&E-KU’s Facility Rating Program, and trained the appropriate personnel on the use and implementation of Cascade. The prior violation was considered and distinguished because it dealt with a reconfiguration of equipment, which resulted in a reduced Facility Rating and was not updated for approximately two months. The instant issue involved the improper application of the FRM, which was mitigated by addressing high temperature conductors in the revised FRM. The rating of the affected line was not reduced in the current issue. | SERC verified that LG&E-KU completed the following actions: 1. Reviewed all of its transmission conductor ratings to verify that the conductor ratings were consistent with the FRM; 2. Reviewed all of its transmission Facility Ratings to verify that all transmission Facility Ratings were equal to the most limiting applicable equipment rating of the individual equipment that comprises that Facility; and 3. Updated the FRM to address the existence of high temperature conductors on the LG&E-KU Bulk Electric System.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2011008216 | FAC-008-1 | R1 | This remediated issue is based on a consolidation of a Self-Report and a Compliance Audit finding. On August 26, 2011, LAFA, as a Generator Owner (GO) and a Transmission Owner (TO), self-reported its noncompliance with FAC-008-1 R1 because it had not included relay protective devices in its Facility Ratings Methodology (FRM) for its generator and transmission facilities. In a subsequent Compliance Audit conducted on September 22, 2011, the SPP RE audit team identified noncompliance with FAC-008-1 R1, finding that LAFA’s FRM for establishing the Facility Rating for its generating facilities did not specifically reference the spreadsheet by which LAFA determines generator Ratings; did not clearly identify the methodology by which bus Ratings were determined; did not include Normal and Emergency Ratings; and did not clearly identify the method for determining Normal and Emergency Ratings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Notwithstanding LAFA’s failure to adequately document its FRM and include protective relays in its FRM analysis, the Facility Ratings established by LAFA for its transmission and generation facilities were consistent with the actual Ratings of the facilities and no new limiting elements were identified. Accordingly, the changes made to LAFA’s FRM in response to this instance of noncompliance did not result in any changes to the Ratings of LAFA’s transmission and generating facilities. Additionally, the Emergency Ratings for LAFA’s generating facilities are the same as its Normal Rating of the facilities, thereby further reducing the risk to the BPS. | LAFA modified its Generator Ratings Methodology to include: the determination of Normal and Emergency Ratings; identification of how its Facility Ratings are determined; and address the determination of bus Ratings. LAFA further modified its FRM to include relay protective devices in the determination of Facility Ratings for transmission and generation facilities.
Southwest Power Pool Regional Entity (SPP RE) | Oklahoma Gas And Electric Co. (OG&E) | NCR01130 | SPP201100547 | VAR-002-1.1b | R3.1 | During an SPP RE Compliance Audit conducted from April 18, 2011 to April 21, 2011, the SPP RE audit team discovered that OG&E was noncompliant with VAR-002-1.1b R3.1. While reviewing an OG&E plant voltage summary for September 27, 2010, the SPP RE audit team noticed that the automatic voltage regulator (AVR) for two of OG&E’s generation facilities were shown to be in manual mode. The SPP RE audit team requested evidence that OG&E’s generator operators had notified the transmission operators within 30 minutes of this AVR status changes. OG&E could not provide evidence that the communication of manual AVR operation for September 27, 2010, was within 30 minutes. This instance of noncompliance applies to OG&E's Generator Operator (GOP) function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although OG&E’s plant voltage summary for September 27, 2010 indicated two of its generation facilities were in manual AVR mode, OG&E’s plant records indicate that the plants' AVRs were actually in automatic mode the entire time. OG&E found that one generation facility’s AVR was incorrectly displayed in manual mode, via a supervisory control and data acquisition (SCADA) signal, from March 27, 2010 until October 26, 2010. The second generation facility’s AVR manual status was due to an error by a transmission system operator. OG&E’s transmission system operators have the ability to toggle the status of a unit’s AVR upon receiving communication from a generation operator. This ability either reminds a transmission system operator of the status of a unit’s AVR or communicates the status to another transmission operator in the event of a shift change. OG&E's second generation facility’s status change occurred on September 27, 2010, only, and it occurred as a toggle error on the part of the operator rather than an actual status change. | OG&E inspected its SCADA terminals and associated equipment to ensure that the equipment was in proper working order to accurately communicate AVR statuses. Also, OG&E revised its Instructions & Methods (I&M) NERC Standard VAR-002-1.1b to improve its communication processes. It also created a NERC Voltage Regulator Outage Log to better document communication of AVR status changes to the transmission system operators. OG&E developed training for the I&M NERC Standard VAR-002-1.1b and NERC Voltage Regulator Outage Logs, and implemented this training.
Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP201000419 | PRC-005-1 | R1.2 | On October 1, 2010, Westar self-reported its noncompliance with PRC-005-1 R1.2. Specifically, Westar reported that three of its power plants did not include a summary of maintenance and testing procedures in their Protection System testing and maintenance programs for station batteries. Westar has an Electrical Maintenance Manual,which identifies Westar's maintenance and testing program for all Protection System components. It includes intervals and testing procedures for Protection System devices. However, Westar opted to include further battery maintenance and testing programs at individual plants and the Electrical Maintenance Manual could no longer cover the three plants identified in the Self-Report. At the time of the Self-Report, Westar had plant-specific Protection System testing and maintenance programs at each of its 13 power plant locations. This instance of noncompliance applies to Westar's Generator Owner (GO), Transmission Owner (TO) and Distribution Provider (DP) functions. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Westar did not have a summary of station battery maintenance and testing procedures in its Protection System maintenance and testing program for three of its 13 plant locations, Westar’s Protection System maintenance and testing program documentation was otherwise complete through the implementation of its Electrical Maintenance Manual. Also, Westar had performed visual inspections of the station batteries at the three 3 plants during the period of non-compliance, thereby further reducing the risk to the BPS. | Westar created a generic Generation Battery Inspection, Maintenance, and Test Procedure to address requirements at all plant locations on the Westar system. This procedure documents the basis, and sets the minimum requirements for battery system maintenance and testing at Westar's generating plants.
Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP201000438 | VAR-001-1 | R1 | From October 4, 2010 to October 7, 2010, the SPP audit team conducted a Compliance Audit of Westar, as a Transmission Operator (TOP), and discovered that Westar was noncompliant with VAR-001-1 R1. Although Westar had implemented a formal policy for monitoring and controlling voltage levels and megavolt-ampere reactive (Mvar) flows, the SPP RE audit team found that Westar’s policy lacked sufficient procedural instructions to ensure that its transmission system operators could monitor and control voltage levels and Mvar flows within Westar's individual areas and with the areas of the neighboring TOPs. More specifically, the audit team found that Westar's policy lacked documentation of Westar’s generator voltage schedules; a procedure for how to obtain target system voltage (only the voltage range was defined within the policy); a procedure to explain what actions are necessary when addressing Mvar flow; and a procedure for automatic control for reactive devices on the Westar system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although not specifically documented in the Westar procedure, Westar’s transmission system operators provide voltage schedules to the Westar generating plants. Westar’s System Operating Manual establishes a target system voltage by stating a voltage range based on a percentage of the nominal voltage. System operators operate to the representative nominal voltage and within the range indentified. Although Westar did not address when reactive resources are activated within its System Operating Manual, transmission system operators monitor voltage-ampere reactive (VAR) flows via the Westar supervisory control and data acquisition (SCADA) system and utilize manual and automatic control of reactive resources to control system voltage. | Westar revised its System Operating Manual-Electric, as well as its System Voltage Regulation Procedure to include specific elements for generator voltage schedules, target voltage, Mvar flow policy, and automatic control of reactive devices. The revised procedure was effective on March 20, 2011.
Texas Reliability Entity, Inc (Texas RE) and Southwest Power Pool Regional Entity (SPP RE) | Kiowa Power Partners, LLC (KPP) | NCR04088 | TRE201100482 SPP2011008328 | PRC-005-1 | R2 | On October 7,2011 and October 13, 2011,KPP, as a Generator Owner (GO), self-reported to Texas RE and SPP RE, respectively, noncompliance with PRC-005-1 R2. KPP's Generator Protection System maintenance and testing program provided that unit and station battery maintenance frequency should be conducted on a weekly, monthly and quarterly frequency for various tasks. Collection of records for an internal review of NERC compliance revealed that numerous inspection interval records were missing. In 2009, KPP discussed and decided to eliminate weekly voltage battery checks and to modify the scope of the existing monthly and quarterly maintenance. Weekly, monthly and quarterly maintenance were considered due to the continuous monitoring of battery systems' voltage characteristics. In spite of KPP's 2009 decision, the maintenance and testing program description required by PRC-005-1 remained unchanged. Moreover, battery maintenance tasks were included in KPP's Computerized Maintenance Management System (CMMS) but were not tagged in the CMMS as NERC compliance-related Preventive Maintenance (PM) tasks. As a result, weekly battery tasks were routinely omitted between February 1, 2009 and September 19, 2011. This remediated issue involved a total of ten batteries. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE and SPP RE considered this remediated issue to be documentation-related, as it represents a failure of KPP to update its maintenance and testing program to accurately reflect the actual testing intervals. Furthermore, all battery banks were continuously monitored and set to alarm in the Control System on high and low voltage, as well as ground fault and communication issues. KPP has also submitted its maintenance and testing reports to demonstrate that it has consistently performed monthly and quarterly testing on its batteries throughout the period at issue. None of the battery systems showed any indications of issues through monitoring or on the inspection subsequent to a missed interval. | KPP has since updated its maintenance and testing program to reflect the correct intervals at which KPP performs tests.
Western Electricity Coordinating Council (WECC) | City of Riverside Public Utilities (CYRS) | NCR05093 | WECC2012010798 | EOP-004-1 | R3 | On July 30, 2012, CYRS, as a Load Serving Entity, self-reported an issue with EOP-004-1 R3. Subsequently, a WECC Subject Matter Expert (SME) contacted CYRS to discuss its Self-Report. CYRS stated that it discovered in an internal review that it failed to submit a disturbance report to NERC and WECC after its system experienced a reportable disturbance. Specifically, on October 26, 2007, CYRS experienced a disturbance where it lost more than 50% of its total load for approximately four hours. Although CYRS did not submit the disturbance report within twenty-four hours, CYRS did submit a report to both NERC and WECC on October 29, 2007 (within forty-eight hours). The SME concluded that CYRS had an issue with EOP-004-1 R3 and referred the matter to WECC Enforcement (Enforcement). Enforcement reviewed CYRS’s Self-Report, as well as the SME’s findings. Enforcement determined that CYRS had an issue with EOP-004-1 R3 because its system experienced a reportable event and CYRS did not submit a report to NERC and WECC within twenty-four hours, as required by the Standard. Enforcement determined the issue began on October 27, 2007, when CYRS should have submitted its report to NERC and WECC, and ended on October 29, 2007, when CYRS did submit its report to NERC and WECC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because CYRS notified the Department of Energy (DOE), NERC, and WECC of the disturbance affecting the entity's load within twenty-four hours. CYRS submitted the disturbance report as required by the Standard within seventy-two hours after the start time of the event to DOE, NERC, and WECC. In addition, CYRS restored all load within four hours of the disturbance and it did not trip off any generation or affect any WECC interconnection. | CYRS addressed this issue when it submitted the disturbance report to NERC and WECC within seventy-two hours of the event. To prevent future occurrences of this issue, CYRS adopted a Standard Practice document on August 8, 2008 specifically addressing disturbances (SP 230.001). In the Standard Practice document, disturbances are analyzed, and DOE and NERC-required reports are completed and provided to the DOE, NERC, WECC, the WECC Reliability Coordinator and the California ISO. In addition, CYRS is implementing additional training for its personnel in Energy Delivery Dispatch Operations regarding the revisions to SP 230.001. Also, on September 9, 2008, CYRS adopted an Internal Compliance Program that provides an overall framework for its compliance activities.
Western Electricity Coordinating Council (WECC) | Gila River Power, LP (PGR) | NCR05170 | WECC2012010801 | TOP-005-2a | R3 | On July 13, 2012, PGR, as Purchasing-Selling Entity, self-reported an issue with TOP-005-2a R3. PGR self-reported that it failed to deliver information as requested by its Host Balancing Authority (BA) and Transmission Operator (TOP) that require daily information updates. PGR produces the Gila River 7-Day Availability Report (Report) daily (except weekends). The Report contains information about the next seven days regarding plant availability (planned and unscheduled outages), Automatic Voltage Regulator and Power System Stabilizer status, and the status of the telecommunications and metering equipment. On June 26, 2012, PGR provided a 7-Day Availability Report providing operational information through July 3, 2012. On July 7, 2012, PGR provided another 7-Day Availability Report, leaving a reporting gap of three days July 4, 2012 through July 6, 2012. PGR discovered the issue when the BA contacted PGR and asked for the Reports. WECC determined that PGR had an issue with TOP-005-2a R3 because PGR had not provided information as requested by its BA and TOP to enable them to conduct operational reliability assessments and coordinate reliable operations. Enforcement determined that although PGR did not provide the Report, it did conduct a daily operational call with its BA and TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because PGR had daily phone calls with the TOP and the BA knew the status of all generation and transmission resources available for use. PGR had daily phone calls with the TOP to ensure that it knew the status of all generation and transmission resources available for use. The BA was able to access PGR’s current-day and next-day scheduled operations through the Open Access Technology, Inc. system at any time. Also during the issue period, PGR confirmed that all units were running as expected, and there were no unplanned or scheduled outages. PGR’s generation plant is a natural gas plant that only operates when it is economically feasible, and is not part of the base generation necessary to serve load. | WECC determined that PGR remediated this issue. Upon discovery, PGR resumed providing the Report to its TOP and BA.
Western Electricity Coordinating Council (WECC) | Gila River Power, LP (PGR) | NCR05170 | WECC2012010802 | TOP-006-2 | R1 | On July 13, 2012, PGR, as a Generator Operator, self-reported an issue with TOP-006-2 R1. PGR and Sundevil Power Holdings, LLC are affiliates and are co-owners of the Gila River plant. PGR self-reported that the Gila River 7-Day Availability Report (Report) was not delivered daily to its Transmission Operator (TOP) and Balancing Authority (BA) as required by TOP-006-2 R1. This Report is produced daily (except weekends) and contains information about the next seven days regarding plant availability (planned and unscheduled outages), Automatic Voltage Regulator and Power System Stabilizer status, and the status of the telecommunications and metering equipment. On June 26, 2012, PGR provided a Report providing operational information through July 3, 2012; and on July 7, 2012, PGR provided another Report, leaving a reporting gap of three days: July 4, 2012 through July 6, 2012. PGR discovered the issue when BA contacted PGR and asked for the Reports. WECC determined that PGR had an issue with TOP-006-2 R1, specifically sub-requirement R1.1, because PGR did not inform its TOP and BA of all generation resources available for use as required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because PGR had daily phone calls with the TOP and the BA knew the status of all generation and transmission resources available for use. PGR had daily phone calls with the TOP to ensure that it knew the status of all generation and transmission resources available for use. The BA was able to access PGR’s current-day and next-day scheduled operations through the Open Access Technology, Inc. system at any time. Also during the issue period, PGR confirmed that all units were running as expected, and there were no unplanned or scheduled outages. PGR’s generation plant is a natural gas plant that only operates when it is economically feasible, and is not part of the base generation necessary to serve load. | WECC determined that PGR remediated this issue. Upon discovery, PGR resumed providing the Report to its TOP and BA.
Western Electricity Coordinating Council (WECC) | Gila River Power, LP (PGR) | NCR05170 | WECC2012010964 | TOP-002-2b | R3 | On July 13, 2012, PGR, as Generator Operator and a Load Serving Entity, self-reported an issue with TOP-002-2b R3. PGR and Sundevil Power Holdings, LLC are affiliates and are co-owners of the Gila River plant. PGR self-reported that the Gila River 7-Day Availability Report (Report) was not delivered daily to its Transmission Service Provider (TSP) and Balancing Authority (BA) as required by the Standard. This Report is produced daily (except on weekends) and contains information about the next seven days regarding plant availability (planned and unscheduled outages), Automatic Voltage Regulator and Power System Stabilizer status, and the status of the telecommunications and metering equipment. On June 26, 2012, PGR provided the Report providing operational information through July 3, 2012; and on July 7, 2012, PGR provided another Report, leaving a reporting gap of three days: July 4, 2012 through July 6, 2012. PGR discovered the issue when the BA contacted PGR and asked for the Reports. A WECC subject matter expert (SME) reviewed the Self-Report and conducted an interview with PGR compliance personnel. The SME determined that PGR had an issue with TOP-002-2b R3 because PGR had not coordinated its current-day, next-day and seasonal operations with its TSP and BA. WECC Enforcement determined that even though PGR did not provide this Report, it did conduct a daily operational call with its BA and TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because PGR had daily phone calls with the TOP and the BA knew the status of all generation and transmission resources available for use. PGR had daily phone calls with the TOP to ensure that it knew the status of all generation and transmission resources available for use. The BA was able to access PGR’s current-day and next-day scheduled operations through the Open Access Technology, Inc. system at any time. Also during the issue period, PGR confirmed that all units were running as expected, and there were no unplanned or scheduled outages. PGR’s generation plant is a natural gas plant that only operates when it is economically feasible, and is not part of the base generation necessary to serve load. | WECC determined that PGR remediated this issue. Upon discovery, PGR resumed providing the Report to its TSP and BA.
Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2012011017 | BAL-004-WECC-01 | R2 | During a Compliance Audit, conducted from July 9, 2012 to July 20, 2012, WECC determined that IPCO, as a Balancing Authority synchronously connected to the Western Interconnection, failed to notify other Balancing Authorities of Automatic Time Error Correction (ATEC) outages on seven occasions between November 30, 2009 and July 6, 2011 in accordance with BAL-004-WECC-01 R2. In its pre-audit disclosures, IPCO reported that it “uses the WECC Net Messaging System to notify the other Balancing Authorities in the interconnection whenever its Automatic Generation Control (AGC )system is expected to be out of Automatic Time Error Correction mode for a significant time frame (2 or more hours).” On July 18, 2012, WECC issued a data request to IPCO for all copies of communications to WECC Balancing Authorities for all instances in which IPCO was not operating ATEC in its AGC system between August 8, 2009 and July 20, 2012. IPCO identified ten instances that it operated in any AGC operating mode other than ATEC between November 30, 2009 and July 6, 2011. In seven of these instances, IPCO removed ATEC from service for less than two hours, and, per its policy, did not issue notice required under BAL-004-WECC-01 R2. The WECC Audit Team determined that IPCO’s failure to notify Balancing Authorities of ATEC outages lasting less than two hours constitutes an issue with BAL-004-WECC-01 R2. WECC Enforcement reviewed the WECC Audit Team's findings and IPCO disclosures. Enforcement determined that BAL-004-WECC-01 R2 requires Balancing Authorities that operate synchronously to the Western Interconnection to notify other Balancing Authorities through the designated Interconnection communication system when it operates in any ACG operating mode other than ATEC. In this case, IPCO removed ATEC from service on seven occasions between November 30, 2009, and July 6, 2011. Enforcement determined that IPCO was required to issue notice to other Balancing Authorities per BAL-004-WECC-01 R2 on each occasion. Enforcement, therefore, determined that IPCO had an issue with BAL-004-WECC-01 between November 30, 2009, and July 6, 2011. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because ATEC outages in this case were limited to seven instances of less than two hours duration. Long-term operation without ATEC in service coincident with large inadvertent energy accumulations may result in more frequent manual time error corrections. Balancing Authorities are not required to acknowledge that they are aware of the change in status or to take any actions in response. | IPCO revised its operation policy to require all operators to notify other Balancing Authorities that operate synchronously to the Western Interconnect when it operates AGC in a mode other than ATEC for any duration. IPCO also instructed operations staff to notify all Balancing Authorities in the event of an ATEC outage for any amount of time. IPCO completed mitigation activities as of July 27, 2012.
Western Electricity Coordinating Council (WECC) | Judith Gap Energy LLC (JUGE) | NCR05503 | WECC2012010808 | PRC-004-2a | R3 | On July 31, 2012, JUGE, as a Generator Owner, self-reported an issue with PRC-004-2a R3. On August 16, 2012, a WECC Subject Matter Expert (SME) contacted JUGE to discuss its Self-Report. According to the WECC SME, on March 23, 2012, JUGE’s system experienced one, isolated relay misoperation and JUGE failed to report that relay misoperation with sixty days of submitting its report for the second quarter of 2012. In this instance, the relay misoperation occurred at a relay on one of JUGE’s 34.5 kV buses. The bus reported a fault and sent a signal to the 230 kV breaker to trip. The 230 kV operated correctly and tripped off the generation running at that time. The relay involved was set erroneously, which resulted in the misoperation. The SME referred the matter to WECC Enforcement. WECC Enforcement reviewed JUGE’s Self Report and the SME’s findings. Enforcement determined that JUGE's issue with PRC-004-2a R3 existed from May 31, 2012, the date by which it should have reported the relay misoperation, until August 31, 2012, when it remediated this issue by reporting the relay misoperation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system . JUGE did not provide WECC its misoperations analysis and corrective actions plans within the time frame of two months for non-major Remedial Action Schemes and Transmission paths. As compensating measures, JUGE did submit the report the following quarter. In addition, JUGE’s generation facility is rated at 135 MW and is not critical to its Transmission Operator. | In order to remediate this issue, JUGE reported its relay misoperation in its third quarter report to WECC. In order to prevent the failure to report a misoperation in the future, JUGE purchased and implemented software for protection system queries and analysis, as well as implemented quarterly protection system to record events and review of those events between JUGE’s engineering department, its site manager, and its compliance manager.
Western Electricity Coordinating Council (WECC) | Sundevil Power Holdings, LLC (SDPH) | NCR11146 | WECC2012010807 | TOP-006-2 | R1 | On July 13, 2012, SDPH, as a Generator Operator, self-reported an issue with TOP-006-2 R1. SDPH and Gila River Power, LP are affiliates and are co-owners of the Gila River plant. Gila River Power, LP self-reported that the Gila River 7-Day Availability Report (Report) was not delivered daily to its Transmission Operator (TOP) and Balancing Authority (BA) as required by TOP-006-2 R1. This Report is produced daily (except weekends) and contains information about the next seven days regarding plant availability (planned and unscheduled outages), Automatic Voltage Regulator and Power System Stabilizers status, and the status of the telecommunications and metering equipment. On June 26, 2012, SDPH provided a Report providing operational information through July 3, 2012; and on July 7, 2012, SDPH provided another Report, leaving a reporting gap of three days: July 4, 2012 through July 6, 2012. SDPH discovered the issue when the BA contacted SDPH and asked for the Reports. WECC determined that SDHP had an issue with TOP-006-2 R1, specifically sub-requirement R1.1, because it did not inform its BA and TOP of all generation resources available for use as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because SDPH had daily phone calls with its TOP and the BA knew the status of all generation and transmission resources available for use. SDPH had daily phone calls with the TOP to ensure that it knew the status of all generation and transmission resources available for use. The BA was able to access SDPH’s current-day and next-day scheduled operations through the Open Access Technology, Inc. system at any time. Also during the issue period, SDPH confirmed that all units were running as expected, and there were no unplanned or scheduled outages. SDPH’s generation plant is a natural gas plant that only operates when it is economically feasible, and is not part of the base generation necessary to serve load. | WECC determined that SDPH remediated this issue. Upon discovery, SDPH resumed providing the Report to its TOP and BA.
Western Electricity Coordinating Council (WECC) | Sundevil Power Holdings, LLC (SDPH) | NCR11146 | WECC2012010938 | TOP-002-2b | R3 | On July 13, 2012, SDPH, as a Generator Operator, self-reported an issue with TOP-002-2b R3. SDPH and Gila River Power, LP are affiliates and are co-owners of the Gila River plant. Gila River Power, LP self-reported that the Gila River 7-Day Availability Report (Report) was not delivered daily to its Transmission Service Provider (TSP) and Balancing Authority (BA) as required by TOP-006-2 R1. This Report is produced daily (except on weekends) and contains information about the next seven days regarding plant availability (planned and unscheduled outages), Automatic Voltage Regulator and Power System Stabilizer status, and the status of the telecommunications and metering equipment. On June 26, 2012, SDPH provided the Report providing operational information through July 3, 2012; and on July 7, 2012, SDPH provided another Report, leaving a reporting gap of three days: July 4, 2012 through July 6, 2012. SDPH discovered the issue when the Host BA contacted SDPH and asked for the Reports. A WECC subject matter expert (SME) reviewed the Self-Report and conducted an interview with SDPH compliance personnel. The SME determined that SDPH had an issue with TOP-002-2b R3 because SDPH had not coordinated its current-day, next-day and seasonal operations with its BA and its TSP as required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because SDPH had daily phone calls with its TOP and the BA knew the status of all generation and transmission resources available for use. SDPH had daily phone calls with the TOP to ensure that it knew the status of all generation and transmission resources available for use. The BA was able to access SDPH’s current-day and next-day scheduled operations through the Open Access Technology, Inc. system at any time. Also during the issue period, SDPH confirmed that all units were running as expected, and there were no unplanned or scheduled outages. SDPH’s generation plant is a natural gas plant that only operates when it is economically feasible, and is not part of the base generation necessary to serve load. | WECC determined that SDPH remediated this issue. Upon discovery, SDPH resumed providing the Report to its TSP and BA.
Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC2012010635 | TOP-002-2b | R14 | On July 3, 2012, UNWW, as a Generator Operator, self-reported an issue with TOP-002-2b R14. UNWW’s Lower Monumental Project has six hydroelectric units with a total output of 2,529 MW. According to UNWW’s Self-Reports, on January 6, 2012, two of the six hydroelectric units were generating 250 MW of their 297 MW capacity. Two units were idle, but listed as available, and the other two units were out of service for maintenance and for an exciter upgrade. As part of the next phase of exciter replacement, a UNWW operator performed testing on the two units that were not in-service, but available. UNWW did not report the changes in real output capabilities to the Balancing Authority (BA) during the tests or restoration of the units, or the restoration of the related circuit breaker. These operations required a total of 42 minutes. A WECC subject matter expert (SME) reviewed the Self-Report and conducted an interview with UNWW's compliance personnel, and determined that UNWW had an issue with TOP-002-2b R14. WECC Enforcement reviewed the Self-Report and the SME’s findings and determined that for a gap of 42 minutes UNWW had an issue with TOP-002-2b R14 because it failed to notify its BA and Transmission Operator (TOP) of changes in its generator availability. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. UNWW knew that it could bring the unit into service within the required time period, if requested by the BA. As compensating measures, during the 42 minutes that one of the units listed as available was in fact not available, the units that were in-service were capable of generating an additional 47 MW if requested by the BA. Additionally, if the host BA or TOP requested the unit be put into service during the 42 minutes of downtime, UNWW had other units that could be brought online. Each of the six units at the Lower Monumental Project is rated at 155 MW. UNWW had the capability to bring at least one additional generating unit on-line at any time. | WECC determined that UNWW addressed this issue. On September 5, 2012, UNWW submitted mitigation activities. UNWW proposed to train its operators on the need and purpose for outage coordination with its BA. UNWW remediated the issue when two units were again available, consistent with the information it had given its BA.
Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC2012010709 | TOP-006-2 | R1 | On July 3, 2012, UNWW, as a Generator Operator, self-reported an issue with TOP-006-2 R1. UNWW’s Lower Monumental Project has six hydroelectric units with a total output of 2,529 MW. According to UNWW’s Self-Report, on January 6, 2012, two of the six hydroelectric units were generating 250 MW of their 297 MW capacity. Two units were idle, but listed as available, and the other two units were out-of-service for maintenance and for an exciter upgrade. As part of the next phase of exciter replacement, a UNWW operator performed testing on the two units that were not in-service, but available. UNWW did not report the changes in real output capabilities to the Balancing Authority (BA) during the tests or restoration of the units, or the restoration of the related circuit breaker. These operations required a total of 42 minutes. A WECC subject matter expert (SME) reviewed the Self-Report and interviewed UNWW's compliance personnel, and determined that UNWW had an issue with TOP-006-2 R1. WECC Enforcement reviewed the Self-Report and determined that UNWW failed to notify its BA and Transmission Operator (TOP) of changes in its generator availability, and therefore had an issue with TOP-006-2 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. UNWW knew that it could bring the unit into service within the required time period, if requested by the BA. As compensating measures, during the 42 minutes that one of the units listed as available was in fact not available, the units that were in-service were capable of generating an additional 47 MW if requested by the BA. Additionally, if the host BA or TOP requested the unit be put into service during the 42 minutes of downtime, UNWW had other units that could be brought online. Each of the six units at the Lower Monumental Project is rated at 155 MW. UNWW had the capability to bring at least one additional generating unit on-line at any time. | On September 5, 2012, UNWW submitted mitigation plans to address this issue. On October 11, 2012, UNWW submitted its Certification of Completion, certifying completion on October 11, 2012. To mitigate this issue, UNWW developed and reviewed its training program. It provided a PowerPoint presentation that was given to all UNWW operators, as well as training logs. WECC determined UNWW completed this mitigation plan on October 11, 2012, the date the training was complete for all operators.