## Public Non-CIP Nov. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2012011147 | MOD-008-1 | R1; R1.2 | During a Compliance Audit on September 27, 2012, FRCC discovered that SEC, as a Transmission Operator, had an issue with MOD-008-1 R1. SEC's Transmission Reliability Margin Implementation Document (TRMID) did not include the description of the method used to allocate Transmission Reliability Margin (TRM) across SEC's Available Transfer Capability (ATC) Paths for the reserve sharing requirement portion of the TRM. SEC's response to an FRCC Audit data request includes a description of the method used, but that description is not included in the TRMID, as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that SEC was performing according to the methodology stated in the data request and all of the requirements were being met and implemented for the compliance period, but the TRMID documentation was lacking a description of the methodology. | To mitigate this issue, SEC revised its TRMID, contained within department practice SOP-Guide-013, to include a description of the method used to allocate TRM across SEC’s ATC Paths for the reserve sharing requirement portion of the TRM. Also, SEC posted the revised TRMID to its Open Access Same-Time Information System (OASIS) website as well as to the FRCC website for operating entities, and affected entities were notified of the revised document. FRCC has verified the Mitigation Plan completion.
Midwest Reliability Organization (MRO) | Tatanka Wind Power, LLC (TWP) | NCR10245 | MRO2012011005 | IRO-001-1.1 | R8 | On September 4, 2012, TWP as a Generator Operator, self-reported an issue with IRO-001-1.1 R8 because it failed to comply with reliability directives issued by its Reliability Coordinator (RC). On July 12, 2011, Dickey County, North Dakota (where TWP is partially located) experienced severe weather and as a result transmission facilities were constrained. Therefore, TWP was under a production curtailment of varying levels per direction of its RC from July 12, 2011 until December 19, 2011 (Constrained Period). TWP's RC provided several levels of production curtailment, limiting TWP generation from 105 MW to 120 MW at different times during the Constrained Period. There were ten instances where TWP unintentionally and momentarily exceeded the production curtailment level. On average, the duration of each excursion was 6.5 minutes for 7.6 MW. The highest point of excursion was 19 MW. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TWP exceeded its production curtailment level a small number of times, ten times, for an average of 7.6 MW for 6.5 minutes. TWP is interconnected to a 230 kV transmission line and such small and short excusions (7.6 MW for 6.5 minutes) would not pose anything more than a minimal risk to the 230 kV transmission line and to the BPS. Additionally, TWP is a non-dispatchable intermittent wind generation resource, consisting of 120 1.5 MW wind turbine generators (WTGs) for an aggregate capability of 180 MW, straddling the border of North Dakota and South Dakota. | TWP has taken the following actions to minimize the reoccurrence of similar events: 1) On August 2, 2011, TWP installed two autopilot programs in order to decrease the reaction time for responding to wind speed variations, thus, assisting in keeping TWP under the production curtailment level; 2) On August 12, 2011, TWP revised the settings in the autopilot program to further improve their response time; 3) TWP implemented a protocol that requires the autopilot program to be shut down and restarted on a monthly basis to ensure that it is operating as designed, and to safeguard its effectiveness to adhering to the TWP production curtailment level; 4) TWP implemented a protocol under which its server resets are scheduled through one individual with the responsibility to ensure that TWP will not exceed production curtailment during the resets, by, among other things, ensuring that the electric system operator (ESO) has manually stopped enough WTGs at their maximum generation rating to ensure that at no time would TWP be capable of exceeding the production curtailment during the server reset; and 5) TWP purchased a new, integrated generation control system which will be more robust than autopilot because it is a product provided by TWP’s software vendor and it runs on the program logic controllers and is a hardware solution. The ESO uses the supervisory control and data acquisition system only as an interface into this system, therefore resetting or rebooting the servers has no effect on generation control.
Midwest Reliability Organization (MRO) | Tatanka Wind Power, LLC (TWP) | NCR10245 | MRO2012011006 | TOP-001-1 | R3 | On October 28, 2011, TWP as a Generator Operator, self-certified an issue with TOP-001-1 R3 because it failed to comply with reliability directives issued by its Reliability Coordinator (RC). On July 12, 2011, Dickey County, North Dakota (where TWP is partially located) experienced severe weather and as a result transmission facilities were constrained. Therefore, TWP was under a production curtailment of varying levels per direction of its RC from July 12, 2011 until December 19, 2011 (Constrained Period). TWP's RC provided several levels of production curtailment, limiting TWP generation from 105 MW to 120 MW at different times during the Constrained Period. There were ten instances where TWP unintentionally and momentarily exceeded the production curtailment level. On average, the duration of each excursion was 6.5 minutes for 7.6 MW. The highest point of excursion was 19 MW. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TWP exceeded its production curtailment level a small number of times, ten times, for an average of 7.6 MW for 6.5 minutes. TWP is interconnected to a 230 kV transmission line and such small and short excusions (7.6 MW for 6.5 minutes) would not pose anything more than a minimal risk to the 230 kV transmission line and to the BPS. Additionally, TWP is a non-dispatchable intermittent wind generation resource, consisting of 120 1.5 MW wind turbine generators (WTGs) for an aggregate capability of 180 MW, straddling the border of North Dakota and South Dakota. | TWP has taken the following actions to minimize the reoccurrence of similar events: 1) On August 2, 2011, TWP installed two autopilot programs in order to decrease the reaction time for responding to wind speed variations, thus, assisting in keeping TWP under the production curtailment level; 2) On August 12, 2011, TWP revised the settings in the autopilot program to further improve their response time; 3) TWP implemented a protocol that requires the autopilot program to be shut down and restarted on a monthly basis to ensure that it is operating as designed, and to safeguard its effectiveness to adhering to the TWP production curtailment level; 4) TWP implemented a protocol under which its server resets are scheduled through one individual with the responsibility to ensure that TWP will not exceed production curtailment during the resets, by, among other things, ensuring that the electric system operator (ESO) has manually stopped enough WTGs at their maximum generation rating to ensure that at no time would TWP be capable of exceeding the production curtailment during the server reset; and 5) TWP purchased a new, integrated generation control system which will be more robust than autopilot because it is a product provided by TWP’s software vendor and it runs on the program logic controllers and is a hardware solution. The ESO uses the supervisory control and data acquisition system only as an interface into this system, therefore resetting or rebooting the servers has no effect on generation control.
ReliabilityFirst Corporation (ReliabilityFirst) | American Transmission Co. LLC (ATC) | NCR00685 | RFC2011001267 | FAC-009-1 | R1 | On December 21, 2011, ATC self-reported an issue with FAC-009-1 R1 to ReliabilityFirst,as a Transmission Owner. On September 8, 2011, ATC commenced a project at its Butler Substation to remedy congestion issues in southeastern Wisconsin (Project). Upon completion of the Project, ATC planned to establish a rating of 1688 amps for its Granville-Butler 138 kV transmission line (Line 3453). ATC established the planned 1688 amp rating in accordance with its Facility Ratings Methodology (Methodology). The outage associated with the Project also provided ATC with an opportunity to evaluate Line 3453 pursuant to the NERC Facilities Ratings Alert. On September 9, 2011, ATC discovered a field condition on Line 3453 that required ATC to establish a more restrictive Facility Rating. The field condition ATC discovered on September 9, 2011, was a clearance to underbuild discrepancy. ATC remediated the field condition on March 28, 2012 when it lowered the underbuild at issue. Upon discovery of the field condition, ATC approved an interim rating for Line 3453 of 1420 amps consistent with its Methodology. ATC authorized the 1420 amp rating to stay in effect until May 1, 2012 to allow sufficient time to complete any necessary corrective actions in the field on Line 3453. Upon completion of the Project in late September 2011, ATC incorrectly recorded the rating for Line 3453 as 1688 amps. On October 12, 2011, ATC approved and validated the 1688 amp rating for Line 3453 and uploaded it into ATC’s energy management system (EMS) and provided the rating to its Reliability Coordinator (RC). On November 3, 2011, during a closeout review of the Project, ATC identified that the 1688 amp rating was the incorrect rating for Line 3453 and that due to a discovered field condition, the rating should be 1420 amps. In response to the discovery, ATC revised its Facility Rating for Line 3453 to 1420 amps. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. First, the maximum loading of Line 3453 during the duration of the issue was 770 amps. Second, ATC has a documented Methodology which it used to determine both Facility Ratings associated with Line 3453. Finally, the issue does not indicate a systemic issue with ATC's Methodology or its application. Rather, the issue was an isolated incident which ATC immediately mitigated upon discovery. | In its Self-Report, ATC stated that on November 11, 2011, it revised its ratings on Line 3453 from 1688 amps to 1420 amps so as to be consistent with its Methodology.
ReliabilityFirst Corporation (ReliabilityFirst) | Northampton Generating Company (Northampton) | NCR00852 | RFC2011001268 | FAC-008-1 | R1; R1.2 | During the Compliance Audit, ReliabilityFirst discovered an issue with FAC-008-1 R1 by Northampton, as a Generator Owner. ReliabilityFirst analyzed Northampton’s Facility Ratings Methodology dated August 23, 2010. ReliabilityFirst determined that this methodology did not include a specific method for rating current sensing devices, or current transformers (CTs). Instead, this methodology stated that the ratings for CTs would meet or exceed full load current. ReliabilityFirst reviewed Northampton’s Facility Ratings Methodology in place prior to August 23, 2010 and determined that it contained a substantially similar statement with respect to CTs. In August of 2010, Northampton switched operating companies to NAES Corporation. As a result of this switch, Northampton modified its NERC-related programs, including its Facility Ratings Methodology. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Northampton provided commissioning test data for CTs which demonstrated that ratings for those CTs existed. The ratings were consistent with the Facility Ratings Methodology. Furthermore, throughout the pendency of this issue, Northampton maintained and implemented a Facility Ratings Methodology that considered all required elements, although the document lacked specificity regarding Northampton’s consideration of CTs. Finally, Northampton designed its generator so that CTs would not limit the rating of the associated element or facility. | Northampton revised its Facility Ratings Methodology to include statements regarding the method by which it determines ratings for CTs.
ReliabilityFirst Corporation (ReliabilityFirst) | Northampton Generating Company (Northampton) | NCR00852 | RFC2011001269 | PRC-005-1 | R1 | During the Compliance Audit, ReliabilityFirst discovered an issue with PRC-005-1 R1 by Northampton, as a Generator Owner. Northampton’s Protection System maintenance and testing program, submitted to demonstrate compliance with PRC-005-1 R1, stated that Northampton did not perform periodic maintenance and testing for current transformers (CTs) and potential transformers (PTs) at defined intervals. Rather, Northampton waited until a device exhibited problems and performed maintenance and testing at that time. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Northampton provided evidence demonstrating that it tested its CTs and PTs upon commissioning the generating station in 1995. Northampton had not required periodic maintenance for CTs and PTs based on recommendations from the devices’ manufacturers. The manufacturer designed these particular CTs to require very little maintenance. Additionally, Northampton had summarized the maintenance and testing procedures to be applied if a CT or PT experienced a problem. | Northampton revised its Protection System maintenance and testing program to require periodic testing of CTs and PTs. Northampton also committed to complete testing on its CTs and PTs during an outage.
ReliabilityFirst Corporation (ReliabilityFirst) | Northampton Generating Company (Northampton) | NCR00852 | RFC2011001270 | PRC-005-1 | R2 | During the Compliance Audit, ReliabilityFirst discovered an issue with PRC-005-1 R2 by Northampton, as a Generator Owner. Specifically, ReliabilityFirst discovered that Northampton was missing records demonstrating that it tested its two battery systems quarterly, as required by its maintenance and testing program. Specifically, Northampton failed to produce testing records for the fourth quarter of 2008, and the first, third and fourth quarters of 2010. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Northampton provided work orders indicating that Northampton requested testing to be performed by a contractor and that such testing was scheduled for completion during the impacted calendar quarters. ReliabilityFirst considered these work orders as strong evidence that these quarterly tests did occur. | Northampton revised its procedures for maintenance and testing of batteries to more clearly delineate tasks associated with this maintenance and testing. Northampton also completed quarterly testing in accordance with these revised procedures
ReliabilityFirst Corporation (ReliabilityFirst) | Wabash Valley Power Association, Inc. (Wabash) | NCR00940 | RFC2011001251 | PRC-005-1 | R1 | On December 8, 2011, Wabash self-reported to ReliabilityFirst an issue with PRC-005-1 R1, as a Distribution Provider that owns a transmission Protection System. Wabash determined that it did not have a maintenance and testing program for Protection System devices in two of its substations that interconnect above 100 kV. The configuration of the two substations at issue is extremely rare for Wabash. In the ReliabilityFirst region, Wabash has approximately 297 points at which it is interconnected with transmission facilities owned by other utilities. Only approximately 8% of the interconnection points are operated at 100 kV or above, and only 1% of the interconnection points are operated at 100 kV or above and contain a transmission Protection System necessitating a maintenance and testing program. Specifically, Wabash has one Protection System relay and one battery system consisting of 60 battery cells at its Wheatfield substation (Wheatfield). Wheatfield provides protection from the high side of the 138 kV/12.47 kV transformer to the low side 12.47 kV station bus. Wabash’s single Protection System relay at Wheatfield ties into the protection scheme operated by an interconnected utility, Northern Indiana Public Service Company (NIPSCO), thereby requiring Wabash’s compliance with PRC-005-1 R1. If the Wheatfield breaker fails to operate or misoperates, it will send a trip command to two upstream NIPSCO-owned 138 kV breakers. Wabash’s Northwest substation (Northwest) has one Protection System relay and one battery system consisting of 24 battery cells. Northwest also provides protection from the high side of a 138 kV/12.47 kV transformer to the low side 12.47 kV station bus, and Northwest’s one Protection System relay ties into the protection scheme operated by NIPSCO in the same manner as Wheatfield. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk posed to the BPS was mitigated by the following factors. The extent of Wabash’s issue includes two Protection System Relays and two Protection System battery systems. During the duration of the issue, Wabash contracted with a third-party to conduct maintenance and testing of its Protection System battery systems at Wheatfield and Northwest. Wabash’s contractor performed maintenance and testing on its Wheatfield and Northwest Protection System battery systems annually, with the exception of Wheatfield in 2010. Testing was halted by Wabash in 2010 due to safety concerns Wabash had with the contractor. As a result of these concerns, Wabash hired a new contractor, Energy Systems Maintenance LLC, to provide testing and services in for Wheatfield in 2011 and 2012. The maintenance and testing of Protection System batteries included a visual inspection for corrosion, testing each cell for specific gravity and temperature, as well as voltage readings of each battery cell. Additionally, the two Protection System relays at issue are microprocessor relays that were monitored by Wabash and NIPSCO during the duration of the issue. As a result, NIPSCO would have had visibility into any operations issues related to these relays. Finally, there were no operational issues or misoperations of the Protection System devices at Wheatfield or Northwest during the duration of the issue. | Wabash developed a maintenance and testing program for its Protection System devices at Wheatfield and Northwest. Wabash also committed to complete maintenance and testing on its Protection System devices located at Wheatfield and Northwest pursuant to its program.
ReliabilityFirst Corporation (ReliabilityFirst) and Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Service Corporation as agent for Appalachian Power Company, Columbus Southern Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, and Wheeling Power Company; American Electric Power Service Corp. As Agent For Public Svc. Co. Of Oklahoma & SW Ele Pwr Co. (AEP) | NCR00682; NCR01056 | RFC2012010608; SPP2012010531 | EOP-008-0 | R1; R1.3; R1.6 | From June 11, 2012 through June 14, 2012, ReliabilityFirst and SPP RE conducted a Compliance Audit of AEP, during which ReliabilityFirst discovered an issue with EOP-008-0 R1, as a Transmission Operator (TOP). AEP performs the TOP function in ReliabilityFirst from two control centers in New Albany, Ohio and Roanoke, Virginia. AEP has a contingency plan to continue reliability operations in the event its control center becomes inoperable for each of these control centers. While there is a list of the critical facilities in its New Albany, Ohio contingency plan, the Roanoke, Virginia contingency plan does not include the list of the critical facilities, as required by EOP-008-0 R1.3. Also during the Compliance Audit of AEP, SPP RE discovered an issue with EOP-008-0 R1, as a Balancing Authority (BA). AEP performs the BA function in SPP RE from two control centers. AEP performs the TOP function in SPP RE from three control centers: one in New Albany, Ohio, one in Tulsa, Oklahoma, and one in Shreveport, Louisiana. AEP has a contingency plan for each of these control centers to continue reliability operations in the event its control center becomes inoperable. The New Albany, Ohio contingency plan did not list the TOP or BA critical facilities, as required by EOP-008-0 R1.3. In addition, the Columbus, Ohio and Shreveport, Louisiana contingency plans did not include procedures and responsibilities for providing annual training, as required by EOP-008-0 R1.6. | ReliabilityFirst and SPP RE determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. Regarding EOP-008-0 R1.3, although the list of critical facilities was not in the contingency plans, the list of critical facilities did exist and was located in the New Albany, Ohio contingency plans. Although there are separate contingency plans for separate control centers, this plan included the list of all critical facilities. Regarding EOP-008-0 R1.6, although the requirement to provide training was not in the contingency plans, AEP provided evidence that it completed the required annual training. | AEP revised the New Albany, Ohio plan to include a list of critical facilities. In addition, AEP revised its Tulsa, Oklahoma and Shreveport, Louisiana plans to include procedures and responsibilities for providing annual training. AEP posted each of the plans to the Transmission Operations SharePoint site so that its transmission operators and dispatchers have access to it.
SERC Reliability Corporation (SERC) | Hot Spring Power Company, LLC (Hot Spring) | NCR01257 | SERC2012010982 | PRC-005-1 | R2 | On August 28, 2012, Hot Spring, as a Generator Owner, self-reported an issue with PRC-005-1 R2, stating that during an internal assessment of Hot Spring's Protection System, it could not locate documentation for the 2008 interval for capacity load testing of the two Valve Regulated Lead Acid (VRLA) batteries. Hot Spring located a work order from March 2008 that indicated capacity load testing had been performed, but vendor test records do not include capacity load tests. Hot Spring subsequently tested both batteries twice within the defined intervals. SERC reviewed a spreadsheet compiled by Hot Spring providing a complete inventory of its Protection System devices, with defined intervals, and maintenance and test dates for the most current and previous dates listed for each Protection System device. SERC verified the assigned intervals based on a review of Hot Spring’s Protection System maintenance and testing procedure, ensuring consistency with the listed intervals provided in the spreadsheets. Based on this review, SERC determined that Hot Spring failed to have test or maintenance records for two out of three station batteries (66.6%). In total, Hot Spring failed to have test or maintenance records for two out of 229 Protection System devices (0.87%). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) Hot Spring’s battery charger and DC system has basic alarming in the control system. These alarms are part of a supervisory control and data acquisition system that allows the operators to monitor the alarms continuously 24 hours a day, seven days a week. This alerts personnel to a battery or charger failure; 2) Hot Spring conducted monthly and annual inspections and maintenance on the batteries, including voltage check, grounds detection and electrolyte levels and found no issues; and 3) Hot Spring’s plant is a merchant power plant and does not have a long term contract in place. | SERC verified that Hot Spring conducted capacity load testing of all batteries in December 2010 and November 2011.
SERC Reliability Corporation (SERC) | Hot Spring Power Company, LLC (Hot Spring) | NCR01257 | SERC2012010983 | PRC-005-1 | R1 | On August 28, 2012, Hot Spring, as a Generator Owner, self-reported an issue with PRC-005-1 R1, stating that Hot Spring's Protection System maintenance and testing procedure did not include associated communication systems (ACS) devices. Although Hot Spring does not own ACS devices, its Protection System maintenance and testing procedure does not include a statement to that effect. SERC reviewed Hot Spring’s Protection System maintenance and testing procedure and verified that it included protective relays, voltage and current sensing devices, batteries, and DC control circuitry, including the maintenance and testing intervals and their basis, and a summary of maintenance and testing for each of these device types. SERC also verified that Hot Spring did not address ACS devices in its Protection System maintenance and testing procedures until April 1, 2011, when it included a statement that it did not own ACS devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the only omission from Hot Spring’s Protection System maintenance and testing procedure was a statement that Hot Spring does not own any ACS devices. | SERC verified that Hot Spring revised its Protection System maintenance and testing procedure to include a statement that Hot Spring does not own ACS devices.
SERC Reliability Corporation (SERC) | Sabine River Authority of TX/LA (Sabine) | NCR01305 | SERC2011007292 | PRC-005-1 | R1 | On May 25, 2011, Sabine, as a Generator Owner (GO), self-reported an issue with PRC-005-1 R1, stating that its Protection System maintenance and testing program did not include maintenance and testing intervals and their basis, or a summary of maintenance and testing procedures for all Protection System devices. Sabine self-reported this issue after being informed by the Generator Operator (GOP) that SERC had identified deficiencies in the GOP’s Protection System maintenance and testing procedure, which Sabine used for its GO function along with internal Sabine procedures. Sabine’s and the GOP’s Protection System maintenance and testing procedures that were in effect at the beginning of the compliance period did not include the summary of maintenance and testing for the batteries or DC control circuitry devices. Sabine did not have battery maintenance and testing procedures until 2009. In addition, Sabine’s maintenance and testing procedures did not address Associated Communication System (ACS) devices. Although Sabine does not have any ACS devices, neither its internal procedure nor that of the GOP noted that fact. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) Sabine’s generator Protection System devices were being maintained and tested through the GOP’s automated maintenance management system, which identified, tracked, and documented completion of maintenance and testing of the Protection System devices using work orders. This system also identified the test intervals and due dates to ensure that the Protection System devices were scheduled and tested at the appropriate date. The work order issued by this system contained the necessary procedures and technical information to conduct maintenance and testing for each relevant Protection System device; and 2) Since Sabine does not have any ACS devices, the omission of this Protection System device type was not significant. | SERC verified that Sabine completed the following actions: 1) Sabine's personnel conducted an in-depth review to improve their understanding of the requirements of the Standard and scheduled an annual review of the requirements of the Standard; 2) Conducted a complete review of Sabine's GO facilities with the GOP and verified that all Protection System components have been included in the inventory as required by the Standard; 3) Developed a separate Protection System maintenance and testing procedure for its Transmission Facilities that includes the maintenance and testing intervals and their basis and a summary of maintenance and testing for all its Transmission Owner (TO) Protection System devices; 4) Revised its Protection System maintenance and testing procedure for its Generation Facilities to include maintenance and testing intervals and their basis and a summary of maintenance and testing and a statement that Sabine owns no ACS devices that require testing; 5) Added the components that had been omitted from the Protection System maintenance and testing program to the maintenance and testing program that tracks and schedules future testing of the components; 6) Conducted a complete review of the TO facilities with the Transmission Operator (TOP) and verified that all components have been included in the inventory as required by the Standards; and 7) Revised the current Protection System maintenance and testing preventative maintenance basis document to outline the basis for testing the TO components that aligns with the TOP’s maintenance and testing program.
SERC Reliability Corporation (SERC) | Sabine River Authority of TX/LA (Sabine) | NCR01305 | SERC2011007293 | PRC-005-1 | R2 | On May 26, 2011, Sabine, as a Generator Owner (GO), self-reported an issue with PRC-005-1 R2 stating it could not provide evidence all Protection System devices were maintained and tested within the defined intervals and the date each Protection System device was last tested or maintained. SERC reviewed spreadsheets prepared by Sabine that included each of Sabine’s Protection System devices for its GO and Transmission Owner (TO) registrations and the defined maintenance and testing intervals, the most recent test date and the previous test date for each device. SERC reviewed test dates for all test periods since the beginning of the enforceable period. SERC verified the assigned intervals based on a review of Sabine’s Protection System maintenance and testing procedures ensuring consistency between the listed intervals provided in the spreadsheets and those included in Sabine’s procedures. SERC determined that Sabine tested one out of one station batteries (100%) outside of interval and failed to have previous testing or maintenance records for 24 out of 68 voltage and current sensing devices (35.3%). In total, SERC determined that Sabine was non-compliant for 25 out of 157 Protection System devices (15.9%). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Sabine’s maintenance contractor provided email records stating that the battery monthly tests were performed during the three months with missing records, but these specific records were lost or misplaced. Sabine reviewed the monthly battery test records for the months before and after each missing record and found no abnormalities with the battery system; 2) Sabine was up to date with all of its Protection System device maintenance and testing activities by March 31, 2011 and Sabine found no issues with the missed Protection System devices; and 3) Sabine is an 81 MW hydro station which operates intermittently for a few hours each day Monday through Friday based on the reservoir water level. It is not dispatched at any other times, and is not considered a critical asset to the reliability of the BPS. Power generated is routed to a single 138 kV step-up transformer then through a 138 kV substation that is tied to an adjacent utility. | SERC verified that Sabine completed the following actions: 1) Sabine's personnel conducted an in-depth review to improve their understanding of the requirements of the Standard and scheduled an annual review of the requirements of the Standard; 2) Conducted a complete review of Sabine's GO facilities with the Generator Operator and verified that all Protection System components have been included in the inventory as required by the Standard; 3) Added the components that had been omitted from the Protection System maintenance and testing program to the maintenance and testing program that tracks and schedules future testing of the components; 4) Performed the required tests on the components determined to be out of compliance and obtained copies of the reports verifying the work was performed and components are functioning properly; 5) Conducted a complete review of the TO facilities with the Transmission Operator and verified that all components have been included in the inventory as required by the Standards; and 6) Reviewed maintenance contractor documentation of component testing and verified they provide sufficient detail to meet the Standard.
SERC Reliability Corporation (SERC) | Tenaska Alabama Partners, L.P. (Tenaska-AL) | NCR01335 | SERC2011007288 | VAR-002-1.1b | R3 | On May 24, 2011, Tenaska-AL, as a Generator Operator, self-reported an issue with VAR-002-1.1b R3, stating that on May 10, 2011, the control room operator observed that the power system stabilizers (PSS) on three units were in the “Off” position. The operator then changed the PSSs to the “On or Armed/Active” position and notified Plant Management. However, Tenaska-AL did not notify the appropriate Transmission Operator (TOP) within 30 minutes of the change in PSS status as required by VAR-002-1.1b R3. Further investigation by Tenaska-AL determined that two units had their respective PSSs in the “Off” position. SERC requested and reviewed additional documents in order to complete its assessment. Tenaska-AL operates Lindsay Hill Generating Station, which has three combustion turbines (CT1, CT2, and CT3), and one steam turbine, with a total rating of 1,041 MVA for the station (199 MVA for each CT and 444 MVA for the steam turbine). SERC learned that Lindsay Hill Generating Station is located adjacent to a generating station with an approximate capacity of 885 MW. The two plants monitor and coordinate the MVAR/MW ratio with each other to control the switchyard voltage that is common to both plants. SERC determined that Tenaska-AL operated the CT1 and CT3 units with their respective PSSs off. On May 4, 2011, Tenaska-AL started and released the CT1 unit to the grid system with its PSS off. On May 10, 2011, after realizing that the PSS was in the incorrect position, the operator turned it on but did not notify the TOP within 30 minutes of the change in PSS status. Tenaska-AL operated the CT1 unit several times with the PSS off between May 4 and May 10, 2011 for a total of approximately 33 hours. On May 9, 2011, Tenaska-AL started and released the CT3 unit to the grid system with its PSS off. On May 10, 2011, after realizing that the PSS was in the incorrect position, the operator turned it on but did not notify the TOP within 30 minutes of the change in PSS status. Tenaska-AL operated the CT3 unit several times with the PSS off between May 9 and May 10, 2011 for a total of approximately 18 hours. During this time, Tenaska-AL started and released the steam turbine and CT2 unit to the grid, on May 4 and May 10, 2011, respectively, with their PSSs turned on. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) While the CT1 and CT3 units were online with their respective PSSs off, the steam turbine was operating with its PSS on and was controlling the voltage; 2) The Tenaska-AL facility control room is manned by a control room operator who is responsible for maintaining the plant voltage schedule provided by the TOP. The facility is located adjacent to another generating station with an approximate capacity of 885 MW. The two plants monitor and coordinate the MVAR/MW ratio with each other to control the voltage at a switchyard common to both plants; and 3) During the seven days it operated the units with their PSSs off, Tenaska-AL operated the CT1 unit for approximately 33 hours and CT3 for approximately 18 hours. | SERC verified that Tenaska-AL completed the following actions: 1) Provided instructions to all of the control room operators to verify the status of the PSSs during shift turnover and prior to starting any generator; 2) Installed alarms on the plant control system to alert the operator when any PSS control is in the "Off" position; 3) Provided written instructions to all plant personnel specifically highlighting that, when the status of the PSS changes, the TOP must be provided notification of both the status change and expected duration within 30 minutes; 4) Completed program changes that added a start permissive to each turbine requiring the PSS to be in the "Armed\Active" position in order to start the unit; 5) Created a poster and placed it in the control room to provide a quick reference to the operators by detailing when communication with the TOP is required. This poster was reviewed individually with all of the operators during their normal shifts; 6) Added requirements to the board reviews for all plant operators that plant operators explain what events require them to communicate with the TOP as well as what the communication must include, including the need to communicate the change in state and expected duration to the TOP within 30 minutes, name the items listed on the control room poster, and explain what must be done if the TOP communications are not done properly; 7) The plant manager and plant engineer reviewed the event with other plants during regularly scheduled calls with plant managers and the NERC Compliance Committee; 8) The plant manager reviewed the incident with all plant employees at scheduled monthly safety meetings; and 9) Submitted an event report to Operations management in Omaha to be forwarded to all Tenaska plants to prevent this type of event from occurring at the other plants.
Southwest Power Pool Regional Entity (SPP RE) | Midwest Energy, Inc. (Midwest) | NCR01118 | SPP2012010123 | EOP-008-0 | R1 (R1.5, R1.6) | During a Compliance Audit of Midwest, conducted from April 24, 2012 to April 26, 2012, SPP RE identified non-compliance with EOP-008-0 R1.5 and R1.6. The Midwest's plan for loss of control center functionality (Plan) required the deployment of field personnel to critical facilities for the purpose of communicating field conditions back to operations staff. The Plan also provided in part, “[o]n an annual basis[,] System Operators and other assigned personnel will be subjected to a review of the process and procedures to be implemented in the event the Primary Control Center is lost.” SPP RE determined that an annual training session and table top exercise were conducted with operations staff in accordance with the Plan. However, field personnel did not participate in the training session, did not participate in the communication exercises with operations staff, and were not deployed to the critical facilities. This remediated issue applies to Midwest's Transmission Operator function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The operations staff charged with overseeing the Plan implementation were trained in the Plan implementation, underwent a table top exercise, and were prepared to respond in an emergency situation. Therefore, the individuals charged with managing the Plan implementation were prepared to respond in an emergency situation. Additionally, the referenced field personnel at issue are the same individuals that inspect the critical facilities on a monthly basis. Therefore, the field personnel are familiar with the location of the critical facilities and where to gather any data requested by the operations staff. The role of the field personnel in the Plan implementation is limited to critical facility site deployment and the recording and reporting of system data to operations staff. | Midwest amended its Plan to require that “System Operators not working the desk will test the plan . . . by deploying Substation Technicians [(field personnel)] to the appropriate locations. Testing of all data and voice links at the service center will be conducted by the System Operator[s] as a part of the test.” Midwest also conducted training on the new procedure and carried out a drill involving both operations and field personnel. This drill included deployment of the field staff to critical facilities and involved two-way communication between the operations staff at the back-up facility and field personnel at the critical substations.
Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP201000339 | TOP-002-2a | R11 | On July 27, 2010, EDE submitted a Self-Report for noncompliance with TOP-002-2a R11 because it was no longer performing current and next-day Bulk Electric System studies consistent with the requirements of TOP-002-2a R11. EDE had previously relied on the Southwest Power Pool Reliability Coordinator (SPP RC) to perform its current and next-day studies. The SPP RC had informed EDE that although it would continue to perform system current and next-day studies, these studies would not be performed on EDE’s behalf. Because there was no agreement between SPP RC and EDE to perform the studies, the SPP RC was not obligated to do so and EDE could not rely on the SPP RC to perform EDE's current and next-day studies. This remediated issue applies to EDE's Transmission Operator function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the SPP RC stated that it was not performing current and next-day studies on EDE’s behalf, the SPP RC continued to perform system current and next-day studies and these studies were available to EDE. EDE had trained its system operators to review the contingency analysis studies that were provided by the SPP RC and continued to establish System Operating Limits (SOLs) utilizing the SPP RC studies. EDE provided SPP RE with evidence that it not only reviewed the SPP RC studies on a daily basis, but also communicated with the SPP RC regarding the identification of SOLs. | EDE entered into a formal agreement with SPP RC whereby the SPP RC would perform next day, current day, and seasonal studies for EDE. Additionally, EDE modified its policies and procedures to incorporate the formal agreement, and to educate system operators on their responsibilities as a result of the formal agreement, including the daily documented review of the studies.
Texas Reliability Entity, Inc (Texas RE) | Pattern Gulf Wind LLC (Pattern Gulf) | NCR11020 | TRE201100551 | PRC-005-1 | R2 | On November 2, 2011, Pattern Gulf Wind, as a Generator Owner (GO), self-certified an issue with PRC-005-1 R2 and subsequently self-reported the same issue on November 8, 2011. Pattern Gulf purchased the generation facility at issue, from Texas Gulf Wind and ownership was transferred on March 17, 2010. The previous owner, Texas Gulf Wind, did not provide any documentation to support the implementation of a Protection System maintenance and testing program (Program) prior to the asset being owned by Pattern Gulf. There were no maintenance and testing records available from July, 13, 2009 to March 17, 2010. Upon the ownership change, the implementation of the Program could be documented, as required. However, the actual execution of all maintenance and testing was contracted to BluArc Management Group until December 17, 2010. Therefore, from March 17, 2010 to December 17, 2010, weekly maintenance and tests were not documented. The remediated issue period was from March 16, 2010, the date Pattern Gulf was registered as a GO, to December 17, 2010, the date Pattern Gulf can show supporting documentation of operational maintenance in place. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because BluArc Management Group had provided an attestation that testing was being done during the remediated issue period despite the lack of documentation. Pattern Gulf had shown that it was performing comprehensive system maintenance and testing from December 17, 2010 onwards. | On December 17, 2010, a new Facility Manager and Assistant Facility Manager were put in charge of the facility. The Assistant Facility Manager is in charge of execution of all maintenance and testing and proper documentation of all executed maintenance and testing reports. The Facility Manager oversees and verifies proper execution and documentation of all maintenance and testing. With the new management on site, all of the maintenance and testing is executed within the intervals in accordance with the Program and properly documented. All mitigating activities have been verified as complete by Texas RE.
Texas Reliability Entity, Inc (Texas RE) | Pattern Gulf Wind LLC (Pattern Gulf) | NCR11020 | TRE2012010269 | PRC-018-1 | R3 | On May 14, 2012, Pattern Gulf, as a Generator Owner (GO), self-reported an issue with PRC-018-1 R3. During a pre-audit assessment, Pattern Gulf discovered that the owner of the Disturbance Monitoring Equipment (DME) installed in the Pattern Gulf substation was using a different piece of equipment for disturbance monitoring than Pattern Gulf had been reporting to the Regional Reliability Organization, in this case the Electric Reliability Council of Texas (ERCOT). As a result, Pattern Gulf did not maintain and report the correct piece of equipment to ERCOT, as per the regional requirement and as required by PRC-018-1 R3. The remediated issue violation period was from March 16, 2010, the date Pattern Gulf was registered as a GO, to May 10, 2012, the date the error was discovered and corrected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because it was an administrative issue concerning the proper identification of assets assigned to record system disturbances. Pattern Gulf began reporting the correct DME information to ERCOT as of May 10, 2012. The incorrect device was being reported to ERCOT for system disturbance monitoring, even though the correct equipment was in place and fully functional. However, if information was required to report a disturbance, the Pattern Gulf technicians knew to use the correct relay installed to provide this function. Documents from Pattern Gulf show that the DME (SEL-311L) used for event and fault recording was in service during the time of the alleged violation. Once Pattern Gulf realized its mistake, it began reporting to ERCOT the correct information on the SEL-311L that was actually performing the task of disturbance monitoring and recording. | Pattern Gulf has reviewed the relay specifications and verification of the relays capabilities. The DME devices (relays) at the facility meet the requirements and are available to monitor the facility and disturbances and to record disturbance data that can and will be provided to the RC as requested, and are tested and maintained properly.
Texas Reliability Entity, Inc (Texas RE) | Tenaska Gateway Partners LTD (Tenaska) | NCR04137 | TRE201100483; SPP2011008312 | PRC-005-1 | R2 | On October 12, 2011, Tenaska, as a Generator Owner (GO), self-reported to Texas RE and SPP RE that Tenaska did not have documentation to verify the maintenance and testing of all DC control circuitry. Although maintenance and testing occured at defined intervals on most of the Protection System components at Tanaska's plant, testing of the DC control circuitry hads not been performed and documented in a manner sufficient to demonstrate compliance with PRC-005-1 R2. Tenaska follows the National Electrical Testing Association's (NETA) maintenance testing specifications for testing of its Protection System components. This remediated issue applies to 36 DC circuits, out of a total 384 Protection System devices (9.37%). The remediated issue period was from June 28, 2007, the date of Tenaska's registration as a GO, to May 1, 2012, the day that DC Circuit tests were documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Tenaska had been performing tests and maintenance on its remaining Protection System equipment (i.e. relays, batteries, communication systems, and Current Transformers and Potential Transformers. Also, Tenaska used relay events and successful equipment starts as evidence of functional testing of the DC control circuitry at issue. Moreover, the remediated issue applied to 9.37 % of Tenaska's Protection System Devices, thereby reducing the risk to the BPS. Additionally, when Tenaska did perform tests on its DC control circuitry, all units were deemed to be operating properly. Furthermore, Tenaska reviewed all plant Protection System operations and did not identify any misoperations during the pendency of this remediated issue. | Tenaska had identified and written procedures for all untested DC circuits, sent out and received bids for contracting the testing, and lastly, performed the required tests. All mitigating activities have been verified as complete by Texas RE.