## Public Non-CIP Dec. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
ReliabilityFirst Corporation (ReliabilityFirst) | Ameren Energy Generating Company (AEGC) | NCR00677 | RFC2011001176 | PRC-005-1 | R1 | From July 11, 2011 to July 22, 2011, ReliabilityFirst conducted a Compliance Audit of AEGC, during which ReliabilityFirst discovered an issue with of PRC-005-1 R1. AEGC, as a Generator Owner, did not include maintenance and testing intervals for voltage and current sensing devices in its Protection System maintenance and testing program (Program) as required by PRC-005-1 R1.1. Although AEGC stated in its Program that it performed continuous monitoring as an alternative to defined intervals of maintenance and testing, ReliabilityFirst determined that AEGC’s monitoring did not identify all types of instrument transformer failures and is therefore insufficient to qualify as an alternative to testing and maintenance intervals for those devices. As a result, AEGC’s Program also failed to include a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AEGC has in place an overall comprehensive maintenance and testing program, including partial continuous monitoring of instrument transformers with alarming, thermography, and commissioning testing. AEGC also conducts informal visual inspections of relays and instrument transformers. Lastly, no generating unit outage, equipment failure, or confirmation of any current and voltage sensing misoperation occurred during the period of the issue. | AEGC updated its Program to address the issue with PRC-005-1 R1. AEGC modified its Program, creating Revision 5 on September 14, 2012, to include a 12-year interval for load check and excitation tests on current sensing devices that were not subject to continuous monitoring.
ReliabilityFirst Corporation (ReliabilityFirst) | Ameren Energy Generating Company (AEGC) | NCR00677 | RFC2011001177 | PRC-005-1 | R2; R2.2 | From July 11, 2011 to July 22, 2011, ReliabilityFirst conducted a Compliance Audit of AEGC, during which ReliabilityFirst discovered an issue with PRC-005-1 R1. AEGC, as a Generator Owner, did not include maintenance and testing intervals for voltage and current sensing devices in its Protection System maintenance and testing program (Program) as required by PRC-005-1 R1.1. Although AEGC stated in its Program that it performed continuous monitoring as an alternative to defined intervals of maintenance and testing, ReliabilityFirst determined that AEGC’s monitoring did not identify all types of instrument transformer failures and is therefore insufficient to qualify as an alternative to testing and maintenance intervals for those devices. As a result, AEGC’s Program also failed to include a summary of maintenance and testing procedures for voltage and current sensing devices, as required by PRC-005-1 R1.2. In conjunction with the PRC-005-1 R1 issue, AEGC also failed to provide documentation of the date each voltage and current sensing device was last tested or maintained, as required by PRC-005-1 R2.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AEGC has in place an overall comprehensive maintenance and testing program, including partial continuous monitoring of instrument transformers with alarming, thermography, and commissioning testing. AEGC also conducts informal visual inspections of relays and instrument transformers. Lastly, no generating unit outage, equipment failure, or confirmation of any current and voltage sensing misoperation occurred during the period of the issue. | AEGC updated its Program to address the issue with PRC-005-1 R2. AEGC modified its Program, creating Revision 5 on September 14, 2012, to include a 12-year interval for load check and excitation tests on current sensing devices that were not subject to continuous monitoring. In addition, the responsible personnel were informed of the revision to the Program.
ReliabilityFirst Corporation (ReliabilityFirst) | Calumet Energy Team, LLC (Calumet) | NCR00252 | RFC2011001094 | PRC-005-1 | R2 | From July 11, 2011 to July 22, 2011, ReliabilityFirst conducted a Compliance Audit of Calumet, during which ReliabilityFirst discovered an issue with PRC-005-1 R2. Calumet, as a Generator Owner, did not provide ReliabilityFirst with documentation demonstrating that voltage and current sensing devices, direct current (DC) control circuitry, and protective relay devices were maintained and tested within defined intervals, as required by PRC-005-1 R2.1. Specifically, Calumet did not provide complete documentation to evidence testing of voltage and current sensing devices because the device designations from the prior test cycle are different than, and could not be correlated with, the device designations from the current records. Additionally, Calumet Energy did not provide any prior test records for DC control circuitry. Finally, Calumet Energy did not provide a test record relating to one protective relay. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although, for certain devices, Calumet failed to maintain proper documentation, it did conduct scheduled testing and maintenance for protective relays and voltage and current sensing devices. Additionally, although Calumet did not perform functional testing on DC control circuitry prior to 2010, it did verify continuity and functionality of trip circuits during normal unit shutdowns. | Calumet implemented a planned maintenance activity for performing DC circuitry testing to ensure that testing is performed in addition to the relay calibration tests. Calumet also developed appropriate designations for voltage and current sensing devices and matched those designations with the one-line diagram to ensure that all voltage and current sensing devices are tested and documented. Calumet Energy provided evidence of its updated preventative maintenance schedule for DC circuitry and updated documentation showing a clear correlation between test data for voltage and current sensing devices and the same devices on one-line diagrams.
ReliabilityFirst Corporation (ReliabilityFirst) | Delmarva Power & Light Company (Delmarva) | NCR00752 | RFC2012011122 | PRC-008-0 | R2 | On September 18, 2012, Delmarva, as a Distribution Provider, self-reported an issue with PRC-008-0 R2 to ReliabilityFirst. Delmarva did not maintain test results to demonstrate that it tested a distribution microprocessor relay with an under frequency load shedding (UFLS) scheme within the time frame specified in Delmarva’s PRC-008-0 Protective System Schemes Protection and Maintenance Program & Procedures (Procedures). Specifically, Delmarva’s Procedures require that it trip test UFLS microprocessor relays every eight years with a 10% grace period (9.6 months). Delmarva has evidence that it trip tested the relay on March 4, 2003 as part of the relay installation process. Based on the Procedures, the relay should have been trip tested again no later than December 21, 2011. In addition, Delmarva has spreadsheets showing the relay was trip tested on March 4, 2007, before the December 21, 2011 testing due date, but Delmarva was unable to locate test results evidencing the March 4, 2007 trip test. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relay in question represents less than 1% of Delmarva’s UFLS equipment. If Delmarva had experienced an under frequency excursion, it has sufficient UFLS equipment to meet the required load shedding without this relay. The relay was set to trip at the 58.9 Hertz (Hz) frequency level, which is the second set point in Delmarva’s UFLS program. At this set point, Delmarva had planned to be able to shed 15.1% of its estimated annual peak load, even though its UFLS program only required it to shed 10% of its estimated annual peak load. Even if the relay had not operating correctly, Delmarva still would have been able to shed 13.7% of its estimated annual peak load. Similarly, if the relay had experienced a false trip, it only would have tripped one distribution circuit with 20 MW of load at peak. Additionally, the relay is a self-monitoring microprocessor relay and is therefore designed to alert operators if it fails. During the time period of the issue, the relay issued no alarms. Furthermore, the relay functioned as expected throughout the period in question and the July 31, 2012 trip test results confirm that the relay was functioning as intended. Prior to performing the trip test, a health check was performed and the report shows that the relay was functioning. During the time period of the issue, the multipurpose distribution relay correctly tripped for faults which tested the trip circuit and proved that the trip circuit was properly functioning. The relay did not experience any under frequency false trips during the time period of the alleged violation. Furthermore, there were no system under frequency events that required the UFLS function in the relay to operate during the period in question. Finally, this was an isolated incident that was discovered during a compliance activity, which Delmarva routinely conducts to ensure that it performs testing pursuant to its Procedure. | Delmarva trip tested the relay on July 31, 2012, the day after the discovery of this potential discrepancy, while a search for evidence continued. The July 31, 2012 test confirmed that the relay was functioning as intended. After completing the relay test, Delmarva reviewed its documentation for all UFLS equipment and determined that it had appropriate testing documentation for all other relays. Delmarva had also already implemented procedures to ensure that it performed testing per the Procedure. Furthermore, Delmarva already routinely conducted compliance activities to ensure that it performs testing pursuant to its Procedure.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn East 2 | NCR11145 | RFC2011001133 | PRC-005-1 | R2; R2.1 | On September 30, 2011, GenOn East 2, as a Generator Owner, self-certified an issue with PRC-005-1 R2. GenOn East 2 failed to perform maintenance and testing on one of its 85 relays within the defined interval of four years (plus a 10% grace period). GenOn East 2 tested this relay, the backup relay for a primary relay, at a different time than the rest of the relays. GenOn East 2 did, however, maintain and test the primary relay within its defined interval. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relay at issue is a backup relay for a primary relay that GenOn East 2 did maintain and test within its defined interval. The primary relay responds in a shorter timeframe to an event than the backup relay, and there are alarms in place that alert the control room when the devices operate or misoperate. In addition, GenOn East 2 discovered this issue while conducting a self-assessment. The issue occurred for approximately three months, and GenOn East 2 timely discovered and corrected this issue. | To address the issue, GenOn East 2 performed maintenance and testing on the relay at issue. GenOn revised its Protection System maintenance and testing program, which will aid to prevent recurrence.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Power Midwest | NCR11136 | RFC2012010406 | VAR-002-1.1b | R1 | On May 30, 2012, GenOn Power Midwest, as a Generator Operator and Generator Owner, self-reported an issue with VAR-002-1.1b R1 to ReliabilityFirst. On April 11, 2012, GenOn Power Midwest started its Brunot Island Unit 4 with the automatic voltage regulator (AVR) in manual mode. GenOn Power Midwest operated this unit in manual mode for approximately 29 hours, from April 11, 2012 through April 13, 2012, without notifying the Transmission Operator that the AVR was in manual mode. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GenOn Power Midwest has a program in place requiring operation of the AVR in automatic mode, and there is alarming on Units 2, 3 and 4 for the AVR status. This instance, therefore, was an isolated occurrence. GenOn Power Midwest maintained the voltage schedule for Brunot Island during the time period of the issue and was aware that the AVR was in manual mode. | GenOn Power Midwest completed the following mitigating actions: 1) added a specific alarm for the AVR not operating in automatic mode; 2) reviewed current station operating procedures as well as the NERC compliance procedure and addressed any gaps; and 3) provided further training on VAR-002-1.1b and GenOn internal compliance procedures with plant personnel.
ReliabilityFirst Corporation (ReliabilityFirst) | GenOn REMA 1 | NCR11141 | RFC2012010745 | VAR-002-1.1b | R2 | On July 9, 2012, GenOn REMA 1, as a Generator Operator and a Generator Owner, self-reported an issue with VAR-002-1.1b R2 to ReliabilityFirst. During a self-assessment, GenOn REMA 1 discovered that for its Sayreville and Werner generating stations, it failed to maintain generator voltage schedule without an exemption from the Transmission Operator on certain occasions. The Sayreville generating station consists of four combustion turbines totaling 224 MW, and the Werner generating station consists of four combustion turbines totaling 212 MW. On December 15, 2011 and December 21, 2011 the Werner station experienced voltage schedule excursions where the voltage was higher than the schedule. The Werner station was only operating two of its generating units at the time of the excursions. On December 23, 2011, February 21, 2012, March 2, 2012, and March 3, 2012, the Sayreville station experienced voltage schedule excursions where the voltage was slightly above or slightly below than the schedule. On each of those dates except February 21, 2012, the Sayreville station was only operating one of its generating units at the time of the excursions. On February 21, 2012, the Sayreville station was only operating two of its generating units at the time of the excursion. The greatest voltage excursion was only 1.13% above the voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The greatest voltage excursion was only 1.13% above the voltage schedule. In addition, the Automatic Voltage Regulators were in automatic mode during each of the voltage excursions. | GenOn REMA 1 completed the following mitigating actions: 1) initiated a review of the self-assessment incident findings with all employees, conducted training classes and review of VAR-002 requirements with all operators; 2) installed laminated guidelines on all dedicated voltage monitoring screens; 3) installed voltage schedule monitoring screens in all control rooms; and 4) updated operating start-up/shut-down check-off sheets to include the voltage schedule.
ReliabilityFirst Corporation (ReliabilityFirst) | NedPower Mount Storm, LLC (Ned Power) | NCR00293 | RFC2012010024 | PRC-005-1 | R2; R2.1 | On April 3, 2012, NedPower, as a Generator Owner, self-reported an issue with PRC-005-1 R2.1 to ReliabilityFirst. In preparation for an upcoming audit, NedPower conducted a review of its Reliability Standards compliance documentation for, among other Reliability Standards, PRC-005-1. During the review, NedPower discovered that it did not maintain evidence that it conducted two monthly battery inspections. From April 30, 2012 to May 16, 2012, ReliabilityFirst conducted a Compliance Audit of NedPower. ReliabilityFirst discovered additional facts related to NedPower’s issue with PRC-005-1 R1. Specifically, NedPower did not maintain evidence that it performed visual inspections or heat scans for current and voltage sensing devices, as required within its Protection System maintenance and testing program (Program). Additionally, NedPower did not maintain evidence that it tested its control circuitry as required within its Program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NedPower missed two monthly battery inspections, with all remaining inspections immediately before and after each missed inspection demonstrating sufficient battery functioning and identifying no issues with the batteries. NedPower also performed a load test in August 2009 that showed no issues with the batteries. Additionally, NedPower’s batteries and battery control house were installed in Fall 2007, with climate control in the control house, thereby protecting the batteries against degradation that would have limited their effectiveness. Furthermore, the batteries are monitored through continuous automatic alarms and regulator operator checks. In terms of its current and potential sensing devices, although NedPower missed the visual and heat scan inspections, NedPower did perform electrical testing on these devices when it performed the relay testing and NedPower would have discovered any problems with the devices during this testing. | NedPower completed the following mitigating actions: 1) addition of an additional layer of automation and protection to the compliance program to ensure that it completes monthly battery inspections; 2) implementation of a verification process to ensure that records of conducting heat scans are documented, signed, and dated; and 3) documentation of its verification that the control circuitry operational checks pass inspection and retains signed and dated verification sheets.
SERC Reliability Corporation (SERC) | City of Springfield, IL – CWLP (CWLP) | NCR01328 | SERC2012009691 | PRC-005-1 | R1; R1.1; R1.2 | On February 2, 2012, in preparation for a SERC audit, CWLP discovered an issue with its Generator Battery Maintenance Program for Dallman Unit 4. On February 9, 2012, CWLP, as a Generator Owner, self-reported an issue with PRC-005-1 R1, stating that its Protection System maintenance and testing program did not include maintenance and testing intervals and a summary of maintenance and testing procedures for the Dallman Unit 4 generator battery. The Self-Report also stated that Dallman Unit 4 entered commercial operation on November 20, 2009. SERC reviewed CWLP’s Protection System maintenance and testing program and determined that CWLP’s Protection System maintenance and testing procedures for station batteries did not include the battery testing and maintenance program for Dallman Unit 4 until February 9, 2012. SERC confirmed that CWLP’s maintenance and testing procedures for its Transmission Owner and Distribution Provider functions had no issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) Although the Dallman Unit 4 battery system was not included in CWLP’s Protection System maintenance and testing procedure prior to February 9, 2012, CWLP maintained and tested the Unit 4 battery system in accordance with the same procedure it used to maintain and test the Unit 3 battery system which called for monthly and semi-annual testing of the Unit 3 batteries; and 2) After the Unit 4 battery system was included in CWLP’s Protection System maintenance and testing procedure, CWLP tested the Unit 4 battery system in accordance with the updated procedure and found no problems, indicating that the battery system likely would have performed as intended. | SERC verified that CWLP completed the following actions: 1) Confirmed that the battery and maintenance testing intervals for the Dallman Unit 4 generator battery have been entered into the new MAXIMO system to ensure compliance with the current CWLP generator battery maintenance program; 2) Incorporated the Dallman Unit 4 generator battery into the CWLP generator battery maintenance program document and added language to the document requiring an annual review by CWLP generation personnel. The review will be coordinated with the CWLP Compliance Committee Chairman and the CWLP Chairman assigned responsibility for maintaining compliance with PRC-005; and 3) Updated the current contract with the vendor performing battery and maintenance testing as described in the CWLP generator battery maintenance program to include the Dallman Unit 4 generator battery.
SERC Reliability Corporation (SERC) | City of Springfield, IL – CWLP (CWLP) | NCR01328 | SERC2012009692 | PRC-005-1 | R2; R2.1; R2.2 | On February 2, 2012, in preparation for the SERC Compliance audit, CWLP discovered an issue with its Generator Battery Maintenance Program with Dallman Unit 4. On February 9, 2012, CWLP, as a Generator Owner, self-reported an issue with PRC-005-1 R2, stating that it did not have evidence that one generator battery system was maintained and tested within the defined intervals, and did not provide the date when the battery was last tested and maintained. The Self-Report also stated that Dallman Unit 4 entered commercial operation on November 20, 2009. SERC reviewed spreadsheets prepared by CWLP that included each of CWLP’s Protection System devices and the defined maintenance and testing intervals, the most recent test date and the previous test date for each device. SERC verified the assigned intervals based on a review of CWLP's Protection System maintenance and testing procedure and determined that CWLP could not provide records of the last maintenance or testing date for one out of 13 station batteries (7.7%). In total, CWLP failed to have maintenance or test records for one out of 1,054 Protection System devices (0.1%). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) CWLP has local and control room alarms on its battery systems that would alert CWLP personnel of a problem; 2) Although the Dallman Unit 4 battery system was not included in CWLP’s Protection System maintenance and testing procedure prior to February 9, 2012, CWLP maintained and tested the Unit 4 battery system in accordance with the same procedure it used to maintain and test the Unit 3 battery system which called for monthly and semi-annual testing of the Unit 3 batteries; and 3) After the Unit 4 battery system was included in CWLP’s Protection System maintenance and testing procedure, CWLP tested the Unit 4 battery system in accordance with the updated procedure and found no problems, indicating that the battery system likely would have performed as intended. | SERC verified that CWLP completed the following actions: 1) Confirmed that the battery and maintenance testing intervals for the Dallman Unit 4 generator battery have been entered into the new MAXIMO system to ensure compliance with the current CWLP generator battery maintenance program; 2) Incorporated the Dallman Unit 4 generator battery into the CWLP generator battery maintenance program document and added language to the document requiring an annual review by CWLP generation personnel. The review will be coordinated with the CWLP Compliance Committee Chairman and the CWLP Chairman assigned responsibility for maintaining compliance with PRC-005; and 3) Updated the current contract with the vendor performing battery and maintenance testing as described in the CWLP generator battery maintenance program to include the Dallman Unit 4 generator battery.
SERC Reliability Corporation (SERC) | City of Springfield, IL – CWLP (CWLP) | NCR01328 | SERC2012009985 | FAC-009-1 | R1 | On March 29, 2012, CWLP, as a Transmission Owner, self-reported an issue with FAC-009-1 R1, stating that an engineer discovered a transposition error regarding the winter emergency rating in its Facility Rating for a transmission conductor. CWLP stated that a transposition error was made in a summary table after the calculation of the equipment ratings was completed. The transposition error affected the winter emergency ratings on nine branches on the CWLP 138 kV transmission system. The winter emergency rating was incorrectly listed as 1,373 Amps instead of the correct value of 1,337 Amps, a difference of 36 Amps (2.62%). SERC reviewed the CWLP Facility Rating Methodology (FRM) and ratings summary spreadsheets dated before and after the self-reported event. The spreadsheets included a calculation of conductor rating, which was calculated to be 1,337 Amps for CWLP’s 795 thousand circular mills (MCM) Aluminum Conductor Steel Reinforced (ACSR) transmission conductors. The summary table in the same spreadsheet contained manually entered values for the Facility Ratings rather than the calculated values, wherein the tens and unit digits were erroneously transposed, resulting in a stated transmission line rating of 1,373 Amps, instead of 1,337 Amps as was calculated. CWLP listed the incorrect conductor rating in the spreadsheet dated October 18, 2011 and corrected the conductor rating in the spreadsheet dated April 25, 2012. SERC reviewed data sheets used to transmit Facility Ratings to the entities requesting that data and found that CWLP determined and distributed a normal summer, normal winter, emergency summer, and emergency winter rating for 60 facilities, for a total of 240 Facility Ratings. Only the winter emergency ratings for nine facilities were affected by the manual input error. SERC determined that CWLP failed to establish nine out of 240 Facility Ratings (3.75%) for its solely and jointly owned facilities in a manner consistent with its FRM. SERC also reviewed CWLP's generation Facility Rating documents and confirmed that the issue does not apply to the Generator Owner function of CWLP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) CWLP has a supervisory control and data acquisition (SCADA) system in place which provides an alarm to the system operator when the facility loading is at 90% of summer normal and winter normal ratings. This alarm provides sufficient time for CWLP to take action to prevent the load from approaching the emergency limits; 2) The affected facilities have never been included in the list of MISO Interconnection Reliability Operating Limit, Transmission Operator congested flow gates, or Critical Facilities List, and the facilities have never been identified by the CWLP vulnerability and risk assessment as a critical facility; and 3) After CWLP correctly applied the FRM to determine the Facility Ratings, the nine facilities’ capacity rating was reduced by 2.62% for the winter emergency rating. | SERC verified that CWLP completed the following actions: 1) Coordinated the ratings change between the CWLP Compliance Chairman and the CWLP Operations engineer on March 20, 2012; 2) Implemented the ratings change with MISO Operations by using the web based modeling tool on March 20, 2012; 3) Received confirmation from MISO via email that the ratings had been updated in the MISO Real Time Model on March 20, 2012; 4) Coordinated the initiation of the change in the MISO Model on Demand (MOD) database between the CWLP Compliance Chairman and CWLP Planning on March 20, 2012, and submitted the change on March 22, 2012 due to the MISO MOD availability; and 5) Revised the CWLP Transmission Ratings Review Procedures to require that schedule calculations be performed to confirm that the correct ratings are being provided to CWLP Operations and CWLP Planning.
Southwest Power Pool Regional Entity (SPP RE) | City of Gardner, (Gardner) | NCR10190 | SPP201100622 | FAC-008-1 | R1 | During a June 8, 2011 to June 9, 2011 Compliance Audit, the SPP RE Audit Team determined that Gardner, as a Transmission Owner, was noncompliant with FAC-008-1 R1. Between December 20, 2007 and June 10, 2010, Gardner did not have an established Facility Ratings Methodology (FRM), and between June 10, 2010 and June 9, 2011, Gardner’s FRM failed to address the ratings of its current transformers (CTs). | SPP RE determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Gardner is a municipal electric utility with a peak load of 39.6 MW. It owns 3.6 miles of 161 kV transmission line, two 161 kV interconnections with its Transmission Operator (TOP) at one substation (Moonlight Substation), and no Bulk Electric System generation. The Moonlight Substation is jointly owned by Gardner and its TOP. Except for the feeds to Gardner, the TOP owns the remainder of the substation and the ties to the BPS. The Gardner system has minimal impact on flows through the Moonlight Substation, and therefore minimal impact on the surrounding BPS. The TOP has identified the ratings of equipment in the Moonlight Substation, and notwithstanding the lack of a Gardner FRM, the TOP is aware of the ratings of the Gardner facilities for planning purposes. | As of June 9, 2011, Gardner has established a FRM, which it will maintain and revise as needed.
Southwest Power Pool Regional Entity (SPP RE) | Exelon Wind 4, LLC (Exelon) | NCR10122 | SPP2012010552 | PRC-005-1 | R2 | During a June 25, 2012 Compliance Audit of Exelon, the SPP RE Audit Team identified noncompliance with PRC-005-1 R2. Exelon, as a Generator Owner, could not provide evidence that it conducted annual testing on one battery bank during 2010, nor could it provide evidence of monthly battery inspections for the months requested by the SPP RE Audit Team. The Audit period covered October 31, 2007 to June 25, 2012. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Exelon is a 79.8 MW wind facility that sells non-firm power. Exelon demonstrated that all its PRC-005 devices, except its battery bank, were tested and maintained within intervals defined in its Protection System maintenance and testing program. The single annual battery testing failure occurred in 2010, and Exelon provided evidence of battery testing for 2011, which showed no battery degradation. Furthermore, Exelon’s battery bank is monitored and will alert inspection personnel of battery voltage issues. Although Exelon could not provide evidence of monthly battery inspections, it provided evidence that its inspection personnel conducted monthly inspections of the facilities where the battery bank was located. | Exelon performed maintenance and testing of its batteries in accordance with its maintenance and testing program in September 2011, and has revised the testing and inspection records to ensure documentation of monthly inspections and annual testing of its battery bank.
Southwest Power Pool Regional Entity (SPP RE) | Flat Ridge Wind Energy, LLC (Flat Ridge) | NCR10312 | SPP2012010127 | VAR-002-1.1b | R2; R2.2 | Flat Ridge, as a Generator Operator, self-certified noncompliance with VAR-002-1.1b R2.2 on April 30, 2012 because of its inability to comply with its Transmission Operator’s (TOP) voltage schedule. Flat Ridge’s TOP provided it with a voltage schedule of 139 kV +/- 4 kV at the point of interconnection (POI) from December 17, 2009 through March 3, 2011 and a voltage schedule of 138 kV +/- 7 kV at the POI from March 3, 2011 through May 1, 2012. On April 27, 2012, Flat Ridge was notified by its new TOP that it would be required to adhere to a voltage schedule of 139 kV +/- 4 kV as of May 1, 2012. The new TOP directed Flat Ridge to “comply at all times, while the generator is on line, with the [new] Voltage Schedule and operate with the Automatic Voltage Regulator (AVR) in service and controlling voltage to maintain a constant voltage output at the interconnection point.” Following notification of the new voltage schedule and while conducting a compliance review for the aforementioned self-certification, Flat Ridge identified voltage schedule deviations outside of its mandated voltage schedule, the majority of which were less than 1 kV, which occurred between December 17, 2009 and April 30, 2012. Flat Ridge was previously unaware of the deviations from the TOP’s voltage schedule and had not notified its TOP that the deviations had occurred. Subsequently, Flat Ridge determined that it was unable to comply with the new TOP’s voltage schedule due to facility limitations. The Flat Ridge wind facility relies on a tap changing transformer and a shunt capacitor bank control system for dynamic voltage control. These devices were determined to be incapable of maintaining the facility’s voltage within 139 kV +/- 4 kV at all times. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By design, the Flat Ridge wind facility’s generators absorb reactive power and are incapable of contributing any substantial voltage support to the BPS. Finally, the majority of the voltage schedule excursions deviations by Flat Ridge were less than 1 kV and presented a minimal risk to the TOP’s transmission system. | Flat Ridge coordinated a change with its TOP for a voltage schedule of 139 kV +/-4 kV to 141 kV +4/ -6 kV. This provided a voltage range that was sustainable given the wind facilities' design restrictions. Flat Ridge commissioned a third-party engineering analysis of its facility to determine if its capacitors could be modified to adhere to a tighter voltage range. The engineering study determined that the capacitors were correctly set for voltage priority, and that the devices were already configured properly to maintain the POI voltage within required limits. Flat Ridge also drafted and implemented a procedure to detect and notify its TOP of voltage deviations outside the newly established voltage range, and detailed mitigating activities that should be undertaken by operations personnel to remedy voltage schedule deviations.
Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2011008215 | EOP-008-0 | R1.6 | During a September 19, 2011 to September 22, 2011 Compliance Audit of LAFA, the SPP RE Audit Team discovered noncompliance with EOP-008-0 R1.6. LAFA’s contingency plan called for all of LAFA’s personnel to receive annual training in the plan. However, the Audit Team determined that LAFA could not demonstrate that three out of five of its operators actually received annual training for loss of the primary control center in 2009 and 2010. This remediated issue applies to LAFA's Balancing Authority and Transmission Operator functions. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LAFA did have a contingency plan in place during 2009 and 2010, and the Audit Team determined that the plan addressed the requirements of EOP-008-0, except for R1.6. Although LAFA could not demonstrate that three of its five operators had received annual training on the contingency plan, LAFA’s system operators have been with LAFA for over five years and have had training on LAFA’s contingency plan, including participating in drills, prior to 2009. All operators have had recent training on LAFA’s contingency plan after 2010. | In order to assure that all LAFA operators complete site specific training for the loss of the primary control center in the future, LAFA scheduled its training in the following manner for each upcoming year: 1) Scheduled classroom instruction and discussion on the LAFA procedure as part of the operator’s bi-monthly meeting in the first quarter of each year; 2) Scheduled each operator to perform the drill for the loss of the primary control center during the first quarter of each year on a date when there is no conflict with contracted training for certification hours. Should an emergency occur in the LAFA system or BES that requires the delay of this drill, it will be performed after the emergency has ceased on the next workday for the scheduled operator; 3) Added a field to its Training Tracking Tool for a requirement of completion of loss of primary control center training and updated to indicate that this training is required for the operators; and 4) Implemented an audit process and flagging and monitoring for this requirement in the LAFA Training Tracking Tool. Included classroom instruction and drills for the Loss of the Primary Control Center in the annual training plan for operators. Copies will be distributed to each operator and the supervisor in December of each year. Any time a change occurs in an employee training schedule, they are notified. Supervisors are sent monthly updates.
Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2012009184 | FAC-009-1 | R1 | On January 17, 2012, LEAPP, as a Generator Owner, self-reported noncompliance with FAC-009-1 R1. LEAPP stated that it had not previously established the facility rating for its Hobbs Generating Station in accordance with its Facility Ratings Methodology (FRM). LEAPP had adopted a FRM calling for it to establish the Hobbs Generating Station Facility Rating by considering the individual ratings of the equipment comprising the station, ambient conditions, operating limitations and other factors. However, in application of its FRM, LEAPP had identified its Facility Rating as the “Net Capability” of the generating station, as identified in its Power Purchase Agreement (PPA) and identified the most limiting element of the Hobbs facility as the combustion turbine generators. LEAPP’s PPA is not a factor in the determination of the facility rating of the Hobbs generating station and the most limiting elements of the facility are the step-up transformers for the combustion turbine and steam turbine generators. | SPP RE determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although LEAPP had not developed the rating of the Hobbs facility based on its FRM, in practice, LEAPP operated the Hobbs units at their maximum capacity based upon operating limitations and ambient conditions. The maximum capacity rating, which LEAPP initially used, was more limiting than the actual nameplate rating. Accordingly, the operating capacity of the Hobbs generating facility was known to its Transmission Operator, Balancing Authority and Reliability Coordinator. Moreover, the Facility Rating of the Hobbs facility did not appreciably change once LEAPP's FRM was applied. | LEAPP reviewed and revised its site’s Facility Rating to ensure the correct determination was presented on the summary page. LEAPP updated its Facility Rating to reference actual equipment limitations based upon name plate data or specification sheets when name plate data was not available. This review and revision was complete on January 17, 2012.
Southwest Power Pool Regional Entity (SPP RE) | Midwest Energy, Inc. (Midwest) | NCR01118 | SPP2012009972 | PRC-005-1 | R2; R2.1 | On March 30, 2012, Midwest, as a Distribution Provider and a Transmission Owner, self-reported noncompliance with PRC-005-1 R2.1. The Midwest Protection System Maintenance and Testing Procedure (PSMP) required the testing of station battery banks to occur within a five-year interval. Midwest determined that eight (34.8%) of its 23 station battery banks had not been tested within the five-year interval. Five of the battery banks exceeded the required testing date by three months or less. The remaining three battery banks exceeded the testing interval by two to 3.5 years. All of the identified battery banks had been tested as of April 3, 2012. On April 19, 2012, Midwest supplemented its original Self-Report of PRC-005-1 R2.1 with a letter describing a failure to test three (0.4%) of its 715 Protection System relays within the three-year interval prescribed by the Midwest PSMP. Midwest indicated that these microprocessor-based relays were tested upon commissioning in February 2008 but were not tested again until April 23, 2012, which is one year and two months beyond the prescribed interval. | SPP RE determined the remediated issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three microprocessor-based relays were subject to monthly visual inspections and were constantly monitored by the Midwest Supervisory Control and Data Acquisition System (SCADA) for failure. Additionally, testing of the three relays occurred within four years and two months of the previous tests. This testing period was shorter than the recommended seven to 10 year testing interval identified in the NERC Protection System Maintenance Technical Reference (NERC Reference) for monitored microprocessor based relays. The station battery banks were also subject to monthly inspections that included corrosion checks, jumper contact checks, and the recording of battery charger DC voltage. Additionally, battery bank voltage is constantly monitored via Midwest’s SCADA system. In this case, testing occurred at 5.25 years, 7 years, and 8.5 years, which falls within the maximum ten-year testing interval identified in the NERC Reference for monitored battery banks. No equipment failures resulted from the missed battery or relay testing intervals. | Midwest conducted testing on all battery banks exceeding the five-year testing interval and tested the three relays exceeding the three year-testing interval by April 23, 2012. Midwest also implemented electronic reminders to ensure staff is notified of pending equipment testing deadlines.
Texas Reliability Entity, Inc (Texas RE) | American Electric Power Service Corp as agent for AEP Texas North Co, AEP Texas Central Co, and Public Service of Oklahoma (AEP) | NCR04006 | TRE2012010885 | EOP-008-0 | R1; R1.3; R1.7 | During a August 10, 2012 Audit, it was discovered that AEP, as a Transmission Operator (TOP), did not include a list of critical transmission facilities in its control center contingency plan, as required by EOP-008-0 R1.3. In addition, AEP did not perform an annual review and update of its control center contingency plan in 2011, as required by R1.7. Texas RE determined the duration of this remediated issue to be from May 4, 2010, when AEP was registered as a TOP, to September 16, 2012, when AEP conducted an annual review of its control center contingency plan and included a list of critical transmission facilities in it. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). With respect to the instance of noncompliance with EOP-008-0 R1.3, Texas RE determined that AEP’s control center contingency plan addressed the monitoring and control of all AEP transmission facilities. However, the plan was missing a list of facilities that were being monitored and controlled as critical or otherwise. During the Audit, it was confirmed that AEP had a list of critical transmission facilities that should be considered and addressed in the contingency plan but failed to include the list in its plan. Therefore, Texas RE considered this instance of noncompliance to be documentation related. With respect to the instance of noncompliance with EOP-008-0 R1.7, Texas RE determined that the risk to the BPS was minimal because AEP’s plan was reviewed and updated within a 14 month period and no material changes were made after the review. | AEP took immediate action to correct this remediated issue and updated its control center contingency plan. The plan now includes the location where the critical facilities list can be accessed. The annual review and update of AEP’s plan is now being tracked in a document control process to ensure the annual requirement is met. This issue was mitigated on February 28, 2012. Texas RE has verified the mitigation activities as complete.
Texas Reliability Entity, Inc (Texas RE) | Texas Medical Center Central Heating and Cooling Services Corp (TECO) | NCR11116 | TRE2012011048 | CIP-001-2a | R1 | On August 28, 2012, TECO, as a Generator Owner, self-reported a remediated issue with CIP-001-2a R1 because TECO’s previous company procedures did not fulfill the requirements for the recognition of and for making operating personnel aware of sabotage events. Texas RE determined the duration of this remediated issue to be from October 1, 2011, when TECO was required to comply with this Standard, to August 2, 2012, when TECO updated its sabotage reporting procedure to include recognition of and making operating personnel aware of sabotage events. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because TECO's generation unit is 48 MW and a potential failure of this generator would present a minimal risk to the BPS due to the low amount of power supplied. Approximately 80% of the MWh generated by TECO are consumed within TECO’s Private Use Network (PUN). Finally, TECO did have security procedures in place prior to August 2, 2012; however, they did not address the specific requirements of CIP-001-2a R1. TECO's prior procedures had instructions to inspect grounds and report suspicious activity and included bomb threat emergency and acts of violence emergency and had instructions to notify operating personnel identified by title. Therefore, TECO's personnel was prepared to act if a sabotage event occurred. | TECO took actions to correct this remediated issue and executed an updated sabotage reporting procedure, which includes: 1) definitions for recognizing suspected sabotage events and responses for each; and 2) provisions for making operating personnel aware of sabotage events. Texas RE has verified the mitigation activities as complete.
Texas Reliability Entity, Inc (Texas RE) | Texas Medical Center Central Heating and Cooling Services Corp (TECO) | NCR11116 | TRE2012011049 | CIP-001-2a | R3 | On August 28, 2012, TECO, as a Generator Owner, self-reported an issue with CIP-001-2a R3 because TECO did not provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. Texas RE determined the duration of this remediated issue to be from October 1, 2011, when TECO was required to comply with this Standard, to November 19, 2012, when TECO provided the updated sabotage reporting procedure to all operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because TECO's generation unit is 48 MW and a potential failure of this generator would present a minimal risk to the BPS due to the low amount of power supplied. Approximately 80% of the MWh generated by TECO are consumed within TECO’s Private Use Network (PUN). Finally, TECO did have security procedures in place prior to August 2, 2012; however, they did not address the specific requirements of CIP-001-2a R1. TECO's prior procedures had instructions to inspect grounds and report suspicious activity and included bomb threat emergency and acts of violence emergency and had instructions to notify operating personnel identified by title. Therefore, TECO's personnel was prepared to act if a sabotage event occurred. | TECO took action to correct this remediated issue and provided its updated sabotage reporting procedure to current operating personnel and included the procedure in new personnel training. Texas RE has verified the mitigation activities as complete. Additional sabotage awareness training is also scheduled by TECO.
Western Electricity Coordinating Council (WECC) | Central Arizona Water Conservation District (CAWC) | NCR05060 | WECC2012010810 | INT-004-2 | R2 | On August 1, 2012, CAWC submitted three Self-Reports citing possible noncompliance with INT-004-2 R2. Specifically, CAWC reported that on three occasions CAWC traders failed to update tags pursuant to INT-004-2 R2, sub-requirements R2.1 and R2.2. CAWC is registered in the NERC Compliance Registry as an entity performing the function of a Purchasing-Selling Entity. On February 29, 2012, the average energy profile for Navajo Generation was prescheduled at 364 MW. At 22:00 a Navajo unit was forced offline due to an unplanned outage. Although actual hourly interchange deviated from the hourly average energy profile by more than (-) 10%, CAWC did not update eight tags for the next available scheduling hours, HE24 through HE10. On May 7, 2012, a trader instructed the Navajo Generation Plant to ramp down to a level below the day-ahead planned interchange schedule. Consequently, the actual Navajo output for May 7, 2012, HE19 through HE24 deviated from the average hourly energy profile by more than 25 MW. On May 24, 2012, at 17:03, CAWC received notification of a planned outage of Navajo Unit 1 between 22:00 on May 25, 2012, and 14:00 on May 26, 2012. CAWC traders failed to update three Dynamic Interchange tags in anticipation of the planned outage. This failure resulted in the loss of 183 MW of resources used to serve load and excess sales. Further, traders failed to identify the Dynamic Interchange Schedule deviations and adjust the corresponding Dynamic Interchange tags for future hours during the planned outage. WECC's subject matter experts determined that, given the circumstances described in R2.1 and R2.2, CAWC failed to update a total of 12 tags on three occasions. WECC Enforcement also determined that in each of the three instances in which tags were not updated, traders acting on behalf of CAWC failed to follow established procedure that required tagging updates. WECC Enforcement dismissed possible violations WECC2012010811 and WECC2012010812 as separate enforcement actions. WECC Enforcement, therefore, determined to include the full scope of CAWC noncompliance with INT-004-2 R2 in a single enforcement action. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). INT-004-2 R2 requires Purchasing-Selling Entities to ensure that tags are updated for the next available scheduling hour and future hours under circumstances described by R2.1, R2.2 and R2.3. Failure to update the tags may cause potential loading voltage instability. In this case, CAWC failed to update 12 tags under the circumstances described by sub requirements R2.1 and R2.2. Human error was the cause of the noncompliance in each of the three instances in which CAWC failed to update tags. Traders acting on behalf of CAWC failed to follow established rules and procedures that required tagging updates per INT-004-2 R2. In each instance, CAWC was aware of the status of generation plant interties and load profiles in real-time through SCADA. Further, CAWC had an hourly load profile for each load location. The tags were limited to those associated with the hourly load profile of the Navajo generation unit. In each instance, CAWC would have been able to ramp up generation at other locations to compensate for the generation shortage at Navajo and prevent loading voltage instability to the system as a whole. WECC, therefore, determined that CAWC noncompliance with INT-004-2 R2, a remediated issue, posed a minimal risk to the BPS. | CAWC completed the following action by December 5, 2012, to remediate noncompliance with INT-004-2 R2: 1) CAWC implemented completed INT-004-2 retraining for CAWC staff and traders acting on behalf of CAWC; and 2) the two responsible traders were released from employment effective on June 21, 2012, and July 14, 2012, respectively.
Western Electricity Coordinating Council (WECC) | Dynegy Power, LLC (DYN) | NCR00200 | WECC2012010759 | VAR-002-1.1b | R2 | On July 9, 2012 DYN, as a Generator Operator and as a Generator Owner, submitted a Self-Report regarding a potential issue with VAR-002-1.1b R2. On July 23, 2012, DYN submitted a Self-Certification, which incorporated the Self-Report, reporting potential noncompliance with VAR-002-1.1b R2. In the Self-Certification, DYN reported that on June 6, 2012 one of its generators was operating at a higher terminal voltage than its Transmission Operator (TOP) target level allows. DYN reported that its TOP required its generators to operate at a voltage of 21.7 kV plus or minus 0.2 kV. In this instance, the DYN Operation Technician failed to adjust the power factor for two hours following the end of startup of the generator. DYN reported that for those two hours the generator was operating at a voltage which was 0.5 kV higher than its TOP’s target levels. DYN noted that the operator recognized that the generator was operating at a voltage above the TOP’s target level and adjusted the generator voltage to a voltage which is within the target level of its TOP. On July 18, 2012, a WECC Subject Matter Expert (SME) contacted DYN to discuss its Self-Report and Self-Certification. The SME determined that DYN had a possible issue with VAR-002-1.1b R2 for failing to operate its generators in accordance with its TOP’s target levels. The SMEs determined, that for two hours on June 6, 2012, DYN operated one of its generators at a voltage level above the target levels set by its TOP. WECC Enforcement (Enforcement) reviewed DYN’s Self-Report, Self-Certification, and the SME’s findings. Enforcement determined that DYN had an issue with VAR-002-1.1b R2 because it allowed its generator to operate at a higher voltage level than that specified by its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DYN had a specific policy in place to prevent violations of VAR-002-1.1b. DYN had provided this information to its operators and the operators acted in accordance to this procedure. Following the procedure, DYN quickly resolved the issue once it was discovered. During the two hour time frame the TOP did not notice any changes in voltage in their system and did not contact the entity regarding the voltage output. Accordingly, WECC determined that this remediated issue posed a minimal risk to the BPS. | The issue was resolved when DYN’s operation technician adjusted the voltage levels of the generator to comply with the TOP’s target levels. DYN also submitted and completed a mitigation plan that required DYN to review its past voltage records to ensure compliance with VAR-002-1.1b R2, conduct a training session to refresh its employees in its procedures, and installed an alarm that is intended to remind the operator to adjust generator voltage when the unit reaches 32 MW. The actual completion date of the mitigation activities was October 17, 2012.
Western Electricity Coordinating Council (WECC) | GenOn California I (GCAI) | NCR11148 | WECC2012010731 | VAR-002-1.1b | R1 | On July 20, 2012, GCAI, as a Generator Operator, submitted a Self-Certification citing possible noncompliance with VAR-002-1.1b R1. Specifically, GCAI reported that on May 31, 2012, at 08:43 AM, Etiwanda Unit 4 (Unit 4) was brought online in “manual” operating mode. Per standard operating procedure, the Automatic Voltage Regulator (AVR) at Unit 4 should trigger once the generator reaches a minimum load point. In this case, however, GCAI reported that at approximately 08:50 AM, Unit 4 reached the minimum load point, but that the AVR did not activate. Rather, Unit 4 remained in “manual” operating mode until 09:30 AM. GCAI made its Transmission Operator (TOP) aware that the unit was offline and that GCAI was planning on re-starting the unit. At 09:30 AM GCAI switched Unit 4 to AVR operating mode and notified its TOP of the change in Unit 4's operating status (specifically, that it switched from manual mode to AVR mode). WECC Subject Matter Experts (SMEs) reviewed GCAI’s Self-Certifications and contacted the entity to request additional information. SMEs determined that on May 31, 2012, between 08:50 and 09:30 AM, GCAI failed to operate in AVR mode. SMEs forwarded their findings to WECC Enforcement (Enforcement). Enforcement reviewed GCAI’s Self-Certifications and the SMEs’ findings. Enforcement determined that per VAR-002-1.1b R1 entities are required to operate in AVR. In this case, Enforcement determined that between 08:50 and 09:30 AM, GCAI failed to operate Unit 4 in AVR. The TOP expected the unit to come online with the AVR in service controlling voltage. Enforcement, therefore, determined that GCAI had issues with VAR-002-1.1b R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AVR operation is necessary to ensure that generation automatically adjusts for varying voltage levels and reactive flows on the BPS. Failure of a Generator Operator to operate in AVR may cause system disturbances with voltage variation. In this case, GCAI failed to operate Unit 4 in AVR for a period of approximately 40 minutes. Unit 4 comprises one out of a total of three units in service at Etiwanda. The other two units were operating in AVR, and were available to respond to voltage variation at the interconnection during the 40 minute period in which AVR at Unit 4 was disabled. During the 40 minute period in which Unit 4 AVR was not in operation, GCAI maintained the voltage schedule set by its Transmission Operator. Further, Unit 4’s operating status was detected by GCAI dispatch at 08:50 AM. GCAI Generator Operators were notified and AVR was switched on by 09:30 AM. Enforcement, therefore, determined that GCAI's noncompliance with VAR-002-1.1b R1 posed a minimal risk to the BPS. | On September 24, 2012, GCAI completed the following action to remediate noncompliance with VAR-002-1.1b R1 and R3: GCAI added AVR alarming to make its operating personnel aware of changes in status. GCAI revised its Start-up Checklist to include the following: 1) a requirement to ensure that the AVR is in-service; and 2) a requirement to ensure that the Power System Stabilizer (PSS) is in-service. GCAI added E-Alert notification for plant management regarding the operating status of AVR and PSS. To avoid future instances of possible noncompliance with VAR-002-1.1b R1 and R3, GCAI provided training on the modified start-up checklist for all plant operators.
Western Electricity Coordinating Council (WECC) | GenOn California I (GCAI) | NCR11148 | WECC2012010734 | VAR-002-1.1b | R3 | On July 20, 2012, GCAI, as a Generator Operator, submitted a Self-Certification citing possible noncompliance with VAR-002-1.1b R3. Specifically, GCAI reported that on May 31, 2012, at 08:43 a.m., Etiwanda Unit 4 (Unit 4) was brought online in “manual” operating mode. Per standard operating procedure, the Automatic Voltage Regulator (AVR) at Unit 4 should trigger once the generator reaches a minimum load point. In this case, however, GCAI reported that at approximately 08:50 a.m., Unit 4 reached the minimum load point, but that the AVR did not activate. Rather, Unit 4 remained in “manual” operating mode until 09:30 a.m. GCAI made its Transmission Operator (TOP) aware that the unit was offline and that GCAI was planning on re-starting the unit. At 09:30 a.m GCAI switched Unit 4 to AVR operating mode and notified its TOP of the change in Unit 4's operating status (specifically, that it switched from manual mode to AVR mode). WECC Subject Matter Experts (SMEs) reviewed GCAI’s Self-Certifications and contacted the entity to request additional information. SMEs determined that on May 31, 2012, between 08:50 and 09:30 a.m., GCAI failed to operate in AVR mode. Further, SMEs determined that GCAI’s failure to notify the TOP of Unit 4’s manual operating status between 08:50 and 09:30 a.m. was not in compliance with VAR-002-1.1b R3. SMEs forwarded their findings to WECC Enforcement (Enforcement). Enforcement reviewed GCAI’s Self-Certification and the SMEs’ findings. Enforcement determined that per VAR-002-1.1b R3, entities are required to notify the TOP within 30 minutes of a change in status of a reactive resource, including AVR. In this case, Enforcement determined that between 08:50 and 09:30 a.m. GCAI failed to operate Unit 4 in AVR. The TOP expected the unit to come online with the AVR in service controlling voltage. Enforcement also determined that GCAI failed to notify the TOP of its operating status within 30 minutes, or by 09:20 a.m. Enforcement, therefore, determined that GCAI had an issue with VAR-002-1.1b R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AVR operation is necessary to ensure that generation automatically adjusts for varying voltage levels and reactive flows on the BPS. Failure of a Generator Operator to operate in AVR may cause system disturbances with voltage variation. In this case, GCAI failed to operate Unit 4 in AVR for a period of approximately 40 minutes. Unit 4 comprises one out of a total of three units in service at Etiwanda. The other two units were operating in AVR, and were available to respond to voltage variation at the interconnection during the 40 minute period in which AVR at Unit 4 was disabled. During the 40 minute period in which Unit 4 AVR was not in operation, GCAI maintained the voltage schedule set by its Transmission Operator. Further, Unit 4’s operating status was detected by GCAI dispatch at 08:50 a.m. GCAI Generator Operators were notified and AVR was switched on by 09:30 a.m. Enforcement, therefore, determined that GCAI noncompliance with VAR-002-1.1b R3 posed a minimal risk to the BPS. | On September 24, 2012, GCAI completed the following action to remediate noncompliance with VAR-002-1.1b R1 and R3: GCAI added AVR alarming to make its operating personnel aware of changes in status. GCAI revised its Start-up Checklist to include the following: 1) a requirement to ensure that the AVR is in-service; and 2) a requirement to ensure that the Power System Stabilizer (PSS) is in-service. GCAI added E-Alert notification for plant management regarding the operating status of AVR and PSS. To avoid future instances of possible noncompliance with VAR-002-1.1b R1 and R3, GCAI provided training on the modified start-up checklist for all plant operators.