## Public Non-CIP Jan. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
ReliabilityFirst Corporation (ReliabilityFirst) | Dynegy Power, LLC (Dynegy) | NCR00200 | RFC2012010720 | VAR-002-1.1b | R3 | On July 6, 2012, Dynegy, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with VAR-002-1.1b R3 that also described issues with VAR-002-1.1b R1 and R2. After discovering a voltage schedule issue at its Ontelaunee generating plant, Dynegy reviewed its compliance with VAR-002-1.1b R1 and R3. Dynegy identified three instances where it failed to provide notification that it was not operating the automatic voltage regulator (AVR) in automatic voltage control mode or that there was a status change on its generator’s AVR. First, on August 1, 2011, during shutdown, Dynegy switched the AVR to power factor mode for 16 minutes and failed to notify the Transmission Operator (TOP) that there was a status change on the AVR once it switched back to automatic voltage control mode, as required by R3. Second, on November 14, 2011, during startup and following a planned outage on Combustion Turbine #2, Dynegy was conducting tuning with the AVR in power factor mode for three hours and forty minutes. The Ontelaunee logs do not indicate that it notified the Transmission Owner (TO), who notifies the TOP, however, the logs indicate that the TOP was aware when unit testing began and ended. Third, on April 7, 2012, during shutdown, Dynegy switched the AVR to power factor mode for 40 minutes and failed to notify the TOP that there was a status change on the AVR, as required by R3. The Ontelaunee logs do not indicate that Dynegy notified the TO, who notifies the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Ontelaunee remained within its assigned voltage schedule during the time period of the issue. In addition, during the November 14, 2011 incident, the TOP was aware that Dynegy was conducting testing, increasing the likelihood that the TOP would expect AVR status changes. Furthermore, Dynegy has a policy in place that requires notification of the TOP if the AVR is not operating in automatic voltage control mode and of any change in status of the AVR within 30. Dynegy simply failed to implement this policy on these occasions. | Dynegy created a new Plant Operator Standing Order to address compliance with the AVR notifications, provided refresher training to operators, and requested a blanket notification from its TOP, PJM Interconnection LLC (PJM), allowing an exemption for Ontelaunee from notifying PJM of every instance that it operated in a mode other than automatic voltage control mode during startup and shutdown.
ReliabilityFirst Corporation (ReliabilityFirst) | Dynegy Power, LLC (Dynegy) | NCR00200 | RFC2012010905 | VAR-002-1.1b | R1 | On July 6, 2012, Dynegy, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with VAR-002-1.1b R3 that also described issues with VAR-002-1.1b R1 and R2. After discovering a voltage schedule issue at its Ontelaunee generating plant, Dynegy reviewed its compliance with VAR-002-1.1b R1 and R3. Dynegy identified three instances where it failed to provide notification that it was not operating the automatic voltage regulator (AVR) in automatic voltage control mode or that there was a status change on its generator’s AVR. First, on August 1, 2011, during shutdown, Dynegy switched the AVR to power factor mode for 16 minutes and failed to notify the Transmission Operator (TOP) that it was not operating in automatic voltage control mode, as required by R1. Second, on November 14, 2011, during startup and following a planned outage on Combustion Turbine #2, Dynegy was conducting tuning with the AVR in power factor mode for three hours and forty minutes. The Ontelaunee logs do not indicate that it notified the Transmission Owner (TO), who notifies the TOP, however, the logs indicate that the TOP was aware when unit testing began and ended. Third, on April 7, 2012, during shutdown, Dynegy switched the AVR to power factor mode for 40 minutes and failed to notify the TOP that it was not operating in automatic voltage control mode, as required by R1. The Ontelaunee logs do not indicate that Dynegy notified the TO, who notifies the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Ontelaunee remained within its assigned voltage schedule during the time period of the issue. In addition, during the November 14, 2011 incident, the TOP was aware that Dynegy was conducting testing, increasing the likelihood that the TOP would expect AVR status changes. Furthermore, Dynegy has a policy in place that requires notification of the TOP if the AVR is not operating in automatic voltage control mode and of any change in status of the AVR within 30 minutes. Dynegy simply failed to implement this policy on these occasions. | Dynegy created a new Plant Operator Standing Order to address compliance with the AVR notifications, provided refresher training to operators, and requested a blanket notification from its TOP, PJM Interconnection LLC (PJM), allowing an exemption for Ontelaunee from notifying PJM of every instance that it operated in a mode other than automatic voltage control mode during startup and shutdown.
ReliabilityFirst Corporation (ReliabilityFirst) | Dynegy Power, LLC (Dynegy) | NCR00200 | RFC2012010906 | VAR-002-1.1b | R2 | On July 6, 2012, Dynegy, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with VAR-002-1.1b R3 that also described issues with VAR-002-1.1b R1 and R2. The voltage schedule in place for Dynegy’s Ontelaunee generating plant, a 526 MW combined cycle natural gas fired facility interconnected at 230 kV, is 237 kV plus or minus 0.5%. On May 19, 2012, for approximately one hour, Dynegy exceeded that voltage schedule by operating at 238.435 kV, or 0.6% above 237 kV. Dynegy later learned that the automatic voltage regulator (AVR) reached its maximum adjustment limit of plus or minus 0.5% of the target voltage, which is in place to help prevent destabilizing voltage swings. Dynegy operating personnel could have manually changed the setpoint, however, to attempt to maintain the voltage schedule, and failed to do so. Dynegy reviewed voltage schedule history beginning August 31, 2011, and discovered no additional voltage schedule excursions. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The voltage schedule excursion was 0.1% above the voltage schedule limit, and lasted for one hour. In addition, Dynegy did not exceed the Transmission Operator’s, PJM Interconnection LLC's, default voltage schedule (the schedule in place if a more specific schedule is not defined), the upper bound of which is 239 kV. | Dynegy created a new Plant Operator Standing Order to address compliance with the voltage schedule and provided refresher training to operators.
ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2012010719 | VAR-002-1.1b | R3 | On July 9, 2012, IPL, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with VAR-002-1.1b R3. IPL has a standing notification with its Transmission Operator (TOP) that it will operate its automatic voltage regulator (AVR) at the Eagle Valley generating plant in automatic voltage control mode. On June 27, 2012, IPL started its Eagle Valley Unit #5, but a component essential to the operation of the AVR in automatic voltage control mode was not functioning. As a result, IPL unintentionally started the unit’s AVR in manual voltage control mode. IPL failed to notify the TOP of the status change on this unit’s AVR within 30 minutes. IPL discovered that it had not notified the TOP of this status change, and notified the TOP approximately four hours after it was required to do so. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. IPL was manually controlling voltage and followed the voltage schedule during the time period of the issue. As a result, IPL was aware of the situation, and thereby decreased the likelihood of a damaging voltage excursion. In addition, there were additional units online at the generating plant with the AVR in automatic mode that could have provided voltage support, if necessary. | IPL developed training for control board operations personnel to address the issue and required that training be taken by all control board operations personnel.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2012010019 | PRC-005-1 | R2 | During a Compliance Audit, ReliabilityFirst determined that NIPSCO, as a Distribution Provider and Transmission Owner, had an issue with PRC-005-1 R2. Specifically, NIPSCO's maintenance and testing records for its station batteries were incomplete. NIPSCO’s provided maintenance and testing records demonstrating specific gravity readings for 58 of 60 inspections, but could not locate two specific gravity readings. NIPSCO was unable to provide specific gravity readings for its maintenance and testing performed on August 4, 2010 and September 13, 2010. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NIPSCO provided specific gravity readings for 58 of 60 inspections during the audit period but could not locate readings for two occasions. For 60 out of 60 occasions, NIPSCO provided cell voltage readings, internal resistance readings, and inter-cell resistance readings. None of the readings indicated any issues with the batteries, including the two batteries for which NIPSCO could not provide specific gravity readings, during the duration of the issue. NIPSCO determined that the batteries would have functioned properly if called upon during the duration of the issue. | NIPSCO included a check box in its maintenance and testing battery software that does not allow the maintenance and testing task to be marked as complete until after NIPSCO enters specific gravity readings. NIPSCO also now requires supervisors to review battery inspections and sign off on the inspection with their names and the date of approval. Finally, NIPSCO revised its Protection System maintenance and testing program to reflect these changes.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company GO GOP (NIPSCO) | NCR02610 | RFC2011001121 | PRC-005-1 | R2 | On September 30, 2011, NIPSCO, as a Generator Owner, self-reported, within 90 days of a scheduled Compliance Audit, an issue with PRC-005-1 R2 to ReliabilityFirst. NIPSCO discovered that it tested 5 out of 8,877 relays 85 days past the date required by its Protection System maintenance and testing program (Program). Additionally, NIPSCO discovered that, on 41 of 2,790 maintenance and testing occasions between 2009 and 2011, NIPSCO did not test or maintain 10 sets of batteries within the 60 days required by its Program. The issue was caused by a malfunction in NIPSCO's job tracking software. The job tracking software did not track preventative maintenance (PM) when a PM task was completed but not closed out in the software. As a result, the software would not generate a subsequent PM task notice within the interval described in NIPSCO’s Program. Finally, NIPSCO did not have records to demonstrate it performed monthly and quarterly maintenance and testing on batteries at its Sugar Creek generating plant within the 60 days required by its Program. Although, NIPSCO did perform maintenance and testing of its batteries at the Sugar Creek generating plant within the 60 days required by its Program, records of the testing were never entered into its tracking software and are therefore unavailable. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five relays at issue are not the primary protection scheme at this location. Rather, the five relays are secondary to the primary overcurrent and differential protection scheme. Furthermore, the five relays are associated with a small 78 MW generating unit. NIPSCO can provide records demonstrating it had annual maintenance and testing performed on the batteries at its Sugar Creek generating plant. NIPSCO contracts with an unaffiliated registered entity to perform annual maintenance and testing on the batteries in its Sugar Creek generating plant and has records to demonstrate the unaffiliated registered entity completed the maintenance and testing. Additionally, NIPSCO has voltage and charger alarms on its battery banks which would notify system operators of a malfunction. Finally, upon testing the Protection System devices at issue, NIPSCO determined all the Protection System devices were within specifications and would have operated correctly during the duration of the issue if needed. | NIPSCO conducted maintenance and testing of the Protection System devices at issue. NIPSCO also modified its maintenance and testing tracking software to ensure that it would track preventative maintenance and generate a request for preventative maintenance within the defined interval even in the event the prior preventative maintenance task was not closed out in the software. Finally, NIPSCO conducted PRC-005-1 training for personnel involved in maintenance and testing of Protection System devices.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company GO GOP (NIPSCO) | NCR02610 | RFC2012010011 | VAR-002-1.1a . | R2 | During a Compliance Audit, ReliabilityFirst determined that NIPSCO, as a Generator Operator, had an issue with VAR-002-1.1a R2. Specifically, on two occasions, NIPSCO's 160 MW Baily Unit 7 generating unit (Unit 7) was outside its voltage schedule. ReliabilityFirst discovered that on June 10, 2009 and August 9, 2011, NIPSCO operated Unit 7 outside its voltage schedule. NIPSCO was not operating Unit 7 at its MVAR limit and did not have an exemption to operate Unit 7 outside its voltage schedule on either of the two occasions. Additionally, ReliabilityFirst discovered that during Unit 7’s AVR outage from October 3, 2010 to November 29, 2010, NIPSCO did not maintain the generator voltage within its voltage schedule on numerous occasions. ReliabilityFirst determined that NIPSCO did not maintain its generator voltage within the voltage schedule provided by the TOP for all days except: October 6, 2010 to October 13, 2010; October 15, 2010; November 3, 2010 to November 6, 2010; and November 26, 2010 to November 28, 2010. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the duration of the issue, NIPSCO’s voltage schedule allowed for a deviation of only +/- 1%. Each of NIPSCO’s deviations from its schedule was minor, with the largest deviation 1.87 kV outside the tolerance band. Following the issue, NIPSCO received an expanded voltage schedule which, had it been in place during the duration of the issue, would not have resulted in an issue with VAR-002-1.1a R2. | NIPSCO studied its current voltage schedule to determine proper modification to the schedule. NIPSCO received a modified voltage schedule with an expanded bandwidth that will help assure NIPSCO operates within its schedule while still operating at safe limits.
ReliabilityFirst Corporation (ReliabilityFirst) | Wisconsin Electric Power Company (Wisconsin Electric) | NCR00951 | RFC2012011082 | VAR-002-1.1b | R1 | On August 10, 2012, Wisconsin Electric, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with VAR-002-1.1b R1. Wisconsin Electric’s Oak Creek Unit 6 is equipped with a low speed exciter, a high speed exciter, and an emergency exciter. When the unit is synchronized to the system using the combination of the emergency and high speed exciter, the unit is not capable of automatic voltage regulation. Oak Creek Units 5 and 6 are the only two of Wisconsin Electric’s generating units to have a low speed exciter, a high speed exciter, and an emergency exciter. On August 6, 2012 at 0327 Central Standard Time (CST), Oak Creek Unit 6, a 250 MW coal-fired generating unit, tripped from service due to high bearing temperature on the low speed exciter. At 0503 CST and again at 0527 CST after a subsequent boiler trip, Wisconsin Electric brought Oak Creek Unit 6 back online using the combination of the emergency and high speed exciter, but Wisconsin Electric failed to notify the Transmission Operator that the unit was not operating in automatic voltage control mode prior to bringing the unit online. Wisconsin Electric's operator assumed that another individual had provided notification to the Transmission Operator, when in fact that individual had not done so. At 0602 CST, Wisconsin Electric notified the Transmission Operator that Oak Creek Unit 6 was not operating in automatic voltage control mode. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Wisconsin Electric identified the issue within one hour of it occurring and began conducting mitigating activities the following day. Wisconsin Electric manually controlled voltage within the limits of its voltage schedule during the time period of the issue. In addition, Oak Creek Unit 6 constitutes 3.9% of Wisconsin Electric’s 6,349 MW. As a result, it was less likely that Oak Creek Unit 6’s operation in manual voltage control mode would have caused Wisconsin Electric to be unable to respond to changes in voltage or provide voltage support to the system. | Wisconsin Electric installed a placard the day following the issue in the control room for Oak Creek Units 5 and 6 to remind its operators to notify the Electric System Operations Power System Operator, who in turn reports to the Transmission Operator, prior to every synchronizing attempt with the emergency exciter. In addition, Wisconsin Electric reviewed and revised its operating procedures to better ensure compliance with VAR-002.1.1b R1. Furthermore, Wisconsin conducted training to inform control room operators of its VAR-002 R1 and R3 procedures.
SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2011008230 | MOD-030-2 | R2 | On September 29, 2011, Duke, as a Transmission Operator (TOP), self-reported an issue of MOD-030-2 R2 because it failed to update the Total Flowgate Capability (TFC) within seven calendar days of being notified by the Transmission Owner (TO) of a change in the Rating that would affect the TFC of a Flowgate used in the Available Flowgate Capability (AFC) process. SERC requested and reviewed additional information in order to complete its assessment. SERC determined that, on May 31, 2011, Duke, as a TO, issued a Rating change due to the replacement of a 230 kV/100 kV transformer. This Rating change would affect the TFC of the Flowgate used in the AFC process. Duke, as a TOP, was notified of the Rating change on May 31, 2011, but it did not comply with the seven day criteria to update the TFC, as required by MOD-030-2 R2.5.1. The Rating change should have occurred no later than June 7, 2011. On June 15, 2011, while preparing data for the exchange of model updates with adjacent Transmission Service Providers (TSPs), Duke, as a TOP, discovered the Rating change had not been entered into the AFC powerflow base case. Duke, as a TOP, implemented the Rating change into the AFC process and notified adjacent TSPs the same day. After the identification of the error, Duke reviewed the Flowgate ratings and discovered no other instances of noncompliance. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) The scheduled flows never exceeded 73% of the revised Facility Rating; 2) While the transfer capability was impacted by the Rating change, the real-time reliability assessments had the correct Rating and did not indicate they were exceeding the revised Rating or presenting any reliability issues; and 3) Even though the Rating change was not incorporated into the next day study process and for the calculation of AFC/TFC within seven days as required, it was reflected in the real-time Energy Management System on the day of the Rating change notification. Any impacts to the Duke TOP Area would have been reflected in the Duke real-time contingency analysis application. | SERC staff verified that Duke completed the following actions: 1) Implemented a new process, which provides the steps to be followed when a rating change occurs; 2) Updated the job aid for updating the TFC and provided training to relevant employees; and 3) Designated a single point of contact and a backup for addressing rating changes.
SERC Reliability Corporation (SERC) | North Carolina Electric Membership Corporation (NCEMC) | NCR01279 | SERC2012009594 | PRC-005-1a | R2 | On January 25, 2012, NCEMC, as a Generator Owner (GO), self-reported an issue with PRC-005-1a R2, stating that it could not produce evidence of fourth quarter 2011 testing of the batteries for two units as required by its Protection System maintenance and testing procedure. NCEMC’s Protection System maintenance and testing procedures for the combustion turbine plants call for quarterly testing of unit batteries with one of those quarters counting as the annual test. During the annual review process for the 2011 year, NCEMC discovered that one set of quarterly test data for batteries at two units was missing for the fourth quarter of 2011. NCEMC believes that it completed the testing, but it could not locate the evidence of testing. This issue coincided with NCEMC initiating the use of a handheld test device instead of using a fluke meter and pencil and paper. SERC requested additional information in order to complete its assessment. NCEMC provided SERC with spreadsheets identifying NCEMC’s Protection System devices for its GO and Transmission Owner functions and the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC verified the assigned intervals based on a review of NCEMC’s Protection System maintenance and testing procedures. SERC determined that NCEMC could not provide records of the last testing date for two out of 13 station batteries (15.4%), both located at NCEMC’s Anson plant. In total, NCEMC failed to have test records for two out of 265 Protection System devices (0.8%). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) NCEMC’s batteries have alarms for ground trip, loss of AC power, and low DC voltage. The alarms are locally visible at each battery charger and the alarms alert plant operators in the plant control rooms in the event of problems; 2) NCEMC conducts monthly testing on a sample of cells. NCEMC has November and December 2011 monthly reports for the two batteries with missing test records which show that the sample cells were in satisfactory condition; and 3) NCEMC conducted its next quarterly test of the batteries two months after it believed it conducted the quarterly tests in the fourth quarter of 2011. NCEMC personnel found no problems during this subsequent quarterly test. | SERC verified that NCEMC completed the following actions: 1) Updated its Protection System maintenance and testing process to ensure that NCEMC personnel save static electronic copies of test reports and that those records are available in time to retest within the required period if needed; and 2) Reemphasized to plant staff, through training, the importance of the tests and records of testing.
Southwest Power Pool Regional Entity (SPP RE) | City of Malden – Board of Public Works (Malden) | NCR01073 | SPP201100628 | PRC-008-0 | R1 | During a June 27, 2011 Compliance Audit, SPP RE’s Audit Team discovered that Malden did not have a Under Frequency Load Shedding (UFLS) equipment maintenance and testing program that identified the UFLS equipment or the schedule for the testing and maintenance of the UFLS equipment prior to April 4, 2011. Additionally, after April 4, 2011, Malden failed to include the potential transformer (PT) associated with its only underfrequency relay. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Malden did not have a documented UFLS maintenance program prior to April 4, 2011, and it failed to include the PT until August 16, 2011, Malden did provide evidence that it had been testing its UFLS protection system within the manufacturer’s recommended testing intervals, thereby reducing the risk to the BPS. As a result, SPP RE determined that the this issue was documentation-related. In addition, Malden has no assets connected at 100 kV or above, its load is served by a 69 kV connection with another entity, it had a summer peak load of 13.3 MW (occurring in 2010), and it owns one UFLS relay. | Malden established a documented UFLS equipment maintenance and testing program, and revised it to include language concerning the PT associated with its UFLS relay.
Texas Reliability Entity, Inc (Texas RE) | Lower Colorado River Authority (LCRA) | NCR04093 | TRE2012009906 | PRC-005-1 | R2 | LCRA, as a registered Generator Owner (GO), self-reported on January 17, 2012 and later on August 20, 2012, two instances of noncompliance with PRC-005-1 R2. Because the two instances are related, Texas RE combined the two instances into one issue. After reviewing one of its interconnection agreements, LCRA reported that it discovered that it owned current transformers (CTs) that were used by the interconnected Transmission Owner (TO). The discovery of the ownership and maintenance and testing responsibility for these devices prompted LCRA to perform a review of its Protection System device inventory. Consequently, LCRA added some new devices to that inventory. LCRA reported that it could not produce maintenance and testing records as required by its Protection System maintenance and testing program (Program) for the Protection System devices at the Fayette Power Project and Sims Gideon generation plants. At the Fayette Power Project plant, which houses three generating units, 46 current and voltage sensing devices and six DC control circuitry components did not have documented testing, as required by the Program. At the Sims Gideon plant, which houses three generating units, three current and voltage sensing devices and nine DC control circuitry components did not have documented testing, as required by the Program. Therefore, LCRA failed to test a total of 49 current and voltage sensing devices and 15 DC control circuitry components, or a total of 64 devices. The devices involved were last tested prior to the Reliability Standards becoming mandatory and enforceable. LCRA's maintenance and testing interval for current and voltage sensing devices is 12 years and for DC control circuitry components it is six years. Texas RE determined the duration of this issue to be from June 18, 2007, when LCRA was required to comply with this Standard, to October 30, 2012 when the last device was tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Texas RE determined that the number of devices discovered to be LCRA’s responsibility for maintenance and testing constitute a small portion of LCRA's total Protection System devices. Twenty seven of the total 64 (55.10%) voltage and current sensing devices at issue provide signals to LCRA's TO Protection Systems, not to LCRA's GO Protection Systems. The remaining 37 of the total 64 devices (57.8%) at issue are part of the GO’s Protection Systems and represent 3.3% of the total LCRA's GO Protection System devices. The 27 of the total 64 devices found, that are not a part of the GO’s Protections Systems, represent 2.4% of the total GO Protection System devices. These 27 devices are owned by the GO but are used for TO signals. Finally, no issues were found with the 64 devices at issue during their testing as part of the Mitigation Plan. | LCRA performed preventative maintenance for the CTs, potential transformers and DC circuits, in accordance with its Program. LCRA also updated its tracking matrix and assigned asset numbers for future tracking and maintenance intervals. Texas RE has verified the mitigation activities as complete.
Texas Reliability Entity, Inc (Texas RE) | Mesquite Wind, LLC (Mesquite) | NCR04097 | TRE2012009736 | TOP-002-2 | R13 | From a February 15, 2012 Self-Report, Texas RE determined that Mesquite did not perform reactive capability verification and provide the results to the Balancing Authority (BA) or Transmission Operator personnel as requested. Pursuant to the Electric Reliability Council of Texas’ (ERCOT) protocols dated August 18, 2009, the Generation Resource Entity should conduct reactive capability testing and provide the results to ERCOT upon initial qualification and once every two years. Mesquite, as a Generator Operator (GOP), performed the testing and submitted the results upon initial qualification on November 29, 2007. Mesquite failed to conduct and provide testing results to ERCOT by November 29, 2009, two years later. Mesquite later performed the testing and submitted the results to ERCOT on June 30, 2010. Thus, the duration of the issue is November 27, 2009 to June 30, 2010. This issue applies to Mesquite's GOP function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the results Mesquite submitted to ERCOT on June 30, 2010 did not change from its results conducted at initial qualification on November 29, 2009. The BA was already aware of the reactive capabilities of the generation resource, so the failure to provide test results to the BA would have no effect on the BA's management of reactive capabilities. | On June 30, 2010, Mesquite provided the results of the reactive capability testing to ERCOT as the BA. Mesquite also provided test results in subsequent years, as required. Texas RE has verified the mitigation activities as complete.
Texas Reliability Entity, Inc (Texas RE) | Post Oak Wind, LLC (POW) | NCR10167 | TRE201100365 | TOP-002-2 | R13 | During a Compliance Audit conducted June 7, 2011 through June 9, 2011, Texas RE discovered that POW did not perform reactive capability verification and provide the results to the Balancing Authority (BA) or Transmission Operator (TOP) personnel as requested. Pursuant to the Electric Reliability Council of Texas’ (ERCOT) protocols dated August 18, 2009, the Generation Resource Entity should conduct reactive capability testing and provide the results to ERCOT upon initial qualification and once every two years. POW, as a Generator Operator (GOP), performed the testing and submitted the results upon initial qualification on August 20, 2007. However, POW failed to conduct and provide testing results to ERCOT by August 20, 2009, two years later. POW later performed the testing and submitted the results to ERCOT on June 30, 2010. Thus the duration of the issue is August 20, 2009 to June 30, 2010. This issue applies to POW's GOP function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the results POW submitted to ERCOT on June 30, 2010 did not change from its results conducted at initial qualification on August 20, 2007. The BA was already aware of the reactive capabilities of the generation resource, so the failure to provide test results to the BA would have no effect on the BA's management of reactive capabilities. | On June 30, 2010, POW provided the results of the reactive capability testing to ERCOT as the BA. Texas RE has verified the mitigation activities as complete.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC2012011047 | MOD-008-1 | R1 | Between August 20, 2012 and August 30, 2012, WECC conducted an on-site Audit of WACM’s compliance with certain NERC Reliability Standards. During the course of the Audit, the Audit Team determined that WACM’s Transmission Reliability Margin (TRM) Implementation Document (TRMID) did not explicitly identify the TRM calculation used for operations for each of the time periods described in R1.3.1 through R1.3.3 of the Standard. Rather, the Audit Team determined that WACM’s TRMID identified a single TRM calculation without reference to any specific time period. The Audit Team, therefore, found WACM, as a Transmission Operator, was in noncompliance with MOD-008-1 R1.3 and forwarded their findings to WECC Enforcement (Enforcement). MOD-008-1 R1 requires Transmission Operators to maintain a TRMID. Pursuant to R1.3, the TRMID must identify the TRM calculation used for three time periods: “Same day and real-time (R1.3.1),” “Day-ahead and pre-schedule (R1.3.2),” and “Beyond day-ahead and pre-schedule, up to thirteen months ahead (R1.3.3).” After reviewing Audit Team findings, Enforcement determined that WACM failed to identify the TRM calculation used for the three time periods pursuant to R1.3. Enforcement determined that although WACM used a single TRM calculation for all three time periods, compliance with R1.3 requires WACM’s TRMID to explicitly identify the TRM calculation used for each time period. Enforcement, therefore, determined that WACM’s TRMID failed to satisfy MOD-008-1 R1.3 between April 1, 2010, the effective date of the Standard, and October 5, 2012, the date by which WACM completed remediation activity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WACM failed to explicitly state that it uses the same TRM calculation for each time period, WACM did include the TRM calculation in its TRMID. WACM used a single TRM calculation for all three time periods. Further, the TRMID did identify components of uncertainty used in establishing TRM pursuant to R1.1. The TRMID included a description of the method used to allocate TRM across Available Transfer Capability Paths pursuant to R1.2. WACM made its TRMID available to requisite parties pursuant to Requirements R3 and R5. Lastly, WACM established TRM values in accordance with the TRMID at least once every 13 months per R5. | WACM completed the following remediation activities: 1) WACM revised the TRMID to include specific language on how the TRM is calculated for each of the three time periods described in R1.3.1 through R1.3.3; 2) WACM posted the revised TRMID on WACM's OASIS website (WACM's tool for sharing information on transmission prices and product availability); and 3) WACM shared the revised TRMID with all applicable entities (internal and external).