## Public Non-CIP Feb. FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Northeast Power Coordinating Council, Inc. (NPCC) | Lake Road Generating Company, LP (Lake Road) | NCR07131 | NPCC2011007724 | VAR-002-1 | R1 | On July 22, 2011, Lake Road, as a Generator Operator, submitted a Self-Report to NPCC identifying an issue with VAR-002-1 R1. The Self-Report was submitted as a result of a NERC industry webinar that occurred on July 15, 2011 which clarified the notification obligation with respect to automatic voltage regulator (AVR) controls at generating facilities. Lake Road reported that since June 21, 2007, its three units had not been operating in automatic voltage control mode, but rather in reactive power control mode. Lake Road failed to notify the TOP that it was not operating in automatic voltage control mode, as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the AVRs were controlling reactive power, Lake Road was following the voltage schedule provided by the Transmission Operator (TOP) at all times for the duration of the issue. | To mitigate this issue, Lake Road notified the TOP on July 22, 2011 that the plant was operating in the reactive power control mode. Lake Road tested the AVRs on the automatic voltage control mode, developed an operating procedure, and trained the generating control room operators on the correct control mode and notification to the TOP. NPCC has verified the completion of all mitigation activity.
Northeast Power Coordinating Council, Inc. (NPCC) | Lake Road Generating Company, LP (Lake Road) | NCR07131 | NPCC2011007726 | VAR-002-1 | R3 | On July 22, 2011, Lake Road, as a Generator Operator, submitted a Self-Report to NPCC identifying an issue with VAR-002-1 R3. The Self-Report was submitted as a result of a NERC industry webinar that occured on July 15, 2011 which clarified the notification obligations with respect to automatic voltage regulator (AVR) controls at generating facilities. Lake Road reported that since June 21, 2007, its three units had not been operating in automatic voltage control mode, but rather in reactive power control mode. Lake Road had misinterpreted the Standard and therefore had not notified its Transmission Operator (TOP) that the AVR was operating in the mode controlling reactive power and was outside the 30-minute notification requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the AVRs were controlling reactive power, Lake Road was following the voltage schedule provided by the Transmission Operator (TOP) at all times for the duration of the issue. | To mitigate this issue, Lake Road notified the TOP on July 22, 2011 that the plant was operating in the reactive power control mode. Lake Road tested the AVRs on the automatic voltage control mode, developed an operating procedure, and trained the generating control room operators on the correct control mode and notification to the TOP. NPCC has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Chambers Cogeneration, LP (CCLP) | NCR00708 | RFC2012011449 | PRC-005-1 | R1; R1.1 | On November 13, 2012, CCLP, as a Generator Owner, self-reported an issue with PRC-005-1 R1.1. CCLP reported that its Protection System maintenance and testing program (Program) specified that instrument transformers are tested at plant commissioning and as required when problems are suspected. The Program did not include periodic maintenance and testing for these devices. During a self-assessment for compliance, CCLP determined that this method of maintenance and testing for instrument transformers does not appropriately address risk and may not be compliant with PRC-005-1. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. CCLP conducted testing on the instrument transformers at plant commissioning in October 1993. Based on recommendations from the devices’ manufacturers, CCLP had not required periodic maintenance for instrument transformers. CCLP’s Protection System uses many instrument transformers creating overlapping zones of protection, which ensures protection if a single instrument transformer should fail unexpectedly. Finally, upon performing maintenance and testing, CCLP determined the instrument transformers were operational and performed appropriately throughout the duration of the issue. | To mitigate the issue, CCLP: 1) scheduled testing of its instrument transformers; 2) completed all testing and reviewed the results; and 3) revised its Program to include a specific interval for testing instrument transformers.
ReliabilityFirst Corporation (ReliabilityFirst) | City of Cleveland, Dept. of Public Utilities, Division of Cleveland Public Power (CPP) | NCR00712 | RFC2012001309 | PRC-005-1a | R2 | On January 11, 2012, CPP, as a Transmission Owner and Distribution Provider, self-reported an issue with PRC-005-1a R2.1. CPP self-reported that, in October 2011 and November 2011, it failed to timely complete monthly substation maintenance checks for 10 substations according to its Protection System maintenance and testing program (Program). At the West 41st Street, East Industrial, Pofok, and South East substations, October 2011 checks were conducted seven days late on November 7, 2011. At the Nottingham substation, November 2011 checks were conducted five days late on December 5, 2011. At the Division and Ridge Road substations, November 2011 checks were conducted six days late on December 6, 2011. At the Collinwood and Northeast substations, November 2011 checks were conducted eight days late on December 8, 2011. At the Lake Road substation, November 2011 monthly checks were conducted nine days late on December 9, 2011. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. CPP performed all maintenance checks within 10 days of the intervals set in the Program. Upon performing maintenance and testing, CPP determined all equipment was operable and would have performed appropriately if called upon during the duration of the issue. | To mitigate the issue, CPP: 1) revised its Program procedures to require maintenance activities to be completed earlier in the month, with an option for an approved extension, to ensure that tasks are complete by month’s end even when unexpected circumstances place additional demand on operational personnel; 2) revised the Program procedures to include supervisor sign-off of completed and signed maintenance work forms and a process to request assistance for operational matters that avoids conflicts with scheduled reliability maintenance and testing; and 3) provided informal training to employees who perform the maintenance and testing to ensure they understand the procedure and policy changes.
ReliabilityFirst Corporation (ReliabilityFirst) | Duke Energy Corporation (Duke) | NCR00761 | RFC2012011204 | EOP-004-1 | R3 | On September 30, 2012, Duke, as a Balancing Authority, Generator Operator, Load Serving Entity, Transmission Operator self-reported an issue with EOP-004-1 R3 to ReliabilityFirst. On June 29, 2012, Duke experienced a customer outage that was a reportable incident pursuant to Attachment 2-EOP-004 because it affected more than 50,000 customers for at least one hour. Duke provided a copy of the preliminary written report to the U.S. Department of Energy (DOE), but Duke failed to provide a copy of the preliminary report to NERC and ReliabilityFirst. When it began to submit the final report, Duke discovered that due to a technological issue with the submittal software, it failed to submit the preliminary report to NERC and ReliabilityFirst. On July 2, 2012, Duke provided a copy of the final report to DOE, and provided a copy of both the preliminary report and final report to NERC and ReliabilityFirst. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with of EOP-004-1, R3 has the potential to affect the reliable operation of the BPS by enabling entities to incur reportable incidents of which DOE, NERC, and the Regional Entity are unaware. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. Duke timely submitted the preliminary report to DOE, and Duke submitted the final reports shortly after the reportable storm-related incident to DOE, NERC, and ReliabilityFirst. | To mitigate the issue, Duke reviewed and revised the current procedure for reporting disturbance events and reviewed procedure changes with employees responsible for reporting disturbances.
ReliabilityFirst Corporation (ReliabilityFirst) | PSEG Fossil LLC (PSEG Fossil) | NCR00893 | RFC2012009966 | PRC-005-1 | R2 | On March 21, 2012, PSEG Fossil, as a Generator Owner, self-reported an issue with PRC-005-1 R2 to ReliabilityFirst. PSEG Fossil relies on the local Transmission Owner, Public Service Electric & Gas Company (PSE&G) to perform maintenance and testing on its behalf for certain of its Protection System devices. During a discussion at the end of 2011 regarding the assignment of responsibility for future Protection System maintenance and testing, PSEG Fossil and PSE&G discovered that the last test record for the synchronizing breaker flash-over relay scheme associated with the Mercer Generating Station Unit No. 2 was from 2002. The flash-over relay scheme consists of two relays and a timer that operates in the event the breakers are open and there is either phase or ground current present. PSEG Fossil mistakenly believed that PSE&G was responsible for the maintenance and testing of this relay scheme. That relay had a maintenance and testing interval of five years, so PSEG Fossil failed to perform maintenance and testing on that relay scheme within the defined maintenance and testing interval. On December 27, 2011, PSEG Fossil performed maintenance and testing on the relays. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). A violation of PRC-005-1 R2 has the potential to affect the reliable operation of the BPS by allowing important Protection System devices to remain unmaintained and untested. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. PSEG Fossil has several relays that are part of the generator protection that can provide backup protection, including negative sequence relays and overcurrent relays. In addition, there are two fault detectors as part of the flashover scheme, and both must fail to lose all flashover protection. In addition, this issue affected only one relay scheme. | To mitigate the issue, PSEG Fossil: 1) performed outstanding maintenance and testing on the relays, reviewed all bulk electric system Protection System devices to ensure that all devices were within their maintenance and testing interval; 2) reviewed all Protection System devices that reside at the point of interconnection to ensure that no other Protection System devices lack clarity of ownership; and 3) completed an agreement between PSEG Fossil and PSE&G regarding maintenance and testing of relay schemes.
ReliabilityFirst Corporation (ReliabilityFirst) | PSEG Fossil LLC (PSEG Fossil) | NCR00893 | RFC2012010420 | VAR-002-1.1b | R3 | On May 29, 2012, PSEG Fossil, as a Generator Operator self-reported an issue with VAR-002-1.1b R3 to ReliabilityFirst. On March 22, 2012, PSEG Fossil notified the Transmission Operator (TOP) that it would start a 628 MW generating unit’s automatic voltage regulator (AVR) at the Bergen Generating Station in manual mode. When PSEG Fossil reset the AVR to automatic voltage control mode, however, PSEG Fossil failed to notify the TOP of this status change within 30 minutes. PSEG Fossil notified the TOP one hour after the status change, 30 minutes beyond the requisite notification period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Due to this failure to notify, the Balancing Authority remained unaware that the PSEG Fossil unit was ready for dispatch from minimum output levels, so for the 30 minute duration, the unit remained at minimum output level. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. PSEG Fossil has a defined procedure in place directing notification of the TOP that the operator failed to follow in this instance, demonstrating that this issue was an isolated occurrence. In addition, the operator notified the Transmission Owner, and PSEG Fossil notified the TOP 30 minutes after it was required to do so. | To mitigate the issue, PSEG Fossil: 1) reinforced the requirement of communicating all AVR changes to the generation desk with the station personnel involved in this incident; 2) disciplined the operator with a verbal reminder, which is the first level of discipline for the employee; and 3) gave the senior operations supervisor an adverse note in the leadership performance record.
ReliabilityFirst Corporation (ReliabilityFirst) | Triton Power Michigan, LLC (Triton Power) | NCR11174 | RFC2012010612 | PRC-005-1a | R1 | From April 30, 2012 to May 11, 2012, ReliabilityFirst conducted a Compliance Audit of Triton Power, as the Generator Owner for Jackson Power Company LLC. During the Compliance Audit, although Triton Power provided ReliabilityFirst with the Protection System maintenance and testing program (Program) revised on March 12, 2012, ReliabilityFirst did not review the Program. Triton Power had revised the Program after ReliabilityFirst sent a 90 day audit notification to Triton Power. During the Compliance Audit, ReliabilityFirst determined Triton Power did not include in its Program a basis or interval for its DC control circuitry and did not include a basis for its five-year interval for nickel cadmium batteries pursuant to PRC-005-1a R1.1. Additionally, ReliabilityFirst determined that Triton Power did not include in its Program a summary of maintenance and testing procedures for relays, voltage sensing devices, station batteries, and DC control circuitry pursuant to PRC-005-1a R1.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that the issue was a documentation error. During the Compliance Audit, Triton Power provided ReliabilityFirst with evidence demonstrating Triton Power performed maintenance and testing on its Protection System devices within defined intervals during the duration of the issue. Specifically, Triton Power was able to provide the last date of maintenance and testing for each Protection System device as requested by ReliabilityFirst. Additionally, Triton Power had documented maintenance and testing procedures but did not have those procedures summarized in its Program, as required. | To mitigate the issue, Triton Power revised its Program to include maintenance and testing intervals and their basis, as well as summaries of maintenance and testing procedures for all its Protection System devices.
ReliabilityFirst Corporation (ReliabilityFirst) | Triton Power Michigan, LLC (Triton) | NCR11174 | RFC2012009965 | PRC-005-1a | R2; R2.1 | On February 14, 2012, Triton Power, as the Generator Owner for Jackson Power Company LLC, self-reported an issue with PRC-005-1 R2.1. Triton Power failed to perform maintenance and testing on two current differential relays (the Relays) within the five-year interval included in its Protection System maintenance and testing program (Program). The Relays protect transmission lines leaving the Triton Power facility. Triton Power believed its Transmission Owner (TO) performed maintenance and testing on the relays in connection with identical relays at the TO’s end of the transmission lines. Upon discovering that the TO was not responsible for performing maintenance and testing on the Relays, Triton Power determined it had not performed the maintenance and testing on the Relays within the required interval. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. Triton Power’s TO performed maintenance and testing within its interval on an identical set of relays at its substation. These identical relays have the ability to separate the Triton Power facility from the BPS. Additionally, Triton Power has redundant primary trip relays and back-up trip relays protecting its facility which Triton Power tested within its Program interval. Finally, upon performing maintenance and testing, Triton Power determined that the Relays would have performed appropriately if called upon during the duration of the issue. | To mitigate the issue, on February 14, 2012, Triton Power added the Relays to its tracking spreadsheet and conducted maintenance and testing of the Relays by February 28, 2012.
ReliabilityFirst Corporation (ReliabilityFirst) | Triton Power Michigan, LLC (Triton Power) | NCR11174 | RFC2012010614 | FAC-009-1 | R1 | During the Compliance Audit, conducted from April 30, 2012 to May 11, 2012, ReliabilityFirst determined that Triton Power, as a Generator Owner, had an issue with FAC-009-1 R1. Triton Power did not determine ratings for six transmission conductors, the collector bus, and an underground cable. Because Triton did not determine ratings for these devices, the lack of ratings was not consistent with Triton’s Facility Ratings Methodology pursuant to FAC-009-1 R1. ReliabilityFirst initially determined this issue actually related to an issue with FAC-008-1 R1. Subsequently, ReliabilityFirst determined the appropriate Reliability Standard was not FAC-008-1 R1, but rather FAC-009-1 R1. ReliabilityFirst dismissed the tracking number associated with the issue with FAC-008-1 R1 (RFC201201613) and incorporated the facts of the issue with FAC-008-1 R1 as an issue with FAC-009-1 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that the Triton Power facility was designed so that none of its generators could exceed the limitations of its associated electrical equipment. Triton Power’s electrical equipment was designed with sufficient capacity to accommodate all the generators simultaneously operating at maximum output. Specifically, Triton Power cannot exceed the limitations of any of its electrical equipment since the electrical equipment was designed with sufficient capacity to accommodate the maximum output. | To mitigate the issue, Triton Power revised its Facility Ratings Methodology to include the missing components and also revised its overall Facility Ratings to reflect the most limiting element at the time all generation is leaving the facility.
ReliabilityFirst Corporation (ReliabilityFirst) | Wolverine Power Supply Cooperative, Inc. (Wolverine) | NCR00954 | RFC2012010407 | EOP-008-0 | R1; R1.3 | On May 16, 2012, ReliabilityFirst conducted a Compliance Audit of Wolverine. ReliabilityFirst determined that Wolverine, as a Transmission Operator, had an issue with EOP-008-0 R1.3. Specifically, Wolverine’s contingency plan document, Back-up Control Center Implementation Plan, revision 6, dated December 30, 2011, failed to address the monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events for loss of control center functionality. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). An issue with EOP-008-0 R1.3 has the potential to affect the reliable operation of the BPS by enabling a registered entity to have a deficient contingency plan in the event its control center becomes inoperable. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. Wolverine has a small transmission footprint with a single, looped 138 kV interconnection and does not have any critical transmission facilities. In addition, although Wolverine failed to specifically address each required element in EOP-008-0 R1.3, some of those elements were not applicable, and all others were indirectly addressed by an instruction in the Back-up Control Center Implementation Plan to validate that certain relays are working properly. As a result, the issue was documentary in nature and not reflective of a lack of contingency planning. | To mitigate the issue, Wolverine updated its Back-up Control Center Implementation Plan to specifically address each item in R1.3 and validated those changes with an operational run at its back-up control center.
Southwest Power Pool Regional Entity | Oklahoma Municipal Power Authority (OMPA) | NCR04108 | SPP2012011463 | PRC-008-0 | R2; R2.1, R2.2 | On November 30, 2012, OMPA, as a Distribution Provider, self-reported an issue with PRC-008-0 R2. Specifically, OMPA failed to test 7 of its 42 (16.67%) Under Frequency Load Shedding (UFLS) relays within the three-year interval defined in OMPA’s PRC-008-0 R1 procedure. Of the seven relays that weren’t tested within interval, the five relays located at Ponca City were not tested within the three-year interval due to a scheduling error by OMPA’s testing consultants. The one relay located at Kingfisher was not tested because of the amount of load on the substation at the time OMPA was testing, precluded removing the UFLS relay from service. The one relay at OMPA’s Pawhuska substation had not been tested because it had been removed from service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Only 16.67% of the UFLS relays were tested out of OMPA’s defined testing interval. Of the seven, the five relays located at Ponca City were tested less than one month past the three-year interval. The other two relays were tested within a year of the due date. Furthermore, OMPA’s three-year interval for its UFLS relays is conservative because the NERC Technical Reference document recommends an interval of 10 years for testing UVLS or UFLS relays. Finally, the seven relays, combined, shed only 35.5 MW of OMPA’s peak load of 736 MW and had frequency setpoints spread across the three frequency load shed points (59.3 Hz, 59.0 Hz, and 58.7 Hz). | OMPA tested the seven relays it had failed to test within the defined three-year interval, the five relays located at Ponca City were tested in January 2012, and the relay at Kingfisher was tested in November 2012. OMPA installed a relay, which had been tested on November 21, 2011, at Pawhuska on December 18, 2012. OMPA had tested these relays one year prior to installation. Additionally, after OMPA tested the Kingfisher relay, it replaced it with a spare relay, which had been tested on December 7, 2011. OMPA also updated its Protection System Maintenance Program (PSMP) and its NERC Procedure PRC-008 to change testing intervals from three years to six years to prevent reoccurrence. SPP RE verified completion of the mitigating activities.
Texas Reliability Entity, Inc (Texas RE) | EDF Trading North America, LLC (EDF Trading) | NCR00551 | TRE2012009735 | VAR-002-1.1b | R3 | On February 13, 2012, EDF Trading, as a Generator Operator, self-reported an issue with VAR-002-1.1b R3. EDT Trading stated that on February 1, 2012, a unit at the Altura Cogen Facility was out of automatic voltage control from approximately 21:34 p.m. to approximately 23:19 p.m. This was not reported to the Transmission Operator (TOP) within 30 minutes of the status change, as required by this Standard. After the warm-up of the unit, the plant board operator commenced ramping-up the unit at approximately 21:34 p.m., which is also when the operator observed unusual MW and MVAR flows. Immediately afterwards, the plant board operator contacted the on-call electrician to assess the situation. While the troubleshooting did not reveal any equipment defects, at about 23:18 p.m., it was discovered that the Voltage Regulator had shifted to manual. At that time, the Unit received a “Master Reset,” which returned the Voltage Regulator to automatic. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was corrected within one hour and 45 minutes. The incident occurred during a routine start-up of the unit that was providing 55 MW of power at the time. Also, the unit was still ramping-up and was not in Automatic Generation Control (AGC). Therefore, the unit had not been released to the Electric Reliability Council of Texas (ERCOT) economic dispatch control when the incident occurred. | EDF Trading has provided training to all on-site operators to monitor and detect changes in the status or capability of the Voltage Regulator, and updated the Emergency Operating Procedure to include these steps. The steps are identified as "immediate actions" when indications for possible Voltage Control issues appear. Texas RE has verified that the mitigation activities are complete.
Western Electricity Coordinating Council (WECC) | Colorado Energy Management - MPC (COMPC) | NCR10378 | WECC2012011383 | VAR-002-1.1b | R3 | On November 9, 2012 and January 4, 2013, COMPC, as a Generator Operator, submitted Self-Reports citing issues with VAR-002-1.1b R3 and VAR-501-WECC-1 R1. According to the Self-Reports, on October 26, 2012, COMPC began a startup of its Gas Turbine 12. Upon startup, COMPC employees mistakenly informed its Transmission Operator (TOP) that the Power System Stabilizer (PSS) for Gas Turbine 12 was in service and active when, in actuality, the PSS had changed to manual mode and was inactive. After the unit had been online approximately eight hours, COMPC realized that the PSS was in manual mode and was not active or in service. COMPC reported that it switched the PSS to automatic mode and alerted its TOP of the status change as soon as it discovered that the PSS was in manual mode. COMPC reported, however, that it did not report the status change of the PSS to its TOP within 30 minutes of the change as required by VAR-002-1.1b R3.1. Furthermore, COMPC stated that as a result of its PSS being offline on October 26, 2012, the PSS was not in service for at least 98% of all operating hours in the fourth quarter of 2012. Specifically, COMPC noted that for the fourth quarter of 2012 the PSS should have been in service for 244.7 hours but was actually in service 235.9 hours or 96.4% of all operating hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, the risks to the reliability of the BPS were minimized by COMPC’s compensating measures. During the duration of the issue, COMPC maintained its TOP’s established voltage schedule. Additionally, the automatic voltage regulator attached to Gas Turbine 12 was in automatic mode and would have reacted appropriately if a change in voltage would have occurred. Furthermore, COMPC’s other turbine units were equipped with an automatic PSS; these devices were available to respond in the appropriate manner and would have operated to prevent any damaging consequences that could have resulted from any increased voltage levels or reactive flows. Moreover, COMPC’s internal procedures ensured that once the issue was discovered the TOP was immediately notified of the change and duration of the status change. Finally, COMPC serves only as a peaking plant at the direction of its TOP, thus if anything were to occur at the plant it would have minimal impact on the service of the TOP. | To mitigate this issue, COMPC: 1) retrained its employees on the importance and requirements of VAR-002-1.1b R3, specifically focusing on the requirement to report status changes within thirty minutes; and 2) reemphasized the procedures for handling and reporting status changes as required by VAR-002-1.1b. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Colorado Energy Management - MPC (COMPC) | NCR10378 | WECC2013011658 | VAR-501-WECC-1 | R1 | On November 9, 2012 and January 4, 2013, COMPC, as a Generator Operator, submitted two Self-Reports citing issues with VAR-002-1.1b R3 and VAR-501-WECC-1 R1. According to the Self-Reports, on October 26, 2012, COMPC began a startup of its Gas Turbine 12. Upon startup, COMPC employees mistakenly informed its Transmission Operator (TOP) that the Power System Stabilizer (PSS) for Gas Turbine 12 was in service and active when, in actuality, the PSS had changed to manual mode and was inactive. After the unit had been online approximately eight hours, COMPC realized that the PSS was in manual mode and was not active or in service. COMPC reported that it switched the PSS to automatic mode and alerted its TOP of the status change as soon as it discovered that the PSS was in manual mode. COMPC reported, however, that it did not report the status change of the PSS to its TOP within 30 minutes of the change as required by VAR-002-1.1b R3.1. Furthermore, COMPC stated that as a result of its PSS being offline on October 26, 2012, the PSS was not in service for at least 98% of all operating hours in the fourth quarter of 2012. Specifically, COMPC noted that for the fourth quarter of 2012 the PSS should have been in service for 244.7 hours but was actually in service 235.9 hours or 96.4% of all operating hours. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, the potential risks to the BPS were minimized by COMPC’s compensating measures. During the duration of the issue, COMPC maintained its TOP’s established voltage schedule. Additionally, the automatic voltage regulator attached to Gas Turbine 12 was in automatic mode and would have reacted appropriately if a change in voltage would have occurred. Furthermore, COMPC’s other turbine units were equipped with an automatic PSS; these devices were available to respond in the appropriate manner and would have operated to prevent any damaging consequences that could have resulted from any increased voltage levels or reactive flows. Moreover, COMPC’s internal procedures ensured that once the issue was discovered the TOP was immediately notified of the change and duration of the status change. Finally, COMPC serves only as a peaking plant at the direction of its TOP, thus if anything were to occur at the plant it would have minimal impact on the service of the TOP. | To mitigate this issue, COMPC: 1) retrained its employees on the importance and requirements of VAR-002-1.1b R3, specifically focusing on the requirement to report status changes within thirty minutes; and 2) reemphasized the procedures for handling and reporting status changes as required by VAR-002-1.1b. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | El Paso Electric Company (EPE) | NCR05140 | WECC2012009553 | BAL-002-0 | R4 | From December 5, 2011, WECC conducted a Compliance Audit of EPE. BAL-002-0 R4 was not included in the NERC 2011 Compliance Monitoring and Enforcement Program (CMEP) Implementation Plan of Actively Monitored Standards; therefore it was not in the original scope of the Audit. During the course of the Audit however, the audit team’s evaluations of EPE, as a Balancing Authority, resulted in the discovery of a possible Disturbance Control Performance issue. On June 18, 2010, a reportable disturbance occurred and EPE failed to activate the contingency reserves of the Southwest Reserve Sharing Group (SRSG) making EPE responsible for disturbance recovery for this event. Specifically, EPE did not recover its Area Control Error (ACE) until 22 minutes after the disturbance was issued. This disturbance took EPE seven minutes beyond the required Disturbance Recovery Period of 15 minutes to return its ACE to zero. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The event addressed herein represents an isolated case of EPE recovering its ACE seven minutes late. This resulted in EPE's Disturbance Control Standard (DCS) for the second quarter of 2010 being less than 100% because it had failed to recover from a single DCS reportable event within the allowable timeframe. Although EPE failed to recover its ACE within the 15 minute time limit, EPE only lost 101 MW of generating capability over a period of seven minutes. In addition, EPE did not experience an overload nor did the tie lines experience any voltage issues during the delay. Despite the recovery delay, the Reserve Sharing Group met the DCS requirement for more than 90% of the reportable disturbances. | To mitigate this issue, EPE: 1) EPE recovered its ACE 22 minutes from the initiation of the disturbance; and 2) EPE engaged in discussions with appropriate parties, including its reserve sharing group and the operator of the unit that tripped. The discussions between EPE and unit operator centered around the conduct of the operator on duty that day, and the discussions between EPE and the reserve sharing group administrator centered around the reserve sharing group Participation Agreement and its associated operating procedures governing disturbance reporting.
Western Electricity Coordinating Council (WECC) | PacifiCorp (PAC) | NCR05304 | WECC2012011291 | PRC-004-WECC-1 | R1 | On October 25, 2012, PAC, as a Transmission Owner, submitted a Self-Report citing an issue with PRC-004-WECC-1 R1. PAC disclosed that on three occasions it failed to analyze relay operations within 20 business days as required under R1.2. PAC disclosed that on July 23, 2012, two relays tripped on the Dillon Salmon Big Grassy 161 kV, WECC Path 18. PAC also disclosed that on July 28, 2012, there was another relay trip on the same line. PAC System Operators reviewed all three relay trips within 24 hours and determined that no misoperation occurred. System protection personnel did not review the three operations within 20 business days per R1.2. Rather, PAC system protection personnel analyzed the three operations on September 4, 2012. Operations that occurred on July 23, 2012, were reviewed after 31 business days. The operation on July 28, 2012, was reviewed after a lapse of 27 business days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by PAC's issue is, limited. Within 24 hours, PAC operators detected the relay trips and determined that there had been no misoperation. Further, protection system personnel did quickly analyze relay operations. Personnel determined there was no malfunction or equipment damage and that the relays had operated normally. This analysis, although late occurred seven to eleven days beyond the 20 day timeline described in R1.2. | To mitigate this issue, PAC: 1) analyzed the three relay operations; and 2) provided additional training to operational personnel regarding the proper response to relay operations including, but not limited to what parties are to be notified as well as tracking requirements. WECC has verified the completion of all mitigation activity.