## Public Non-CIP March FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council, Inc. (FRCC) | Covanta Pasco Inc. (COVPA) | NCR00018 | FRCC2012010028 | PRC-005-1 | R1; R1.2 | During the April 2012 FRCC Compliance Audit, FRCC determined that COVPA, as a Generator Owner, had an issue with PRC-005-1 R1. COVPA's generation Protection System maintenance and testing program failed to have a summary of maintenance and testing procedures for associated communication systems while owning one pilot wire relay, as demonstrated on its one-line diagram. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Operators performed rounds daily and would have noticed and addressed any alarms from the relay in the relay panel. The pilot wire relay was operated in 2008 and 2010 and found to be functional. In addition, the facility at issue is a small generator (23 MW) and accounts for less than 1% of regional generation. | To mitigate this issue, COVPA revised its Protection System procedure to include a summary of the procedure for maintenance and testing on associated communication systems, including pilot wire schemes. This document includes communication and coordination with all relevant entities.
Florida Reliability Coordinating Council, Inc. (FRCC) | Covanta Pasco Inc. (COVPA) | NCR00018 | FRCC2012010029 | PRC-005-1 | R2 | During the April 2012 FRCC Compliance Audit, FRCC determined that COVPA, as a Generator Owner, had an issue with PRC-005-1 R2. There was no evidence that COVPA's pilot wire relay was tested prior to November 8, 2011. Thus, COVPA failed to provide all of the documentation of its generation Protection System maintenance and testing program required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, only one out of 39 relays was not tested. All other relays were tested within the defined intervals. When tested, the relay at issue was found to be fully functional and passed testing. In addition, the pilot wire relay operated in 2008 and 2010 and was found to be functional. The facility is a small generator (23 MW) and accounts for less than 1% of regional generation. | To mitigate this issue, COVPA tested the pilot wire relay at issue and when tested, it passed testing. In addition, regular testing is now in place.
Florida Reliability Coordinating Council, Inc. (FRCC) | Florida Municipal Power Agency (FMPA) | NCR00022 | FRCC2012010610 | MOD-012-0 | R1 | On June 25, 2012, FMPA submitted a Self-Report to FRCC that, as a Generator Owner and Resource Planner, it had an issue with MOD-012-0 R1. During an internal review, FMPA determined that planned resource models for the power system stabilizers (PSSs) for two generating units, Cane Island #4 and Treasure Coast, were inadvertently not included with the models sent to FRCC, as required by the FRCC planning procedure in the FRCC Handbook since November 2005. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The model data supplied, with the PSSs' data models inadvertently not included, resulted in model data that, in its totality, was more conservative than a model data set with the PSSs included. As the name PSS implies, modeling the PSSs would have resulted in more stable results; therefore, by not modeling them, the results of stability analyses were more conservative in planning simulations. Specifically, although the model of the system would have had more dampening equipment to prevent instability if the PSSs had been included with the models sent to FRCC, there were no operating limits established in the areas where the units are. Therefore, even if the PSSs had been included, there still would have been no change to system operating limits. | To mitigate this issue, FMPA: 1) Determined which generating units have operating PSS units; 2) Determined whether the PSS units identified in milestone #1 are modeled; 3) Modeled any PSS units that were incorrect or were not currently in the model; 4) Provided corrected model data to others as required by MOD-012 R2; and 5) Instituted a quality control process for modeling data.
ReliabilityFirst Corporation (ReliabilityFirst) | Public Service Electric & Gas Company (PSE&G) | NCR00896 | RFC2012011210 | PRC-005-1b | R2 | On September 28, 2012, PSE&G, as a Transmission Owner, self-reported an issue with PRC-005-1b R2 to ReliabilityFirst. During an extensive internal review of all of PSE&G’s Protection System maintenance and testing activities, where PSE&G reviewed test records for approximately 4,750 Protection System schemes, PSE&G discovered two maintenance and testing gaps. First, PSE&G discovered that it failed to perform maintenance and testing on one of its approximately 4,650 relays. The relay, a breaker failure relay, has a defined maintenance and testing interval of four years with maintenance and testing to be completed during the calendar year it is due. This relay is located at PSE&G’s 230 kV Bergen switching station. PSE&G committed a manual entry error in its work management system and as a result the maintenance and testing activity initiating maintenance on this relay appeared in the maintenance queue one year later than required. As a result, PSE&G should have performed maintenance and testing on this relay by January 1, 2012, but instead completed maintenance and testing on June 13, 2012 after discovering this error. Second, PSE&G discovered that it failed to perform maintenance and testing on one of its 724 direct current control circuits within the defined interval of four years with maintenance and testing to be completed during the calendar year it is due. The circuit is part of the auto ground relay scheme for a phase angle regulator located at PSE&G’s 230 kV Waldwick switching station. PSE&G did not complete the maintenance and testing on the circuit on May 29, 2009, the last testing date. PSE&G completed all maintenance and testing activities except for a closing test to the auto ground switch. PSE&G did not complete this test because the individual responsible for scheduling the maintenance and testing did not realize that the closing test required an outage to be scheduled in advance. PSE&G discovered the error on August 1, 2012 during an extensive internal review. PSE&G should have performed maintenance and testing on this circuit on May 29, 2009, but instead completed maintenance and testing on August 6, 2012 after discovering this error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Regarding the relay, a failure of the breaker failure relay normally would not result in a substantial impact to the BPS because the breaker failure relay is designed to sense a failure of a breaker to open during a fault event. In the event that the breaker did not open and the breaker failure relay did not operate, there are step-distance relays in adjoining substations that would operate in a short time (less than a second) to isolate the fault. In addition, PSE&G completed the maintenance and testing only six months after it was due and discovered no abnormalities. Regarding the circuit, the primary protective system for the phase angle regulator was in place to protect the BPS. The circuit is part of the auto ground relay scheme, which is a backup system for the rest of the transformer differential protection system. PSE&G performed maintenance and testing on the primary scheme within the defined intervals. In addition, the automatic ground switch has a neon light indicating that it is operational, and PSE&G inspects the light on a weekly basis. There was no indication that this was compromised in any way, and when PSE&G performed maintenance and testing, it discovered no abnormalities. | To mitigate this issue, PSE&G: 1) created a review process to ensure the accuracy of the final entry into the maintenance and testing system; 2) added a NERC compliance relay test engineer at each of its four division headquarters to review current orders against the database of previously completed orders; and 3) specified in the test engineers’ job function documentation that they are to update Protection System review procedures by requiring division relay supervisors to complete the maintenance review of all test records no later than two weeks from the maintenance completion date. The relay test engineer located at each division headquarters now assists with the review process to ensure that all documents are reviewed and all tests are performed.
ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE Electric) | NCR00753 | RFC2012011203 | VAR-002-1.1b | R2 | On October 1, 2012, DTE Electric, as a Generator Operator (GOP), self-reported an issue with VAR-002-1.1b R2 to ReliabilityFirst. On October 1, 2012, DTE Electric verbally informed ReliabilityFirst of this issue, and on October 5, 2012, DTE Electric submitted a written Self-Report to ReliabilityFirst, DTE Electric is the GOP for the Gratiot Wind facility, a 212.4 MW wind generation facility. Invenergy owns and is registered as the Generator Owner (GO) of Gratiot County Wind, a 110.4 MW generating facility. DTE Electric owns and is registered as the GO of Gratiot Wind Park, a 102.4 MW generating facility. DTE Electric is registered as the GOP of the entire facility, with a total generating capacity of 212.4 MW. DTE Electric has delegated several specific GOP responsibilities to Invenergy, including the duty to notify the Transmission Operator (TOP) of status changes on the Automatic Voltage Regulator. On May 4, 2012, DTE Electric contracted with EDF Renewable Energy to operate and maintain the DTE Electric-owned Gratiot Wind Park. The DTE Electric-owned portion of the facility began commercial operation on January 23, 2012, and the Invenergy-owned portion of the facility began commercial operation on May 16, 2012. From January 23, 2012 through September 9, 2012, there were numerous instances when the actual generator bus voltage at the Facility exceeded the voltage schedule limit provided by the Transmission Operator (TOP). Many of these instances occurred when generation was at or near zero, and several other instances occurred during the early months of operation. In fact, during the first two months of operation of Gratiot Wind Park from January 23, 2012 through March 3, 2012, DTE Electric and the TOP provided a temporary adjustment to the high operating limit due to the voltage excursions. This operating limit adjustment did not qualify as an exemption to DTE Electric’s voltage schedule because it applied only to the Facility’s operating limits and did not modify the applicable voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DTE Electric requested and received a revised voltage schedule for the facility. From January 23, 2012 through March 3, 2012, there were several instances when DTE Electric would have been operating outside the revised voltage schedule, but the TOP had provided a temporary operating adjustment within which DTE Electric operated. After March 3, 2012, there was only one occurrence where the voltage level would have exceeded the revised voltage schedule, and the excursion was less than 1 kV when the generation output was only 10.9 MW. | To mitigate this issue, DTE Electric: 1) requested a revised voltage schedule from the TOP; and 2) requested that the voltage schedule include an exemption from compliance with the schedule when actual generation output is at or near zero. In addition, Invenergy created a voltage alarm for voltage readings, updated its procedure to reflect the new voltage schedule, and required notifications when voltage exceeds upper or lower control limits.
ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE Electric) | NCR00753 | RFC2012011574 | VAR-002-1.1b | R3 | On November 20, 2012, DTE Electric, as a Generator Operator (GOP), self-reported an issue with VAR-002-1.1b R3 to ReliabilityFirst. On November 20, 2012, DTE Electric verbally informed ReliabilityFirst of this issue, and on November 27, 2012, DTE Electric submitted a written Self-Report to ReliabilityFirst. DTE Electric is the GOP for the Gratiot Wind facility, a 212.4 MW wind generation facility. Invenergy owns and is registered as the Generator Owner (GO) of Gratiot County Wind, a 110.4 MW generating facility. DTE Electric owns and is registered as the GO of Gratiot Wind Park, a 102.4 MW generating facility. DTE Electric is registered as the GOP of the entire facility, with a total generating capacity of 212.4 MW. DTE Electric has delegated several specific GOP responsibilities to Invenergy, including the duty to notify the Transmission Operator (TOP) of status changes on the Automatic Voltage Regulator (AVR). On May 4, 2012, DTE Electric contracted with EDF Renewable Energy to operate and maintain the DTE Electric-owned Gratiot Wind Park. The DTE Electric-owned portion of the facility began commercial operation on January 23, 2012, and the Invenergy-owned portion of the facility began commercial operation on May 16, 2012. Pursuant to an agreement between DTE Electric and EDF Renewable Energy, it is EDF Renewable Energy’s responsibility to monitor AVR status for Gratiot Wind Park and report status changes to Invenergy, and pursuant to an agreement between DTE Electric and Invenergy, it is Invenergy’s responsibility to provide status change notifications to the TOP. On July 10, 2012, the wind farm management system on the DTE Electric-owned Gratiot Wind Park failed to operate as a result of a failed power quality meter. EDF Renewable Energy did not discover the failure until July 23, 2012. EDF Renewable Energy replaced the power quality meter on July 30, 2012, and the AVR resumed normal operation. DTE Electric subsequently determined that during the time period that the wind farm management system failed to operate, the AVR failed to operate as well. As a result, Invenergy, and therefore DTE Electric, failed to notify the TOP of a status change on the AVR within 30 minutes, as required by VAR-002-1.1b R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were four occasions during the time period of the issue where the facility was operating outside the voltage schedule, addressed in the issue VAR-002-1.1b R2 (RFC2012011203). The voltage did not exceed the schedule by more than 0.4 kV during this time, and the voltage was within the voltage schedule subsequently provided by the TOP pursuant to RFC2012011203 at all times. | To mitigate this issue, DTE Electric: 1) installed AVR alarming capability; and 2) required EDF Renewable Energy to revise the AVR notification procedure for the facility.
SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2012010001 | MOD-030-2 | R5 | On April 2, 2012, Duke submitted a Self-Report to SERC stating that, as a Transmission Service Provider (TSP), it had an issue with MOD-030-2 R5.2 because it failed to include some of the expected generation and transmission outage data when calculating the Available Flowgate Capability (AFC). SERC requested and reviewed additional information in order to complete its assessment. SERC determined that Duke, as a Transmission Operator (TOP), was not uploading some of its generation and transmission outage data to the OATI System Data Exchange (SDX) because of a software coding error in the program used to upload the data. Duke, as a TSP, uses the data automatically uploaded to the SDX for its AFC calculations. SERC determined that, from September 28, 2011 at 9:45 a.m. to October 4, 2011 at 11:00 a.m., Duke, as a TSP, was using a transmission model provided by Duke, as a TOP, that did not include new generation and transmission outage data because of the software coding error in the program used to upload the data. During this period, the data posted to the SDX consisted of the correct values for daily and hourly net interchange, operating reserve, and load forecast, all of which Duke considers the Load Data. The generation and transmission outage data was not being uploaded, however, due to the software coding error. Instead, the program incorrectly sent a message that reported a successful transfer of data before all the data, including outage data, had been uploaded. On October 4, 2011, a Duke analyst discovered the failure to upload outage data during a validation of AFC calculations. While running the next-day study, the analyst found that the results were different than what was expected. In particular, the analyst knew there was an outage but could not find that information in the SDX. Duke immediately notified support personnel and mitigated the issue the same day. Duke subsequently reviewed its available SDX log files and verified that this was the only instance of non-compliance with this Requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were no generation or transmission outages that would have significantly changed Duke’s AFC calculations during the time the outage data was not uploaded or would have contributed to a System Operating Limit or Interconnection Reliability Operating Limit violation. Duke accounted for the generation and transmission outage data already in effect before the outage data was not uploaded in next day studies. In addition, Duke would have addressed any generation or transmission outage data that was not included in the SDX data during the time the outage data was not uploaded as part of its next-day system study conference call with affected Balancing Authorities and TOPs, which uses data from a source other than the SDX output. Duke continued to account for and study generation and transmission outages during the time the outage data was not uploaded in other outage study processes that did not rely on the SDX output. | To mitigate this issue, Duke: 1) corrected the error in the program used to upload the data; 2) implemented three additional manual steps to assist with the prevention of reoccurrence; 3) modified the job aid for the next day study to add additional steps which specify what data should be verified; 4) added additional columns to the next day study procedure to capture the initials of the engineer performing the study and the time the engineer performed the SDX review; and 5) educated the system operations engineering group that utilizes the next day study job aid on the changes to the job aid. Training information was captured for those receiving training and follow-up occurred for those not present at the initial training. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCE&G) | NCR00915 | SERC2012010790 | PRC-005-1 | R2 | On June 1, 2012, SCE&G submitted a Self-Certification to SERC stating that, as a Transmission Owner (TO), Generator Owner (GO) and Distribution Provider (DP), it had an issue with PRC-005-1a R2 because several Protection System devices were not tested in accordance with its maintenance and testing procedure. SERC requested additional information in order to complete its assessment. On September 7, 2012, SCE&G submitted a spreadsheet of Protection System devices for the TO, the DP and the GO functions. On November 7, 2012, SCE&G submitted an updated spreadsheet of Protection System devices for the TO and the GO functions in order to clarify some questions regarding the original submission. SERC reviewed the spreadsheets, the defined maintenance and testing intervals, the most recent test date, and the previous test date for each device. SERC verified the assigned intervals based on a review of SCE&G’s PRC-005 maintenance and testing procedures. SERC determined that SCE&G could not provide records of the last maintenance or testing date for 8 out of 3,086 relays (0.26%), 2 out of 167 associated communication systems (1.20%), 8 out of 3,078 PT/CTs (0.26%) and 17 out of 3,086 DC control circuitry (0.55%). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCE&G was able to provide evidence of maintenance and testing records for 99% of its Protection System devices. The DC control circuitry for the generator is associated with the underfrequency trip of the generator, which protects the primary mover of the generator, not the networked transmission system. If the DC control circuitry had not operated as intended, only the generator would be affected. In addition, the probability of receiving a an underfrequency trip is small. The remaining DC control circuitry, relays, associated communication devices and voltage and current sensing devices were to protect two inline voltage regulators. The voltage regulators are part of a transmission line with additional and separate protective relaying at each end of the line. If the voltage regulator protection systems were to not operate when called upon to do so, the additional line protection would operate taking that segment of line out of service resulting in a local outage, while preventing a cascade. The associated communication devices are also monitored through a loss of guard frequency alarm to the Energy Management System. | To mitigate this issue, SCE&G: 1) either maintained and/or tested the Protection System devices that were identified or, if deemed appropriate by the transmission planning department, removed the Protection System devices from service. 2) obtained the dates for most recent and the previous tests on all additional Protection System devices. All of the other Protection System devices had been tested in accordance with the maintenance and testing procedure. 3) provided reinforcement training to field personnel regarding identifying protection systems and understanding the maintenance and testing activities required. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCE&G) | NCR00915 | SERC2012011170 | VAR-002-1 | R1 | On October 1, 2012, SCE&G submitted a Self-Certification to SERC stating that, as a Generator Operator, it had an issue with VAR-002-1 R1 because the automatic voltage regulator (AVR) was in VAR control mode at two plants and in power factor control mode at one plant instead of automatic voltage control mode without prior notification to the Transmission Operator (TOP). SERC requested more information in order to complete the assessment. SERC learned that SCE&G was operating its Jasper and Fairfield Pump Storage plants in VAR control mode. SERC also learned that these plants were operating in the mode that was best for system reliability based on a study performed by the Transmission Owner. However, SCE&G had no formal record that it notified the TOP that it would be operating the units in the VAR control mode prior to changing from automatic voltage control mode. SCE&G was operating its Cope plant in power factor control mode due to an operational oversight and therefore did not notify the TOP. After discovering this issue, SCE&G reviewed the AVR status of its 28 generators subject to VAR-002 and confirmed that these three plants were the only plants operating in a mode other than automatic voltage control mode. SERC also reviewed SCE&G’s compliance document for VAR-002 and determined that SCE&G has an established AVR notification procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCE&G operated its Fairfield and Jasper plants in the mode that was best for system reliability. SCE&G maintained its voltage schedules during the period of the issue, was able to respond to all changes that were required while in VAR and power factor control modes, and could respond to TOP directives. SCE&G is vertically integrated and there is regular communication between the plants and system control regarding the voltage control and VAR output of the plants. There were no known abnormal or stressed system conditions during the time of the issue. Cope has a net generating capacity of 415 MW, approximately 6.8% of SCE&G’s total generation of 6,148 MW. | To mitigate this issue, SCE&G: 1) re-trained applicable personnel on the VAR-002 requirements. 2) required plant operators to regularly check and document the status of the AVRs as part of their daily duties. 3) rechecked the labeling on the AVR controls and where needed, enhanced the labeling. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | Tennessee Valley Authority - TVAM (TVAM) | NCR01341 | SERC2012010846 | INT-004-2 | R2; R2.2 | On July 30, 2012,TVAM submitted a Self-Report to SERC stating that, as a Purchasing Selling Entity, it had an issue with INT-004-2 R2.2 because it failed to update the Dynamic Interchange Schedule tag for the next available scheduling hour for a period of four hours in which the average energy profile was less than 250 MW and in those hours the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 25 megawatt-hours (MWh). SERC requested more information to complete its assessment. SERC reviewed the Dynamic Interchange Schedules 24 hours before and after the event, including the comparison of tagged and actual Dynamic Schedules. On June 21, 2012, from the hours ending 7:00 a.m. through 10:00 a.m., TVAM did not update the dynamic tag for the estimated Cayuga Ridge wind farm generation because of inaccurate information on display screens TVAM used to monitor wind generation. A software configuration change to add the Bishop Hill wind generation facility to the Resource Market Operator (RMO) Portal led to a source code error involving a time zone conversion, which caused the wind generation monitoring screens to display incorrect data. The monitoring screens indicated that the Cayuga Ridge generation was 0 MW so the dynamic tag was adjusted to 24 MW to be within the allowed +/- 25 MW range for the next available scheduling hour. However, the actual average hourly Cayuga Ridge generation ranged from 78 to 132 MW for the four hour time span. TVAM did not revise the dynamic tag hourly for the aforementioned timeframe because the monitoring systems incorrectly indicated that the tag did not need to be adjusted. After self-reporting the June 21, 2012 incident, TVAM performed an extent of condition review on Cayuga Ridge for the period of March 21, 2012 through June 21, 2012. TVAM discovered that there were 12 additional occurrences totaling 36 hours over a three month period where TVAM failed to properly adjust the tags at Cayuga Ridge. The actual average hourly Cayuga Ridge generation during these 12 occurrences ranged from 26 to 177 MW. There were no indications that the data display issues in the June 21, 2012 incident were present during these occurrences. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. No Transmission Loading Reliefs (TLRs) were issued as a result of these events. TVAM’s failure to update the wind forecasts in the flowgate calculations could have caused no more than 1% error in proposed corrective actions for any TLRs posted during the time of the issue. | To mitigate this issue, TVAM: 1) identified and corrected the coding error which caused the incorrect wind generation data; 2) conducted an extent of condition review and summarized the findings; 3) revised the dynamic tag adjustment instruction to improve tag adjustments; 4) provided each power trader with individual training regarding the June 21, 2012 non-adjustment event, the results of the extent of condition review, and the revised Dynamic Tag Monitoring and Adjustment instructions; 5) implemented a communication protocol requiring Operations Applications personnel to notify Power Trading personnel prior to any work which might affect the RMO Portal data; and 6) provided training to Operations Applications personnel regarding the event which caused inaccurate wind generation data and the communication protocol for any work that might impact the RMO Portal. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | Owensboro, KY Municipal Utilities (OMU) | NCR01290 | SERC2012011498 | EOP-004-1 | R3 | On November 16, 2012, SERC sent OMU an initial notice of a Compliance Audit scheduled for May 20, 2013 through May 24, 2013. On December 5, 2012, OMU submitted a Self- Report to SERC stating that, as a Load Serving Entity, it had an issue with EOP-004-1 R3.1 because it failed to provide a preliminary report to the U.S. Department of Energy, NERC, and SERC after experiencing a reportable event, as required. SERC requested and reviewed additional information in order to complete its assessment. SERC learned that on May 25, 2012, an OMU unit was taken off-line due to a tube leak. OMU was unable to purchase power from the market to replace the loss of the unit because no Available Transfer Capability (ATC) was available. OMU notified its Transmission Service Provider (TSP) that no ATC was available and Unit 1 capacity would not be sufficient to cover native load. After unsuccessful attempts to resolve the impending capacity deficiency with its TSP, Balancing Authority (BA) and Reliability Coordinator (RC), OMU’s RC issued an EEA (Energy Emergency Alert) 0, EEA 1, and EEA 2 in succession. OMU lowered system voltage and made public appeals for customers to reduce use as part of the EEA 2 requirement. However, OMU did not submit an EIA-417 for the May 25, 2012 event as required by EOP-004-1 R3.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OMU maintained direct communication with its RC, BA, and neighboring Transmission Operators during the entirety of the event. OMU followed the EEA procedures. | To mitigate this issue, OMU: 1) updated its energy emergency procedure so that it refers to OMU’s disturbance reporting procedure; 2) updated its load shedding plan so that it refers to OMU’s disturbance reporting procedure; 3) updated the annual disturbance reporting training; and 4) conducted disturbance reporting training. SERC has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2012009182 | PRC-005-1 | R1 | On January 17, 2012, Lea Power Partners (LEAPP), as a Generator Owner, self-reported non-compliance with PRC-005-1 R1. LEAPP stated that the Protection System maintenance and testing program (PSMTP) it had adopted, included maintenance and testing intervals and their bases but did not describe procedures for maintaining and testing each type of Protection System device. The devices at issue included batteries, current and potential transformars, DC circuitry, and relays. This issue lasted from January 30, 2009 until December 20, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although LEAPP did not have a summary of maintenance and testing procedures within its PSMTP, it did perform testing and maintenance on its Protection System devices in a manner consistent with manufacturer/industry recommendations and within those required intervals. | LEAPP undertook a complete review of its PSMTP and developed and documented a more detailed summary of maintenance and testing procedures for each Protection System device.
Southwest Power Pool Regional Entity (SPP RE) | Piggott Light & Water (Piggott) | NCR01136 | SPP2012010675 | PRC-008-0 | R2 | On July 11, 2012, during a Compliance Audit of Piggott, as a Distribution Provider,SPP RE discovered that Piggot was noncompliant with PRC-008-0 R2. Specifically, the Audit Team found that Piggott had not updated its Under Frequency Load Shedding (UFLS) relay settings following an October 26, 2007 change to its UFLS program. The three relays identified in the amended UFLS program were not tested to verify that the relays would initiate a breaker trip at the appropriate frequencies. On October 26, 2007, Piggott amended its UFLS Relay Testing and Battery Maintenance/Inspection Program to include three distribution load shed points that would respond to an underfrequency event, i.e., three UFLS relays at the following locations: Rail Road Circuit serial number 200195, Gas Pump Circuit serial number 200194, and East Circuit serial number 200188. Piggott’s UFLS maintenance and testing program called for these three relays to be tested on a five year cycle, with a three month grace period should unforeseen circumstances result in a delay in the testing. Prior to implementation of its October 26, 2007 UFLS program, Piggott’s UFLS program called for shedding load at two points, i.e., two UFLS relays at the following locations: Main T1 Breaker serial number 200198, and Main T2 Breaker serial number 200192. Operation of these relays would cause Piggott's entire 11 MW of peak load to be shed at 59.3 Hz in response to an underfrequency event. Piggott subsequently discovered that although it had changed its UFLS program to include three distribution load points, changes were not made to the identified relays and it actually continued to operate under the program which would shed Piggott's 11 MW of load at two distribution points. On March 3, 2012, Piggott revised its relay settings to eliminate Main T1 Breaker and Main T2 Breaker loads and to include the loads identified with the aforementioned three distribution circuits. However, as of March 3, 2012, Piggott’s three aforementioned distribution circuits were set to trip below the load shed points identified in the Southwest Power Pool (SPP) underfrequency load shed plan, which allows for three stages of load shed at frequencies of 59.3, 59.0, and 58.7 Hz. Under the SPP plan, an entity sheds 10% of its load at each of the three stages, up to 30% of its load. On March 3, 2012, Piggott set the East Circuit relay to trip at a frequency of 58.5 Hz, and the Rail Road and Gas Pump relays were set to trip at a frequency of 58.0 Hz. Although, all three relays were set below the frequencies established in the SPP UFLS plan, all three would have responded in the event system frequency continued to decline. From March 3, 2012 to July 19, 2012, Piggot failed to set the appropriate tripping point for the three relays. After that, Piggot tested and set the relays at the appropriate level. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Piggott failed to change its relay settings following the program changes in 2007, the two relays that were being utilized to perform UFLS would have automatically tripped Piggott’s entire load at a frequency of 59.3 Hz, which is the first load shed point identified in the SPP UFLS plan. These two relays were armed through March 3, 2012 which is when Piggott set the three UFLS relays at issue to shed distribution load. The two relays identified with UFLS program prior to October 26, 2007 were tested within the five year interval as stated in Piggott’s documented UFLS maintenance program. Even though Piggott could not demonstrate that its three relays were set to automatically trip at the appropriate load shed points identified in the SPP underfrequency load shed plan on March 3, 2012, the East Circuit relay would have tripped at 58.5 Hz, and both the Rail Road and Gas Pump Circuits would have tripped at 58.0 Hz. Therefore, despite trip set errors, Piggot's system could have shed all required load had system frequency continued to decline. Furthermore, Piggott's UFLS program is part of an overarching UFLS plan by its Transmission Operator (TOP). This UFLS plan calls on eight municipalities for support, with Piggot being one of the smallest municipalities within this group and the eight municipalities could automatically shed load in 10% increments up to a total of 30% of their load. If operating at peak load of 11 MW, Piggott's contribution could have been to shed up to 3 MW in response to an underfrequency event. Piggott's contribution to the highest load shed frequency of 59.3 Hz could have been about 1 MW at its peak load capacity, which is a negligeble amount compared with the load that could be shed by the rest of the municipalities at 59.3 Hz. In addition, the TOP, the Southwestern Power Administration (SWPA), has a manual load shed program in place, which ensures that load is shed by the eight municipalities in response to an frequency event. Under SWPA's program, the large municipalities in the group are subject to manual load shedding first, followed by municipalities like Piggott, which have less MW of load. Finally, Piggott's failure to establish the appropriate tripping point lasted four months, thereby further reducing the risk to the BPS. | On July 19, 2012, Piggott tested its relays. The results showed: (1) Rail Road Circuit relay tested at 59.3 Hz.; (2) Gas Pump circuit relay tested at 59.0 Hz.; and (3) East Circuit relay tested at 58.7 Hz. Piggott re-wrote its UFLS program, adding a paragraph stating that "in the event that a circuit in the UFLS is changed, said relay must be tested at the frequency of the circuit it is replacing. Changes shall be made to the UFLS program, and SWPA, its TOP, must be notified by e-mail of said changes with a copy of new UFLS program.” Piggott also posted its UFLS program in its substations to make the program more visible to operators. Additionally, Piggott informed SWPA, its TOP, of its UFLS relay frequency set points and identified distribution loads to be shed, as may be required.
Southwest Power Pool Regional Entity (SPP RE) | PowerSmith Cogeneration Project, LP (PowerSmith) | NCR11119 | SPP201100654 | FAC-008-1 | R1 | On July 31, 2011, PowerSmith, as a Generator Owner, self-reported an issue of non-compliance with FAC-008-1 R1. Between April 22, 2011, PowerSmith's registration date, and December 16, 2011, PowerSmith did not have a documented methodology used for developing Facility Ratings of its generation facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although PowerSmith did not have a documented Facility Ratings Methodology (FRM), PowerSmith performed capacity tests in accordance with the Southwest Power Pool criteria and reported the results to its Transmission Operator. Further, the violation timeframe was limited to eight months and the facility's net output was 120 MW. | PowerSmith developed and implemented a FRM for its generation facility.
Southwest Power Pool Regional Entity (SPP RE) | PowerSmith Cogeneration Project, LP (PowerSmith) | NCR11119 | SPP201100655 | FAC-009-1 | R1 | On July 31, 2011, PowerSmith, as a Generator Owner, self reported an issue of non-compliance with FAC-009-1 R1. Between April 22, 2011, PowerSmith's registration date, and December 16, 2011, PowerSmith did not establish a Facility Ratings for its generating facility that were consistent with a documented Facility Ratings Methodology (FRM). PowerSmith did not have a documented FRM during this period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although PowerSmith had not established Facility Ratings consistent with a documented FRM, PowerSmith performed capacity tests in accordance with the Southwest Power Pool Criteria and reported the results to its Transmission Operator. Further, the violation timeframe was limited to eight months. | PowerSmith established Facility Ratings for its generation facilities consistent with its FRM.
Southwest Power Pool Regional Entity (SPP RE) | Western Farmers Electric Cooperative (WFEC) | NCR01160 | SPP2012011398 | FAC-008-1 | R1.2.1 | During a November 5, 2012 though November 8, 2012 Compliance Audit of WFEC, the SPP RE identified an issue of non-compliance with FAC-008-1 R1.2.1. Specifically, due to a documentation error, WFEC had omitted relay protective devices, in the scope of equipment used to determine generation Facility Ratings in its current generation Facility Ratings Methodology (FRM) (Rev. 3, dated August 20, 2012). This issue applies to WFEC's Generator Operator function. The issue period was from June 22, 2010 to November 8, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WFEC’s generation FRM (Rev. 3, dated August 20,2012) did not include relay protective devices, WFEC in fact included relay protective devices in the scope of equipment used to determine its generation Facilities’ Ratings. SPP RE determined that WFEC’s omission of relay protective devices from its generation FRM at issue was a documentation error. A prior version of WFEC’s FRM (Ver. 1, dated June 22, 2010) included relay protective devices in the scope of equipment used to determine WFEC’s Facility Ratings. | To mitigate its issue of non-compliance with FAC-008-1 R1.2.1, WFEC revised its generation FRM to include relay protective devices in the scope of equipment used to determine its generation Facility Ratings.
Texas Reliability Entity, Inc (Texas RE) | APX Power Markets, Inc. (APX) | NCR11034 | TRE2013011727 | CIP-001-1 | R1 | During a January 15, 2013 through January 17, 2013 Compliance Audit, Texas RE determined that APX as a Generator Operator (GOP), had an issue with CIP-001-1 R1. APX failed to have procedures for the recognition of sabotage events or procedures to make its staff aware of sabotage events on its facilities and multi-site sabotage affecting larger portions of the Interconnection. APX was in non-compliance with CIP-001-1 R1 from May 3, 2010, when APX was registered as a GOP, until August 10, 2010, the date APX implemented its sabotage recognition and reporting procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because APX had a formalized sabotage procedure three months after its registration date. During that time period of this issue, APX developed working drafts of the procedure. Also, during the issue period, APX did not own or directly operate any generators connected to the BPS. | APX created and implemented a sabotage and reporting procedure on August 10, 2010. APX also provided documents showing that sabotage reporting training was conducted in 2010 and 2012. Texas RE has verified the mitigation activities as complete.
Western Electricity Coordinating Council | San Diego Gas & Electric (SDGE) | NCR05377 | WECC2012011056 | PRC-005-1b | R2 | On September 14, 2012, during SDGE’s on-site Compliance Audit, WECC discovered SDGE, as a Transmission Owner, had an issue with PRC-005-1b R2 because SDGE failed to timely perform its August 12, 2012 quarterly battery inspection for one battery, less than 3% of SDGE's total battery devices. According to SDGE’s Transmission Protection System Maintenance and Testing Program, station batteries are maintained and tested quarterly with a one month tolerance period (buffer). A newly installed (installed on April 14, 2012) battery at the Encina substation was inspected 12 days late. According to SDGE’s maintenance interval and schedule, SDGE had until August 12, 2012 to perform the required maintenance; however it was not maintained and tested until August 24, 2012, which was outside the defined interval (120 days) by 12 days. Although SDGE failed to test the Encina battery device within its scheduled three month (90 day) basis with an additional 30 days to allow for scheduling conflicts, SDGE promptly recognized the failure and tested the battery on August 24, 2012 (12 days late). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SDGE has alarms installed on all battery devices’, meaning if a battery fails an alarm is automatically sent to the electric grid operations center and a response team is contacted to investigate and cure the alarm. Further, SDGE maintained and tested all other protection equipment within defined intervals. A Settlement Agreement covering a violation of PRC-005-1 R2 for SDGE was filed with FERC under NP10-2-000 on October 14, 2009. On November 13, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A NOCV covering a violation of PRC-005-1 R2 for SDGE was filed with FERC under NP10-146-000 on July 30, 2010. On August 27, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that the instant issue is appropriate for FFT treatment. The instant issue involved testing a single, newly installed battery making up less than 3% of SDGE’s total battery devices. WECC determined the instant issue involves different facts and circumstances than the prior violation filed in NP10-2-000 because the prior violation involved a management system being improperly set which resulted in a failure to test. While the prior violation filed in NP10-146-000 involved similar facts a battery bank not being maintained within defined intervals, WECC determined that the instant issue is appropriate for FFT treatment because the prior violation involved SDGE’s Protection Systems related to its Generator Owner function and was due to a preventive maintenance task in SDGE’s system being “locked” causing work orders not to be generated for the maintenance crew members. | To mitigate this issue, SDGE: 1) implemented an automatic email alert system for the battery maintenance and testing program. These alerts will enhance SDGE’s weekly maintenance reporting system by notifying responsible personnel to take corrective action before the maintenance period expires. The alert system is independent of the weekly maintenance reports used to monitor the maintenance and testing program; and 2) trained personnel responsible for the battery system inspection and maintenance program on the new Cascade automatic alerts. WECC has verified the completion of all mitigation activity.