## Public Non-CIP April FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council, Inc. (FRCC) | Kissimmee Utility Authority (KUA) | NCR00042 | FRCC2012011634 | PRC-005-1b | R2 | On December 21, 2012, KUA submitted a Self- Report stating that, as a Generator Owner, it failed to maintain its Protection System devices within the defined intervals. Specifically, relay tests for three functions of a generator microprocessor relay were due on November 10, 2012 and November 14, 2012; however, the relay technicians did not complete the necessary testing of the relay until November 29, 2012. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The tests were a maximum of 19 days late, and the units were in an outage. The relay set runs continuous self-diagnostic tests and sends a signal to the distributed control system to alarm the power plant personnel in the case of a relay failure. The relay is also checked during the daily plant operating personnel’s rounds. In addition, this relay set is backed up by another microprocessor-based relay set which provides similar redundant protective relay functions and also runs internal self-check diagnostics test reporting any abnormalities to the DCS. Furthermore, the issue only affected one relay out of 308 KUA bulk electric system relays. | To mitigate this issue, KUA: 1) tested all active functions for the affected relay, Cane Island Unit 3 CT RS1 Relay, on November 29, 2012; and 2) updated the associated PRC-005 maintenance and testing program documents to better accommodate the realities of generation outage schedules. The document 201210101 Protective Relay & DC Control Circuit Testing Schedule was updated on March 5, 2013.
Florida Reliability Coordinating Council, Inc. (FRCC) | Pinellas County Resource Recovery (PCR) | NCR00060 | FRCC2012010598 | FAC-009-1 | R1 | During a Compliance Audit conducted on June 26, 2012, FRCC determined that PCR, as a Generator Owner, had an issue with FAC-009-1 R1. PCR had insufficient documentation to demonstrate that PCR established Facility Ratings for its solely and jointly owned Facilities that are consistent with its associated Facility Ratings Methodology. Specifically, the audit team observed during an inspection of the switchyard that PCR owns tubular aluminum bus in its switchyard that was not identified in the Facility Ratings Worksheet, and therefore was not considered in the calculation of the Facility Rating as specified in its Facility Rating Methodology. In addition, the audit team observed, during inspection of the switchyard, that PCR owns two different size aluminum jumpers in its switchyard, but only identified one size jumper (1000MCM bare aluminum) in the Facility Ratings Worksheet. The audit team observed that the jumpers on either side of breaker B02 were larger than the jumpers on either side of breaker B01. PCR was unable to identify which jumpers were actually 1000MCM bare aluminum, and what size the other jumpers in the switchyard were. This demonstrated that at least one of the different size jumpers was not considered in the calculation of the Facility Rating as specified in its Facility Rating methodology. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PCR has performed various full load infrared thermographic heat scans and no hot spots were identified on the aluminum bus bar or the jumpers. In addition, neither the jumpers nor the tubular bus were limiting elements. The generator was the limiting element as designed. PCR is a small 75 MW generator that is connected to the BPS via a single radial 230 kV line and accounts for less than 1% of the regional generation. | To mitigate this issue, PCR: 1) identified the tubular aluminum bus and jumpers that were not included on the Facility Ratings Worksheet; 2) reviewed its outage schedule to confirm that cold iron outage preparations were on track and were performed on schedule in November 2012; 3) determined the ratings for the additional tubular aluminum bus and jumpers were established during the annual cold iron outage in November 2012; and 4) evaluated Facility Ratings to determine whether any change was warranted based on the Facility Ratings identified for the additional bus and jumpers, and no modification was necessary. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council, Inc. (FRCC) | Lee County Resource Recovery (LCRR) | NCR00046 | FRCC2012010533 | FAC-008-1 | R1; R1.2.1 | During a Compliance Audit conducted on June 19, 2012, FRCC determined that LCRR, as a Generator Owner, had an issue with FAC-008-1. LCRR had insufficient documentation to demonstrate that its Facility Rating Methodology included all terminal equipment within its Facilities Ratings Methodology. Specifically, the LCRR's Facility Rating Methodology did not include the 52-L2 circuit breaker for its 28 MW Unit #2 generator. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The missing component was not the most limiting element; the 28 MW Unit #2 generator was the most limiting element. LCRR is a 48 MW facility on a 138 kV radial line and was operating to manufacturer's specifications (nameplate). | To mitigate this issue, LCRR, immediately upon discovery in May 2012 of the omitted Unit #2 generation system equipment, the pertinent procedure was revised to include the omitted equipment and was approved and disseminated on June 1, 2012. FRCC has verified the completion of all mitigation activity.
Midwest Reliability Organization (MRO) | Dairyland Power Cooperative (DPC) | NCR00979 | MRO201100321 | PRC-008-0 | R2 | During a regularly scheduled Compliance Audit, conducted from March 7, 2011 through March 11, 2011, MRO discovered that DPC, as a Distribution Provider and Transmission Owner, failed to implement its Under Frequency Load Shedding (UFLS) equipment maintenance and testing program and provide UFLS maintenance and testing program results upon request as required by PRC-008-0 R2. Specifically, DPC failed to perform specific gravity tests for one station battery in 2009. The battery accounts for approximately 5.5 MW of DPC's UFLS load. DPC performed a comprehensive review of its UFLS equipment maintenance and testing records and did not identify any other issues. DPC reported that it has: 32 UFLS relays; 27 voltage and current sensing device; 27 station batteries; and 45 DC control circuits subject to PRC-008-0 R2. Of those devices, DPC failed to test one station battery, approximately 1% of its devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although DPC failed to conduct specific gravity test for one station battery, it measured individual cell and battery voltage every month and individual cell and battery total impedance each year and did not identify any issues with the battery tests that were conducted. Additionally, DPC's total load obligation was 274 MW in 2010, and it was capable of shedding 298 MW in 2010. The UFLS load tied to the station battery at issue was 5.5 MW. Therefore, DPC could have met its load obligation without the station battery at issue. | To mitigate the issue, DPC: 1) trained staff involved with UFLS substation equipment testing and maintenance; 2) corrected documented issues by completing specific gravity test at the six substations; 3) completed a comprehensive review of UFLS substations to verify that testing and maintenance was complete per DPC's UFLS maintenance and testing procedure; and 4) updated documentation to minimize probability of reoccurrence of any issues found in the comprehensive review. MRO has verified the completion of all mitigation activity.
Midwest Reliability Organization (MRO) | Great River Energy (GRE) | NCR00992 | MRO2012009814 | FAC-003-1 | R2 | On August 26, 2011, GRE, as a Transmission Owner, self-reported noncompliance with FAC-003-1 R2 because it failed to implement its annual plan for vegetation management work to ensure the reliability of the system. GRE's Transmission Vegetation Management Program (TVMP) requires aerial and ground patrols of its transmission lines. The lines are patrolled by air at a minimum of six times annually and by ground at a minimum of once every two years. During an internal review of its TVMP records, GRE discovered that it did not have evidence of bi-annual ground patrols for some of its transmission lines. Upon discovery, GRE performed a comprehensive review of its records and reported that it failed to implement an annual plan for vegetation management work for six out of 34 of its high voltage transmission lines subject to FAC-003-1. The vegetation management work was associated with ground inspections from 2007 and 2008, which required air patrol at a minimum of six times annually and ground patrol at a minimum of once every two years. Three of the transmission lines were not ground patrolled for more than two years and up to three years in a row and the ground patrol interval for the other three transmission lines was not established. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although six high voltage transmission lines subject to FAC-003-1 were not patrolled by ground per GRE’s TVMP, the lines were patrolled by air seven times between 2007 and 2008. Additionally, MRO performed a random selection review on 16 of GRE's high voltage transmission lines from 2009 to 2011 and did not identify any additional issues. Therefore the issue occurred for a short period of time from 2007 to 2008, shortly after the Standard became mandatory and enforceable. | To mitigate the issue, GRE revised its TVMP to clearly indicate how it will patrol its system. MRO has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Wisconsin Electric Power Company (Wisconsin Electric) | NCR00951 | RFC2013011663 | TOP-002-2.1b | R14 | On December 20, 2012, Wisconsin Electric, as a Generator Operator, submitted a Self-Report to ReliabilityFirst identifying an issue with TOP-002-2.1b R14. Wisconsin Electric owns Blue Sky Green Field (BSGF), a wind park with a generating capacity of 145.2 MW. BSGF consists of 88 wind turbines from which production is collected on eight distribution circuits and connected to the bulk power system (BPS) by one 34.5 kV to 345 kV step-up transformer. On December 4, 2012, at approximately 5:58 p.m., BSGF experienced a circuit failure on one of the circuits. The circuit failure caused all of the turbines to trip offline, and production dropped from 135 MW to zero. All turbines tripped, and only nine turbines automatically restarted within 15 minutes and returned to production with an output of approximately 7 MW. Wisconsin Electric was aware of the issue and dispatched a troubleshooter to the substation to address the issue. Wisconsin Electric failed to notify the Transmission Operator (TOP) and Host Balancing Authority (BA) that the capability of BSGF was limited due to tripping of the collector circuit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to the BPS was mitigated by the following factors. Both the TOP and the Host BA received five second data on the output of the park and were therefore aware of its output. Actual output of a wind generator, in addition to capability, is critical operating information due to the wind generator’s intermittent nature and inability to increase production beyond wind availability. In addition, the issue occurred for a short duration, and BSGF was unavailable overnight when demand is lower, reducing the risk of affecting BPS reliability. | To mitigate this issue, Wisconsin Electric: 1) advised relevant Power Generation, Electric System Operations, and Wholesale Energy and Fuels personnel that forced outage or derate information that affects BSGF capability other than derates due to lack of wind must be reported in compliance with TOP-002 R14. Such reporting will conform with Wisconsin Electric’s EOP-OP-001-R6 Generation Outages and derates procedure and MISO Business Practice Manual Outage Operation. 2) updated existing operating protocols to clarify that BSGF is included; and 3) performed a comprehensive review of NERC Standards applicable to BSGF to determine whether further improvements are warranted.
ReliabilityFirst Corporation (ReliabilityFirst) | Entergy Nuclear Palisades, LLC (ENP) | NCR08052 | RFC2013011746 | FAC-008-1 | R1; R1.2 | During a Compliance Audit, conducted from November 7, 2011 through November 18, 2011, ReliabilityFirst determined that ENP, as a Generator Owner, had an issue with FAC-008-1 R1. ReliabilityFirst determined that ENP’s Facility Rating Methodology did not include the method by which it determined Facility Ratings for relay protective devices and did not include Normal and Emergency Ratings for relay protective devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to the BPS was mitigated by the following factors. Although no Facility Ratings existed for relay protective devices, ENP provided calculations for the generator differential protective relay and generator reverse power protective relay which demonstrated that current and potential transformers used in this analysis were adequately sized for the device with which they are associated. In addition, relay protective devices were not the most limiting element of the facility. | To mitigate this issue, ENP updated its Facility Rating Methodology to include the method by which ratings of relay protective devices are determined and to include Normal and Emergency Ratings for relay protective devices. ReliabilityFirst has verified the completion of all mitigation activity.
ReliabilityFirst Corporation (ReliabilityFirst) | Richmond Power and Light (RP&L) | NCR00909 | RFC2012011196 | PRC-005-1 | R1 | On October 2, 2012, RP&L, as a Distribution Provider, self-certified an issue with PRC-005-1 R1. RP&L reported that due to a misunderstanding of the Standard, it failed to have a Protection System maintenance and testing program (Program) as required by PRC-005-1. Specifically, RP&L believed that because it did not own transmission Protection Systems, it was not subject to PRC-005. In preparation for a Compliance Audit, RP&L hired a consultant to review its compliance program, who identified the lack of a formal Program as a possible compliance violation. As a result, RP&L submitted the self-certification to ReliabilityFirst, noting its mistake in interpreting the Standard and identifying that although it does not own transmission Protection Systems, it does own transformer protection and batteries that impact the transmission Protection Systems of American Electric Power Service Corporation as agent for Appalachian Power Company, Columbus Southern Power Company, Indiana Michigan Power company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, and Wheeling Power Company (AEP), supplies DC voltage to AEP’s 138 kV breakers, and owns a transformer differential relay that operates an AEP lockout relay that ultimately operates breakers at both ends of the connected transmission lines. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RP&L’s two points of interconnection with AEP are both connected to transmission lines that are deemed non-critical by AEP and have a low reporting status according to the Reliability Coordinator, PJM. PJM maintains a monitoring and report status based on its Energy Management System model and does not monitor RP&L’s equipment nor require notification from RP&L in the event of a disturbance. PJM requires notification from AEP for these transmission lines only for unusual circumstances. Despite the lack of a formal Program designed for NERC compliance, RP&L conducted regular testing of relays and batteries, for which it provided evidence to ReliabilityFirst. In addition, RP&L experienced no misoperations on any of the Protection System equipment through the duration of the issue, and upon conducting testing found no problems with its three devices that protect the BPS. Furthermore, although RP&L did not have a documented Program, it did perform some maintenance and testing activities. Specifically, RP&L continuously monitors battery output voltage and supply voltage to battery chargers and tests battery cells annually. RP&L tests differential relays every five years. | To mitigate this issue, RP&L: 1) created a formal written Program; 2) completed any outstanding testing and maintenance; and 3) provided training to personnel related to the new Program.
ReliabilityFirst Corporation (ReliabilityFirst) | Richmond Power and Light (RP&L) | NCR00909 | RFC2012011197 | PRC-005-1 | R2 | On October 2, 2012, RP&L, as a Distribution Provider, self-certified an issue with PRC-005-1 R2. RP&L reported that due to a misunderstanding of the Standard, it failed to have and therefore failed to document and implement a Protection System maintenance and testing program (Program) as required by PRC-005-1. Specifically, RP&L believed that because it did not own transmission Protection Systems, it was not subject to PRC-005. In preparation for a Compliance Audit, RP&L hired a consultant to review its compliance program, who identified the lack of a formal Program as a possible compliance violation. As a result, RP&L submitted the self-certification to ReliabilityFirst, noting its mistake in interpreting the Standard and identifying that although it does not own transmission Protection Systems, it does own transformer protection and batteries that impact the transmission Protection Systems of American Electric Power Service Corporation as agent for Appalachian Power Company, Columbus Southern Power Company, Indiana Michigan Power company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, and Wheeling Power Company (AEP), supplies DC voltage to AEP’s 138 kV breakers, and owns a transformer differential relay that operates an AEP lockout relay that ultimately operates breakers at both ends of the connected transmission lines. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RP&L’s two points of interconnection with AEP are both connected to transmission lines that are deemed non-critical by AEP and have a low reporting status according to the Reliability Coordinator, PJM. PJM maintains a monitoring and report status based on its Energy Management System model and does not monitor RP&L’s equipment nor require notification from RP&L in the event of a disturbance. PJM requires notification from AEP for these transmission lines only for unusual circumstances. Despite the lack of a formal Program designed for NERC compliance, RP&L conducted regular testing of relays and batteries, for which it provided evidence to ReliabilityFirst. In addition, RP&L experienced no misoperations on any of the Protection System equipment through the duration of the issue, and upon conducting testing found no problems with its three devices that protect the BPS. Furthermore, although RP&L did not have a documented Program, it did perform some maintenance and testing activities. Specifically, RP&L continuously monitors battery output voltage and supply voltage to battery chargers and tests battery cells annually. RP&L tests differential relays every five years. | To mitigate this issue, RP&L: 1) created a formal written Program; 2) completed any outstanding testing and maintenance; and 3) provided training to personnel related to the new Program.
SERC Reliability Corporation (SERC) | Craven County Wood Energy Limited Partnership (Craven) | NCR01212 | SERC2012011533 | PRC-005-1 | R2 | On December 11, 2012, Craven submitted a Self-Report to SERC stating that, as a Generator Owner, it had an issue with PRC-005-1 R2 because it could not provide documentation that its DC control circuitry devices were tested within the defined intervals in 2009 and 2011. Craven personnel did not understand the meaning of DC control circuitry in the definition of the Protection System and assumed that DC control circuitry only referred to communications circuitry. Based on this misunderstanding, Craven did not perform relay functional testing for its DC control circuitry devices. SERC reviewed Craven’s Protection System procedures and a spreadsheet created by Craven, which includes a complete inventory of the Craven Protection System devices, defined intervals, and maintenance and test dates for the most current and previous dates listed for each Protection System device. SERC determined that Craven tested 13 out of 13 DC control circuitry devices (100%) outside of the defined interval because it failed to perform relay functional testing for its DC control circuitry devices since the Standard became mandatory and enforceable. In total, SERC determined that Craven could not provide evidence that 13 out of 32 Protection System devices (40.6%) were compliant with PRC-005-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although Craven did not test the DC control circuitry within the defined interval, it had maintained the associated relays within the defined interval. Craven subsequently trip-tested the relays associated with the DC control circuitry and found no problems. Craven is a 50 MW wood-waste fueled plant with a 230 kV connection with its Transmission Operator and sells the energy output into the market. A Notice of Confirmed Violation covering a violation of PRC-005-1 R1 for Craven was filed with FERC under NP08-27-000 on June 5, 2008. On July 3, 2008, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that the instant issue is appropriate for FFT treatment because the prior violation involved incomplete documentation of Craven's Protection System maintenance and testing program and occurred in the initial period prior to December 31, 2007 established by Order No. 693. In this issue, the Protection System maintenance and testing program was compliant and the issue resulted from a misunderstanding of what constituted DC control circuitry. | To mitigate this issue, Craven: 1) Added the individual DC control circuitry devices associated with each relevant Protection System relay to its Protection System maintenance and testing program; 2) Tested the relevant DC control circuitry devices; and 3) Entered an activity into the facility's computerized maintenance management system, which will automatically send a work order to the manager or delegate(s) responsible for performing the specified duties under PRC-005-1.
SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC2012010506 | MOD-001-1a | R6 | On June 8, 2012, PEC, submitted a Self-Report to SERC stating that, as a Transmission Operator, it had an issue with MOD-001-1a R6 because when calculating Total Flowgate Capability (TFC), it used assumptions for three transmission lines that were more limiting than those used in the planning of operations. On May 4, 2012, PEC was contacted by a neighboring Balancing Authority regarding PEC’s flowgate information for the Canton-Walters 115 kV white line. PEC determined that the line rating used for the Available Flowgate Capability (AFC) process was incorrect. The power flow cases are used in the AFC process for calculating the TFC. SERC learned that PEC has normal and study ratings in its Facility Ratings database. The study rating is a record of unique cases where PEC has line-tie switches or circuit breaker bypass switches for the purposes of equipment maintenance. The study rating is for reference and is used only in special studies. For the Canton-Walters line, the study rating (including a 600 amp line-tie switch) was incorrectly used in the power flow case that was ultimately used for the AFC process. The Canton-Enka Switching Station 115 kV line also had the incorrect rating for the same reason. PEC implemented an AFC process update to correct the rating to 209 MVA the same day that it discovered the issue at the Canton-Walters line. Transmission Planning reviewed its modeling and corrected its power flow data base cases on May 14, 2012. According to PEC, after reviewing its TFC models, it found an additional instance. On March 31, 2011, PEC transmission planning communicated that the current transformer tap ratios had been upgraded on the Robinson-Rockingham 230 kV line, which is associated with some PEC flowgates. The upgrade increased the effective summer line rating from 478 MVA to 539 MVA. As a result, the rating used in the AFC process was more limiting than what was used in planning of operations. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Even though the assumptions used could have affected commercial activity, the ratings used in the energy management system for operating and monitoring of the PEC transmission system were correct. | To mitigate this issue, PEC: 1) Corrected the incorrect line ratings that had been used in the AFC process; 2) Completed a review of all of the ratings in the AFC process; 3) Modified the Facility Ratings spreadsheet documentation to clarify the proper use of normal and study ratings so that only the normal ratings are to be used in transmission Facility Ratings; and 4) Developed a process document that addresses how System Operations Engineering maintains ratings used in AFC case development, which includes roles and responsibilities between System Operations Engineering and Transmission Planning.
SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC2012010587 | MOD-001-1a | R7 | On June 27, 2012, PEC, submitted a Self-Report to SERC stating that, as a Transmission Service Provider, it had an issue with MOD-001-1a R7 because when calculating Available Flowgate Capability (AFC), it used assumptions for three transmission lines that were more limiting than those used in the planning of operations. On May 4, 2012, PEC was contacted by a neighboring Balancing Authority regarding PEC’s flowgate information for the Canton-Walters 115 kV white line. PEC determined that the line rating used for the AFC process was incorrect. The power flow cases are used in the AFC process. SERC learned that PEC has normal and study ratings in its Facility Ratings database. The study rating is a record of unique cases where PEC has line-tie switches or circuit breaker bypass switches for the purposes of equipment maintenance. The study rating is for reference and is used only in special studies. For the Canton-Walters line, the study rating (including a 600 amp line-tie switch) was incorrectly used in the power flow case that was ultimately used for the AFC process. The Canton-Enka Switching Station 115 kV line also had the incorrect rating for the same reason. PEC implemented an AFC process update to correct the rating to 209 MVA the same day that it discovered the issue at the Canton-Walters line. Transmission Planning reviewed its modeling and corrected its power flow data base cases on May 14, 2012. According to PEC, after reviewing its AFC models, it found an additional instance of a rating error. On March 31, 2011, PEC transmission planning communicated that the current transformer tap ratios had been upgraded on the Robinson-Rockingham 230 kV line, which is associated with some PEC flowgates. The upgrade increased the effective summer line rating from 478 MVA to 539 MVA. As a result, the rating used in the AFC process was more limiting than what was used in planning of operations. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Even though the assumptions used could have affected commercial activity, the ratings used in the energy management system for operating and monitoring of the PEC transmission system were correct. | To mitigate this issue, PEC: 1) Corrected the incorrect line ratings that had been used in the AFC process; 2) Completed a review of all of the ratings in the AFC process; 3) Modified the Facility Ratings spreadsheet documentation to clarify the proper use of normal and study ratings so that only the normal ratings are to be used in transmission Facility Ratings; and 4) Developed a process document that addresses how System Operations Engineering maintains ratings used in AFC case development, which includes roles and responsibilities between System Operations Engineering and Transmission Planning.
SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | SERC2012011424 | VAR-002-1.1b | R1 | On November 12, 2012, SCPSA submitted a Self-Report to SERC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R1 because it did not notify the Transmission Operator (TOP) when the Automatic Voltage Regulator (AVR) was not operated in automatic voltage control mode from September 27, 2012 until October 2, 2012. On September 27, 2012 at 11:13 a.m., SCPSA started up and synchronized Jefferies Generating Station Unit 4 (Unit 4). SCPSA’s control system records show the AVR entered the manual mode later that day at 8:56 p.m. without operator action. On October 2, 2012 at 4:25 p.m., the unit operator noticed that generator MVARs were slightly low with unit load at 109 MW and elected to raise them using the computer-based control system. The operator noticed the AVR toggle switch indication highlighting the manual state. After confirming with the shift supervisor that this was not the expected condition of the AVR, the operator placed the AVR in the automatic state. At 4:33 p.m., the operator toggled the AVR from automatic to manual back to automatic to test that the state had actually changed. The unit operator failed to notify the TOP of either period of operation with the AVR out of automatic controlling voltage. SCPSA maintained voltage within the prescribed limits of the voltage schedule throughout the period in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCPSA maintained the voltage schedule during the period in question. In addition, SCPSA subsequently conducted a study to compare voltages at area buses and facility loadings under selected contingency conditions with Unit 4 providing voltage regulation and then without regulation. SCPSA concluded that the presence or absence of voltage regulation at Unit 4 would have had no significant impact on area bus voltages or facility loadings for the period in question. Furthermore, Unit 4 was only 144 MW of SCPSA’s 2,870 MWs of generation on-line (5.0%) during the period in question. | To mitigate this issue, SCPSA: 1) Conducted operator refreshing training that covered the unit operator's responsibilities under VAR-002, identification of proper indication of an accurate status of the AVR, and any changes made to the control systems based on the verifications conducted at all SCPSA generating stations; 2) Posted a list of standard reports required by the NERC Reliability Standards near each unit operator's station at all SCPSA generating stations; 3) Changed the Jefferies Generating Station distributed control system to give a priority audible alarm requiring operator acknowledgement when the AVR is not in automatic controlling voltage mode; 4) Verified that the control systems at all SCPSA generating stations adequately draw the unit operator's attention to an unexpected change in the AVR or changed the control systems to do so where the hardware will support this setting; 5) Changed the control screens used by the operator at Jefferies Generating Station to plainly display the state of the AVR; and 6) Verified that the control screens used by operators at all SCPSA generating stations plainly display the state of the AVR or changed the control screens to do so where the hardware will support this setting.
SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | SERC2012011425 | VAR-002-1.1b | R3 | On November 12, 2012, SCPSA submitted a Self-Report to SERC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R3.1 because it did not notify the Transmission Operator (TOP) within 30 minutes of a change in the status of an Automatic Voltage Regulator (AVR). On September 27, 2012 at 11:13 a.m., SCPSA started up and synchronized Jefferies Generating Station Unit 4 (Unit 4). SCPSA’s control system records show the AVR entered the manual mode later that day at 8:56 p.m. without operator action. On October 2, 2012 at 4:25 p.m., the unit operator noticed that generator MVARs were slightly low with unit load at 109 MW and elected to raise them using the computer based control system. The operator noticed the AVR toggle switch indication highlighting the manual state. After confirming with the shift supervisor that this was not the expected condition of the AVR, the operator placed the AVR in the automatic state. At 4:33 p.m., the operator toggled the AVR from automatic to manual back to automatic to test that the state had actually changed. In both instances, the unit operator failed to notify the TOP within 30 minutes of the status change of the AVR once the operator switched the AVR to automatic and controlling voltage. SCPSA maintained voltage within the prescribed limits of the voltage schedule throughout the period in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCPSA maintained the voltage schedule during the period in question. In addition, SCPSA subsequently conducted a study to compare voltages at area buses and facility loadings under selected contingency conditions with Unit 4 providing voltage regulation and then without regulation. SCPSA concluded that the presence or absence of voltage regulation at Unit 4 would have had no significant impact on area bus voltages or facility loadings for the period in question. Furthermore, Unit 4 was only 144 MW of SCPSA’s 2,870 MWs of generation on-line (5.0%) during the period in question. | To mitigate this issue, SCPSA: 1) Conducted operator refreshing training that covered the unit operator's responsibilities under VAR-002, identification of proper indication of an accurate status of the AVR, and any changes made to the control systems based on the verifications conducted at all SCPSA generating stations; 2) Posted a list of standard reports required by the NERC Reliability Standards near each unit operator's station at all SCPSA generating stations; 3) Changed the Jefferies Generating Station distributed control system to give a priority audible alarm requiring operator acknowledgement when the AVR is not in automatic controlling voltage mode; 4) Verified that the control systems at all SCPSA generating stations adequately draw the unit operator's attention to an unexpected change in the AVR or changed the control systems to do so where the hardware will support this setting; 5) Changed the control screens used by the operator at Jefferies Generating Station to plainly display the state of the AVR; and 6) Verified that the control screens used by operators at all SCPSA generating stations plainly display the state of the AVR or changed the control screens to do so where the hardware will support this setting.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEPCO-Trans) | NCR01214 | SERC2012011536 | FAC-009-1 | R1 | On August 8, 2012, SERC sent VEPCO-Trans an initial notice of a Compliance Audit scheduled for February 4, 2013 through February 8, 2013. On December 13, 2012, VEPCO-Trans submitted a Self-Report to SERC stating that, as a Transmission Owner, it had an issue with FAC-009-1 R1 because the Facilities Rating for a single facility was not determined consistently with its Facility Ratings Methodology (FRM). SERC requested and reviewed additional information to complete its assessment. SERC learned that the FRM used by VEPCO-Trans was revised September 1, 2011 to include consideration of a “load dump” relay setpoint, which was required by its agreement with PJM Interconnection, LLC, the Regional Transmission Organization. VEPCO-Trans defines load dump as the rating at which a piece of equipment can operate for at least 15 minutes with acceptable loss of equipment life or other impacts at a specified ambient temperature. Prior to the September 1, 2011 FRM, load dump ratings were not included. VEPCO-Trans determines and distributes load dump ratings in addition to its normal and emergency ratings. While investigating a possible PRC-023 issue on August 23, 2012, VEPCO-Trans discovered that the Facility Rating for Chesterfield Line 208 incorrectly showed the conductor, instead of the relay, as the limiting element. As a result, the published ratings were incorrect for those three specific load dump calculations. The other normal and emergency calculations remained unaffected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The highest peak load recorded on Chesterfield Line 208 during the time period of this issue was 338 MVA (848 Amps at 230 kV) on September 14, 2011. The highest seasonal Facility Rating of Chesterfield Line 208 is 2026 Amps. Therefore, the highest peak load recorded has never exceeded 42 percent of the highest seasonal Facility Rating, which indicates that the actual flow was never close to exceeding the rating limits. Planning assessments have never identified Chesterfield Line 208 as being a problem for contingency loading that exceeded the highest seasonal Facility Rating of 2026 Amps. | To mitigate this issue, VEPCO-Trans: 1) Modified the field relay setting sheets by adding a field that indicates the required status of the Zone 3 relay trip function; 2) Corrected the relay setting on Chesterfield Line 208; and 3) Investigated the remaining 3-phase impedance relay sets at other VEPCO-Trans locations and identified no additional issues.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEPCO-Trans) | NCR01214 | SERC2012011535 | PRC-023-1 | R1 | On August 8, 2012, SERC sent VEPCO-Trans an initial notice of a Compliance Audit scheduled for February 4, 2013 through February 8, 2013. On December 13, 2012, VEPCO-Trans submitted a Self-Report to SERC stating that, as a Distribution Provider and Transmission Owner, it had an issue with PRC-023-1 R1.1 because it identified a single 3-phase set of relays that were not set to operate at or above 150% of the highest seasonal Facility Rating of a circuit for the available defined loading duration nearest 4 hours. On August 23, 2012, while performing a protection settings review for an upcoming project on Chesterfield Line 208, an engineer identified a discrepancy between the relay control drawings and the relay setting documentation. Chesterfield Line 208, which utilizes a 3-phase set of impedance protection relays, required that the Zone 3 tripping function be disabled to meet compliance with R1.1. The as-issued relay setting documentation indicated that Zone 3 tripping was to be disabled while the relay control drawing indicated that Zone 3 tripping was still enabled. A field technician was immediately dispatched to investigate and confirmed that the Zone 3 tripping was still enabled. As a result, the Chesterfield Line 208 was incorrectly set at 110.31% as opposed to at least 150% of the highest seasonal Facility Rating of the circuit. VEPCO-Trans investigated the 54 remaining 3-phase impedance relay sets of this type. No additional issues were identified. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The highest peak load recorded on Chesterfield Line 208 during the time period at issue was 444.7 MVA (1116 Amps at 230 kV) on December 2, 2010. The highest seasonal Facility Rating of Chesterfield Line 208 is 2026 Amps. Therefore, highest peak load recorded on Chesterfield Line 208 has never exceeded 60 percent of the highest seasonal Facility Rating, indicating the unlikeliness the setpoints would have limited loadability. Planning assessments have never identified Chesterfield Line 208 as being a problem for contingency loading that exceeded the highest seasonal Facility Rating of 2026 Amps. | To mitigate this issue, VEPCO-Trans: 1) Modified the field relay setting sheets by adding a field that indicates the required status of the Zone 3 relay trip function; 2) Corrected the relay setting on Chesterfield Line 208; and 3) Investigated the remaining 3-phase impedance relay sets at other VEPCO-Trans locations and identified no additional issues.
Southwest Power Pool Regional Entity (SPP RE) | PowerSmith Cogeneration Project, LP (PowerSmith) | NCR11119 | SPP201100656 | PRC-005-1 | R1 | On July 31, 2011, PowerSmith submitted a Self-Report to SPP RE stating that, as a Generator Owner and Generator Operator, it had an issue with PRC-005-1 R1. PowerSmith did not have a maintenance and testing program for Protection Systems that included intervals and their basis for testing or a summary of maintenance and testing procedures for its relays. SPP RE expanded the scope of the Self-Report because PowerSmith did not have a maintenance and testing program for all its Protection System devices. The devices subject to the maintenance and testing program were about 150, the majority of which were batteries. This issue occurred between April 22, 2011, PowerSmith’s registration date, and May 31, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although PowerSmith did not have a PRC-005-1 R1 maintenance and testing program in place upon registration, PowerSmith provided evidence that it had tested and maintained its Protection System devices within regular intervals which are more conservative than those intervals recommended by the NERC technical Reference on PRC-005. PowerSmith maintained its Protection System devices within annual intervals, except for relays, which were tested and maintained every two years. Additionally, PowerSmith did have a documented Instrument Calibration Program, which included intervals for testing of its relays. | PowerSmith developed a Protection System maintenance and testing program, and trained its staff on the program.
Western Electricity Coordinating Council (WECC) | California Independent System Operator (CISO) | NCR05048 | WECC2013011933 | EOP-001-0b | R6 | On September 11, 2008, CISO acquired compliance responsibility for EOP-001-0b R6 per Coordinated Functional Registration (CFR) JRO00010. Specifically, as the entity responsible for compliance, CISO shall ensure copies of updated emergency plans are provided to the Reliability Coordinator (RC), the neighboring Transmission Operators (TOPs), and associated Balancing Authorities (BAs), as required by EOP-001-0b R6. On February 15, 2013, CISO submitted a Self-Report to WECC reporting that, as a BA and TOP, it had failed to provide a copy of an updated emergency plan to neighboring TOPs. Specifically, CISO failed to distribute Pacific Gas and Electric’s (PGAE's) updated 2011 Electric System Restoration Guideline (ESRG) emergency plan to three neighboring TOPs: Trans Bay Cable, Turlock Irrigation District, and Silicon Valley Power. CISO should have provided the plan to the three neighboring TOPs on November 23, 2011, however it did not provide the updated plan until June 20, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although CISO failed to share the updated 2011 emergency plan with three TOPs, it did share the plan with the RC and the neighboring BAs. The three TOPs had CISO's prior emergency plan on file. The updated emergency plan included only minor changes and clarifications to existing procedures that affect the BAs. In the event of an emergency, the three TOPs that did not have the recent version of the emergency plan would still have to coordinate with the RC, thereby preventing any issues with voltage and loading conditions. | CISO distributed the updated emergency plan to Trans Bay Cable, Turlock Irrigation District, and Silicon Valley.
Western Electricity Coordinating Council (WECC) | US Bureau of Reclamation (USBR) | NCR05441 | WECC2012011522 | FAC-501-WECC-1 | R3 | On December 13, 2012, USBR submitted a Self-Report to WECC stating that, as a Transmission Owner, it had an issue with FAC-501-WECC-1 R3. USBR reported that it could not demonstrate that it had fully implemented its Transmission Maintenance and Inspection Plan (TMIP) because it could not produce a work completion order for motion analysis testing for one transfer breaker. USBR reported that it was to conduct a motion analysis testing on its transfer breakers every four years. USBR reported that it had created a work order on October 29, 2008, requiring motion analysis testing for one transfer breaker. USBR stated that it could not supply documentation demonstrating that the motion analysis test had ever been completed. USBR remediated the issue on June 26, 2012, when it conducted the appropriate motion analysis testing on the transfer breaker. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the duration of the issue, USBR did complete maintenance and testing on its other associated transfer breakers. Additionally, the transfer breaker involved in this incident was a secondary breaker. As a secondary breaker, if a triggering event would have occurred (on the breaker associated with this issue) another layer of breakers would have reacted to prevent any damaging effects. Finally, the breaker involved in the incident is attached to a small generator producing only 13 percent of the plant’s total capacity and only 4.7 percent of USBR’s total 15,000 MW capacity. | To mitigate this issue, USBR completed the required maintenance and testing on the transfer breaker involved.
Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2012011141 | INT-006-3 | R1 | On September 27, 2012, SCL submitted a Self-Report to WECC stating that as a Balancing Authority, it had an issue with INT-006-3 R1. In the Self-Report, SCL stated that it had failed to respond timely to two Arranged Interchanges (Electronic Tag(s) or e-tag(s)) prior to the expiration of the reliability assessment period on August 17, 2012. SLC stated this was because of internal e-tag service problems. On October 19, 2012, SCL submitted an additional Self-Report citing an additional occurrence of INT-006-3 R1. In the Self-Report, SCL stated that it had failed to respond timely to one e-tag on September 26, 2012 prior to the expiration of the reliability assessment period, again because of internal e-tag service problems. SCL’s system software utilizes Java. During the duration of the issue, Java sent an update to SCL’s system software. The update caused conflicts and generated bugs between SCL’s e-tagging program and the system software, rendering the two programs incompatible. As a result, two e-tags expired on August 17, 2012, and one on September 26, 2012, both of which required SCL’s approval. In all three instances, SCL manually reviewed and approved the e-tags. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, although SCL failed to evaluate the e-tags prior to expiration on three separate occurrences, SCL manually reviewed and approved the e-tags prior to scheduling the interchanges. The potential risks to the reliability of the BPS were further minimized by measures taken during the duration of the issue. Each e-tag was discovered by the marketing operator on duty within one to four minutes after the expiration period. The operator communicated the software problems with SLC’s system operator and remained in constant communication with the operations desk. Adjustment e-tags were submitted as soon as the tagging software (PowerOps) regained functionality. In each case, the transactions were not affected and took place as originally planned. | To mitigate this issue, SCL: 1) proposed, demonstrated, and obtained internal SCL approval for Open Access Technology International, Inc. (OATI) e-tag approval service; 2) signed an agreement between SCL and OATI to provide e-tag approval service; 3) identified SCL process changes required to use OATI e-tag approval service and train staff to use OATI e-tag approval service; 4) modified NERC Transmission System Information Networks and North American Energy Standards Board Electric Industry Registry uniform resource locator data to point to the OATI approval service; and 5) switched over to OATI e-tag approval service. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2013012112 | PRC-004-2a | R3 | On December 19, 2012, WECC notified CHPD that WECC would be conducting an on-site Compliance Audit at CHPD’s office from March 18, 2013 through March 28, 2013 (Audit Notice). After WECC sent the Audit Notice, but prior to WECC’s arrival for the on-site Compliance Audit, CHPD submitted a Self-Report stating that, as a Transmission Operator, it had an issue with PRC-004-2a R3. In the Self-Report, CHPD stated that a protective relay misoperation occurred on a non-major WECC transmission path on August 13, 2012. CHPD stated that it conducted a thorough analysis of the misoperation and created a Corrective Action Plan to fix and prevent reoccurrence of the misoperation. In this case, because the misoperation occurred on a non-major WECC transmission path, CHPD was required to report the misoperation to its Regional Reliability Organization (RRO) within two months after the end of the quarter in which the misoperation occurred. CHPD reported however, that it did not report the misoperation of the relay to its RRO within two months after the end of the quarter in which the misoperation occurred. CHPD should have reported the misoperation by November 30, 2012 but did not report the misoperation to its RRO until February 11, 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, the potential risks associated with this possible issue were minimized due to CHPD’s compensating measures. The misoperation related to this issue occurred on a non-major WECC transmission path. CHPD followed proper procedure and correctly analyzed the misoperation and promptly created a Corrective Action Plan to prevent similar future misoperations. Additionally, WECC determined that this is one instance of noncompliance and that there is not a systematic breakdown involved with this issue. CHPD’s consistent application of its procedures allowed it to discover its oversight and correct the issue in a timely manner. Finally, CHPD’s late submission did not impede WECC’s ability to review and properly analyze the misoperation. | To mitigate this issue, CHPD: 1) revised its reporting methodology to include a new tracking mechanism; 2) modified its relay operation reporting form; and 3) included additional senior management review for misoperation reporting. WECC has verified the completion of all mitigation activity
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2012011516 | VAR-002-1.1b | R3 | On December 13, 2012, PGE submitted a Self-Report to WECC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R3. PGE reported that on July 9, 2012, at 11:35 a.m., the Biglow Canyon wind farm lost 1 MVAR of reactive power due to a bad power supply in a static synchronous compensator device, a reactive resource. PGE reported, however, that in its capacity as the Generator Operator at Biglow, it failed to notify the Transmission Operator (TOP), the Bonneville Power Authority, of the loss within thirty minutes as required under VAR-002-1.1b R3.2. PGE did not notify its TOP until July 10, 2012, at 2:35 p.m. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the loss of 1 MVAR represents a loss of 1.2 percent of the windfarm’s capability and would not have impacted BPS operations in the event that the TOP had to rely on Biglow as a reactive power resource. | To mitigate this issue, PGE: 1) notified its TOP of the capability change at Biglow on July 10, 2012, at 2:35 p.m.; 2) updated its VAR-002-1b R3.2 reporting procedure at Biglow; and 3) trained staff on procedural revisions.