## Public Non-CIP May FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council, Inc. (FRCC) | Covanta Southeastern Florida Renewable Energy (SEFLOR), LTD. (COVS) | NCR11009 | FRCC2013011686 | VAR-002-1.1b | R1 | On January 9, 2013, COVS submitted a Self-Report to FRCC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R1. On January 1, 2013, COVS notified Progress Energy, the Balancing Authority, and Florida Power & Light Company, the Transmission Operator, that Turbine Generator #2 (T/G #2), had been brought back online; however plant personnel failed to inform its respective BA and TOP that the Turbine Generator #2 automatic voltage regulator (AVR) was in manual operation instead of the required automatic mode from 9:57 p.m. on January 1, 2013 to 3:27 a.m. on January 2, 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. COVS notified the BA and TOP that T/G #2 had been brought back online and the BA and TOP would have been able to monitor the line voltage of the units through the supervisory control and data acquisition system. In addition the COVS facility maintained the required voltage schedule and the facility’s total generation is only 60 MW. Furthermore, the AVR was in manual for a short time, approximately four hours. | To mitigate this issue, COVS: 1) notified the BA and TOP at 9:30 a.m. on January 2, 2013 that the AVR had been in manual from 9:57 p.m. on January 1, 2013 to 3:27 a.m. on January 2, 2013; 2) terminated conductors properly in the 501 Circuit Breaker. 3) conducted NERC compliance refresher training for all responsible personnel; 4) posted a summary of NERC reporting requirements in both the turbine control room and the main control room, along with updated subject matter expert (SME) contact information. 5) ensured that all SMEs are aware of the need to be available for plant support; 6) implemented written disciplinary action for the shift supervisor responsible for communicating AVR manual status; 7) Alstom, a third-party vendor, SME to verify logic of AVR sequences on Turbine Generator #1 and Turbine Generator #2. 8) revised its Turbine Generator Standard Operating Procedures (SOP) that incorporate NERC-specific actions. 9) incorporated a visual message to accompany distributed control system alarming when AVR falls out of automatic operation mode; and 10) retrained all affected personnel on the revised SOP March 31, 2013.
Florida Reliability Coordinating Council, Inc. (FRCC) | Covanta Southeastern Florida Renewable Energy (SEFLOR), LTD. (COVS) | NCR11009 | FRCC2013011690 | VAR-002-1.1b | R3 | On January 9, 2013, COVS submitted a Self-Reported to FRCC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R3. On January 1, 2013, COVS notified Progress Energy, the Balancing Authority (BA), and Florida Power & Light Company, the Transmission Operator (TOP), that Turbine Generator #2, had been brought back online; however, plant personnel failed to inform its respective TOP that the Turbine Generator #2 automatic voltage regulator (AVR) was in manual operation instead of the required automatic mode from 9:57 p.m. on January 1, 2013 to 3:27 a.m. on January 2, 2013. Therefore, COVS failed to notify its TOP that of change in AVR status within 30 minutes of the change as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. COVS notified the BA and TOP that T/G #2 had been brought back online and the BA and TOP would have been able to monitor the line voltage of the units through the supervisory control and data acquisition system. In addition the COVS facility maintained the required voltage schedule and the facility’s total generation is only 60 MW. Furthermore, the AVR was in manual for a short time, approximately four hours. | To mitigate this issue, COVS: 1) notified the BA and TOP at 9:30 a.m. on January 2, 2013 that the AVR had been in manual from 9:57 p.m. on January 1, 2013 to 3:27 a.m. on January 2, 2013; 2) terminated conductors properly in the 501 Circuit Breaker. 3) conducted NERC compliance refresher training for all responsible personnel; 4) posted a summary of NERC reporting requirements in both the turbine control room and the main control room, along with updated subject matter expert (SME) contact information. 5) ensured that all SMEs are aware of the need to be available for plant support; 6) implemented written disciplinary action for the shift supervisor responsible for communicating AVR manual status; 7) Alstom, a third-party vendor, SME to verify logic of AVR sequences on Turbine Generator #1 and Turbine Generator #2. 8) revised its Turbine Generator Standard Operating Procedures (SOP) that incorporate NERC-specific actions. 9) incorporated a visual message to accompany distributed control system alarming when AVR falls out of automatic operation mode; and 10) retrained all affected personnel on the revised SOP March 31, 2013.
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2012010474 | PER-002-1 | R2; R2.1 | During a Compliance Audit, conducted on June 8, 2012, FRCC auditors found that VERO was unable to provide sufficient evidence to demonstrate that VERO has a training program for all operating personnel in positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System (BES), as required by PER-002-1 R2.1. Specifically, the supervisor of the transmission and distribution system operations job description lists the principal responsibilities of that person as: plans, organizes, controls and provides direction of electrical system dispatch operations including supervisory control and data acquisition operations. This person should have been, but was not listed in the training program as someone requiring training. Due to the job description as someone with primary responsibilities for the real-time operation of the interconnected BES, the person should have been included in the training program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected individual did receive training and was just not documented as someone who required training. In addition, VERO is a small municipal with 14 miles of 138 kV transmission (less than 1% of regional transmission) serving 210 MW peak load and no registered generation (144 MW of non-registered generation connected at 69 kV). | To mitigate this issue, VERO: 1) edited the job description of the supervisor of the transmission and distribution system operations to accurately reflect the duties of that position, in that this position does not have the primary responsibility, either directly or through communication with others, for the real-time operation of the interconnected BES, and to not require that position to have training.
Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2012010476 | PER-002-1 | R4 | During a Compliance Audit on June 8, 2012, FRCC auditors found that VERO was unable to provide sufficient evidence to demonstrate that for personnel identified in PER-002-1 R4, VERO provided its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. Specifically, two out of six system operators completed 26.5 hours of the required 32 hours using realistic simulations of system emergencies in 2010. The issue occurred due to a miscalculation by VERO of the hours each person completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VERO is contained within a much larger Balancing Authority/Transmission Operator (Florida Power & Light Company) footprint. The affected employees were long-term employees. One employee began working for VERO in 1996 and the other began in 2006. Although VERO's operations staff was not adequately trained and as a result, might make operational errors, such errors would more likely only impact VERO's own load and non-registered generation. Also, while the hours were not met in 2010, they were met in 2009 and 2011 and missed by only 5.5 hours each person in 2010. | To mitigate this issue, VERO: 1) revised its PER-002 R4 EOP training documentation improvements; 2) took steps to ensure that its operators receive the required 32 hours of EOP training since 2010. All operators received the required training in 2011 and all are on schedule to receive the required training in 2012; 3) implemented documentation to identify and schedule the 32 hours of EOP training required annually and to record the EOP training delivered for each operator; and 4) performed a review by the supervisor of system operations, on an ongoing basis, of the documentation at least quarterly to assure that all operators will receive the required training.
Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2012011486 | BAL-005-0.1b | R16 | On September 27, 2012, LES, as a Balancing Authority, self-reported noncompliance with BAL-005-0.1b R16. Specifically, LES failed to sample data at the same periodicity with which Area Control Error (ACE) is calculated and also failed to flag missing or bad data for operator display and archival purposes. LES performed an internal review of all 15 inputs (14 Tie Line inputs and a frequency source input) into its ACE equation in order to ensure that all 15 inputs were being scanned at an interval equal to or greater than its ACE calculation rate, every two seconds. During the review, LES discovered that 1 of its 15 ACE inputs was scanning at a rate of once every four seconds instead of once every two seconds. This setting discrepancy caused one of the Tie Lines to provide two second old "stale" data into the ACE calculation every other scan. Therefore, half of the ACE calculations received all of the coincident data from all 15 inputs and the other half of the ACE calculations received coincident data from 14 of the 15 inputs. LES became aware of this scan rate discrepancy on September 19, 2012, and after investigating, LES staff changed the scan rate back to every two seconds on the same day, September 19, 2012. Over the next two days, an in-depth investigation was performed in order to determine why the scan rate change was made and when it was made. LES discovered that the scan rate change was made on March 18, 2011 in order to troubleshoot one of its Tie Line remote terminal units (RTUs). Although the scan rate frequency was determined not to be the cause of the RTU issue, the substation technician decided to leave the scan rate at every four seconds in order to reduce the traffic on the RTU. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). One of the 15 inputs was scanned at a rate of every four seconds rather than every two seconds, and LES mitigated the issue by reconfiguring the setting within two hours of discovering the scan rate discrepancy. Additionally, LES collects the data necessary in the calculation of ACE every two seconds, which is below the six second requirement referenced in BAL-005-0.1b R8. Therefore, MRO determined that this issue posed a minimal risk to the BPS due to the extremely small error that this scan rate discrepancy introduced into LES’s ACE calculation. | To mitigate this issue, LES: 1) performed a full internal investigation to determine the scope of the issue; and 2) implemented notes and pushpins on the RTU configuration page, in addition to all applicable Tie Lines and frequency source inputs, alerting users that the sampling rate should remain at two seconds in compliance with BAL-005-0.1b R16.
Northeast Power Coordinating Council, Inc. (NPCC) | ANP Bellingham Energy Company (ANP Bellingham) | NCR07006 | NPCC2011008239 | PRC-005-1 | R2 | On September 22, 2011, ANP Bellingham submitted a Self-Report to NPCC stating that, as a Generator Owner, it had an issue with PRC-005-1 R2. ANP Bellingham conducted an internal assessment of its relay testing and determined that, for 2 out of 17 of its instrument transformers, there were missing test certificates from 2007, the previous defined testing four year interval. In addition, during the previous testing interval, the contractor who performed the testing did not provide any test certificates for relay functional checks. Although the planned maintenance form clearly stated that each relay was to be calibrated, a functional trip test was to be performed, and the maintenance activity was completed, the formal documentation was missing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While it appears that the testing interval has been exceeded, this was a documentation issue and the affected relays were actually tested and maintained within the defined interval. | To mitigate this issue, ANP Bellingham: 1) performed all the testing to correct the deficiencies noted above; and 2) revised its Protection System testing procedure to require the contractor deliver a complete and accurate report before final payment is made
Northeast Power Coordinating Council, Inc. (NPCC) | NAES Corporation - Lockport (NAES Lockport) | NCR07167 | NPCC2012010183 | CIP-001-1a | R2. | During a Compliance Audit conducted from March 1 to April 5, 2011, NPCC determined that NAES, as a Generator Operator, had an issue with CIP-001-1a R2. Specifically, NAES Lockport failed to have any procedures directing the communication of information concerning sabotage reporting to appropriate parties in the Interconnection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). When necessary, NAES Lockport has directed communications with other parties in the Interconnection through the use of the Plant Managers Standing Orders (OP-101. Therefore, should NAES Lockport need to direct communication of information concerning sabotage events to appropriate parties in the Interconnection, it would do so using the Plant Managers Standing Orders (OP-101). | To mitigate this issue, NAES Lockport: 1) updated its sabotage reporting procedure to specifically address the communication of sabotage events to the Interconnection parties that need to be contacted; and 2) required the affected personnel to review the specific changes to the procedure.
ReliabilityFirst Corporation (ReliabilityFirst) | Michigan South Central Power Agency (MSCPA) | NCR00823 | RFC2013012160 | FAC-009-1 | R1 | From October 17, 2012 through November 9, 2012, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that, as a Generator Owner, MSCPA had an issue with FAC-009-1, R1 because MSCPA did not use a common unit of measure on its facilities ratings sheet, which prevents a proper comparison of equipment elements to identify the most limiting element affecting output of the generator in the process of establishing Facility Ratings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue was a documentation issue. Despite not using common units, MSPCA had correctly determined that the total output of its generating unit was 50 MVA and that this output would not result in exceedences of the rating of any individual piece of equipment. In addition, MSCPA has a relatively small contribution to the BPS. | To mitigate this issue, MSCPA revised its Facility Ratings documentation to use a single unit of measure for FAC-009.
ReliabilityFirst Corporation (ReliabilityFirst) | Michigan South Central Power Agency (MSCPA) | NCR00823 | RFC2013012161 | PRC-001-1 | R1 | From October 17, 2012 through November 9, 2012, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that, as a Generator Operator, MSCPA had an issue with PRC-001-1 R1 because MSCPA failed to provide evidence that its personnel were familiar with the purpose and limitations of protective system schemes applied in its area. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MSCPA's operators were experienced in power plant operations, including the operation of protective system schemes applied in power plant operations. In addition, MSCPA has a relatively small contribution of to the BPS, consisting of one 55 MW generating unit that interconnects at 138 kV. | To mitigate this issue, MSCPA conducted training of its personnel to review the purpose and limitations of protective system schemes applied in its area.
ReliabilityFirst Corporation (ReliabilityFirst) | Michigan South Central Power Agency (MSCPA) | NCR00823 | RFC2013012162 | PRC-005-1 | R1 | From October 17, 2012 through November 9, 2012, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that, as a Generator Owner, MSCPA had an issue with PRC-005-1, R1 because MSCPA failed to include a summary of maintenance and testing procedures in its Protection System maintenance and testing program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue was a documentation issue because MSCPA performed maintenance and testing in accordance with its program. In addition, MSCPA has a relatively small contribution to the BPS, consisting of one 55 MW generating unit that interconnects at 138 kV. | To mitigate this issue, MSCPA added a summary of maintenance and testing procedures to its Protection System maintenance and testing program.
ReliabilityFirst Corporation (ReliabilityFirst) | Metropolitan Edison Company (MetEd) | NCR00821 | RFC2011001221 | PRC-008-0 | R2 | During a Compliance Audit, conducted from October 4, 2011 through October 7, 2011, ReliabilityFirst determined that MetEd, as a Distribution Provider and Transmission Owner, had an issue with PRC-008-0 R2. Met Ed could not provide Under Frequency Load Shedding (UFLS) program results for three UFLS relays. MetEd could provide database maintenance and testing records that included the dates upon which it last maintained and tested its Fairview, Hokes, and Walker UFLS relays, but not the results of the maintenance and testing. ReliabilityFirst initially determined MetEd could not provide test results for four UFLS relays. However, one of the UFLS relays at issue had test results for 2009, but was missing test results for 2005. ReliabilityFirst determined that MetEd’s missing 2005 test results did not indicate a possible violation of PRC-008-0 R2 as the testing occurred prior to the June 18, 2007, the date on which MetEd had to comply with PRC-008-0 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that this issue was a documentation issue. It was a documentation issue because MetEd could provide evidence demonstrating the most recent dates that each performed maintenance and testing on the three UFLS relays at issue, but not evidence of the results associated with the maintenance and testing. During the Compliance Audit, MetEd provided maintenance and testing dates as well as UFLS Program results for all other UFLS relays as requested by ReliabilityFirst. Additionally, the most recent maintenance and testing dates for the three UFLS relays at issue were within MetEd’s five-year UFLS maintenance and testing interval. | To mitigate this issue, MetEd, where appropriate, disabled or completed maintenance and testing for the three UFLS relays and documented the UFLS Program results pursuant to PRC-008-0 R2 by December 31, 2012.
SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2012010942 | MOD-030-2 | R2 | On August 17, 2012, Entergy submitted a Self-Report to SERC stating that, as a Transmission Operator (TOP), it had an issue with MOD-030-2 R2 because it failed to incorporate a change to the Total Flowgate Capability (TFC) calculation within seven days of being notified of a change in the rating by the Transmission Owner (TO) that would affect the TFC of a Flowgate used in the Available Flowgate Capability (AFC) process. On May 25, 2012, one Flowgate on the Entergy transmission system was derated from 275 MW to 273 MW. The TO notified Entergy of the derate on the same day, but Entergy did not acknowledge receipt of the derate until June 11, 2012. Entergy did not incorporate the change to the TFC model until June 12, 2012, 18 calendar days after it was notified of the derate. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The derate was 2 MW, or 0.7%, of the Flowgate’s capacity. In addition, the resulting TFC has not been approached during operation. Furthermore, the derate did not affect the steps that Entergy would take in the event the Rating had been exceeded. | To mitigate this issue, Entergy: 1) notified the TOP that a Flowgate rating change was necessary; 2) requested a change in the software used to calculate power flows for engineering analysis; 3) updated the AFC inputs database to include the correct rating of the Flowgate; 4) updated necessary documents to reflect the rating change of the Flowgate and sent the necessary documents to the TOP so they could be posted to the Open Access Same-Time Information System (OASIS); 5) received notification from the TOP that the updated documents had been posted to OASIS; 6) developed an AFC checklist to be used every time a rating change notification is received from configuration management to ensure that the AFC Flowgate will be identified and changed within the seven day window; 7) added the AFC checklist to its procedure for updating the transmission system topology in the daily and monthly powerflow models (transmission system topology procedure); and 8) trained applicable personnel on the transmission system topology procedure's AFC checklist. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | Cottonwood Energy Company LP (Cottonwood) | NCR01210 | SERC2012011381 | PRC-005-1 | R2 | On September 18, 2012, SERC sent Cottonwood an initial notice of a Compliance Audit scheduled for March 4, 2013 through March 8, 2013. On November 9, 2012, Cottonwood submitted a Self-Report to SERC stating that, as a Generator Owner, it had an issue with PRC-005-1 R2 because Cottonwood could not provide certain test documentation for 5 current transformers, 1 relay test date, and 5 missed communication system tests for 2 devices. SERC reviewed Cottonwood’s Protection System procedures and a spreadsheet created by Cottonwood, which includes a complete inventory of the Cottonwood Protection System devices, defined intervals, and maintenance and test dates for the most current and previous dates listed for each Protection System device. Based on this review, SERC determined that Cottonwood tested 1 out of 62 protective relays (1.61%), 2 out of 2 associated communication system (ACS) devices (100%), 5 out of 404 voltage and current sensing devices (1.23%), and 1 out of 62 DC control devices (1.61%) outside of the defined intervals. In total, SERC determined that Cottonwood could not provide evidence that 9 out of 540 Protection System devices (1.67%) were compliant with PRC-005-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Cottonwood constantly monitors the communication channels of the ACS devices. In the event communications are lost, an alarm is generated and sent to the Cottonwood control room which is manned at all times, prompting personnel to investigate. Cottonwood’s protective relays are wired such that a relay failure or trip activates alarms in the control center. Cottonwood subsequently tested all the Protection System devices with missed intervals and found that they were fully functional with no issues. | To mitigate this issue, Cottonwood: 1) reassigned the tracking and scheduling of all its Protection System devices; 2) developed a comprehensive list of all Protection System devices and associated test intervals and schedules; 3) tracked these test intervals with automatic reminders via the corporate tracking program, Intelex. This program tasks the responsible person on a quarterly basis to verify that the testing of all Protection System devices is completed in accordance with the intervals defined by its maintenance plan; and 4) tested all elements that were not tested according to scheduled intervals. SERC has verified the completion of all mitigation activities.
SERC Reliability Corporation (SERC) | Mackinaw Power, LLC (MACK) | NCR08082 | SERC2012011014 | PRC-005-1b | R2 | On September 4, 2012, MACK submitted a Self-Report to SERC stating that, as a Generator Owner, it had an issue with PRC-005-1 R2 because it failed to perform the quarterly battery maintenance within the required interval. According to MACK, the preventive maintenance (PM) work order for the battery was generated, but plant personnel failed to initiate the applicable contractor schedule. The issue was discovered during a routine audit of open work orders. SERC reviewed the MACK Protection System procedures and the MACK-compiled spreadsheet, which included a complete inventory of the Protection System devices, the defined intervals, and the maintenance and test dates for the most current and the previous dates listed for each device. SERC determined that MACK tested 1 out of 117 protective relay devices (0.85%) and 4 out of 18 station batteries (22.22%) outside of the defined intervals. In total, 5 out of 435 Protection System devices (1.15%) were not in compliance with PRC-005-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Following the second quarter of 2012, maintenance and testing was completed for the missed batteries in accordance to the maintenance intervals. In addition, during the quarter that the scheduled maintenance and testing was not completed, MACK had performed all of the corresponding monthly maintenance as scheduled. Any deterioration in the performance or condition of the battery system should have been discovered during the monthly maintenance or the subsequent quarterly tests. The results of the tests confirm that the battery system should have performed its functions as designed if needed during that period. The transformer relay at issue was a microprocessor relay equipped with a self-diagnostic feature, which generates an alarm when the self-test results in an error due to relay failure. In addition, the transformer was being protected by a back up relay system consisting of analog and mechanical relays. The facilities are not critical to the BPS. A Notice of Confirmed Violation covering a violation of PRC-005-1 R1 for MACK was filed with FERC under NP09-42-000 on September 25, 2009. On October 23, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC determined that the instant issue is appropriate for FFT treatment because it involves PRC-005-1 R2 and the prior violation involved PRC-005-1 R1. The present issue is separate and distinguished from the prior violation which occurred in 2008 and dealt with associated communication systems not being included in MACK's program even though MACK had and was testing associated communication systems. | To mitigate this issue, MACK: 1) changed the preventative maintenance process by assigning the tasks to plant personnel instead of using outside contracted services; and 2) designed and implemented a tool for the tracking maintenance and testing of protection equipment.
SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEPCO-Trans) | NCR01214 | SERC2012011322 | PRC-008-0 | R2 | On August 8, 2012, SERC sent VEPCO-Trans an initial notice of a Compliance Audit scheduled for February 4, 2013 through February 8, 2013. On October 24, 2012, VEPCO-Trans submitted a Self-Report with two issues to SERC stating that, as a Distribution Provider and Transmission Owner, it had an issue with PRC-008-0 R2 because six Under Frequency Load Shedding (UFLS) relays were tested outside of the defined interval. Furthermore, VEPCO-Trans could not produce the field record maintenance and testing documentation for six additional UFLS relays. In May 2012, VEPCO-Trans discovered that three substations containing two UFLS relays each were tested after the March 31, 2008 date specified in the Protection System Maintenance Program (PSMP). The PSMP required the UFLS relays to be tested annually. SERC staff learned that all six UFLS relays were tested by May 30, 2008. After these six UFLS relays were identified, VEPCO-Trans conducted a review and confirmed that all of the other UFLS relay maintenance and testing had been completed by the date stated in the PSMP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In 2008 VEPCO-Trans reported to SERC a system peak demand of 17,438 MW and a load shed value of 5,497 MW, which equals 31.52%. The three stations (six UFLS relays) tested beyond the compliance date totaled 230 MW. Excluding these three locations would have resulted in a load shed value of 5,266.3 MW (30.20%), which is still in excess of the 30% required by the regional criteria. The six UFLS relays were tested 60 days past the March 31, 2008 testing and maintenance date. When tested, the UFLS relays were found to be functioning properly and should have performed the intended function if called upon to do so. If these relays been called upon to operate due to a UFLS event and had not functioned properly, the 30% load shed value requirement would have still been met. | To mitigate this issue, VEPCO-Trans: 1) maintained and tested the six UFLS relays at issue; and 2) amended the PSMP's testing compliance date to reflect a floating maintenance and testing interval instead of the date-specific maintenance and testing date. This is consistent with other relays on VEPCO-Trans’ transmission system.
SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2012010276 | PRC-011-0 | R2 | On May 17, 2012, Entergy submitted a Self-Report to SERC stating that, as a Transmission Owner and Distribution Provider, it had an issue with PRC-011-0 R2 because it did not have evidence that several metering points associated with its Undervoltage Load Shedding (UVLS) Protection System were properly maintained prior to the inclusion of the metering points in the UVLS program. On July 22, 2010, Entergy implemented a revised UVLS scheme. On that date, Entergy added five additional metering points to the program, making a total of 30 metered points. The five metering points had already been in service prior to being added to the UVLS scheme, but Entergy did not review the maintenance records to assure that the maintenance was current with that required for UVLS scheme metering point applications. Entergy discovered the missing documentation of maintenance and testing during an internal review of maintenance history which was performed in preparation for the 2012 PRC-011-0 Standard Self-Certification. Entergy cannot verify that the five metering points met the maintenance and testing criteria described in its UVLS program document until Entergy conducted scheduled maintenance on the metering points on May 6, 2011. The UVLS system associated with these five metering points protects a geographically limited area in East Texas with a peak load of 293 MW. With the addition of the five points, the UVLS system consists of 30 metering points, 22 batteries, 24 DC control circuits, 30 voltage transformers, and 11 current transformers, for a total of 117 UVLS devices. The five metering points that were not properly maintained constitute 4.27% of the UVLS devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Three of the five affected metering points are redundant with other metering points, so failure of those metering points should neither hinder nor cause the activation of UVLS. The other two metering points had low and high voltage alarms that would alert Entergy personnel in the event of a problem. In addition, the UVLS system protects a geographically limited area in East Texas with a peak load of 293 MW. Furthermore, Entergy subsequently checked the affected metering points and found that they were functioning normally. | To mitigate this issue, Entergy: 1) maintained the five identified metering points; 2) modified its UVLS plan revision process flowchart to provide clarity that voltage monitoring metering points, load monitoring metering points, and load-shed feeder breakers need to be addressed in the UVLS program; and 3) developed a lessons learned and reviewed it with the Entergy personnel responsible for UVLS items. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2012010984 | PRC-023-1 | R1 | On August 27, 2012, Entergy submitted a Self-Report to SERC stating that, as a Transmission Operator, it had an issue with PRC-023-1 R1 after discovering that a transformer overcurrent relay was set below 150% of the transformer’s maximum nameplate rating. This issue was identified during a self-imposed review of PRC-023 setpoints. Setpoints for the transmission line relays had been reviewed prior to the enforcement date of PRC-023-1 (July 1, 2010), but the self-audit revealed that the review had overlooked the autotransformer protection relays. During the ensuing review of the 54 autotransformer relay setpoints, Entergy identified one relay used for protection of a 500 kV transformer that would operate at 149.66% of the highest transformer rating which is 0.34% below the required setpoint of 150%. Entergy reported that the time delay before tripping at 149.66% was 3.3 hours and the delay reduced to 6.1 minutes at 150%. The relay engineer responsible for the setpoint calculation allowed the result to be truncated and rounded to the nearest whole number rather than use Entergy's undocumented practice of using two decimal places. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The historical loading of this transformer has not exceeded 62% of the nameplate rating and the relay would not have operated at loads up to 149.65% of the transformer’s Loadability Rating; thereby, providing opportunity for operator action. Additionally, a loading scenario that exceeds 149.65% for more than three continuous hours would also likely exceed 150% capacity, meaning the relay would likely have actuated even if the setpoint had been correct. Finally, if loading had stopped at 150%, the operators would still have had 6.1 minutes to respond. | To mitigate this issue, Entergy: 1) corrected the relay setting protecting the identified transformer to ensure settings correspond to 150% of the maximum nameplate rating or greater; 2) revised its relay settings procedure and calculations sheets to specify that design settings for overcurrent relays on autotransformers use a target of at least 151% of the maximum nameplate rating; 3) performed an extent of condition on Entergy's PRC-023-1 applicable transformers to ensure that overcurrent protection relays were set at or above 150% of the maximum nameplate rating; 4) implemented a process to ensure and document that PRC-023-1 applicable autotransformer overcurrent settings meet Requirement R1.10; and 5) implemented a process to document limiting factors for PRC-023-1 applicable autotransformer loading. SERC has verified the completion of all mitigation activity.
SERC Reliability Corporation (SERC) | Cottonwood Energy Company LP (Cottonwood) | NCR01210 | SERC2013012003 | VAR-002-1.1b | R3 | On September 18, 2012, SERC sent Cottonwood an initial notice of a Compliance Audit scheduled for March 4, 2013 through March 8, 2013. On February 25, 2013, Cottonwood submitted a Self-Report to SERC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R3 because it failed to notify its Transmission Operator (TOP) of changes in the status of several power system stabilizers (PSSs) within 30 minutes. On January 9, 2013, while performing a required exciter verification data collection test on the exciter and PSS on Unit 2, Cottonwood personnel observed that the data results did not follow the typical model of a PSS signal trending normally. The control room operator turned the Unit 2 PSS off and back on in order to verify the data results. On January 10, 2013, Cottonwood calibrated the PSSs on Units 1, 3, and 4 by toggling the PSSs on and off, which resulted in status changes associated with each unit’s PSS. Cottonwood did not notify the TOP during the test because Cottonwood was testing one generator at a time and Cottonwood had the other units online and running to manage its commitment to load. Cottonwood did not communicate these status changes in the PSSs to the TOP until January 11, 2013 at 3:35 p.m. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). When calibrating the PSSs, Cottonwood removed one unit’s PSS from service at a time. Cottonwood had all eight generators at its facility operating while the calibration was performed over a two-day period. Therefore, Cottonwood had seven generators online with PSSs enabled while the four units’ PSSs were individually calibrated, allowing Cottonwood to manage any changes to the BPS during the testing process. In addition, the longest time a single PSS was out of service was approximately 101 minutes. | To mitigate this issue, Cottonwood: 1) installed e-Notify software that works in conjunction with the plant monitoring software which allows configurable points with the capability to email recipients upon a state change of any given points within the plant monitoring software; 2) developed and posted a list of TOP personnel and system operator phone numbers in the plant control rooms; and 3) performed a review of the VAR-002 procedure with all plant personnel. SERC has verified the completion of all mitigation activities.
Southwest Power Pool Regional Entity (SPP RE) | Golden Spread Panhandle Wind Ranch, LLC (Golden Spread) | NCR11153 | SPP2013011752 | PRC-005-1 | R1; R1.1; R1.2 | On January 30, 2013, Golden Spread submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1 R1. Golden Spread did not specifically include maintenance and testing intervals or a summary of maintenance and testing procedures for its DC control circuitry in its documented Protection System maintenance and testing program (PSMTP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In 2011, during plant commissioning, Golden Spread tested all of its Protection System devices, including DC control circuitry to ensure that its Protection System devices were performing properly. Based on the testing performed in 2011, Golden Spread’s DC control circuitry is only two years into the five-year test interval recommended in the NERC Protection System Maintenance Technical Reference for DC control circuitry. | To mitigate this issue, Golden Spread modified its PSMTP to include maintenance and testing intervals and a summary of maintenance and testing procedures for its DC control circuitry. SPP RE has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (Lea Power) | NCR10301 | SPP2012009183 | PRC-005-1 | R2 | On January 17, 2012, Lea Power, as a Generator Owner, self-reported an issue with PRC-005-1 R2. In its Self-Report, Lea Power stated that it could not provide evidence that it had tested or maintained its three battery banks in 2009, nor could it provide evidence that it had tested or maintained its direct current (DC) control circuits since 2008. More recently, in 2011, Lea Power had failed to test its three station battery banks (100 %) and 92 of its 198 (46.5%) voltage and current transformers within the one and three years intervals, respectively, established in its Protection System maintenance and testing program. Additionally, Lea Power had not tested 28 of its 42 (66.6%) DC control circuits and 28 of its 42 (66.6%) protective relays within the three year interval established in its Protection System maintenance and testing program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Protection Systems at issue belong to one generating facility (Hobbs), consisting of 550 MWs. Hobbs is a new generating unit, commissioned in 2008. All of the Hobbs Protection System devices were functionally tested during the acceptance testing performed at commissioning. Also, the intervals established in Lea Power’s original Protection System maintenance and testing program (one year for station batteries; and three years for DC Control Circuits , protective relays, and instrument transformers) are conservative. The corresponding maximum allowable test intervals established in NERC’s 2007 Protection System Maintenance technical reference are seven years for station batteries, five years for DC Control Circuits and protective relays, and seven years for instrument transformers. All of the implicated protection system devices were tested within the maximum intervals established in the NERC technical reference. In addition, many of the Hobbs’ Protection System devices provide for trouble alarms to a control room manned 24x7. Problems with these Protection System devices would have resulted in operator intervention. The battery bank testing missed in 2009 occurred within one year of commissioning. As to the later battery bank intervals that were missed, testing was performed within one month of the due date. As for the missed intervals for instrument transformers, DC Control Circuits, and protective relays, testing was performed within one to five months of the due date. | Testing was completed on October 18, 2011 for all of the implicated Protection System devices. Manufacturer information, Model, Style information, and Serial Numbers (where applicable) were added to the Protection System Maintenance & Testing Program to assist in recordkeeping retrieval. This information was gathered during both a fall 2011 and spring 2012 outages. The Protection System Maintenance and Testing Program was revised with the updated information on April 3, 2012.
Southwest Power Pool Regional Entity (SPP RE) | Western Farmers Electric Cooperative (WFEC) | NCR01160 | SPP2012011400 | PRC-005-1 | R1; R1.1; R1.2 | During a November 8, 2012, Compliance Audit of WFEC, the SPP RE identified an issue with PRC-005-1 R1.1 and R1.2. WFEC, as a Generator Owner, did not include in its generation protection system maintenance and testing program (Program) the maintenance and testing interval, and the basis (R1.1) or a summary of maintenance and testing procedures (R1.2) for one of its associated communication systems, i.e., a relay pilot wire system. WFEC had previously identified the relay pilot wire system for inclusion in its Program but had mistakenly relied on its engineering consultant’s conclusion that the relay pilot wire system was not an associated communication system under the purview of the PRC-005 Protection System maintenance and testing Standard. The omission of the relay pilot wire system from the Program represented less than one percent (1 of 1,612) of the Protection System devices under WFEC’s Program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although WFEC’s Program did not include its relay pilot wire system, WFEC was continuously monitoring the system via a line current differential relay which provides alarms in the event of any loss of communications to a continuously manned plant control room. Additionally, the relays at each terminal of the relay pilot wire system were being tested in accordance with WFEC’s Program. Finally, the relay pilot wire system at issue represented less than one percent of WFEC's Protection System devices. A Settlement Agreement covering three violations of PRC-005-1 R1, R1 and R2 for WFEC was filed with FERC in 2011. FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering one violation of PRC-005-1 R2 for WFEC was filed with FERC in 2012. FERC issued an order stating it would not engage in further review of the Notice of Penalty. While WFEC’s violation history contains prior violations of PRC-005-1 R1.1 and 1.2, which are similar to the present issue, SPP RE chose FFT treatment for the present issue for the following reasons: 1) the relay pilot wire system was being continuously monitored; 2) WFEC made a good faith effort to include the relay pilot wire system in its Program but mistakenly omitted it; 3) WFEC notified SPP RE prior to the Audit that it had discovered inconsistencies in its consultant’s identification of WFEC’s PRC-005-1 inventory and was taking steps to discover and remediate all issues; 4) WFEC’s cooperation and efforts to improve its compliance culture; and 5) the minimal risk to the BPS posed by this issue. Additionally, the prior two violations of PRC-005-1 R2 are not relevant to the particular set of facts and circumstances in this issue, and do not hinder this issue from being processed as an FFT candidate. | WFEC amended its Program to include the relay pilot wire system, the system’s maintenance and testing interval and its basis, and a summary of the procedure for performing maintenance and testing on the system. SPP RE verified that all mitigating activities were completed.
Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TRE2012011183 | FAC-009-1 | R1 | On August 31, 2012, Oncor, as a Transmission Owner, submitted a Self-Certification identifying an issue with Reliability Standard FAC-009-1 R1. Oncor did not establish facility ratings consistent with Oncor's facility ratings methodology (FRM). Specifically, the 15-mintue ratings for 20 autotransformers were inaccurate. Also, one of these 20 autotransformers, and an additional five autotransformers had faulty cooling equipment, which resulted in inaccurate normal ratings. Both instances constituted inaccurate ratings as defined within Oncor's FRM. The issue period is from June 28, 2007, Oncor's registration date, through August 10, 2012, when the settings were reset. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). The 15-minute ratings were never utilized during the pendency of this issue. In addition, a review of loading levels for this time period for the autotransformers with faulty cooling equipment indicated that load levels were well below the new normal ratings. The inaccurate ratings resulted in incorrect relay overcurrent protection, which posed a possible risk to the protection of the autotransformers but minimal risk to the BPS. | To mitigate this issue, Oncor: 1) reset autotransformer relay settings where engineering studies had been completed; 2) temporarily disabled redundant autotransformer relay, provided protection was not compromised, until new relay settings could be reviewed and installed. All of these relays have been put back in service; 3) initiated a change to autotransformer facility ratings based on existing autotransformer relay setting; and 4) initiated a change to autotransformer facility ratings based on the recalculation of the autotransformer cooling equipment.
Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TRE201100459 | PRC-005-1 | R2; R2.1 | On August 31, 2011, Oncor, as a Transmission Owner and Distribution Provider, submitted a Self-Report to Texas RE, citing non-compliance with Reliability Standard PRC-005-1 R2. Oncor tested its Protection Systems, which are divided into panels, at its different locations. Each panel could include one or more of five Protection Systems. Oncor missed testing on 4 panels, with 4 out of 5 devices on each panel not being tested. One of these 4 panels missed battery testing on the fifth device. From November 30, 2010, thorough August 30, 2011, Oncor missed 4 out of 1,762 panels (0.23%) for testing according to its defined intervals. Oncor identified the following reasons to be the cause of the issue: 1) a work order which was created to test the four Protection Systems was incorrectly closed prior to the work being performed. A new work order was created, but the date did not match the maintenance due date; and 2) a battery was erroneously classified as a non-Oncor asset and therefore was not tested by Oncor in accordance with Oncor's maintenance and testing program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the 4 reported panels that were not tested account for only 0.23% of Oncor’s total of 1,762 relay Protection Systems. Additionally, batteries were not tested at one of the four reported panels but were tested at the other three panels. A Settlement Agreement covering a violation of Reliability Standard PRC-005-1 R2 for Oncor was filed with FERC under NP12-26-000 on April 30, 2012. On May 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE determined that the instant issue is appropriate for a FFT treatment because the prior violation was related to Oncor’s database not being populated correctly. Unlike the prior violation, the instant issue is related to a work order and an ownership classification type of noncompliance. | To Mitigate this issue, Oncor: 1) reviewed the Protection Systems in shared facilities to re-confirm ownership classification and maintenance and testing are properly prioritized and scheduled; 2) instituted a validation procedure to perform periodic assessments to ensure no unexpected intervals have been generated as a result of data entry activity; 3) reviewed and enhanced existing processes for work order data entry and completion; 4) evaluated assets to validate last maintenance test date and create on-going validation tool; 5) developed a training program, training materials, and schedules required to implement the specified process improvements; and 6) reported and documented progress and deliverables, including new procedures, status updates, and completion reports as appropriate. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity, Inc. (Texas RE) | USACE - Tulsa District (USACE) | NCR04156 | TRE2012009734 | MOD-012-0 | R2 | On January 25, 2012, USACE submitted a Self-Report to Texas RE indicating that as a Generator Owner, it had an issue with MOD-012-0 R2. USACE did not provide dynamics system modeling data to its Regional Reliability Organization (RRO), as required by the Standard. In particular, on February 28, 2008, USACE received a dynamics data request from its third-party contractor who had been delegated certain activities related to data submittals. On March 13, 2008, USACE submitted the requested data to the third-party contractor with an expectation that the third-party contractor would forward the data to the RRO. However, during a 2012 internal review, USACE could not find any evidence that the data had been provided to the RRO in 2008. USACE submitted a Self-Report in January 2012, and in December 2012 it submitted the data to the RRO. The duration of this issue was from March 15, 2008, when the data request should have been answered, through December 13, 2012, when the data was supplied to the RRO. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Without the submitted data, the RRO would have relied on simulated data for its analysis, which is a customary practice when data is not readily available. Texas RE determined that the simulation data is very accurate when compared with the modeling data. The data at issue was for current information at the plant, and in the last five years, ERCOT has asked for this data twice. Finally, the nameplate rating of the facility is approximately 80 MW, which further reduced the risk to the BPS. | To mitigate this issue, USACE submitted the revised dynamics data to the RRO via e-mail on December 13, 2012. Texas RE has verified the completion of all mitigation activities.
Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2013011932 | FAC-501-WECC-1 | R2 | On February 15, 2013, PSE submitted a Self-Certification to WECC stating that, as a Transmission Owner that maintains a transmission path in the most current table titled, “Major WECC Transfer Paths in the Bulk Electric System,” it had an issue with FAC-501-WECC-1 R2. PSE stated that it failed to include item 4.b of Attachment 1-FAC-501-WECC-1, “Station Maintenance Details: Contamination Control” in its Transmission Maintenance and Inspection Plan (TMIP). Specifically, PSE stated that it has an internal procedure titled, TL0002: Contamination Control and Insulator Washing (TL0002) that has been included in the TMIP since January 3, 2005 and details PSE’s approach to both station and line insulator contamination control, but that this procedure was referenced in the Transmission Line Maintenance section and did not clearly apply to station maintenance, as required by FAC-501-WECC-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this failure was reduced as a result of existing protections in place during the pendency of the issue. PSE does have an internal document that addressed contamination controls. Specifically, PSE’s internal document TL0002 detailed maintenance intervals and evaluation criteria for substation operations, and this document was available to all employees for the duration of the issue. Furthermore, per this internal procedure, PSE performs contamination control on an as-needed basis. | To mitigate this issue PSE updated its TMIP to include a thorough explanation of its policy for contamination control for both station and line insulators. The updated TMIP also includes reference to PSE's existing contamination control procedure. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Sierra Nevada Region (WASN) | NCR05465 | WECC200801236 | PRC-005-1 | R2 | On December 18, 2008, WASN submitted a Self-Report to WECC stating that, as a Transmission Owner it had an issue with PRC-005-1 R2. Specifically, WASN reported that it had failed to complete maintenance and testing of its DC control circuitry at its Shasta substation (one of 15 WASN substations) within the defined intervals of its Protection System maintenance and testing program. WASN reported that testing was to be completed on December 5, 2008, but, due to several equipment failures, it was unable to complete testing on time. WASN reported that testing was actually completed on December 20, 2008. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WASN performed maintenance and testing on its other Protection System devices at its Shasta substation. Additionally, WASN began maintenance and testing prior to the expiration of the defined interval and only failed to complete testing due to equipment failure. Once WASN realized that testing would not be completed within the defined interval it took immediate steps to resolve the issues preventing testing. Once testing was possible, testing was completed within two weeks of the required date. Further, not only did WASN maintain and test all other protection systems at its Shasta substation within the intervals defined in its program, but WASN also maintained and tested its Protection System devices in accordance with WASN’s defined intervals for the remainder of WASN’s 15 substations. A Settlement Agreement covering a violation of PRC-005-1 R2 for WASN was filed with FERC in the Omnibus filing under NP10-2-000 on October 14, 2009. The instant issue was appropriate for Find, Fix, Track and Report processing because the prior violation also posed a minimal risk to the reliability of the BPS, included only one substation, and testing was late by a limited number of days. | To mitigate this issue, WASN completed annual DC system maintenance at the Shasta Substation. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Hatchet Ridge Wind, LLC (HRWL) | NCR11039 | WECC2013012016 | VAR-002-1.1b | R1 | On February 28, 2013, HRWL submitted a Self-Certification to WECC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R1. Specifically, HRWL reported that its capacitor banks, acting as a part of its automatic voltage control scheme, were operating in manual mode instead of automatic mode as required by the Standard. HRWL reported that its capacitor banks had been operating in manual mode because a relay that controlled its capacitor bank switches was operating in manual mode instead of automatic mode. HRWL reported that, after commissioning, it received indication that the relay controlling the capacitor bank switches was operating in manual mode. HRWL reported that it ignored the indication believing the indication was incorrect. In February of 2013, HRWL reported that it hired a third-party contractor to test the indicator light and, at the time of testing, HRWL was informed that the indicator was correct and that the relay had been operating in manual mode, causing HRWL to operate its generators in a mode other than automatic voltage control mode (with the automatic voltage regulator controlling voltage). HRWL operated in such a mode since it commissioned its units. HRWL reported that it immediately changed the relay controlling its capacitor banks to automatic mode, which in turn, allowed its capacitor banks to operate automatic mode, and informed its Transmission Operator (TOP) of the status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. HRWL's voltage control scheme includes a Load Tap Changer (LTC) located at its point of interconnection with its TOP. The LTC operates independently of the capacitor banks and helps to regulate voltage fluctuations within predefined levels to help limit the potential risks associated with voltage fluctuations. HRWL is a small wind generation facility that produces 101 MW and its load is not considered a base load. HRWL operates at an annual capacity factor of around 20 percent per year. | To mitigate this issue, HRWL: 1) changed the relay controlling its capacitor bank switches from manual mode to automatic mode and notified its TOP of the change within 30 minutes; 2) took preventative steps including adjusting its voltage control setup; developing and implementing improved functional voltage monitoring and control procedures; reviewing, verifying and implementing additional telemetry; and training its personnel on new voltage control procedures.