## Public Non-CIP June FFT Filing
Region | Name of Entity | NCR | Issue Tracking # | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
Florida Reliability Coordinating Council (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2012010053 | BAL-001-0 | R1 | On April 6, 2012, NSB submitted a Self-Report stating that, as a Balancing Authority, it had an issue with BAL-001-0 R1. NSB could not demonstrate that it had operated such that the average of the clock-minute averages (using Area Control Error (ACE)) was less than the limit allowed in the Standard. NSB stated that it had depended upon its services provider to: 1) include NSB within the service provider's own calculation of Control Performance Standards (CPS1) 1; and 2) ensure that NSB’s ACE operated within limits required by the Standard. NSB, however, became aware that the contract with its service provider did not include overlapping service and thus NSB’s CPS1 was not being calculated separately. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NSB was using a long-term interchange contract for supplemental regulation and was supplying its ACE to the entity, Progress Energy Florida, performing that service. NSB's ACE was included in its regulation service provider's so reliability was not impacted. Furthermore, NSB is a very small utility that has non-regulated generation and only 11 miles of BPS transmission line (less than 1% of Regional transmission line) with an all time peak load of 109 MW. | To mitigate this issue, NSB upgraded its supervisory control and data acquisition system with a scheduled change which included a module to automatically calculate CPS 1 and 2 values and meet performance criteria on its own. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2012010054 | BAL-001-0 | R2 | On April 6, 2012, NSB submitted a Self-Report stating that, as a Balancing Authority, it had an issue with BAL-001-0 R2. NSB could not demonstrate that it had operated such that its average Area Control Error (ACE) for at least 90% of clock-ten-minute periods during a calendar month was within the limit allowed in the Standard. NSB stated that it had depended upon its services provider to: 1) include NSB within the service provider's own calculation of Control Performance Standards 2 (CPS2); and 2) ensure that NSB’s ACE operated within limits required by the Standard. NSB, however, became aware that the contract with its service provider did not include overlapping service and thus NSB’s CPS2 was not being calculated separately. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NSB was using a long-term interchange contract for supplemental regulation and was supplying its ACE to the entity, Progress Energy Florida, performing that service. NSB's ACE was included in its regulation service provider's so reliability was not impacted. Furthermore, NSB is a very small utility that has non-regulated generation and only 11 miles of BPS transmission line (less than 1% of Regional transmission line) with an all time peak load of 109 MW. | To mitigate this issue, NSB upgraded its supervisory control and data acquisition system with a scheduled change which included a module to automatically calculate CPS 1 and 2 values and meet performance criteria on its own. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Orlando Utilities Commission (OUC) | NCR00057 | FRCC2012009679 | VAR-001-1 | R6 | On January 31, 2012, NSB submitted a Self-Report that, as a Transmission Operator, it had an issue with VAR-001-1 R6. NSB did not know the status of all transmission Reactive Power resources, including the status of voltage regulators. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The voltage regulator was not set in a manual mode but rather was set to automatic in MVAR control, and the actual mode of control for the unit’s regulator did provide a level of voltage stability to the BPS. | To mitigate this issue, OUC: 1) implemented a process with procedure and training to verbally verify and record status; 2) implemented unit excitation status telemetry; and 3) developed coordination procedure and training. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Orlando Utilities Commission (OUC) | NCR00057 | FRCC2012009954 | FAC-009-1 | R1 | On March 23, 2012, FRCC conducted a Compliance Audit of NSB and determined that NSB, as a Generator Owner, had an issue with FAC-009-1 R1. NSB did not have sufficient evidence to demonstrate it had established Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology. Specifically, Indian River Plant (IRP) Combustion Turbine (CT)-C, CT-D, and Stanton Energy Center Combined Cycle (SEC) B had determined a most limiting piece of equipment for those facilities. In both cases, however all component ratings from the methodology were not evaluated and therefore the most limiting piece of equipment could not be substantiated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OUC was operating to manufacturer's ratings, had proven operational history with no actual impact based on the established ratings, and once the complete ratings were established there was no change in the most limiting piece of equipment. | To mitigate this issue, OUC: 1) updated their facility ratings analysis documents for the units IRP CT C and IRP CT D based on vendor responses to clearly identify the missing component ratings; 2) updated their facility ratings analysis document for the SEC CC B based on vendor documentation and engineering analysis. The engineering analysis established the overall Facility Ratings and documented any acceptance of loss-of-life on any component which would otherwise limit the output of the unit or limit the unit output; 3) identified the missing ratings for all the IRP units (with no change in rating after the review of most limiting factors); and 4) substantiated the existing generator rating associated with SEC unit B as being the most limiting since the generator output is constrained by the Combustion Turbine output capability. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Orlando Utilities Commission (OUC) | NCR00057 | FRCC2012009955 | MOD-001-1a | R2; R2.2; R2.3 | On March 23, 2012, FRCC conducted a Compliance Audit of OUC and determined that OUC, as a Transmission Service Provider, had an issue with MOD-001-1a R2. In calculating firm Available Transfer Capability (ATC), OUC did not subtract Transmission Reliability Margin (TRM) from Total Transfer Capability (TTC) as described in its Area Interchange Methodology (MOD-028-1). Specifically, no TRM was subtracted for days two through seven (R2.2 and 2.3), no TRM was subtracted from the sum of the facility ratings segment (R2), and no TRM was calculated after April 30, 2012 (resulting in no TRM being calculated for at least the next 12 months) (R2.3). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OUC had three import and three export paths, and there were no wheeling paths through OUC. In addition, when making a reservation it would need to be made through both the sending and receiving Transmission Service Providers (TSPs) on the path. Even though OUC was not correctly calculating firm ATC (by not subtracting TRM), the other TSP in the path should have been calculating firm ATC correctly by subtracting TRM and in any case that OUC would have tried to oversell firm ATC, the reservation would have been denied by the partner TSP. Furthermore, the sum of the facility (line) ratings are typically larger than the calculated TTC value and would not be a limiting factor even if TRM is not subtracted correctly. | To mitigate this issue, OUC: 1) began a solution identification; 2) had further discussion at Florida Transmission Capability Determination Group to draft TRM language to handle the static versus engine segment TRM; 3) issued a revised TRM implementation document (ID); 4) started utilizing the TRM_Adder_Hourly calculation function; 5) increased the end date on the TRM entries such that they were more than 26 months into the future so that values were available through the full horizon of calculations; and 6) reviewed and corrected any issues identified; modified TRM ID to correctly reflect the way TRM is calculated. Specifically, this is documenting the changes from a static TRM calculation to TRM that remains constant and then has a gradual reduction. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Orlando Utilities Commission (OUC) | NCR00057 | FRCC2012009956 | MOD-001-1a | R3; R3.1 | On March 23, 2012, FRCC conducted a Compliance Audit of OUC and determined that, as a Transmission Service Provider, OUC had an issue with MOD-001-1a R3. OUC failed to keep current its Available Transfer Capability Implementation Document (ATCID) to include the following information: a description of how the selected methodology has been implemented in such detail that, given the same information used by the Transmission Service Provider (TSP), the results of the Available Transfer Capability (ATC) calculations can be validated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OUC had three import and three export paths. There were no wheeling paths through OUC. In addition, when making a reservation, the reservation would need to be made through both the sending and receiving TSPs on the path. Even though OUC was not correctly calculating firm ATC (by not subtracting TRM), the other TSP in the path should have been calculating firm ATC correctly by subtracting TRM and in the case that OUC would have tried to oversell firm ATC, the reservation would have been denied by the partner TSP. In addition, the sum of the facility (line) ratings are typically larger than the calculated TTC value and would not be a limiting factor even if TRM is not subtracted correctly. | To mitigate this issue, OUC: 1) began a solution identification; 2) had further discussion at Florida Transmission Capability Determination Group to draft TRM language to handle the static versus engine segment TRM; 3) issued a revised TRM implementation document (ID); 4) started utilizing the TRM_Adder_Hourly calculation function; 5) increased the end date on the TRM entries such that they were more than 26 months into the future so that values were available through the full horizon of calculations; and 6) reviewed and corrected any issues identified; modified TRM ID to correctly reflect the way TRM is calculated. Specifically, this is documenting the changes from a static TRM calculation to TRM that remains constant and then has a gradual reduction. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Orlando Utilities Commission (OUC) | NCR00057 | FRCC2012009957 | MOD-008-1 | R1; R1.3.2; R1.3.3 | On March 23, 2012, FRCC conducted a Compliance Audit of OUC and determined that, as a Transmission Service Provider, it had an issue with MOD-008-1 R1. OUC had prepared but did not keep current its Transmission Reliability Margin (TRM) Implementation Document as required by the Standard. Specifically, the document states that OUC will subtract TRM from Total Transfer Capability (TTC) to calculate firm Available Transfer Capability (ATC), which had not been done. For R1.3.2 and R1.3.3, OUC did not actually document the process that had been implemented as no TRM was subtracted for days two through seven, no TRM was subtracted from the sum of the facility ratings segment, and no TRM was applied after April 30, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OUC had three import and three export paths. There were no wheeling paths through OUC. In addition, when making a reservation, the reservation would need to be made through both the sending and receiving TSPs on the path. Even though OUC was not correctly calculating firm ATC (by not subtracting TRM), the other TSP in the path should have been calculating firm ATC correctly by subtracting TRM and in the case that OUC would have tried to oversell firm ATC, the reservation would have been denied by the partner TSP. In addition the sum of the facility (line) ratings are typically larger than the calculated TTC value and would not be a limiting factor even if TRM is not subtracted correctly. | To mitigate this issue, OUC: 1) began solution identification; 2) had further discussion at Florida Transmission Capability Determination Group to draft TRM language to handle the static versus engine segment TRM; 3) started utilizing the TRM_Adder_Hourly calculation function; 4) increased the end date on the TRM entries such that they were more than 26 months into the future so that values were available through the full horizon of calculations; and 5) modified the TRM ID document to correctly reflect the way TRM is calculated. Specifically this is documenting the changes from a static TRM calculation to TRM that remains constant and then has a gradual reduction. FRCC has verified the completion of all mitigation activity.
Florida Reliability Coordinating Council (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC2013012470 | EOP-005-1 | R2 | On June 7, 2013, FRCC conducted a Compliance Audit of PEF and determined that PEF as a Transmission Operator had an issue with EOP-005-1 R2. PEF failed to update its restoration plan when it made a change to its power system network. Specifically, PEF had a change in a loop section of its sample restoration plan provided to the system operators. This change was due to the removal of a 115 kV line. The 115 kV line was retired on December 17, 2012 and PEF removed the line from the one-line of the Energy Management System (EMS). The line was fully removed from the EMS on February 20, 2013. The restoration plan was corrected on June 5, 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This was a documentation issue. PEF performed simulations on January 31, 2013 and April 8, 2013 and the flexibility of the restoration plan allows for the closing of alternate lines, therefore the unavailability of this 115 kV line during multiple simulations had no impact in the restoration of the system. | To mitigate this issue, PEF: 1) immediately updated its restoration plan when it was discovered that there was an discrepancy in the restoration plan; and 2) placed subject matter experts (SMEs) for EOP-005 on the mailing list of the Equipment Status Report. This gives the SMEs notification of changes on the PEF power system network prior to the changes being implemented. The Equipment Status Report is an FRCC document that shows planned changes to the BPS in the FRCC region. FRCC has verified the completion of all mitigation activity.
Midwest Reliability Organization (MRO) | High Prairie Wind Farm II, LLC (HPWF) | NCR10161 | MRO2012009682 | PRC-005-1 | R2; R2.1 | During a Compliance Audit conducted between November 15, 2011 and November 17, 2011, MRO discovered that HPWF, as a Generator Operator and Generator Owner, failed to provide maintenance and testing evidence for one of its Protection System station batteries in accordance with the intervals defined in its Protection System maintenance and testing program, as required by PRC-005-1 R2.1. Specifically, HPWF failed to perform annual station battery testing in 2008. HPWF's generating plant began commercial operation in November 2007. Although HPWF performed a monthly test in November 2007 and December 2007 and a quarterly test in 2009, those tests were only a subset of the required annual test. HPWF's Protection System maintenance and testing program requires an annual test, not a monthly or quarterly test. Although HPWF was required to complete the annual test on or before November 2008, it did not perform the full annual test again until September 2009. Therefore, HPWF missed its annual maintenance and testing interval by nine months. MRO requested that HPWF perform a comprehensive review of its Protection System maintenance and testing records. HPWF reported that it has 9 relays, 5 voltage and current sensing devices, 2 station batteries, and 9 DC control circuits subject to PRC-005-1 R2. Of those devices, HPWF failed to provide maintenance and testing records for one station battery, or 4% of its devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). HPWF missed maintenance and testing for one station battery at one substation for one testing interval by approximately nine months. The plant began commercial operation in November 2007, and HPWF missed the maintenance and testing interval in November 2008. Therefore, the station battery was one year old when it missed its required interval. The facility consists of total installed capacity of 100.65 MW, provided by 61 1.65 MW turbines. Based on the duration of the issue, the other battery testing HPWF performed on a monthly and quarterly basis, the age of the station battery, and the size of HPWF, MRO determined that this issue posed a minimal risk to the BPS. | To mitigate the issue, HPWF: 1) performed the annual battery test on September 15, 2009; 2) implemented a more comprehensive battery testing procedure, to include additional monthly battery inspections in addition to annual battery testing; and 3) developed an internal process to integrate the management of all of its facility testing and maintenance processes and procedures. MRO has verified the completion of all mitigation activity.
Midwest Reliability Organization (MRO) | Muscatine Power & Water (Board Of Water, Electric & Communications) (MPW) | NCR00967 | MRO2013012071 | PRC-005-1b | R2 | On February 28, 2013, MPW submitted a Self-Report to MRO stating that, as a Transmission Owner and Distribution Provider, it had an issue with PRC-005-1b R2.1. MPW failed to provide evidence that the station battery tied to the Protection System devices was maintained and tested within the defined intervals pursuant to the Reliability Standard. Under MPW's Protection System maintenance and testing program, MPW is required to perform a capacity test on the station battery at its unit 9 161 kV substation within six-year intervals. MPW's capacity test was completed on July 19, 2006, which required MPW to complete its next capacity test by July 19, 2012. However, that test was completed on February 19, 2013, which was 217 days past due. MPW received an Administrative Citation for MRO201000194, a previous violation of PRC-005-1 R2, which was filed with FERC under NP11-133-000 on February 28, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In mitigating the previous violation, MPW provided in-house compliance training to substation personnel and completed an inventory of all Protection System components for the unit 9 161 kV substation, but failed to add an automatic notification for capacity testing. As a result, MPW missed the scheduled capacity testing by 217 days. MRO determined that the instant issue is appropriate for FFT treatment because it posed a minimal risk to the BPS based on the facts and that there are no other issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The affected station battery comprised less than one percent of MPW's Protection System elements and the six-year testing interval was missed by seven months. In addition, MPW is a small entity located in Muscatine, Iowa with limited possible impact on the BPS. MPW serves approximately 11,300 electric customers owns and operates one BPS generator and 33 miles of 161 kV transmission line. The violation relates to only batteries at one transmission substation. Further, in addition to capacity testing every six years, MPW performs more frequent tests relating to the substation and battery to ensure proper performance. Lastly, the unit 9 161 kV substation batteries are monitored by MPW's supervisory control and data acquisition system, which provides continuous monitoring of the battery charger, DC system ground conditions, and the DC station service voltage. | To mitigate this issue, MPW: 1) performed the capacity test; 2) performed a comprehensive review of all MPW elements (both generation and transmission), subject to PRC-005-1b R2, to verify the maintenance activities described in the MPW Protection System maintenance and testing program have been performed within the required intervals; 3) created a work order entered into MPW's computerized maintenance management system (CHAMPS) on a six-year interval to create a purchase order for a capacity test; 4) created an auto-generated daily email from CHAMPS that lists all maintenance and testing activities on all MPW elements subject to PRC-005 and PRC-008 within 30 days of its due date for the managers of Reliability Standards compliance and transmission and distribution; 5) created a monthly reminder in Lotus Notes for the manager of Reliability Standards compliance to perform a monthly check of PRC-005 test records to verify that the PRC-005 maintenance activities are on schedule and added the capacity test task to the list; and 6) entered all maintenance work orders and station batteries subject to PRC-005-1b R2, into CHAMPS. MRO verified the completion of all mitigation activity on April 11, 2013.
ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Edison Company (ComEd) | NCR08013 | RFC2012010778 | PRC-005-1a | R2; R2.1 | On June 30, 2012, ComEd submitted a Self-Report to ReliabilityFirst stating that, as a Distribution Provider, it had an issue with PRC-005-1a R2.1. During the review of a daily preventative maintenance look-ahead report, ComEd found that Protection System maintenance tasks were identified as having a due date beyond their interval plus grace period as defined in ComEd’s Protection System maintenance and testing program. ComEd discovered that a ComEd employee’s keystroke error during a data entry resulted in a date change to certain preventive maintenance tasks for four batteries from a 2011 due date to a 2012 due date. Since work orders are generated automatically 45 days in advance of the due date based on these system tasks, ComEd did not timely generate the work orders for the four associated battery inspections and the devices were not maintained and tested within the defined intervals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue implicated four of ComEd’s 1,737 total batteries (0.23% of ComEd batteries) and 7,839 total Protection System devices (0.05% of all ComEd Protection System devices). ComEd performed all other battery maintenance and testing during the time frame of the issue. ComEd reviewed all available data during the timeframe of the issue and determined that no battery health concerns existed to pose a risk to the functionality and performance of the implicated batteries. Two of the implicated batteries, those batteries located at Station 22, were relatively new and ComEd’s surveillance data indicated healthy new batteries. For these two Station 22 batteries, ComEd missed the quarterly inspections, but continued to perform all other battery maintenance during the timeframe of the issue. For the remaining two batteries, those batteries located at Station 16, ComEd performed other testing, during the timeframe of the issue, including annual and quarterly testing that were more rigorous than the missed 10-week inspections. | To mitigate this issue, ComEd: 1) conducted an initial preliminary investigation of maintenance inspection and testing tasks to confirm the continued reliability and safety of the Bulk Electric System; 2) immediately completed the identified outstanding tasks and implemented additional reporting, oversight and management controls; and 3) initiated an investigation to identify all issues and causal factors, implemented other necessary immediate remediation activities, defined a formal Mitigation Plan, and assigned appropriate corrective actions to assure full compliance for maintenance of all Protection System components.
ReliabilityFirst Corporation (ReliabilityFirst) | Delaware City Refining Company LLC (DCR) | NCR11173 | RFC2012011201 | VAR-002-1.1b | R1 | On October 1, 2012, DCR submitted a Self-Certification to ReliabilityFirst stating that, as a Generator Operator and Generator Owner, it had an issue with VAR-002-1.1b R1. Certain of DCR's generators did not always operate in automatic voltage control mode and DCR failed to notify its Transmission Operator (TOP), PJM Interconnection (PJM), of the manual voltage control mode operation as required by VAR-002-1.1b. Specifically, DCR operates four of its steam generators in manual voltage control mode, in order to increase stability of those units. Historically, DCR has found that this manual voltage control mode has provided greater stability than operating the exciters in automatic voltage control mode, in which voltages exhibited large oscillations between the machines. These four generators are directly connected to the same 13.8 kV bus without any isolation transformers, unlike DCR’s two combustion turbine generators, which are effectively controlled by automatic voltage regulation. DCR has operated these steam generators in manual voltage control mode since it acquired the plant and restarted it from an idle state in 2011. Operators control voltage by adjusting transformer taps and adjusting generator exciter output. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DCR’s operation of its steam generators in manual voltage control mode contributes to the stability of those generators and overall BPS stability and reliability. DCR subsequently agreed with its TOP that it should continue to operate in manual control mode, indicating that this operating mode was proper. Finally, DCR’s primary purpose for generating electricity is to ensure the reliable operation of the refinery itself. | To mitigate this issue, DCR obtained an agreement with PJM to operate in manual control mode until further notice. DCR contacted PJM in September 2012 and obtained an agreement to operate in manual voltage control mode until further notice, pursuant to PJM’s Manual 14D. PJM Manual 14D addresses generator operational requirements. It states that generators shall be operated with automatic voltage regulators in service, with exceptions for outages. PJM is considering the condition of these generators a submitted outage by DCR.
ReliabilityFirst Corporation (ReliabilityFirst) | Delaware City Refining Company LLC (DCR) | NCR11173 | RFC2012011202 | VAR-002-1.1b | R3 | On October 1, 2012, DCR submitted a Self-Certification to ReliabilityFirst stating that, as a Generator Operator and Generator Owner, it had an issue with VAR-002-1.1b R3. Certain of DCR's generators did not always operate in automatic voltage control mode and DCR failed to notify its Transmission Operator (TOP), PJM Interconnection (PJM), of the change in status to manual voltage control mode operation as required by VAR-002-1.1b. Specifically, DCR operates four of its steam generators in manual voltage control mode, in order to increase stability of those units. Historically, DCR has found that this manual voltage control mode has provided greater stability than operating the exciters in automatic voltage control mode, in which voltages exhibited large oscillations between the machines. These four generators are directly connected to the same 13.8 kV bus without any isolation transformers, unlike DCR’s two combustion turbine generators, which are effectively controlled by automatic voltage regulation. DCR has operated these steam generators in manual voltage control mode since it acquired the plant and restarted it from an idle state in 2011. Operators control voltage by adjusting transformer taps and adjusting generator exciter output. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DCR’s operation of its steam generators in manual voltage control mode contributes to the stability of those generators and overall BPS stability and reliability. DCR subsequently agreed with its TOP that it should continue to operate in manual control mode, indicating that this operating mode was proper. Finally, DCR’s primary purpose for generating electricity is to ensure the reliable operation of the refinery itself. | To mitigate this issue, DCR obtained an agreement with PJM to operate in manual control mode until further notice. DCR contacted PJM in September 2012 and obtained an agreement to operate in manual voltage control mode until further notice, pursuant to PJM’s Manual 14D. PJM Manual 14D addresses generator operational requirements. It states that generators shall be operated with automatic voltage regulators in service, with exceptions for outages. PJM is considering the condition of these generators a submitted outage by DCR.
ReliabilityFirst Corporation (ReliabilityFirst) | PPL Holtwood, LLC (PPL Holtwood) | NCR00886 | RFC2013012101 | PRC-005-1b | R2 | On February 11, 2013, PPL Holtwood submitted a Self-Report to ReliabilityFirst that, as a Generator Owner, it had an issue with PRC-005-1b R2. In 2011, PPL Generation, LLC, PPL Holtwood's parent company, established a separate relay test group as the group responsible for relay protection at all of the Eastern Fossil & Hydro group subsidiaries, including PPL Holtwood. In December 2012, the relay test group conducted a review to compare a database developed with information used to track testing prior to January 2012. During this review, the relay test group discovered that PPL Holtwood failed to perform maintenance and testing on one relay within the defined interval. The defined interval for this relay is six years with a 10% grace period. PPL Holtwood last performed maintenance and testing on this relay on September 28, 2011, therefore testing was due May 3, 2012. On December 18, 2012, the relay test group identified this missing maintenance and testing, and on December 19, 2012, PPL Holtwood performed maintenance and testing on this relay. When PPL Holtwood performed maintenance and testing on this relay, which constitutes one of PPL Holtwood’s 237 relays, PPL Holtwood determined that the relay was functioning properly. The relay test group discovered no additional relays with missing maintenance and testing. This missed maintenance and testing occurred prior to the relay test group’s monitoring of PPL Holtwood’s maintenance and testing of relays. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PPL Holtwood has alarming in place for certain of its Protection System devices. The primary and backup lockout relays alarm in the control room by lighting indicating lights labeled as “Primary Lockout Trip” and “Backup Lockout Trip.” The span differential protection and exciter trouble alarms are also wired to the control room as well as numerous transformer variables such as winding temperature and oil level. In addition, PPL Holtwood has backup relay protection on the generator buses and generator step-up transformers. Furthermore, the misoperation of this relay would affect only one 12 MW hydro generator. When PPL Holtwood performed maintenance and testing on this relay, it discovered the relay to be in working condition. | To mitigate this issue, PPL Holtwood performed maintenance and testing on the relay.
ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (Eagle Point) | NCR11228 | RFC2012010770 | FAC-008-1 | R1 | On July 1, 2012 Eagle Point submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it had an issue with FAC-008-1 R1. The Facility Ratings methodology for Eagle Point did not include a statement that a Facility Rating shall equal the most limiting applicable equipment rating of the individual equipment that comprises that facility, as required by FAC-008-1 R1.1. In addition, the Facility Ratings methodology for Eagle Point did not include the following equipment as required by FAC-008 R1.2.2: relay protective devices; terminal equipment; and series and shunt compensation devices. Finally, the Facility Ratings methodology for Eagle Point did not include the source of the Facility Ratings. Specifically, the Facility Ratings methodology did not document the consideration of Facility Ratings provided by equipment manufacturers (FAC-008-1 R1.3.1), design criteria (FAC-008-1 R1.3.2), ambient conditions (FAC-008-1 R1.3.3), operating limitations (FAC-008-1 R1.3.4), and other assumptions (FAC-008-1 R1.3.5). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The steam turbine generator has been and continues to be the most limiting element of the Facility. | To mitigate this issue, Eagle Point 1) hired a qualified electrical engineering consultant to provide technical expertise in reviewing Facility Rating documentation. The consultant completed a review of equipment lists and inserted omitted equipment and equipment descriptions. The consultant also established documented Facility Ratings for all equipment; and 2) reviewed the consultant documentation, determined the final Facility Rating, and provided it to appropriate entities for review.
ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (Eagle Point) | NCR11228 | RFC2012010771 | FAC-009-1 | R1 | On July 1, 2012 Eagle Point submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it had an issue with FAC-009-1 R1. Eagle Point did not have Facility Ratings for relay protective devices, terminal equipment, and series and shunt compensation devices, as required by FAC-009-1 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The steam turbine generator has been and continues to be the most limiting element of the Facility. | To mitigate this issue, Eagle Point: 1) hired a qualified electrical engineering consultant to provide technical expertise in reviewing Facility Rating documentation. The consultant completed a review of equipment lists and inserted omitted equipment and equipment descriptions. The consultant also established documented Facility Ratings for all equipment; and 2) reviewed the consultant documentation, determined the final Facility Rating, and provided it to appropriate entities for review.
ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (Eagle Point) | NCR11228 | RFC2012010772 | FAC-008-1 | R2 | On July 1, 2012 Eagle Point submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it had an issue with FAC-008-1 R2. On June 8, 2012, Eagle Point’s Transmission Operator (TOP) requested its Facility Ratings methodology. Eagle Point was unable to provide its TOP with a complete Facility Ratings methodology document because it was still in the process of determining whether the December 19, 2011 Facility Ratings methodology was accurate. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. To the best of Eagle Point’s knowledge, no other entity had previously requested its Facility Ratings Methodology, therefore this was an isolated incident. In addition, when Eagle Point was able to provide the TOP with the methodology document, the TOP indicated it was no longer necessary, reducing the likelihood that this issue would have resulted in a reliability impact. The reason Eagle Point could not provide a complete methodology was because it was verifying the accuracy of the methodology, which demonstrates that Eagle Point had awareness of the issue and was working to address all facility ratings methodology issues. | To mitigate this issue, Eagle Point: 1) hired a qualified electrical engineering consultant to provide technical expertise in reviewing Facility Rating documentation. The consultant completed a review of equipment lists and inserted omitted equipment and equipment descriptions. The consultant also established documented Facility Ratings for all equipment; and 2) reviewed the consultant documentation, determined the final Facility Rating, and provided it to appropriate entities for review.
ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (Eagle Point) | NCR11228 | RFC2012010774 | PRC-005-1 | R1 | On July 1, 2012 Eagle Point submitted a Self-Report to ReliabilityFirst stating that, as a Generator Owner, it had an issue with PRC-005-1 R1. Although Eagle Point has in place a Protection System maintenance and testing program for Protection System devices, the program does not include maintenance and testing intervals and their basis for voltage and current sensing devices and direct current control circuitry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Eagle Point is interconnected by two separate and completely redundant 230 kV feeds from the same interconnection location. Eagle Point also has a backup battery system to supply power to the relays in the event of a failure. In addition, Eagle Point has an alarm system in place that alerts to the control room. Until May 3, 2012, Eagle Point was registered on the NERC Compliance Registry as Sunoco Power Generation LLC (Sunoco). On April 2, 2012, this facility was sold to Thunderbird Power Holdings, LLC, and the new facility name is Eagle Point. Eagle Point discovered this issue in its reviews after purchasing the facility. To the best of Eagle Point’s knowledge, maintenance and testing on all relays was performed within their defined maintenance and testing intervals prior to Eagle Point owning the facility. | To mitigate this issue, Eagle Point 1) hired a qualified electrical engineering consultant to review Sunoco documents, establish a fully consolidated maintenance and testing program, and analyze for gaps in the maintenance under that program; 2) transferred the computerized maintenance management system data from the Sunoco system to the Eagle Point system and reviewed that data and any paper data from Sunoco; and 3) established a consolidated Protection System maintenance and testing program, compared that program to the previous program, and performed a gap analysis to determine a schedule for completing all maintenance and testing pursuant to that program.
ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (Eagle Point) | NCR11228 | RFC2012010769 | COM-002-2 | R1 | On July 1, 2012 Eagle Point submitted a Self-Report to ReliabilityFirst that, as a Generator Owner, it had an issue with COM-002-2 R1. The list of communications for the Eagle Point facility did not include a complete list of all voice communications, including cell phones, and data communications, including email and internet communication. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Since April 2, 2012, Eagle Point had some communications in place, which were staffed and available for addressing a real-time emergency condition at all times. Prior to April 2, 2012, Eagle Point was under different ownership, so Eagle Point is not knowledgeable regarding staffing. | To mitigate this issue, Eagle Point 1) completed the installation of a new telephone system that includes a PJM Interconnection hotline number; and 2) completed installation of the data and network system, revised the communications list and diagram to reflect the new telephone numbers and data communications, notified appropriate entities of the communication changes for emergency communication, and established a procedure for operators indicating when they should notify appropriate entities due to disruption or possible disruption of communication paths.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2011001250 | PRC-008-0 | R2 | On November 29, 2011, NIPSCO submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it had an issue with PRC-008-0 R2. NIPSCO discovered that it inadvertently entered a six-year maintenance and testing interval, rather than the two year interval required by its Under Frequency Load Shedding (UFLS) program, into its relay tracking system database for eight UFLS relays. As a result, NIPSCO did not test or maintain the eight UFLS relays within its UFLS program’s two-year interval. NIPSCO has 167 UFLS relays on its system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The eight relays at issue are microprocessor-based and perform self-testing and alarming. Additionally, all eight relays are monitored by NIPSCO through its distribution management system, which notifies operators of any alarms associated with the relays. Finally, upon performing maintenance and testing on the eight UFLS relays at issue, NIPSCO determined that each relay was set properly and would have responded correctly to an under frequency event. | To mitigate this issue, NIPSCO: 1) performed maintenance and testing on the eight UFLS relays at issue; and 2) assigned the UFLS relays at issue the correct two-year interval in its Relay Tracking System database. On June 14, 2012, ReliabilityFirst verified NIPSCO successfully completed the mitigation plan in accordance with its terms and conditions.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company GO GOP (NIPSCO) | NCR02610 | RFC2012010009 | PRC-005-1 | R1 | From December 6, 2011 through December 13, 2011, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that NIPSCO, as a Generator Owner, had an issue with PRC-005-1 R1. NIPSCO did not address DC Control circuitry in its Protection System maintenance and testing program (Program). Therefore, NIPSCO did not include the maintenance and testing interval and a basis for DC control circuitry or a summary of maintenance and testing procedures for DC control circuitry in its Program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue is a documentation error. It is a documentation error because NIPSCO was conducting functional tests of its DC control circuitry for the duration of the issue. NIPSCO added DC control circuitry to its generator Program prior to ReliabilityFirst’s Compliance Audit, however, the revised generator Program was not reviewed during the Compliance Audit because NIPSCO revised it after ReliabilityFirst’s initial 90 day data request. Specifically, the generator relays utilize the DC control circuitry each time the unit is shut down, effectively testing DC control circuitry. On average, NIPSCO shuts down and restarts its generation units on average at least 10 times per year. ReliabilityFirst accepted NIPSCO’s revised Program, which requires NIPSCO to test and maintain its DC control circuits on a six-year interval, as part of NIPSCO’s Mitigation Plan. NIPSCO can provide logs for the circuits for each shutdown event which demonstrates that it performed functional tests of its DC control circuitry for the duration of the issue. | To mitigate this issue, NIPSCO: 1) revised its Program to include a maintenance and testing interval, a basis for the interval, and a summary of its maintenance and testing procedures for DC control circuitry; 2) will perform, on an ongoing basis, maintenance and testing described in its Program in conjunction with the functional testing performed when it shuts down and restarts its generating units. On December 26, 2012, ReliabilityFirst verified that NIPSCO completed the mitigation activities described in its Mitigation Plan.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2012010012 | EOP-005-1 | R4 | From December 6, 2011 through December 13, 2011, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that NIPSCO, as a Transmission Operator (TOP), had an issue with EOP-005-1 R4. NIPSCO did not coordinate its restoration plans with all the Generation Owners (GOs), specifically the Independent Power Producers (IPPs), within NIPSCO’s area. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The IPPs within NIPSCO’s area do not participate in NIPSCO’s restoration plans. The IPPs in NIPSCO’s area have no blackstart capability and cannot unilaterally inject energy onto the BPS. Furthermore, NIPSCO does not provide cranking power to any of the IPPs in its area as part of its restoration plans. Finally, NIPSCO coordinated its restoration plan with all non-IPP GOs, Balancing Authorities, and Reliability Coordinators in its area as well as neighboring TOPs. | To mitigate this issue, NIPSCO: 1) provided a redacted version of its System Restoration Plans to the IPPs within NIPSCO’s area; and 2) provided all IPPs with the opportunity to view the complete System Restoration Plan upon request. On December 18, 2012, ReliabilityFirst verified that NIPSCO completed the mitigation activities described in its Mitigation Plan.
ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2012010013 | EOP-005-1 | R7 | From December 6, 2011 through December 13, 2011, ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that NIPSCO, as a Transmission Operator and Balancing Authority, had an issue with EOP-005-1 R7. NIPSCO did not verify each restoration procedure by testing or simulation. Specifically, NIPSCO did not verify that each restoration procedure that use intertie assistance were safe and effective in the restoration of its system. NIPSCO’s primary restoration procedure is its black start procedure, which NIPSCO tested and verified pursuant to EOP-005-1 R7. However, NIPSCO included seven attachments to its black start procedure that consisted of restoration procedures using intertie assistance. Although NIPSCO did test and validate its primary intertie restoration procedure, it did not test the six other intertie restoration procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NIPSCO tested and verified its black start restoration procedure and primary intertie restoration procedure pursuant to EOP-005-1 R7. Additionally, following the Compliance Audit, NIPSCO verified all its intertie assistance restoration procedures by simulation. NIPSCO determined that each intertie restoration procedure was a viable restoration solution for its system and would have functioned as intended for the duration of the issue. | To mitigate this issue, NIPSCO verified by simulation that all previously unverified intertie assistance restoration plans are effective for the restoration of its system. On December 18, 2012, ReliabilityFirst verified that NIPSCO completed the mitigation activities described in its Mitigation Plan.
ReliabilityFirst Corporation (ReliabilityFirst) | LSP University Park, LLC (LSP University Park) | NCR11107 | RFC2012010351 | FAC-008-1 | R1; R1.2 | On May 11, 2012, LSP University Park, as a Generator Owner, self-reported an issue with FAC-008-1 R1. Due to an administrative oversight, LSP failed to include all required elements, as well as Normal and Emergency ratings, in its Facility Ratings Methodology. LSP University Park failed to address the following equipment in its Facility Ratings Methodology: transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that none of its generators could exceed the limitations of the most limiting element, which is the generator step-up transformer. Additionally, peak generation for the facility is below the limits established by both the original and revised ratings. Lastly, LSP University Park’s revised Facility Ratings Methodology considers Normal and Emergency ratings to be equal. | To mitigate this issue, LSP University Park: 1) revised its Facility Ratings Methodology to include the missing equipment; and 2) modified its Facility Ratings Methodology to include both Normal and Emergency Ratings.
ReliabilityFirst Corporation (ReliabilityFirst) | LSP University Park, LLC (LSP University Park) | NCR11107 | RFC2012010352 | FAC-009-1 | R1 | On May 11, 2012, LSP University Park, as a Generator Owner, self-reported an issue with FAC-009-1 R1. LSP University Park failed to establish Facility Ratings that were consistent with its Facility Ratings Methodology. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that although LSP University Park’s most limiting applicable equipment rating changed as a result of updating its Facility Ratings Methodology, that equipment component was included in the original Facility Ratings. | To mitigate this issue, LSP University Park updated its Facility Ratings to be consistent with its Facility Ratings Methodology.
ReliabilityFirst Corporation (ReliabilityFirst) | LSP University Park, LLC (LSP University Park) | NCR11107 | RFC2012010353 | PRC-005-1 | R1 | On May 11, 2012, LSP University Park, as a Generator Owner, self-reported an issue with PRC-005-1 R1. LSP University Park did not implement a fully-developed Protection System maintenance and testing program (Program) at facility registration. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that LSP University Park had been performing some maintenance and testing despite the absence of a formal Program. During a Compliance Audit, LSP University Park provided ReliabilityFirst with: records of testing and maintenance on station batteries in 2009 and 2012; testing and maintenance on relays in 2005 and 2009; and commissioning test records for instrument transformers in 2002. | To mitigate this issue, LSP University Park: 1) identified devices to be included in the Program; 2) researched and identified maintenance and testing intervals; 3) created summaries of maintenance and testing procedures; 4) reviewed and approved the Program; and 5) provided training on the Program to relevant personnel.
SERC Reliability Corporation (SERC) | Memphis Light, Gas and Water Division (MLGW) | NCR11066 | SERC2012011167 | EOP-005-1 | R2 | On September 28, 2012, MLGW submitted a Self-Report to SERC stating that, as a Transmission Operator (TOP), it had an issue with EOP-005-1 R2 because it failed to update its restoration plan at least annually for the year of 2012. MLGW reviewed its restoration plan during the 2010, 2011, and 2012 calendar years. During the restoration drill conducted on December 9, 2011, however, MLGW identified needed revisions to the restoration plan, including the addition of a new gate station which was expected to come online in May 2012. The summary of the restoration plan drill included a statement that the restoration plan should be reviewed and updated by May 2012 to include improvements and the new Collierville gate station. Because of delays, MLGW did not complete the new construction project until September 2012 and MLGW overlooked the established May 2012 date to revise the restoration plan. The December 9, 2011 restoration drill identified needed revisions to the restoration plan beyond the addition of the new gate station, including a change in the path used to re-energize the system from a gate to the interchange. Therefore, MLGW should have revised its restoration plan following the drill, regardless of the status of the delayed gate station. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Restoration of the MLGW transmission system is directed by Tennessee Valley Authority (TVA), MLGW’s Reliability Coordinator, Balancing Authority, and adjacent TOP. Restoration requires re-energizing 115 kV and 161 kV network lines and load-serving substations. If MLGW's restoration efforts could not follow the prescribed path, TVA would direct circuit and load restoration through another path. MLGW does not have any blackstart resources in its TOP area and its restoration plan does not require cranking paths to restore station services to any other generators in its TOP area. MLGW transmission facilities are not part of any other TOP-defined cranking paths, whether for restoration of the Interconnection or restoring normal operations. | To mitigate this issue, MLGW: 1) updated its system restoration plan; and 2) enhanced its compliance management software and processes to better remind personnel of intended action dates. SERC has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Service Corp. As Agent For Public Svc. Co. Of Oklahoma & SW Ele Pwr Co. (AEPW) | NCR01056 | SPP20121011325 | VAR-002-1.1b | R3; R3.1 | On October 29, 2012, AEP submitted a Self-Report to SPP RE stating that, as a Generator Operator, it had an issue with VAR-002-1.b R3.1, because it did not report to its Transmission Operator (TOP) within 30 minutes the status change and expected duration of an outage of a power system stabilizer (PSS). At 2:51 a.m. on June 26, 2012, AEP's Stall 6S generator returned to service following a trip caused by loss of the unit’s voltage regulator system. When the Stall generator returned to service the generator operators received a “PSS Control Enabled” alarm. In the investigation that immediately followed, it was determined that the alarm was activated when the PSS was disabled and the label for the alarm was not consistent with the PSS status. The PSS did not enable when the voltage regulator system was placed into service because of a diagnostic fault code indicating a mismatch between the primary and secondary control. Resetting the PSS cleared the fault and enabled the PSS. As a consequence of the faulty alarm, the generator operators were unaware that the PSS was disabled during the investigation, and thus did not notify the TOP of the PSS status change. The diagnostic fault code was reset and the PSS was returned to service at 10:15 a.m. on June 26, 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was limited to the Stall S6 PSS, which was back in service within seven hours and twenty four minutes. Further, although the PSS was removed from service, the generator voltage was monitored and controlled by the generator operators, consistent with the required voltage schedule for the duration of PSS outage. Moreover, the issue did not cause any operating events or loss of load. | To mitigate the issue, AEP: 1) set the proper alarm code of the PSS; and 2) returned the PSS to service. SPP RE has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | Borger Energy Associates, LP (Borger) | NCR01062 | SPP2013012371 | PRC-005-1 | R2 | On May 16, 2013, Borger, as a Generator Owner (GO), self-reported an issue with PRC-005-1 R2 because it had not tested or maintained all of its Protection System devices within the defined intervals set out in its Protection System maintenance and testing program (PSMTP). Specifically, Borger did not test 2 out of 70 instrument transformers during a 2010 testing of its substation Protection System devices. Borger has a total of 100 Protection System devices; therefore, Borger did not test 2% of its total Protection System devices. Borger completed testing of one instrument transformer in April 2011, and of the other in April 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The relays in which the two instrument transformers supply input are alarmed and monitored continuously by Borger operators. Failure of the instrument transformers would have resulted in a control room alarm. No alarms were recorded for these two instrument transformers for the duration of the issue, and the devices passed the maintenance and testing performed on them without any issues. Finally, Borger’s size, a total plant capacity of 230 MW, further reduces risk to the BPS. A Settlement Agreement covering violations of PRC-005-1 R1 and PRC-005-1 R2 (SPP200900102 and SPP200900103) for Borger was filed with FERC under NP11-99-000 on January 31, 2011. On March 2, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE determined that this issue is appropriate for FFT treatment because Borger has demonstrated improvements since its prior violations in 2009. The 2009 PRC-005-1 violations were discovered during a Compliance Audit. The violations were for not having a Protection System maintenance and testing program and for not testing any of its PRC-005-1 devices. Since that time, Borger mitigated the PRC-005-1 R1 violation, and tested almost all of its PRC-005-1 devices, and only failed to include the two at issue because of confusion in its instrument transformer inventory. Furthermore, the fact that Borger self-reported speaks to Borger’s improvements in compliance. | To mitigate this issue, Borger: 1) performed testing and maintenance on the two instrument transformers that had not been tested in 2010; and 2) revised its Protection System inventory to include the two instrument transformers to prevent any future testing and maintenance confusion. SPP RE has verified the completion of all mitigation activity.
Southwest Power Pool Regional Entity (SPP RE) | Oklahoma Gas & Electric Company Co. (OGE) | NCR01130 | SPP201100546 | PRC-005-1 | R2; R2.1; R2.2 | On April 15, 2011, OGE, as a Generator Owner, self-reported an issue with PRC-005-1 R2 because it could not locate documentation that it had implemented its maintenance and testing program for all of its generation Protection System devices, namely: batteries, DC circuitry, and relays. OGE did not have documentation for annual station battery bank tests for 14 generating units, at 4 generating stations, from 2008 to 2010. OGE had documentation of 89% of the required monthly station battery bank inspections and 88% of the required quarterly station battery bank inspections at 3 of the 4 generating stations during that time period. There was no documentation of monthly station battery bank inspections for the fourth generating station; instead, OGE provided closed work orders from its Systems Applications and Products in Data Processing (SAP) system, which showed that 22% of the monthly battery bank inspections occurred in the time period from 2008 to 2010. Additionally, OGE had not tested DC circuitry or relays at its Horseshoe Lake Generating Station A-1 Unit during the same time frame. In all, no more than 20% of OGE’s Protection System devices were affected by this issue. Subsequently, during a Compliance Audit from April 18 through April, 21 2011, SPP RE discovered a number of relay tests that OGE had performed in which the test results were marked as “failed” in the “as left” portion of the test. OGE could not provide documentation to demonstrate that it took corrective action to address the “failed” relays. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) although OGE failed to keep documented records of annual testing for 14 generating units, OGE did have several documented monthly and quarterly inspections, along with documented SAP work orders, to evidence that OGE was performing some testing and maintenance on its station batteries. Additionally, OGE was continuously monitoring all of its batteries during the duration of the issue via its Energy Management System. 2) although OGE did not test DC circuitry or relays at its Horseshoe Lake Generating Station A-1 unit, the unit had a nameplate generating capacity of 2.5 MW. Furthermore, this unit was not directly connected to the BPS; instead, it was connected to, and capable of, supplying power to a gas turbine designated as a blackstart resource. 3) only 12 of 146 relay test results that SPP RE reviewed (8%) were left in a “failed” state. OGE was able to provide evidence explaining these 12 “failures.” OGE used the same series of tests for all of its relays and in doing so, it tested for functions that were not applicable to some relays. Because the non-applicable functions automatically appeared as a failed item, 12 relays showed a “failed” state after testing. The functions that these 12 relays were set to perform were retested and functioned properly. | To mitigate this issue, OGE: 1) revised its Instructions and Methods for maintenance and testing (I&M) to make its procedures clearer to affected personnel, including expressly referencing PRC-005 in the I&M and incorporating specific recordkeeping requirements and checklist forms for employees; 2) used its revised I&M to test the equipment associated with its generating stations. All testing is now up-to-date; 3) developed a process for identifying and documenting equipment left in an “as-left failed” status, including reasons why the equipment is left in a “failed” state, using pre-defined failure codes; and 4) trained supervisors on all new processes and procedures. SPP RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | American Electric Power Service Corp as agent for AEP Texas North Co, AEP Texas Central Co, and Public Service of Oklahoma (AEP) | NCR04006 | TRE2012011184 | VAR-002-1.1b | R1 | On August 31, 2012, AEP self-certified to Texas RE that as a Generator Operator, it had an issue with VAR-002-1.1b R1. Specifically, on February 16, 2012 at 3:30 p.m. Central Standard Time (CST), AEP switched the voltage control mode of the Automatic Voltage Regulator (AVR) at its Oklaunion generation plant from automatic to manual without notifying the Transmission Operator (TOP). AEP has an issue with VAR-002-1.1b R1 from February 16, 2012 when the AVR was switched to manual, to February 18, 2012 when the AVR was set to automatic and the TOP was notified. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the following factors: a) the TOP was aware that the AVR was being tuned and going in and out of service; b) the issue period was approximately 35 hours; c) voltage on the Oklaunion facility was being monitored by AEP; d) the unit maintained its established voltage limits during the issue period; e) during the issue period the Oklaunion facility was fully available and no trips occurred; f) the BPS was not under stress. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with VAR-002-1.1a R1 (SPP201000431) for AEP with the Southwest Power Pool Regional Entity region was filed with FERC under RC12-13-000 on June 29, 2012. The 60-day review period passed on August 28, 2012. A Settlement Agreement covering two violations of VAR-002-1.1b R1 and R3 (RFC2011001111 and RFC201100130) for AEP within the ReliabilityFirst Corporation region was filed with FERC under NP12-27-000 on May 30, 2012. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE determined that the instant issue is appropriate for FFT treatment because it is AEP’s first VAR-002 violation in the Texas RE region. Also, the instant issue involved the commissioning of a new facility. | To mitigate this issue, AEP: 1) placed the facility’s AVR in auto mode; and 2) notified the TOP. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | GIM Channelview Cogeneration LLC (GIM Channelview) | NCR00292 | TRE201100461 | PRC-004-1 | R3 | During a September 14, 2011 Compliance Audit, Texas RE determined that GIM Channelview, as a Generator Owner, had an issue with PRC-004-1 R3. GIM Channelview failed to report to the Regional Reliability Organization (RRO) misoperation when one of its units had a fuse failure and trip on May 22, 2010. Analysis indicated the misoperation to be an unintentional Protection System operation when no fault or other abnormal condition had occurred unrelated to on-site maintenance and testing activity. The failure was caused by a defective fuse on the C-phase potential transformer. The analysis and corrective action plans for this misoperation were not provided to the RRO, the Electric Reliability Council of Texas (ERCOT). The duration of the issue was from May 22, 2010, the date of the misoperation analysis, until September 25, 2011, the date GIM Channelview met the requirement language of the new Standard Version . | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because GIM Channelview did take corrective action at the time of the incident. GIM Channelview replaced the defective fuse on the C-phase potential transformer, and conducted a root cause analysis. The entity also immediately documented the analyses including root causes and corrective action plans of the incident. | To mitigate this issue GIM Channelview provided analysis and corrective action plan during the Compliance Audit. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | GIM Channelview Cogeneration LLC (GIM Channelview) | NCR00292 | TRE201100462 | PRC-005-1 | R2 | During a September 14, 2011 Compliance Audit, Texas RE determined that GIM Channelview, as a Generator Owner, had an issue with PRC-005-1 R2. Two relays were not tested within the program intervals. Testing was due on July 1, 2008 but the relays were not tested until February 22, 2010. GIM Channelview provided evidence that the Protection System devices were maintained and tested within the defined intervals and the date when each Protection System device was last tested and maintained. All requests for Protection System information were satisfied with the exception of two relays. For the two relays, test records were provided showing testing was last performed on February 22, 2010. GIM Channelview provided a 2008 tracking spreadsheet which shows these two relays were previously tested in April 2004. This testing interval (5 years and 10 months) exceeds the program interval of 4 years (with the provision that if maintenance interval exceeds 4 years, then maintenance must be performed during the next unit outage). GIM Channelview was not able to provide any records to demonstrate these two relays were tested within the program interval. GIM Channelview had a total of 172 devices, the two untested relays equaled 1.16% of that amount. The duration of the issue was from July 1, 2008, when the testing was due, until February 22, 2010, the date the last relay was tested. | The violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system and had a minimal risk. The two relays were tested outside of the defined testing interval by about 20 months. GIM Channelview had records from 2004 showing testing was completed. However, GIM Channelview was not registered until July 1, 2008. When the relays were tested in 2010, the test results were satisfactory. The two relays represented 1.16% of the total devices in the program. | To mitigate this issue GIM Channelview tested the two relays. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Papalote Creek II, LLC (Papalote) | NCR11033 | TRE2012009902 | VAR-002-1.1b | R3 | On January 26, 2012, Papalote submitted a Self-Report to Texas RE stating that, as a Generator Owner and Generator Operator (GOP), it had an issue with VAR-002-1.1b R3. Texas RE has reviewed the evidence submitted and has determined that between May 18, 2010 to November 1, 2010, Papalote experienced 12 instances where a change in Automatic Voltage Regulator (AVR) status was not communicated to its Transmission Operator (TOP), the Electric Reliability Council of Texas (ERCOT). The failure to notify the TOP was due to technical communication issues between a third party contractor, which was performing some GOP functions for Papalote, including communicating the AVR status, and ERCOT. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because at no time during the issue period did Papalote experience any voltage issues with its systems. Furthermore, Papalote operators were continuously monitoring voltage levels and were supported by alarms, which trigger when deviations from voltage profile limits occur. Finally, the unit was still able to provide the voltage support needed during the pendancy of the issue. | To mitigate this issue: 1) as of December 1, 2011, EON Climate and Renewables (EC&R) (Papalote Creek II’s parent company) has taken over all GOP functions and no longer depends on a third party contractor for communications with ERCOT. Texas RE has verified that EC&R has been communicating statuses of its facilities to ERCOT, and EC&R has verified that it has not experienced any other instances where it failed to communicate its status; and 2) EC&R has updated its procedures to reflect its responsibility for communicating any changes in reactive capability to the TOP. EC&R has also reviewed these procedures with its operators to ensure that they are aware of their role in these procedures. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (AE) | NCR04030 | TRE201100476 | PRC-005-1 | R1; R1.1; R1.2 | On September 30, 2011, AE submitted a Self-Report, as a Generator Owner, citing an issue with PRC-005-1 R1.1 and R1.2. AE failed to clearly define maintenance and testing intervals and their basis for all of the components. Specifically, AE did not include voltage or current sensing devices, DC control circuitry, and battery testing in its maintenance and testing program. AE failed to include 94 out of 333 devices (28%) in its maintenance and testing program. The duration of the issue was from June 28, 2007, when the Standard become mandatory and enforceable, through December 20, 2011, when the issue was mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because AE stated in its Self-Report and a response to Texas RE questions that testing was completed but AE did not document the evidence of this testing. AE provided an attestation stating that the facilities involved are staffed 24 hours a day and if any issues had occurred, plant staff would have been able to immediately address any operational issues. No generating unit outage, equipment failure, or confirmation of any current and voltage sensing misoperation occurred during the period of the issue. A Settlement Agreement covering three violations for AE of Reliability Standards PRC-005-1 R1, PRC-005-1 R2, and PRC-008-0 R2 was filed with FERC under NP12-18-000 on February 29, 2012. On March 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The prior violations were similar to this instance of noncompliance but pertained AE's Distribution Provider and Transmission Owner functions (NERC Registration ID: NCR04029) for the period from June 28, 2007 through July 27, 2010. Texas RE determined that the instant issue is appropriate for FFT treatment because it occurred around the same time as the violations for NCR04029, and thus should not be considered a repeat instance of noncompliance. | To mitigate this issue, AE: 1) reviewed all aspects of its Protection System maintenance program for its generation assets to ensure that all requirements of PRC-005 are covered; and 2) created a new full-time position in December 2010 that resides within the Power Supply and Market Operations (PSMO) business unit. The PSMO quality and compliance manager focuses on the compliance activities of the PSMO and serves as a primary liaison to the reliability compliance office (RCO) and works closely with the RCO to monitor the Reliability Requirements applicable to AE's generation-related business units. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (AE) | NCR04030 | TRE201100477 | PRC-005-1 | R2; R2.1; R2.2 | On September 30, 2011, AE, as a Generator Owner, submitted a Self-Report citing an issue with PRC-005-1 R2.1 and R2.2. AE failed to provide evidence that all of its Protection System devices were maintained and tested within the defined intervals, which presented an issue with R2.1. In addition, AE did not include the date these systems were last tested and maintained, as required in R2.2. Texas RE determined that AE did not maintain and test 26% of its protective relays, 24% of its voltage and current sensing devices, and 66% of its DC control circuitry. This issue was from June 28, 2007, the date the Standard become mandatory and enforceable, through September 12, 2012, when was the issue mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because AE states that testing was completed but did not document the evidence of this testing. AE provided an attestation stating that the facilities involved are staffed 24 hours a day and if any issues had occurred, plant staff would have been able to immediately address any operational issues. In addition, AE does not have any associate communication systems, the omission of the device type was not significant. Additionally, no generating unit outage, equipment failure, or confirmation of any current and voltage sensing misoperation occurred during the period of the issue. A Settlement Agreement covering violations pertaining to Reliability Standards PRC-005-1 R1, PRC-005-1 R2, and PRC-008-0 R2 was filed with FERC under NP12-18-000 on February 29, 2012. On March 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The prior violations were similar to this instance but pertained to the Distribution Provider and Transmission Owner functions (NERC Registration ID NCR04029) for the period from June 28, 2007 through July 27, 2010. Texas RE determined that the instant issue is appropriate for FFT treatment because it occurred around the same time as the violations for NCR04029, and thus should not be considered a repeat instance of noncompliance. | To mitigate this issue, AE performed maintenance and testing of all relevant equipment and performed quality assurance and quality check of relevant data. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Equistar Chemical, LP (Equistar) | NCR04055 | TRE2012010270 | PRC-005-1 | R1 | During a Compliance Audit conducted from May 15, 2012 through March 17, 2012, Texas RE discovered that Equistar, as a Generator Owner, had an issue with PRC-005-1 R1. Equistar did not have maintenance and testing intervals and their basis for DC circuits and communications. Equistar also failed to provide a basis for adjusting the intervals for its relay maintenance and testing when it updated the document that described the maintenance and testing program intervals in 2011 from the previous version in 2006. Equistar had an issue with PRC-005-1 R1 from June 28, 2007, the date the Standard became mandatory and enforceable, through August 10, 2012, the date Equistar developed intervals and basis for testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The following factors mitigate the risk: 1) the nameplate rating of the plant is 45 MW but the chemical plant uses half of that capacity; normally, the cogen plant exports less than 10 MW to the Electric Reliability Council of Texas's market; 2) the only time Equistar exported more than 20 MW was during the unusually cold weather period in February 2011; 3) Equistar’s policy is to perform maintenance on all the cogen devices during the chemical plant outages every two years and that is a short time frame for testing of plant equipment compared to industry standards; 4) Equistar has one communications circuit to a Transmission Owner (TO) substation it ties to 0.9 miles from the plant; and 5) If an issue did occur in Equistar’s plant due to missed Protection System device maintenance and testing, the TO substation that Equistar ties with would have isolated it from the Bulk Electric System. | To mitigate this issue, Equistar: 1) created a site-specific basis document to define the intervals for testing and maintenance of the Protective System devices; 2) modified its maintenance procedures to reference a new maintenance guideline reliability procedure associated with this Standard; 3) created a new site-specific interval testing and basis document to include DC Circuit and communication system testing. Then modified maintenance procedures to reference new maintenance guideline in PRC-005 R1.
Texas Reliability Entity (Texas RE) | Equistar Chemical, LP (Equistar) | NCR04055 | TRE2012010271 | PRC-005-1 | R2 | During a Compliance Audit conducted from May 15, 2012 through March 17, 2012, Texas RE discovered that Equistar, as a Generator Owner, had an issue with PRC-005-1 R2. Equistar missed at least one maintenance and/or test for all of its Protection System devices except for Potential Transformers (PT) and Current Transformers (CTs), giving it a missing percentage of 70% from the total Protection Devices. The testing intervals for the following devices were as follows: the interval was 2 years for electromechanical relays. Equistar did not present maintenance and test results for testing required for 17 of the 18 (94.5%) electromechanical relays in 2007. Previous maintenance was in 2005 but results were next available in 2009. One of the 18 electromechanical relays (87L) had test results for 1996 and 2010. Test results DC circuits and communications systems were presented only for 2011. The test intervals for batteries were monthly and quarterly. There were four battery systems with missing monthly and quarterly results per the table below: -For 2011 - Missing 1 Monthly; 0 Quarterly -For 2010 - Missing 6 Monthly; 0 Quarterly -For 2009 - Missing 1 Monthly; 5 Quarterly -For 2008 - Missing 3 Monthly; 8 Quarterly -For 2007 (3rd and 4th Quarters) - Missing 2 Monthly; 8 Quarterly The duration of the issue was from June 28, 2007, when the Standard become mandatory and enforceable through April 7, 2011, when the last of the systems, the DC circuits and communication system, was maintained and tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The following factors mitigate the risk: 1) the nameplate rating of the plant is 45 MW but the chemical plant uses half of that capacity; normally, the cogen plant exports less than 10 MW to the Electric Reliability Council of Texas's market; 2) the only time Equistar exported more than 20 MW was during the unusually cold weather period in February 2011; 3) Equistar’s policy is to perform maintenance on all the cogen devices during the chemical plant outages every two years and that is a short time frame for testing of plant equipment compared to industry standards; 4) Equistar has one communications circuit to a Transmission Owner (TO) substation it ties to 0.9 miles from the plant; and 5) if an issue did occur in Equistar’s plant due to missed Protection System device maintenance and testing, the TO substation that Equistar ties with would have isolated it from the Bulk Electric System. | To mitigate this issue, Equistar: 1) created a site-specific basis document to define the intervals for testing and maintenance of the Protective System devices; 2) modified its maintenance procedures to reference a new maintenance guideline reliability procedure associated with this Standard; and 3) corrected the monthly battery Preventative Maintenance (PM) notice in its tracking system and emphasized to the involved personnel the need for the PM to be finished in that month as well as making sure that the records are moved to the proper electronic folder. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | CER - Colorado Bend Energy Partners LP (CBEC) | NCR110067 | TRE201100528 | PRC-005-1 | R1; R1.1; R1.2 | During a Spot-Check conducted from October 10, 2011 through October 14, 2011, Texas RE determined that CBEC, as a Generator Owner (GO), had an issue with PRC-005-1 R1.1 and R1.2. The documented generation Protection System maintenance and testing program that was in effect at the beginning of the enforceable period did not include maintenance and testing intervals and their basis or a summary of maintenance and testing procedures. Beginning on November 18, 2010, the next and subsequent versions of generation Protection System maintenance and testing programs included maintenance and testing intervals that either did not have a documented basis or were not consistent with the documented basis. The issues involved with the second and subsequent versions are limited to defective or missing bases. CBEC had an issue with PRC-005-1 R1.1 and R1.2 from August 17, 2010, the date of its registration as a GO, through May 10, 2013, the date the formal Mitigation Plan was completed. | Texas RE determined the issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The initial maintenance and testing program lacked material specificity for a brief period of three months. The scope of the issue three months after registration was limited to defective basis, specifically support for the chosen maintenance and test intervals. Additionally, all generation Protection System maintenance and test intervals in the subsequent, substantive program issued November 18, 2010, or thereafter were more conservative or equal to the intervals recommended in the NERC Technical Reference “Maximum Verification Interval” maintenance and test intervals document. | To mitigate this issue, CBEC: 1) updated its Maintenance and Testing procedure to include maintenance and testing intervals and their basis. The procedure was revised to align with engineering practices derived from specific sections of the PJM Interconnection's relevant documents; and 2) implemented the procedure by integrating it into the fleet’s NERC compliance program. All relevant personnel were required to review the procedure and implement all applicable changes by the compliance date. The integrated procedures were implemented in early 2013. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | CER - Colorado Bend Energy Partners LP (CBEC) | NCR110067 | TRE201100529 | PRC-005-1 | R2; R2.1; R2.2 | During a Spot-Check conducted from October 10, 2011 through October 14, 2011, Texas RE determined that CBEC, as a Generator Owner (GO), had an issue with Reliability Standard PRC-005-1 R2.1 and R2.2. Specifically, CBEC was either missing certain maintenance and test records or reflected exceeded required intervals. The issues involved 22 out of 54 devices or 40.74% of the total, involving relays and current transformers. CBEC had an issue with PRC-005-1 R2.1 and R2.2 from August 17, 2010, the date of its registration as a GO, through March 20, 2012, the date CBEC completed required maintenance and testing. | Texas RE determined the issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system for the following reasons: 1) although certain test records were missing, the plant was commissioned in 2007 and it was very likely that the subject equipment was in fact maintained and tested during the commissioning process; 2) although relays were not maintained and tested in a timely manner, the final intervals were considerably more conservative than the intervals recommended by the NERC Relay Maintenance Technical Reference; 3) the relays and current transformers were continuously monitored and CBEC would have learned of an equipment issue promptly, had one occurred; and 4) backup relaying was in place had primary systems failed. | To mitigate the issue, CBEC completed all maintenance and testing on undocumented and untimely tested Protection System elements. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | CER - Quail Run Energy Partners LP (QREC) | NCR110068 | TRE201100535 | PRC-005-1 | R1; R1.1; R1.2 | During a Spot-Check conducted from October 10, 2011 through October 14, 2011, Texas RE determined that QREC, as a Generator Owner (GO), had an issue with PRC-005-1 R1.1 and R1.2. The documented generation Protection System maintenance and testing program that was in effect at the beginning of the enforceable period did not include maintenance and testing intervals and their basis or a summary of maintenance and testing procedures. Beginning on November 18, 2010, the next and subsequent versions of generation Protection System maintenance and testing programs included maintenance and testing intervals that either did not have a documented basis or were not consistent with the documented basis. The issues involved with the second and subsequent versions are limited to defective or missing bases. QREC had an issue with PRC-005-1 R1.1 and R1.2 from August 17, 2010, the date of its registration as a GO, through May 10, 2013, the date the formal Mitigation Plan was completed. | Texas RE determined the issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The initial program lacked material specificity for a period of three months. The scope of the issue three months after registration was limited to defective basis, specifically support for the chosen maintenance and test intervals. Additionally, all generation Protection System maintenance and test intervals in the subsequent, substantive program issued November 18, 2010, or thereafter were more conservative or equal to the intervals recommended in the NERC Technical Reference “Maximum Verification Interval” maintenance and test intervals document. | To mitigate this issue, QREC: 1) updated its Maintenance and Testing procedure to include maintenance and testing intervals and their basis. The procedure was revised to align with engineering practices derived from specific sections of the PJM Interconnection's relevant documents; and 2) implemented the procedure by integrating it into the fleet’s NERC compliance program. All relevant personnel were required to review the procedure and implement all applicable changes by the compliance date. The integrated procedures were implemented by early 2013. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | CER - Quail Run Energy Partners LP (QREC) | NCR110068 | TRE201100536 | PRC-005-1 | R2; R2.1; R2.2 | During a Spot-Check conducted from October 10, 2011 through October 14, 2011, Texas RE determined that QREC, as a Generator Owner (GO), had an issue with PRC-005-1 R2.1 and R2.2. Specifically, QREC was either missing certain maintenance and test records or reflected exceeded required intervals. The issues involved 9 out of 58 devices or 15.51% of the total, involving relays and current transformers. QREC had an issue with PRC-005-1 R2.1 from August 17, 2010, the date of registration as a GO, through March 20, 2012, the date QREC completed the required maintenance and testing. | Texas RE determined the issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system for the following reasons: 1) although certain test records were missing, the plant was commissioned in 2007 and it was very likely that the subject equipment was in fact maintained and tested during the commissioning process; 2) although relays were not maintained and tested in a timely manner, the final intervals were considerably more conservative than the intervals recommended by the NERC Relay Maintenance Technical Reference; 3) the relays and current transformers were continuously monitored and QREC would have learned of an equipment issue promptly, had one occurred; and 4) backup relaying was in place had primary systems failed. | To mitigate the issue, QREC completed all maintenance and testing on undocumented and untimely tested Protection System elements. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | EC&R Panther Creek Wind Farm III, LLC (Panther Creek III Wind Farm) | NCR10334 | TRE201100539 | VAR-002-1.1a | R3 | On November 2, 2011, Panther Creek III Wind Farm, as a Generator Operator (GOP), submitted a Self-Certification to Texas RE citing an issue with VAR-002-1.1a R3. Texas RE has reviewed the evidence submitted and has determined that from July 5, 2010 to November 10, 2010, Panther Creek III Wind Farm experienced six instances where it did not communicate a change in reactive capability to its Transmission Operator (TOP), the Electric Reliability Council of Texas (ERCOT). The failure to notify its TOP were due to a general failure of its operators to communicate the change in reactive capability status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Panther Creek III operators were continuously monitoring voltage levels, supported by alarms set to trigger on deviations away from voltage profile limits. At no time during the issue period did Panther Creek III experience any voltage issues with their systems. | To mitigate this issue: 1) as of December 1, 2011, EON Climate and Renewables (EC&R) (Panther Creek III Wind Farm’s parent company) has taken over all GOP functions and no longer depends on a third-party contractor for communications with ERCOT. Texas RE has verified EC&R has been communicating statuses of its facilities to ERCOT, and EC&R has verified that it has not experienced any other instances where it failed to communicate its status to ERCOT; and 2) EC&R has updated its procedures to reflect its responsibility for communicating any changes in reactive capability to the TOP. EC&R has also reviewed these procedures with its operators to ensure that they are aware of their role in these procedures. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | EC&R Panther Creek Wind Farm I & II, LLC (Panther Creek I & II Wind Farm) | NCR10249 | TRE201100541 | VAR-002-1.1a | R3 | On November 2, 2011, Panther Creek I & II Wind Farm, as a Generator Operator (GOP), submitted a Self-Certification to Texas RE citing an issue with VAR-002-1.1a R 3. Texas RE has reviewed the evidence submitted and has determined that on July 29, 2010 Panther Creek I & II Wind Farm experienced one instance where it did not communicate a change in reactive capability to its Transmission Operator (TOP), the Electric Reliability Council of Texas (ERCOT). The failure to notify its TOP was due to a general failure of its operators to communicate the change in reactive capability status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Panther Creek I & II operators were continuously monitoring voltage levels, supported by alarms set to trigger on deviations away from voltage profile limits. At no time during the issue period did Panther Creek I & II Wind Farm experience any voltage issues with their systems. | To mitigate this issue: 1) as of December 1, 2011, EON Climate and Renewables (EC&R) (Panther Creek 1 & 2 Wind Farm’s parent company) has taken over all GOP functions and no longer depends on a third-party contractor for communications with ERCOT. Texas RE has verified EC&R has been communicating statuses of its facilities to ERCOT, and EC&R has verified that it has not experienced any other instances where it failed to communicate its status to ERCOT; and 2) EC&R has updated its procedures to reflect its responsibility for communicating any changes in reactive capability to the TOP. EC&R has also reviewed these procedures with its operators to ensure that they are aware of their role in these procedures. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Papalote Creek I, LLC (Papalote Creek I Wind Farm) | NCR10335 | TRE201100537 | VAR-002-1.1a | R3 | On November 2, 2011, Papalote Creek I Wind Farm, as a Generator Operator (GOP), submitted a Self-Certification to Texas RE citing an issue with VAR-002-1.1a R3. Texas RE has reviewed the evidence submitted and has determined that from July 9, 2010 to October 6, 2010, Papalote Creek I Wind Farm experienced nine instances where it did not communicate a change in reactive capability its Transmission Operator (TOP), the Electric Reliability Council of Texas (ERCOT). The failures to notify the TOP were due to a general failure of its operators to communicate the change in reactive capability status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Papalote Creek I operators were continuously monitoring voltage levels, supported by alarms set to trigger on deviations away from voltage profile limits. At no time during the issue period did Papalote Creek I experience any voltage issues with their systems. | To mitigate this issue: 1) as of December 1, 2011, EON Climate and Renewables (EC&R) (Papalote Creek 1 Wind Farm’s parent company) has taken over all GOP functions and no longer depends on a third-party contractor for communications with ERCOT. Texas RE has verified EC&R has been communicating statuses of its facilities to ERCOT, and EC&R has verified that it has not experienced any other instances where it failed to communicate its status to ERCOT; and 2) EC&R has updated its procedures to reflect its responsibility for communicating any changes in reactive capability to the TOP. EC&R has also reviewed these procedures with its operators to ensure that they are aware of their role in these procedures. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Karnes Electric Cooperative, Inc. (KEC) | NCR10178 | TRE2012010751 | CIP-001-1 | R1 | During a July 24, 2012 through July 26, 2012 Compliance Audit of KEC as a Load Serving Entity, Texas RE discovered an issue with CIP-001-1 R1. KEC’s electric service emergency operations plan manual did not have procedures that related directly to sabotage events. The manual mentioned sabotage and terrorist acts but did not specifically have procedure for recognition of sabotage events as required. The issue was from February 22, 2010, KEC's registration date through, May 11, 2011, the date the sabotage awareness and reporting procedures and guidelines manual that KEC provided was found to have adequate procedures to make its operating personnel recognize and be aware of sabotage events. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because KEC had an emergency plan in place at the time of registration, which made mention of sabotage covered certain emergency events, such as major terrorist events and vandalism. KEC also had a list of appropriate people to contact if the emergencies occurred, as defined by the previous procedure. KEC also attested that operators received some training in 2008 of the emergency plan in place. KEC also has a peak demand at approximately 65 MW. | To mitigate this issue, KEC created its sabotage awareness and reporting procedures and guidelines manual. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Karnes Electric Cooperative, Inc. (KEC) | NCR10178 | TRE2012010766 | CIP-001-1 | R2 | During a July 24, 2012 through July 26, 2012 Compliance Audit of KEC as a Load Serving Entity, Texas RE discovered an issue with CIP-001-1 R2. From February 22, 2010 through May 11, 2011, KEC’s electric service emergency operations plan manual did not have procedures that related directly to communication of sabotage events. Texas RE found only vague guidelines for communicating emergencies. The sabotage awareness and reporting procedures and guidelines manual dated May 11, 2011 that KEC provided was found to have adequate communication procedures to communicate information to appropriate parties in the Interconnection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because KEC had an emergency plan in place at the time of registration, which made mention of sabotage covered certain emergency events, such as major terrorist events and vandalism. KEC also had a list of appropriate people to contact if the emergencies occurred, as defined by the previous procedure. KEC also attested that operators received some training in 2008 of the emergency plan in place. KEC also has a peak demand at approximately 65 MW. | To mitigate this issue, KEC created its sabotage awareness and reporting procedures and guidelines manual. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Karnes Electric Cooperative, Inc. (KEC) | NCR10178 | TRE2012010767 | CIP-001-1 | R3 | During a July 24, 2012 through July 26, 2012 Compliance Audit of KEC as a Load Serving Entity, Texas RE discovered an issue with Reliability Standard CIP-001-1 R3. From February 22, 2010 through May 11, 2011, KEC’s electric service emergency operations plan manual did not directly describe reporting of sabotage events. Additionally, KEC provided inadequate evidence to demonstrate it provided the guideline material to operating personnel. The sabotage awareness and reporting procedures and guidelines manual dated May 11, 2011 that KEC provided was found to have adequate guidelines for reporting disturbances, and was backed-up with training agenda and sign-in sheets of operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because KEC had an emergency plan in place at the time of registration, which made mention of sabotage covered certain emergency events, such as major terrorist events and vandalism. KEC also had a list of appropriate people to contact if the emergencies occurred, as defined by the previous procedure. KEC also attested that operators received some training in 2008 of the emergency plan in place. KEC also has a peak demand at approximately 65 MW. | To mitigate this issue, KEC created its sabotage awareness and reporting procedures and guidelines manual. Texas RE has verified the completion of all mitigation activity.
Texas Reliability Entity (Texas RE) | Karnes Electric Cooperative, Inc. (KEC) | NCR10178 | TRE2012010768 | CIP-001-1 | R4 | During a July 24, 2012 through July 26, 2012 Compliance Audit of KEC as a Load Serving Entity, Texas RE discovered an issue with CIP-001-1 R4. From February 22, 2010 through May 11, 2011, KEC’s electric service emergency operations plan manual did not have procedures for reporting information to local FBI. KEC did not show evidence that communications were established with local FBI prior to the implementation of KEC's CIP-001 Manual. The sabotage awareness and reporting procedures and guidelines manual dated May 11, 2011 that KEC provided was found to have adequate procedures to report information to local FBI, and an e-mail was provided that showed communication with local FBI officials. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because KEC had an emergency plan in place at the time of registration, which made mention of sabotage covered certain emergency events, such as major terrorist events and vandalism. KEC also had a list of appropriate people to contact if the emergencies occurred, as defined by the previous procedure. KEC also attested that operators received some training in 2008 of the emergency plan in place. KEC also has a peak demand at approximately 65 MW. | To mitigate this issue, KEC created its sabotage awareness and reporting procedures and guidelines manual. Texas RE has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Silicon Valley Power (SNCL) | NCR05392 | WECC2012011508 | CIP-001-1 | R2 | On December 13, 2012, SNCL submitted a Self-Report to WECC stating that, as a Generator Operator, Load Serving Entity, and Transmission Operator, it had an issue with CIP-001-1 R2. Specifically, SNCL had one outdated email address for one of its contacts. WECC determined that SNCL failed to update procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SNCL’s reporting procedures did not contain the correct email address for the WECC Reliability Coordinator (RC), SNCL’s electric control center still maintained current contact information for appropriate parties in the Interconnection as well as correct phone numbers for the WECC RC. A Settlement Agreement covering violations of CIP-001-1 R2 for SNCL was filed with FERC under NP11-130-000 on February 28, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that the instant issue is appropriate for FFT treatment because in this instance, although SNCL’s reporting procedures did not contain the correct email address for the RC, SNCL’s electric control center still maintained current contact information for appropriate parties in the Interconnection as well as correct phone numbers for the WECC RC. | To mitigate this issue, SNCL updated its sabotage reporting procedure with the correct information. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2013012062 | FAC-501-WECC-1 | R3 | On March 1, 2013, AVA submitted a Self-Certification to WECC stating that, as a Transmission Owner, it had an issue with FAC-501-WECC-1 R3. AVA reported that it had an established Transmission Maintenance and Inspection Plan (TMIP) that required it to perform biennial infrared inspection on its circuit breakers. AVA reported that it failed to conduct one of its biennial infrared inspections at its W-5482 Walla Walla circuit breaker located in the Grant County PUD’s Wanapum 230 kV switching station. AVA reported that its failure to conduct the biennial infrared inspection resulted in an issue with FAC-501-WECC-1 R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue included only 1 out of 88 (1.14%) circuit breakers included in AVA’s TMIP. Additionally, the circuit breakers are continuously monitored and have alarms attached if a triggering event occurs. | To mitigate this issue, AVA completed the required biennial infrared testing on its W-5482 circuit breaker.
Western Electricity Coordinating Council (WECC) | Simpson Tacoma Kraft Co., LLC (STK) | NCR10303 | WECC2013012191 | VAR-002-1.1b | R1 | On April 5, 2013, STK submitted a Self-Report to WECC stating that, as a Generator Operator and Generator Owner, it had an issue with VAR-002-1.1b R1. Specifically, STK reported that the STK Biomass Cogen unit was taken offline on March 19, 2013 at 12:10 p.m. to replace turbine generator communication cards on the turbine control system. Before taking the generator offline, STK disabled the automatic voltage regulator's (AVR's) power factor mode. On March 19, 2013 at 5:55 p.m., the generator work was completed and the unit came back online. When the unit was resynchronized to the system, the replacement cards caused the unit to synchronize in the power factor mode of operation instead of the required AVR control mode. The incorrect mode of operation was not discovered until 11:30 a.m. on March 20, 2013, at which time STK immediately changed the voltage control from power factor mode to AVR control mode and notified the Transmission Operator (TOP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. STK’s single biomass generator operated in the power factor mode for 17 hours and 35 minutes without STK notifying its TOP. This generator is a steam turbine unit with a name plate rating of 55 MW. Further, at the time the AVR was in power factor mode, STK had a power system stabilizer (PSS) in service that would automatically deliver additional voltage support if needed. As a result, the voltage schedule with the TOP was always maintained. A Settlement Agreement covering a violation of VAR-002-1.1a R1 for STK was filed with FERC under NP12-40-000 on July 31, 2012. On August 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that the instant issue is appropriate for FFT treatment. Previously, WECC determined STK operated its generation unit in the Power Factor mode for a period of two Years. This was a result of the engineering design for the unit did not allow or provide for the use of the AVR in the AVR control mode. WECC determined that this instance of noncompliance is different then the violation addressed herein, because the first instance was due to the capability of the generator controls whereas this issue is a result of human error. For these reasons, WECC considers STK’s compliance history as a factor in its designation of these remediated issues for FFT treatment. | To mitigate this issue, STK: 1) returned AVR to voltage control mode; 2) installed a software jumper around the internal bits to force the output signal to the AVR for power factor control mode to always be off; 3) updated the steam turbine startup process to include steps to confirm the AVR and PSS status after generator synchronization; and 4) performed operator awareness training - Immediate training to ensure all operators understand the AVR operational capabilities/requirements and display indications. WECC has verified the completion of all mitigation activity.
Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2013012223 | VAR-002-1.1b | R3 | On April 15, 2013, PGE submitted a Self-Report to WECC stating that, as a Generator Operator, it had an issue with VAR-002-1.1b R3. PGE reported that on two separate occasions certain power system stabilizers (PSS) were not enabled as its generators were brought online. PGE stated that the first instance occurred on March 19, 2013. PGE reported that on March 18, 2013, while undergoing an economic outage4, a technician was updating the Toolbox programming application of its Coyote Springs Unit 1 Gas Turbine (Unit 1) control system human machine interface (HMI). As part of the update, the technician rebooted Unit 1’s Mark V controllers of the turbine control system and the EX2100e controllers of the generator excitation system. After the controllers were rebooted, the PSS defaulted to the “OFF” or “Not Enabled” state. When the combustion turbine generator (CTG) restarted on March 19, 2013, the PSS was in the “OFF” or “Not Enabled” status on the exciter. PGE reported that its crews discovered the status of the PSS on March 25, 2013 at 1:15 a.m. and that the crews promptly changed the PSS to automatic mode and notified its Transmission Operator (TOP). PGE reported that the second incident occurred on April 3, 2013. PGE reported that a power supply board in its Coyote Springs Unit 2 combustion turbine generator (CTG) exciter was replaced. PGE reported that when it restarted the CTG at approximately 5:00 a.m., the PSS was in the “OFF” or “Not Enabled” state. PGE reported that its crews discovered the status of the PSS at approximately 6:05 a.m. and promptly corrected the status and informed its TOP of the status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PGE had several compensating measures which limited the risks associated with the issue. First, PGE has installed automatic voltage regulators (AVR) on both Unit 1 and Unit 2. The AVRs were fully functional in each occurrence and would have acted properly had any voltage fluctuations or disturbances occurred. Additionally, in each instance, PGE’s other three turbines had functioning PSSs and AVRs that would also have functioned in the event of any voltage fluctuations. A Settlement Agreement covering violations of VAR-002-1.1b R3 for PGE was filed with FERC under NP13-16-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. WECC determined that the instant issue is appropriate for FFT treatment because the current issue relates to PGE’s PSS devices. Each of the Units involved received some type of maintenance and upon restart the PSSs failed to operate as expected. | To mitigate this issue, PGE: 1) changed the PSS attached to Unit 1 from "Not Enabled" to "Enabled" informed its TOP of the status change; and 2) changed the PSS attached to Unit 2 from "Not Enabled to "Enabled" and informed its TOP of the status change.